## ImprovementCostSummary10082020
| Project Cost |  |  |  |  | XFMR MVA
| 345 | 138 | 69 | Total |  | 345 | 138 | 69 | Total
2019 | 205782932.6 | 947267813 | 580255909.5 | 1733306655.1 | 2019 | 2428 | 1320 | 0 | 3748 | For ROS and BOD Reports
2020 | 1063304770 | 1211892928.38 | 374487880 | 2649685578.38 | 2020 | 9980 | 440 | 0 | 10420 | ·All Projects (in engineering, routing, licensing and construction): |  |  |  | 7605492329.94
2021 | 1114350000 | 1321287102.56 | 463180482 | 2898817584.56 | 2021 | 4697 | 634 | 110 | 5441 | ·Transmission Projects Energized in 2020: |  |  |  | 1197262433
2022 | 234241000 | 1159571600 | 4000000 | 1397812600 | 2022 | 2060 | 725 | 0 | 2785
2023 | 179746000 | 339314000 | 308950000 | 828010000 | 2023 | 3000 | 40 | 0 | 3040
2024 | 342823000 | 359534000 | 69450000 | 771807000 | 2024 | 1950 | 60 | 0 | 2010
2025 | 5600000 | 126915000 | 0 | 132515000 | 2025 | 0 | 0 | 0 | 0
2026+ | 20000000 | 100107000 | 4000000 | 124107000 | 2026+ | 675 | 0 | 0 | 675
2020COM | 356771000 | 579251776 | 261239657 | 1197262433 | 2020COM | 5294 | 180 | 0 | 5474
2020PLAN | 706533770 | 632641152.38 | 113248223 | 1452423145.38 | 2020PLAN | 4686 | 260 | 0 | 4946
2019-2026+ | 3165847702.6 | 5565889443.94 | 1804324271.5 | 10536061418.04 | 2019-2026+ | 24790 | 3219 | 110 | 28119
2019-2020 | 1269087702.6 | 2159160741.38 | 954743789.5 | 4382992233.48 | 2019-2020 | 12408 | 1760 | 0 | 14168
2021-2026+ | 1896760000 | 3406728702.56 | 849580482 | 6153069184.56 | 2021-2026+ | 12382 | 1459 | 110 | 13951
| Circuit Miles New |  |  |  | Circuit Miles Rebuilt, Reconductored or Upgraded |  |  |  |  | Total
| 345 | 138 | 69 | Total |  | 345 | 138 | 69 | Total | 345 | 138 | 69 | Total
2019 | 22.7 | 125.445 | 0.04 | 148.185 | 2019 | 0 | 263.847 | 480.948 | 744.795 | 22.7 | 389.292 | 480.988 | 892.98
2020 | 485.072 | 188.267 | 33.11 | 706.449 | 2020 | 116.79 | 382.11 | 284.943 | 783.843 | 601.862 | 570.377 | 318.053 | 1490.292
2021 | 170.8 | 88.27 | 3 | 262.07 | 2021 | 34.6 | 536.42 | 302.401 | 873.421 | 205.4 | 624.69 | 305.401 | 1135.491
2022 | 40.4 | 65.39 | 0 | 105.79 | 2022 | 27 | 299.68 | 0 | 326.68 | 67.4 | 365.07 | 0 | 432.47
2023 | 8.1 | 66.241 | 0 | 74.341 | 2023 | 26.9 | 124.491 | 194.95 | 346.341 | 35 | 190.732 | 194.95 | 420.682
2024 | 81 | 42 | 0 | 123 | 2024 | 200.06 | 164.478 | 40.43 | 404.968 | 281.06 | 206.478 | 40.43 | 527.968
2025 | 0 | 0 | 0 | 0 | 2025 | 11.2 | 4.05 | 0 | 15.25 | 11.2 | 4.05 | 0 | 15.25
2026+ | 0 | 15.9 | 0 | 15.9 | 2026+ | 0 | 40.3 | 2 | 42.3 | 0 | 56.2 | 2 | 58.2
2020COM | 35.422 | 99.277 | 33.11 | 167.809 | 2020COM | 46.99 | 163.94 | 187.193 | 398.123 | 82.412 | 263.217 | 220.303 | 565.932
2020PLAN | 449.65 | 88.99 | 0 | 538.64 | 2020PLAN | 69.8 | 218.17 | 97.75 | 385.72 | 519.45 | 307.16 | 97.75 | 924.36
2019-2026+ | 808.072 | 591.513 | 36.15 | 1435.735 | 2019-2026+ | 416.55 | 1815.376 | 1305.672 | 3537.598 | 1224.622 | 2406.889 | 1341.822 | 4973.333
2019-2020 | 507.772 | 313.712 | 33.15 | 854.634 | 2019-2020 | 116.79 | 645.957 | 765.891 | 1528.638
2021-2026+ | 300.3 | 277.801 | 3 | 581.101 | 2021-2026+ | 299.76 | 1169.419 | 539.781 | 2008.96

## FutureTPIT100120NoCost
OCTOBER BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 10/1/2020
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar ) (-Reactor, +Capacitor ) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number
6718 | Pinnacle Substation Addition | Construct a new substation named Pinnacle off the Culberson to Kunitz transmission line to support a generation interconnection request (19INR0088). Upgrade 8.8 miles of Culberson - Kunitz 138-kV trasnmission line to a minimum 480 MVA rating (Merrimack conductor). |  | Culberson | Kunitz | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2020-10-14 |  | 138 | 0 | 0 | 0 |  | Culberson | Culberson | Tier 4 |  |  |  | 7389, 7387, 71097 | Y | N |  |  | 14501 | 6718
5834 | Salt Creek to Cogdell | RPG Project for Salt Creek (Bus# 743) to Clairmont (Bus# 752) to ONCOR's Cogdell (Bus# 1402) |  |  |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 14032 | 2020-10-15 |  | 138 | 20 | 0 | 0 |  | Kent | Scurry | Tier 2 | 2015-12-21 | 2016-06-27 |  | 731, 752, 720, 729, 743, 6198 | Y |  |  |  | 13576 | 5834
6976 | Riverside Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Riverside Substation. |  | Riverside |  | Planned | 1018925 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018925 | 2020-10-16 |  | 138 | 0 | 0 | 0 |  | Fayette |  | Tier 4 |  |  |  | 7275 | Y | N |  |  | 14793 | 6976
50444 | Adds load to new Escobares Station | LCRA is building the high side and STEC is building the low side of the Escobares station |  | Escobares |  | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-10-16 |  | 138 | 0 | 0 | 0 |  | Starr |  | Tier 4 |  |  |  | 7870 | Y | N |  | 0 | 50445 | 50444
51960 | LCRATSC T137 Warda Giddings TL ADD | Tear down and rebuild the de-energized 69-kV transmission line between Giddings and Warda substations (T137) with 138-kV class structures capable of supporting bundled Drake conductor and OPGW fiber. |  | Giddings | Warda | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2020-10-16 |  | 138 | 0 | 0 | 0 |  | Lee | Fayette | Tier 4 |  |  |  | 7302, 7312 | Y | N |  | 0 | 51961 | 51960
51958 | LCRATSC Lincoln Sub UPG Cap Relocate | Construct a new approximately 0.35 mile 138-kV transmission line from Lincoln Substation to a new point of interconnection at the Enterprise Energy Substation. |  | Lincoln | Enterprise Energy Substation | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2020-10-30 |  | 138 | 0 | 0 | 0 |  | Burleson | Washington | Tier 4 |  |  |  | 7302, 7568 | Y | N |  | 0 | 51959 | 51958
50820A | Deepwater 345/138 kV 800 MVA A1 and loop ckt 70 | Install Deepwater 345/138kV 800MVA Autotransformer A1 | Accelerated project schedule | Deepwater |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-10-30 |  | 345 | 0 | 0 | 800 |  | Harris |  | Tier 4 |  |  |  | 40460, 49054, 40450 | Y | N |  | 0 | 53435 | 50820
50820B | Deepwater 345/138 kV 800 MVA A1 and loop ckt 70 | Re-energize the Deepwater 138kV substation. Loop existing Ckt.70 LYDELL to CHANEL into DPW138 to create new Ckt.70 LYDELL to DPW to CHANEL. | Accelerated project schedule | Deepwater | LYDELL/CHANEL | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-10-30 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 40275, 40460, 41000, 41009 | Y | N |  | Cost included in Phase A | 53436 | 50820
49564 | Mantle: Construct New 345 kV Station | Mantle: Construct New 345 kV Station |  | Bonilla | North Edinburg | Planned | 1035 - 1213 | AEP TCC | Joe Yeagler bcogan@aep.com 918-599-2857 | 3774 | 2020-10-30 20:00 |  | 345 | 0 | 0 | 0 |  | Cameron | Hidalgo | Tier 4 |  |  |  | 8059, 80598, 8383, 8573 | Y | N |  | 0 | 49565 | 49564
49566 | Revilla: Construct New 138 kV Station | Revilla: Construct New 138 kV Station |  | Falcon SS | Lopeno | Planned | 1034 - 1212 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3773 | 2020-10-30 20:00 |  | 138 | 0 | 0 | 0 |  | Starr | Zapata | Tier 4 |  |  |  | 8004, 80084, 8957, 80106 | Y | Y |  | 0 | 49567 | 49566
5964 | Belknap: Build new 69 kV station | Construct new 69 kV ring bus on the Albany to Rainey Creek 69 kV line, remove existing Spillway SW, reterminate Albany to Rainey Creek and Ft Phantom Pump to Onyx lines into Belknap | Updated Schedule & Cost | Belknap |  | Planned | 843 - 1027 | AEP TNC | Jeremy Brazeal mlforcum@aep.com 918-599-2674 | 2684 | 2020-10-31 |  | 69 | 0 | 0 | 0 |  | Jones |  | Tier 4 |  |  |  | 6211, 60409, 6178, 6219, 6220, 6243 | Y | N |  |  | 13679 | 5964
6083 | Wolfgang: Build 69 kV station | Construct new 69 kV ring bus at Wolfgang |  | Wolfgang |  | Planned | 842 - 1026 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2682 | 2020-10-31 |  | 69 | 0 | 0 | 0 |  | Kent |  | Tier 4 |  |  |  | 6162 | Y | N |  |  | 13807 | 6083
7027 | Barrilla Junction to Ft. Stockton SW: Rebuild 69 kV line | Rebuild Barrilla Junction to Ft. Stockton SW to Rio Pecos 69 kV line, convert to 138 kV, reterminate into Solstice, install 138 kV capacitor bank at Solstice, and build new Ft. Stockton Switch 138 kV station |  | Solstice | Fort Stockton Switch | Planned | 908 - 1086 | AEP TNC | Darren O'Hare mlforcum@aep.com 918-599-2674 | 2732 | 2020-10-31 |  | 138 | 0 | 16.3 | 0 |  | Pecos | Pecos | Tier 3 | 2017-12-22 | 2018-02-02 |  | 6645, 60717, 60385, 6653, 38350, 38470 | Y | N |  |  | 14849 | 7027
44359 | Solstice: Install 138 kV PST and capacitor bank | Install PST on the Fort Stockton Plant to Solstice 138 kV line at Solstice, install capacitor bank on the Solstice 138 kV bus |  | Solstice |  | Planned | 984 - 1162 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2734 | 2020-10-31 |  | 138 | 0 | 0 | 0 | 0,14.4 | Pecos |  | Tier 3 | 2017-12-22 | 2018-02-02 |  | 60384, 6645, 60717, 6630, 60385 | Y | N |  | 0 | 44360 | 44359
44361 | Ft. Stockton SW: Build 138 kV station | Rebuild Barrilla Junction to Ft. Stockton SW to Rio Pecos 69 kV line, convert to 138 kV, reterminate into Solstice, install 138 kV capacitor bank at Solstice, and build new Ft. Stockton Switch 138 kV station |  | Fort Stockton Switch |  | Planned | 908 - 1086 | AEP TNC | Darren O'Hare mlforcum@aep.com 918-599-2674 | 2735 | 2020-10-31 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 3 | 2017-12-22 | 2018-02-02 |  | 60717 | Y | N |  | 0 | 44362 | 44361
45503 | Lynx: Expand 138 kV station | Terminate the TNMP 16th Street to Rio Pecos 138 kV line into Lynx station |  | Lynx |  | Planned | 983 - 1161 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2770 | 2020-10-31 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 38330, 6601, 38310, 60400, 130533 | Y | N |  | 0 | 49830 | 45503
48407 | Chaparrosa: Construct New 69 kV Box Bay | Chaparrosa: Construct New 69 kV Box Bay |  | Chaparrosa |  | Planned | 929 - 1107 | AEP | James Nivens bcogan@aep.com 918-599-2857 | 3705 | 2020-10-31 |  | 69 | 0 | 0 | 0 |  | Zavala |  | Tier 4 |  |  |  | 8284, 88284, 8243, 8672, 7867 | Y | N |  | 0 | 48408 | 48407
49540 | Avogadro: Build new 345 kV station | Interconnect Griffin Trail wind farm on the Clear Crossing to Edith Clarke 345 kV line |  | Avogadro |  | Planned | 1017 - 1195 | ETT | Michael Forcum mlforcum@aep.com 918-599-2674 | 2778 | 2020-10-31 |  | 345 | 0 | 0 | 0 |  | Knox |  | Tier 4 |  |  |  | 60506, 60500, 60700 | Y | N |  | 0 | 49541 | 49540
57352 | Max Zuehlke to Gay Hill T-line structure change | Replace existing structure with upgraded structures on Max Zuehlke to Gay Hill transmission line |  | Max Zuehlke | Gay Hill | Under Construction |  | BBEC | Curtis Fischer curtis.fischer@bluebonnet.coop curtis.fischer@bluebonnet (979) 716-0253 |  | 2020-10-31 |  | 138 | 0 | 9.07 | 0 |  | Washington | Washington | Tier 4 |  |  |  |  | Y |  |  | 0 | 57353 | 57352
52565A | PRERGY (PRO) - Generator at HO Clarke Substation (20INR0206) | Expand existing HO Clarke substation [47170] to five-breaker ring bus. Connect expanded HO Clarke bus to new customer-owned PRERGY (PRO) substation. |  | HO Clarke |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-10-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 47170, 111797 | Y | N |  | 0 | 55975 | 52565
52565B | PRERGY (PRO) - Generator at HO Clarke Substation (20INR0206) | Reposition existing Ckt.05A HOC to WAP at HOC bus 47170 |  | HO Clarke | WA Parish | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-10-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | Y | N |  | Cost included in Ckt.26A relocation | 55976 | 52565
52565C | PRERGY (PRO) - Generator at HO Clarke Substation (20INR0206) | Reposition existing Ckt.26A HOC to Karsten from HOC bus 47175 to 47170 |  | HO Clarke | Karsten | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-10-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 42041, 47170, 47175 | Y | N |  | 0 | 55977 | 52565
52565D | PRERGY (PRO) - Generator at HO Clarke Substation (20INR0206) | Upgrade Ckt.90A HO Clarke to Kirby to Garrott to increase thermal limits |  | Kirby | HO Clarke/Garrott | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-10-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 47151, 47155, 47322, 47175, 47660 | Y | N |  | 0 | 55978 | 52565
45023 | Pershing: Build 138 kV station | Construct new 138 kV box bay on the Abilene Northwest to Oak Creek 138 kV line | Update Schedule | Pershing |  | Planned | 979 - 1157 | AEP TNC | Michael Glueck mlforcum@aep.com 918-599-2674 | 2764 | 2020-10-31 01:00 |  | 138 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  | 60724, 6229, 6335 | Y | N |  | 0 | 45024 | 45023
48335 | RGEC Ft. Stockton US 285 138-kV Substation Addition | Provide transmission service to new 25/30/35 MVA 138/24.9-kV substation to replace (transfer load from) Ft. Stockton 69-kV Substation. This is tied to AEP Project ID # 44361 |  | Fort Stockton | Fort Stockton | Planned |  | RGEC/LCRATSC | Larry T. Powell lpowell@rgec.coop 830-563-6178 |  | 2020-10-31 02:00 |  | 138 | 0 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 78926, 6645, 60717 | Y |  |  | 0 | 48340 | 48335
4501 | Trading Post Circuit Breaker Addition | Install Line Breakers at Trading Post on the Trading Post to Marshall Ford and the Trading Post to Cedar Valley 138kV lines (T315). |  | Trading Post |  | Under Construction |  | PEC | Ryan Morlino ryan.morlino@peci.com 830-868-5166 |  | 2020-11-01 |  | 138 | 0 | 0 | 0 |  | Travis |  | Tier 4 |  |  |  | 7505 | Y | N |  |  | 12073 | 4501
50342 | Rebuild Shropshire to Saltdome | Rebuilds 4/0 ACSR to 795 ACSR on double circuit 138 kV capable poles. NERC assessment |  | Saltdome | Shropshire | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-11-01 |  | 69 | 0 | 5.4 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 5551, 5555 | Y | N |  | 0 | 50343 | 50342
45340 | Lemay: Build 138 kV Box Bay | Lemay: Build 138 kV Box Bay on North Laredo SS - Reveille Line | Update Schedule | Lemay |  | Planned | 988 - 1166 | AEP TCC | William Lovelace bcogan@aep.com 918-599-2857 | 3739 | 2020-11-04 |  | 138 | 0 | 0 | 0 |  | La Salle |  | Tier 4 |  |  |  | 8627, 88627, 8612, 8619 | Y | N |  | 0 | 45341 | 45340
51788 | Amos Creek Circuit Breaker Addition | Provide transmission service to a generator. Add a 345-kV bay and associated circuit breakers to the Amos Creek substation.Cut-in Twin Buttes - Brown 345-kV transmission line to the Amos Creek substation. Associated with GINR # 19INR0121 |  | Amos Creek | Amos Creek | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1021517 | 2020-11-24 |  | 345 | 0 | 0 | 0 |  | Concho | Concho | Tier 4 |  |  |  | 1444, 7077, 76009 | Y | N |  | 0 | 51789 | 51788
4488 | Campwood to Uvalde: Rebuild 69 kV line | Rebuild Campwood to Uvalde 69 kV line, built to 138 kV, but energized at 69 kV. |  | Campwood | Uvalde | Planned | 707 - 0877 | AEP | Terry Weeks bcogan@aep.com 918-599-2857 | 2901 | 2020-11-30 |  | 138 | 0 | 37.1 | 0 |  | Real | Uvalde | Tier 3 | 2017-01-17 | 2017-03-20 | 2017-03-20 | 8230, 8633, 8231 | Y | N |  |  | 12057 | 4488
6079 | Childress to Kirkland 69 kV line: Rebuild 69 kV line | Rehab Childress to Kirkland 69 kV line |  | Childress | Kirkland | Planned | 786 - 0971 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2693 | 2020-11-30 |  | 69 | 0 | 5.61 | 0 |  | Childress | Childress | Tier 4 |  |  |  | 6032, 6053 | Y | N |  |  | 13803 | 6079
6569 | Aspermont: Replace the 138/69 kV autotransformer | Replace the 138/69 kV autotransformer at Aspermont with a 130 MVA autotransformer |  | Aspermont |  | Planned | 839 - 1023 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2817 | 2020-11-30 |  | 138 | 0 | 0 | 130 |  | Stonwall |  | Tier 4 |  |  |  | 6156, 6158 | Y | N |  |  | 14320 | 6569
7028 | Ft. Stockton SW to Rio Pecos: Rebuild 69 kV line | Rebuild Barrilla Junction to Ft. Stockton SW to Rio Pecos 69 kV line, convert to 138 kV, reterminate into Solstice, install 138 kV capacitor bank at Solstice, and build new Ft. Stockton Switch 138 kV station |  | Fort Stockton Switch | Rio Pecos | Planned | 908 - 1086 | AEP TNC | Darren O'Hare mlforcum@aep.com 918-599-2674 | 2733 | 2020-11-30 |  | 138 | 0 | 0.42 | 0 |  | Pecos | Pecos | Tier 3 | 2017-12-22 | 2018-02-02 |  | 6641, 6642, 6643, 38470, 60717, 60718, 60719, 60720, 60798, 38471, 6598, 6601, 6645 | Y | N |  |  | 14850 | 7028
44383 | Rio Hondo: Wind Farm Interconnection | Interconnect Las Majadas Wind Farm at Rio Hondo |  | Rio Hondo | Majadas | Under Construction | 943 - 1121 | AEP TCC | Kenneth Haley bcogan@aep.com 918-599-2857 | 3707 | 2020-11-30 |  | 345 | 9 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 8318 | Y | N |  | 0 | 44384 | 44383
44485 | Pig Creek: Build 138 kV terminal | Interconnect 138 kV line to Tar Bush |  | Pig Creek |  | Planned | 938 - 1116 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2751 | 2020-11-30 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  | 60393, 60436, 60385 | Y | N |  | 0 | 44486 | 44485
44854 | Lipton: Build 138 kV Box Bay | New Lipton 138 kV Station, replaces Lipton Hard Tap |  | Lipton |  | Planned | 973 - 1151 | AEP TCC | Nathan Cowan bcogan@aep.com 918-599-2857 | 3731 | 2020-11-30 |  | 138 | 0 | 0 | 0 |  | Zavala |  | Tier 4 |  |  |  | 8285, 88285, 8236, 8283 | Y | N |  | 0 | 44855 | 44854
44862 | Schottky: Build 69 kV Box bay | New Schottky 69 kV Station, replaces Hard Tap |  | Schottky |  | Planned | 971 - 1149 | AEP | Curtis Brown bcogan@aep.com 918-599-2857 | 3729 | 2020-11-30 |  | 69 | 0 | 0 | 0 |  | Live Oak |  | Tier 4 |  |  |  | 8507, 88507, 8400, 8406 | Y | N |  | 0 | 45151 | 44862
45334 | Corichi: Build 138 kV Box Bay | Build New Box Bay on El Campo - Victoria Line |  | Corichi |  | Planned | 986 - 1164 | AEP | Michael Glueck bcogan@aep.com 918-599-2857 | 3737 | 2020-11-30 |  | 138 | 0 | 0 | 0 |  | Wharton |  | Tier 4 |  |  |  | 8099, 88099, 8102, 8117 | Y | N |  | 0 | 45335 | 45334
50902 | Zygon: Build new 138 kV station | Interconnect Kaiser Creek wind farm on the East Abilene to Putnam 138 kV line |  | Zygon |  | Planned | 1047 - 1220 | ETT | Eric Blind mlforcum@aep.com 918-599-2674 | 2795 | 2020-11-30 |  | 138 | 0 | 0 | 0 |  | Callahan |  | Tier 4 |  |  |  | 60450, 6275, 6670 | Y | N |  | 0 | 50903 | 50902
51216A | Ward Winkler RPG | Conversion of TNMP Wink to Pecos 138kV. |  | TNMP Wink (37920 / 37900) | TNMP Pecos (38090) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2020-11-30 |  | 138 | 1.01 | 0 | 0 |  | Winkler | Reeves | Tier 2 | 2019-03-19 | 2019-10-10 |  | 38040, 38090, 38091, 38135, 38136, 38137, 38140, 38141, 38142, 38145, 38150, 38151, 38152, 38160, 38165, 38166, 38167, 38170, 38175, 38180, 38190, 38195, 38200, 38210, 38211, 38212, 38230, 38231, 38232, 37900, 37920, 38049, 38114, 38045 | Y |  |  | 0 | 56656 | 51216
53971 | Sandstone Mountain System Upgrade | To facilitate closing of normally open switch at Sandstone Mountain Substation. |  | Sandstone Mountain |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1023641 | 2020-11-30 |  | 69 | 0 | 0 | 0 |  | Llano |  | Tier 4 |  |  |  | 7116, 7101 | Y | N |  | 0 | 53972 | 53971
44804 | Tinsley: Build 138 kV station | Construct new 138 kV box bay on the Carver to Maxwell 138 kV line |  | Tinsley |  | Planned | 957 - 1135 | AEP TNC | Michael Glueck mlforcum@aep.com 918-599-2674 | 2761 | 2020-11-30 01:00 |  | 138 | 0 | 0 | 0 |  | Sutton |  | Tier 4 |  |  |  | 60440, 8259, 60412 | Y | N |  | 0 | 44805 | 44804
44807 | Crossover: Build 138 kV station | Construct new 138 kV box bay on the Santa Rita to North McCamey 138 kV line |  | Crossover |  | Planned | 954 - 1133 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2759 | 2020-11-30 01:00 |  | 138 | 0 | 0 | 0 |  | Upton |  | Tier 4 |  |  |  | 60723, 60361, 76032 | Y | N |  | 0 | 44808 | 44807
4971 | Magic Valley II: Build new four breaker 345 kV station | Interconnect Magic Valley II Windfarm at Magic Valley II to connect Magic Valley II to the Ajo to Rio Hondo 345 kV line and connect the generator's line to the Cebolla station. |  | Cebolla | Ladekidde | Planned | 731 - 0913 | AEP TCC | William Loveless bcogan@aep.com 918-599-2857 | 3562 | 2020-11-30 11:00 |  | 345 | 0 | 0 | 0 |  | Cameron | Willacy | Tier 4 |  |  |  | 8601, 80509, 80512, 80076, 8902, 161753 | Y |  |  |  | 12721 | 4971
3277 | Shepherd Road - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to Valley line. |  | Shepherd Road | Cagnon-Valley | Planned | S-0774 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0236 | 2020-12-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5378, 5053, 5465 | Y | N |  | There are no transformers associated with this project | 10628 | 3277
4504 | BRYN_4504_Rayburn_Rodgers_Upgrade | Reconductor Rayburn to Rodgers with 1033ACSR |  | 32861 | 32849 | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2020-12-01 |  | 69 | 0 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32861, 32849, 32872 | Y |  |  | 0 | 57319 | 4504
5045 | BRYN_5045_Rodgers_Sub | Construct new Rodgers Substation and remove Nall Lane Substation |  |  |  | Planned |  | BRYN | James Tanneberger jtanneberger@btutilities.com 979-821-5763 |  | 2020-12-01 |  | 69 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32849, 32872, 32874, 32877 | Y |  |  | 0 | 57318 | 5045
6789 | Wirtz to Johnson City to Mountain Top Rebuild to 138kV | Rebuild the Wirtz to Johnson City to Mountain Top 69kV Line and convert to 138kV. Convert Johnson City Substation to 138kV. |  | Johnson City | Mountain Top | Under Construction |  | PEC | Charles Dewitt Charles.Dewitt@peci.com (830) 868-5041 |  | 2020-12-01 |  | 138 | 0 | 25 | 0 |  | Burnet | Blanco | Tier 4 | 2017-10-01 | 2017-12-01 |  | 7104, 7107, 7110, 7514, 7516, 7148, 7480 | Y | N |  | 0 | 51771 | 6789
6934A | Elm Creek - New 345 kV Reactor | Install new 345 kV 60 Mvar Reactor at Elm Creek Substation. | [5 empty] | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0873 | 2020-12-01 |  | 345 | 0 | 0 | 0 | 60,0 | Guadalupe |  | Tier 4 |  |  |  | 5133 | Y |  |  |  | 14753 | 6934
49817 | 4x20 MVAR Pecos Capacitor Bank | Install 80 MVAR Capacitor Bank at Pecos 138 kV switching station. |  | Pecos (Bus # 38090) | Pecos (Bus # 38090) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2020-12-01 |  | 138 | 0 | 0 | 0 | 0,80 | Reeves | Reeves | Tier 4 |  |  |  | 38091 | Y |  |  | 0 | 49818 | 49817
50334 | Rebuild Mccoy to Tordillo | Rebuilds 4/0 ACSR to 795 ACSR on double circuit 138 kV capable poles. NERC assessment and 2019 RTP. |  | McCoy | Tordillo | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-12-01 |  | 69 | 0 | 7.9 | 0 |  | Atascosa | Atascosa | Tier 4 |  |  |  | 5715, 5721 | Y | N |  | 0 | 50335 | 50334
51953 | LCRATSC KENDALL MOST LIMITING SERIES ELEMENT | Increase the rating of T459 transmission line between Kendall and Cagnon Road substations to a minimum of 3000A at 105 degree F ambient temperature by upgrading the Most Limiting Series Element (MLSE) at Kendall Substation. |  | Kendall | Cagnon | Planned |  | LCRATSC | Dylan Rreas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2020-12-01 |  | 345 | 0 | 0 | 0 |  | Medina | Bexar | Tier 4 |  |  |  | 5056, 7046 | Y | N |  | 0 | 51954 | 51953
54255 | Rebuild Rio Pecos-Lynx Ckt 2 (1926 ACSS) | Rebuild AEP Rio Pecos to TNMP Woodward Tap 138kV line and re-terminate Woodward Tap end over to AEP Lynx. |  | AEP Rio Pecos (Bus # 6601) | AEP Lynx (Bus # 60400) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE08314 & NTE08414 | 2020-12-01 |  | 138 | 0.72 | 1.98 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6601, 38310, 60400 | Y |  |  | 0 | 54256 | 54255
55372 | Conversion of TNMP Gomez to 138kV service. |  |  |  |  | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE03020 | 2020-12-01 |  | 138 | 0 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 38471, 60798 | Y |  |  | 0 | 55373 | 55372
57173 | TNMP Soaptree Switching Station | NOMCR IDs: 64303-1 & 64608-1 |  | Rio Pecos (6601), Lynx (60400) & 16th Street (38310) | Soaptree (38450) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2020-12-03 |  | 138 | 0.76 | 1.93 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 38450, 6601, 38310, 60400 | Y |  |  | 0 | 57174 | 57173
45346 | Trade Zone: Build 138 kV Station | Trade Zone: Build 138 kV Station on South McAllen - Stewart Road Line |  | South McAllen | Las Milpas | Planned | 886 - 1064 | AEP TCC | Todd Siegert bcogan@aep.com 918-599-2857 | 3673 | 2020-12-12 |  | 138 | 0 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8644, 8371, 8758 | Y | N |  | 0 | 45347 | 45346
4825 | Crockett - Jewett 138kV Line | Upgrade existing line | Project Deferral | Crockett | Jewett | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6061 | 2020-12-15 |  | 138 | 0 | 39.5 | 0 |  | Houston | Leon | Tier 3 | 2017-09-11 | 2017-12-04 | 2017-12-04 | 3354, 3355, 3357, 3358, 13354, 3345, 3394 | Y | N |  |  | 12432 | 4825
5312 | Mitchell Bend - Rocky Creek 345 kV line | Upgrade existing line | Project Deferral | Mitchell Bend | Rocky Creek | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1736 | 2020-12-15 |  | 345 | 0 | 32.8 | 0 |  | Hood | Tarrant | Tier 4 |  | 2016-07-22 | 2016-08-22 | 1877, 1880 | Y |  |  |  | 12988 | 5312
5440 | Riverton 345 kV Switching Station | Construct new 345 kV switching station |  | Riverton | Riverton | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8351 | 2020-12-15 |  | 345 | 0 | 0 | 1200 |  | Reeves |  | Tier 1 | 2016-04-20 | 2017-05-23 | 2017-06-13 | 11075, 11084, 11085, 11083 | Y | N |  |  | 13143 | 5440
5500 | Lamar Blossom - Paris East Tap 138 kV Line | Construct new 138 kV line and ring bus | Project Deferral | Lamar Blossom | Paris East Tap | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4103 | 2020-12-15 |  | 138 | 10 | 0 | 0 |  | Lamar | Lamar | Tier 4 |  |  |  | 1769, 1770, 1771 | Y | N |  |  | 13240 | 5500
5974 | Saginaw - Denton Ave/Springdale 138 kV DCKT Line | Rebuild existing 69 kV Lines | Construction schedule change | SAGINAW | DENTON AVE | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5245 | 2020-12-15 |  | 138 | 0 | 7.4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1957, 2101, 2146, 2157, 11966 | Y | N |  |  | 13689 | 5974
6019 | North Main - Denton Ave/Springdale Loop | Establish Northmain - Springdale Loop 138 kV line |  | North Main | Springdale | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5240 | 2020-12-15 |  | 138 | 0 | 4.6 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1965, 2102, 2148, 2156, 3010, 2092, 2099, 2101, 2157, 1961, 2146 | Y | N |  | 0 | 52337 | 6019
6255B | Rebuild BEVO to Brundage to Big Wells 69 kV lines. | Rebuild 69 kV line with 795 ACSR on 138 kV and double circuit capable structures 2015- NERC assessment |  | BEVO | Brundage | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-12-15 |  | 69 | 0 | 7.3 | 0 |  | Dimmit | Dimmit | Tier 4 |  |  |  | 5870, 5871 | Y | N |  | 0 | 45067 | 6255
6302 | Black Fork-Tyler West 69 kV to 138 kV Line Conversion | Rebuild existing 69 kV line and convert to 138 kV operation |  | Black Fork | Tyler West | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6071 | 2020-12-15 |  | 138 | 0 | 4.9 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3121, 3132, 3138, 3140, 3142, 3198, 3207, 3139, 3197, 13235, 3141 | Y |  |  | 0 | 56108 | 6302
6780 | Deen 138 kV Switching Station | Rebuild existing Saginaw 138 kV Switching Station |  | Deen |  | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5277 | 2020-12-15 |  | 138 | 0 | 0 | 0 |  | Tarrant |  | Tier 4 |  |  |  | 1957, 2074, 2043, 2047, 2048, 2049, 2067, 2070, 2071, 2077, 2146, 2157 | Y |  |  | 0 | 57900 | 6780
6790 | Sargent Road-East Network 138 kV Line | Construct the new Sargent Road-East Network 138 kV Line | Project Deferral | Sargent Road | Oakland | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4268 | 2020-12-15 |  | 138 | 2.5 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2905, 2949, 2969, 2970, 2971, 12447 | Y | N |  |  | 14588 | 6790
7104 | Owl Hills - Tunstill POD 138 kV Line | Owl Hills - Tunstill POD 138 kV Line |  | Owl Hills | Tunstill | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8428 | 2020-12-15 |  | 138 | 12 | 0 | 0 |  | Culberson | Reeves | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11090, 11183 | Y |  |  |  | 14938 | 7104
7119 | Sand Lake 345 kV Sw. Sta. | Sand Lake 345 kV Sw. Sta. |  | Sand Lake | Sand Lake | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8420 | 2020-12-15 |  | 345 | 0 | 0 | 1200 |  | Ward |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11098, 11099, 11109, 11097 | Y |  |  |  | 14955 | 7119
7129 | DeCordova 345/138kV_Sw. | Rebuild existing switching DeCordova station |  | DeCordova |  | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5066 | 2020-12-15 |  | 345 | 0 | 0 | 0 |  | Hood |  | Tier 3 | 2020-05-05 |  |  | 11890, 1891, 150721, 150722, 150723, 150724 | Y | N |  | 0 | 55615 | 7129
45471 | Lake Creek - Waco East 138 kV Line | Upgrade the Lake Creek Switch - Waco East Switch 138 kV Line to 2071A |  | Lake Creek | Waco East | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R470 | 2020-12-15 |  | 138 | 0 | 9.8 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  | 3410, 3438, 3452 | Y | N |  | 0 | 45472 | 45471
45498 | Shipwreck Substation - Midkiff Switch 138 kV Line | Construct Shipwreck Substation to Midkiff Switch 138 kV Line |  | Shipwreck Substation | Midkiff Switch | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8462 | 2020-12-15 |  | 138 | 0 | 10.3 | 0 |  | Glasscock | Reagan | Tier 4 |  |  |  | 1210, 1211, 1213, 1217, 1219, 11218 | Y |  |  | 0 | 45500 | 45498
52311 | Add Gardendale 345 kV Switch | Add Gardendale 345 kV Switch for 2W Permian Solar |  | Clearfork | Telephone Road | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8506 | 2020-12-15 |  | 345 | 0 | 0 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 11157, 23873, 23876 | Y |  |  | 0 | 52313 | 52311
57731A | Hornsby Substation Addition | Cut-in a temporary 138-kV single-bus/single-breaker substation to the Austin Energy-owned Decker to Sand Hill 138-kV transmission line to initially serve the load via two modular stations, one mobile transformer and 24.9-kV bus work. | For total project cost please see 57731B | Decker | Sand Hill | Planned |  | ERCOT |  |  | 2020-12-15 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 7916, 9187, 9216 | Y | N |  | 0 | 57732 | 57731
58063 | Construct Cedar Elm 345 kV Switch | Construct Cedar Elm 345 kV Switch to Interconnect Wildwind |  | Cedar Elm |  | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5313 | 2020-12-15 01:00 |  | 345 | 0 | 0 | 0 |  | Cooke |  | Tier 4 |  |  |  | 11735, 1730, 2373 | Y | N |  | 0 | 58064 | 58063
14TPIT0057 | Cedar Hill Switch - Liggett 138 kV line | Upgrade Cedar Hill Switch - Dalworth existing line section |  | Cedar HIll Switch | Dalworth | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5041-E | 2020-12-15 02:02 |  | 138 | 0 | 8.6 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 1912, 1922, 2265, 2270, 2271, 2274, 2422 | Y | N |  |  | 10276 | 2926
48822 | Carrollton East - Renner_Northaven Double-circuit Line | Upgrade existing line |  | Carollton East | Alpha Road And Knoll Trail | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4232 | 2020-12-15 12:00 |  | 138 | 0 | 13 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2571, 2575, 2582, 2583, 2584, 2596, 2578, 2598, 2613 | Y | N |  | 0 | 49080 | 48822
6269 | Ennis Creek 138 kV Switching Station | Rebuild existing Ennis Creek 138 kV Switching Station | Project Deferral | Ennis Creek | Ennis Creek | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9026 | 2020-12-15 22:00 |  | 138 | 0 | 0 | 0 |  | Scurry |  | Tier 4 | 2015-12-21 | 2016-10-11 |  | 1410 | Y | N |  |  | 13999 | 6269
4554 | Ennis Creek - Cogdell 69 kV Line | Convert existing line to 138 kV operation |  | Ennis Creek | Cogdell | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9025 | 2020-12-16 |  | 138 | 0 | 8.6 | 0 |  | Scurry |  | Tier 3 | 2015-12-21 | 2016-10-11 |  | 1400, 1401, 1402, 1411, 1412, 11402, 752, 1410 | Y |  |  | 0 | 49764 | 4554
5445 | Riverton-Odessa EHV/Moss 345 kV Line | Riverton-Odessa EHV/Moss 345 kV Line |  | Riverton | Odessa EHV | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8356 | 2020-12-16 |  | 345 | 186 | 16 | 0 |  | Reeves | Ector | Tier 1 | 2016-04-20 | 2017-05-23 | 2017-06-13 | 1018, 11010, 11028, 11084 | Y |  |  | 0 | 51212 | 5445
7120 | Riverton Sw. Sta. - Sand Lake Sw. Sta. 345 kV Line | Riverton Sw. Sta. - Sand Lake Sw. Sta. 345 kV Line |  | Riverton | Sand Lake | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8443 | 2020-12-16 |  | 345 | 26 | 0 | 0 |  | Reeves | Ward | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11084, 11098 | Y |  |  |  | 14956 | 7120
7121 | Sand Lake Sw. Sta. - Solstice 345 kV Line | Sand Lake Sw. Sta. - Solstice 345 kV Line |  | Sand Lake | Solstice | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8380 | 2020-12-16 |  | 345 | 80 | 0 | 0 |  | Ward |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11098, 60404 | Y |  |  |  | 14957 | 7121
52825 | Woodard 345 kV Switch | Establish Woodard 345 kV Switch |  | Woodard |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5291 | 2020-12-16 |  | 345 | 0 | 0 | 0 |  | Lamar |  | Tier 4 |  |  |  | 11699, 1692, 1695, 143062 | Y |  |  | 0 | 52826 | 52825
3877 | Meadow Lake Substation Addtion | Add a new load serving substation (ring-bus) at Meadow Lake. The station will be built between Cushman and Highway 123 off T572. | Customer Schedule Change | Cushman | Highway 123 | Planned |  | LCRATSC/GVEC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1016198 | 2020-12-18 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7720, 7221, 7226 | Y | N |  |  | 12940 | 3877
5356 | Bakersfield: Build 345 kV terminal | Interconnect Maplewood solar farm at Bakersfield | Updated Terminal To, Schedule & Cost | Bakersfield |  | Under Construction | 780 - 0965 | ETT | Greg Crane mlforcum@aep.com 918-599-2674 | 2640 | 2020-12-18 |  | 345 | 2.35 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 135324, 76002 | Y | N |  |  | 13042 | 5356
7116 | Riverton Sw. Sta.- Kyle Ranch 138 kV Line | Riverton Sw. Sta.- Kyle Ranch 138 kV Line |  | Riverton | Kyle Ranch | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8427 | 2020-12-18 |  | 138 | 15 | 0 | 0 |  | Reeves | Loving | Tier 2 | 2018-02-02 | 2018-05-22 |  | 11089, 11083 | Y |  |  |  | 14952 | 7116
50450 | LCRATSC_Escobares Substation Addition | Construct a new 138-kV Escobares substation.The Escobares substation will be located approximately 2 miles east of Roma (AEP) Substation and approximately 3.5 miles west of Garceno (AEP) Substation. |  | Escobares | Escobares | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2020-12-18 |  | 138 | 0 | 0 | 0 |  | Starr | Starr | Tier 4 |  |  |  | 7870, 8796, 8923 | Y | N |  | 0 | 50451 | 50450
50864 | Cenizo - Del Sol: Install Double CKT to Reloj del Sol | Cenizo - Del Sol: Install Double CKT to Reloj del Sol to connect generator into Cenizo |  | Cenizo | Reloj POI | Planned | 1051 - 1224 | ETT | Adam Wells bcogan@aep.com 918-599-2857 | 3777 | 2020-12-21 |  | 345 | 0 | 21 | 0 |  | Webb | Zapata | Tier 4 |  |  |  | 80226, 80220, 162491 | Y | Y |  | 0 | 50865 | 50864
50344 | Rebuild MarkhamTap to Shropshire | Rebuilds 4/0 ACSR to 795 ACSR on double circuit 138 kV capable poles. NERC assessment and 2019 RTP |  | Markham Tap | Shropshire | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-12-23 |  | 69 | 0 | 1.87 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 5554, 5555 | Y | N |  | 0 | 50345 | 50344
43456A | Greens Bayou 138kV Reconfigurations | Connect Greens Bayou 'East' and 'West' buses with (1) 8-Ohm Reactor. |  | Greens Bayou | Greens Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40710, 40715 | Y | N |  | 0 | 50813 | 43456
44818A | Fort Bend to West Columbia 138kV Conversion | Remove Fort Bend 138/69kV Auto A1 from CNP service |  | Ft Bend | Ft Bend | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 |  | 138 | 0 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 3 | 2018-10-30 | 2018-11-26 |  | 44290, 49014, 44280 | Y |  |  | 0 | 52190 | 44818
44818B | Fort Bend to West Columbia 138kV Conversion | Convert existing 69kV Ckt.45 Fort Bend to Big Creek to 138kV service as Ckt.89. Convert Big Creek substation from tap to loop service. |  | Ft Bend | Big Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:01 |  | 138 | 7.4 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 3 | 2018-10-30 | 2018-11-26 |  | 42390, 44070, 44280, 44290 | Y |  |  | Cost Included in 44818A | 52192 | 44818
44818C | Fort Bend to West Columbia 138kV Conversion | Convert existing 69kV Ckt.45 Big Creek to Needville to 138kV service as Ckt.89. Convert Big Creek substation from tap to loop service. |  | Big Creek | Needville | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:02 |  | 138 | 8.2 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 3 | 2018-10-30 | 2018-11-26 |  | 42380, 43000, 44070, 42390 | Y |  |  | Cost Included in 44818A | 52191 | 44818
44818D | Fort Bend to West Columbia 138kV Conversion | Convert existing 69kV Ckt.45 Needville to Damon to 138kV service as Ckt.89 |  | Needville | Damon | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:03 |  | 138 | 10.8 | 0 | 0 |  | Fort Bend | Brazoria | Tier 3 | 2018-10-30 | 2018-11-26 |  | 42340, 42370, 43000, 42380 | Y |  |  | Cost Included in 44818A | 52195 | 44818
44818E | Fort Bend to West Columbia 138kV Conversion | Convert existing 69kV Ckt.45 Damon to West Columbia to 138kV service as Ckt.89 |  | Damon | West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:04 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2018-10-30 | 2018-11-26 |  | 43384, 42370, 42410, 43380, 43390, 44010, 42340, 42980 | Y |  |  | Cost Included in 44818A | 52193 | 44818
44818F | Fort Bend to West Columbia 138kV Conversion | Remove West Columbia 138/69kV Auto A2 from CNP service |  | West Columbia | West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:05 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2018-10-30 | 2018-11-26 |  | 43390, 49034, 43380 | Y |  |  | Cost Included in 44818A | 52194 | 44818
44818H | Fort Bend to West Columbia 138kV Conversion | Remove 7.2 MVAR cap bank from West Columbia Auto A2 tertiary bus |  | West Columbia | West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:07 |  | 69 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2018-10-30 | 2018-11-26 |  | 49034 | Y |  |  | Cost Included in 44818A | 52189 | 44818
6202 | North Ella - Premont 69 kV Line | Rehab North Ella - Premont 69 kV Line |  | North Ella | Premont | Planned | 818 - 1002 | AEP TCC | Joe Yeagler bcogan@aep.com 918-599-2857 | 3615 | 2020-12-30 |  | 69 | 0 | 10.7 | 0 |  | Jim Wells |  | Tier 4 |  |  |  | 8878, 8894 | Y | N |  |  | 13927 | 6202
43456B | Greens Bayou 138kV Reconfigurations | Reposition Ckt.94A (GBY to Humble) to connect to GBY 'West' bus |  | Greens Bayou | Humble | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40710, 40715, 41222 | Y |  |  | Cost Included in 43456A | 50814 | 43456
44940 | Henne and TXI Switch Upgrades/Replacement | Replace and increase fault interrupting rating of breaker 5870 to 63kA, and its continuous rating to 3,000 Amp. Replace CS 5395 and CS 5405 to 40kA units. |  | Henne | TXI | Planned |  | NBU | Gregory Thomas gthomas@nbutexas.com 830-608-8953 |  | 2020-12-30 |  | 138 | 0 | 0 | 0 |  | Comal | Comal | Tier 4 |  |  |  | 7174 | Y | N |  | 0 | 44941 | 44940
50904A | Install two 14.4 MVAR cap banks at Village Creek substation | Cap Bank #1: Install one 14.4 MVAR cap bank at Village Creek substation |  | Village Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-30 |  | 138 | 0 | 0 | 0 | 0,14.4 | Harris | Harris | Tier 4 |  |  |  | 44270 | Y | N |  | 0 | 50905 | 50904
50904B | Install two 14.4 MVAR cap banks at Village Creek substation | Cap Bank #2: Install one 14.4 MVAR cap bank at Village Creek substation |  | Village Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-30 |  | 138 | 0 | 0 | 0 | 0,14.4 | Harris | Harris | Tier 4 |  |  |  | 44270 | Y | N |  | Cost included in 50904A | 50906 | 50904
5530 | Solstice: Build 345 kV station | Construct new 345 kV station with two 345/138 kV autotransformers, reactor, and build new 345 kV line from Solstice to Bakersfield |  | Solstice |  | Planned | 789 - 0974 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2649 | 2020-12-31 |  | 345 | 0 | 0 | 1486 |  | Pecos |  | Tier 1 | 2016-04-01 | 2017-05-23 | 2017-06-21 | 60402, 60404, 60418, 60385 | Y | Y |  |  | 13257 | 5530
5539 | Solstice to Bakersfield: Build 345 kV line | Construct new 345 kV station with two 345/138 kV autotransformers, reactor, and build two new 345 kV lines from Solstice to Bakersfield |  | Solstice | Bakersfield | Planned | 789 - 0974 | AEP TNC/LCRATSC | Brent Harris mlforcum@aep.com 918-599-2674 | 2651 | 2020-12-31 |  | 345 | 136 | 0 | 0 |  | Pecos | Pecos | Tier 1 | 2016-04-01 | 2017-05-23 | 2017-06-21 | 60404, 76002 | Y | Y |  |  | 13267 | 5539
5835 | Rebuild Sardis to Reagor Springs | Rebuild Sardis (Bus #202) to Reagor Springs (Bus #210) |  |  |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 16027 | 2020-12-31 |  | 69 | 0 | 15.46 | 0 |  | Ellis | Ellis | Tier 4 |  |  |  | 202, 210 | Y |  |  |  | 13577 | 5835
6044 | Big Lake to Barnhart 69 kV line: Rebuild 69 kV line | Rehab Big Lake to Barnhart 69 kV line |  | Big Lake | Barnhart | Planned | 786 - 0971 | AEP TNC | James Weaver mlforcum@aep.com 918-599-2674 | 2672 | 2020-12-31 |  | 69 | 0 | 17.71 | 0 |  | Reagan | Irion | Tier 4 |  |  |  | 6530, 6534 | Y | N |  |  | 13763 | 6044
6112 | Causeway - Sunchase 138 kV Line | Rehab Causeway - Sunchase 138 kV Line |  | Causeway | Sunchase | Planned | 826 - 1010 | AEP TCC | Kenneth Haley bcogan@aep.com 918-599-2857 | 3627 | 2020-12-31 |  | 138 | 0 | 3.56 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8744, 8917 | Y | N |  |  | 13838 | 6112
6346 | Menard Phillips T to Junction 69 kV line: Rbld 69 kV line | Rehab Menard Phillips Tap to Junction 69 kV line |  | Menard Phillips Tap | Junction | Planned | 786 - 0971 | AEP TNC | Brian Oyster mlforcum@aep.com 918-599-2674 | 2712 | 2020-12-31 |  | 69 | 0 | 12.2 | 0 |  | Kimble | Kimble | Tier 4 |  |  |  | 6400, 6401 | Y | N |  |  | 14090 | 6346
6349 | CRMWD Tap #1 to Eden 69 kV line: Rebuild 69 kV line | Rehab CRMWD Tap #1 to Eden 69 kV line |  | CRMWD Tap #1 | Eden | Planned | 786 - 0971 | AEP TNC | Brian Oyster mlforcum@aep.com 918-599-2674 | 2710 | 2020-12-31 |  | 69 | 0 | 13.6 | 0 |  | Concho | Concho | Tier 4 |  |  |  | 6372, 6376 | Y | N |  |  | 14093 | 6349
6594 | Solstice: Add 345 kV reactor | Construct new 345 kV station with two 345/138 kV autotransformers, reactor, and build new 345 kV line from Solstice to Bakersfield |  | Solstice |  | Planned | 789 - 0974 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2729 | 2020-12-31 |  | 345 | 0 | 0 | 0 | -50,0 | Pecos |  | Tier 1 | 2016-04-01 | 2017-05-01 | 2017-06-01 | 60404 | Y | N |  |  | 14356 | 6594
6872 | Support 69kV to 138kV Conversion Projects | Removing of Lawler substation from system to support 69kV to 138kV conversion projects |  |  |  | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2020-12-31 |  | 69 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 815, 820, 803, 806 | Y | N |  |  | 14681 | 6872
7007 | CNP_18TPIT7007_WAP_Reactor_Upgrades | Install (2) 5-Ohm Reactors at WA Parish as a fault duty upgrade |  | WAP | WAP | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 4 |  |  |  | 44010, 44015, 44170, 44173, 44651, 44671, 44172, 110013, 110014 | Y |  |  | 0 | 51161 | 7007
43456C | Greens Bayou 138kV Reconfigurations | Reposition Ckt.95C (GBY to Glenwood) to connect to GBY 'West' bus |  | Greens Bayou | Glenwood | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40260, 40352, 40420, 40475, 40611, 40620, 40700, 40710, 40715, 40725, 40830, 40900, 40911, 40720, 40831, 40912, 41221, 41222, 41570, 41651, 41681, 41712, 46290, 49018 | Y |  |  | Cost Included in 43456A | 50815 | 43456
45575 | Solstice: Add second 345 kV reactor | Add a second 345 kV reactor at Solstice |  | Solstice |  | Planned | 997 - 1175 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2771 | 2020-12-31 |  | 345 | 0 | 0 | 0 | -50,0 | Pecos |  | Tier 4 |  |  |  | 60404 | Y | N |  | 0 | 45576 | 45575
48281 | Angleton to West Columbia Ckt 04E Upgrades | Upgrade Ckt 04E Angleton to West Columbia to increase thermal ratings | Now a GO project | Angleton | West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 16.11 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42110, 43381, 43380 | Y | N |  | 0 | 55974 | 48281
48778 | Dustdevil: Construct New Distribution Station | Dustdevil: Construct New Distribution Station |  | Laredo VFT North | Lobo | Planned | 1029 - 1207 | AEP TCC | Michael Richardson bcogan@aep.com 918-599-2857 | 3768 | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Webb | Webb | Tier 4 |  |  |  | 8038, 80013, 80221 | Y | N |  | 0 | 48779 | 48778
48782 | Progreso: Construct New Distribution Station | Progreso: Construct New Distribution Station |  | Rio Rico | Stewart Road | Planned | 1031 - 1209 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3770 | 2020-12-31 |  | 69 | 0 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8040, 8751, 8949 | Y | N |  | 0 | 48783 | 48782
48830 | Pavlov: Construct New 138 kV Station | Pavlov: Construct New 138 kV Station |  | Blessing | Lane City | Planned | 995 - 1173 | AEP TCC | James Ball bcogan@aep.com 918-599-2857 | 3748 | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Matagorda | Wharton | Tier 4 |  |  |  | 8608, 8614, 8121, 8127 | Y | N |  | 0 | 48831 | 48830
49528 | NevillRoadSwitchyardProject | Nevill Road Switchyard Project as for POI |  | Neville Road | North McCamey and Bakersfield | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2020-12-31 |  | 345 | 10.3 | 0 | 0 |  | Upton | Upton | Tier 4 |  |  |  | 844, 845, 76000, 76002, 134905 | Y | N |  | 0 | 49529 | 49528
49548 | Esperanza: Construct New 138 kV Station | Esperanza: Construct New 138 kV Station |  | Esperanza |  | Planned | 993 - 1171 | AEP | James Nivens bcogan@aep.com 918-599-2857 | 3742 | 2020-12-31 |  | 138 | 0.6 | 0 | 0 | 0,46.6 | Matagorda |  | Tier 4 |  |  |  | 8191, 8116, 8558 | Y | N |  | 0 | 49549 | 49548
52365B | Spillman Island Restoration Plan | Upgrade Relays at BAYOU substation on BAYOU to Morgans Point Ckt.79B (Future Option 3 to reconfigure as Ckt.xx STRANG to SYLVAN to BAYOU) |  | BAYOU | Morgans Point | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | Y | N |  | Cost included in Phase A. | 52367 | 52365
52365D | Spillman Island Restoration Plan | Upgrade Relays at QUANUM substation on QUANUM to WALKER to Cedar Bayou Ckt.85A (Future Option 3 to reconfigure as Ckt.xx QUANUM-WALKER-Alexander Island-SRB). |  | QUANUM | WALKER | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | Y | N |  | Cost included in Phase A. | 52369 | 52365
52365E | Spillman Island Restoration Plan | Upgrade equipment at SR Bertron substation on SRB-Alexander Island-CHORIN Ckt.87C (Future Option 3 to reconfigure as Ckt.xx SRB-Alexander Island-WALKER-QUANUM) |  | SRB | Chorin | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | Y | N |  | Cost included in Phase A. | 52371 | 52365
52365C | Spillman Island Restoration Plan | Upgrade Relays at Morgans Point substation on Morgans Point to BAYOU Ckt.79B (Future Option 3 to reconfigure as Ckt.xx Morgans Point to CHORIN). |  | Morgans Point | BAYOU | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | Y | N |  | Cost included in Phase A. | 52368 | 52365
52365I | Spillman Island Restoration Plan | Upgrade Ckt.83A Cedar Bayou to DECKER to increase thermal limits. |  | Cedar Bayou | DECKER | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Harris | Tier 4 |  |  |  | 40439, 40430 | Y | N |  | Cost included in Phase A. | 52375 | 52365
52365G | Spillman Island Restoration Plan | Upgrade Relays at Cedar Bayou substation on Cedar Bayou to STRANG Ckt.87A. |  | Cedar Bayou | STRANG | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | Y | N |  | Cost included in phaseA. | 52373 | 52365
52365F | Spillman Island Restoration Plan | Upgrade Relays at Cedar Bayou substation on Cedar Bayou-WALKER-QUANUM Ckt.85A. |  | Cedar Bayou | Quanum | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | Y | N |  | Cost Included in Phase A. | 52372 | 52365
52365H | Spillman Island Restoration Plan | Upgrade Relays at WARVUE substation on WARVUE to HOPSON Ckt.84D. Upgrade Relays at Cedar Bayou substation on Cedar Bayou to HOPSON Ckt.84D. |  | WARVUE | HOPSON | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  |  | Y | N |  | Cost included in Phase A. | 52374 | 52365
52365A | Spillman Island Restoration Plan | Upgrade Relays at STRANG substation on STRANG to Cedar Bayou Ckt.87A (Future Option 3 to reconfigure as Ckt.xx STRANG to SYLVAN to BAYOU). |  | STRANG | Cedar Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Chambers | Tier 4 |  |  |  |  | Y | N |  | 0 | 52366 | 52365
52376 | MARICK (MCK) 138kV Customer Substation | MARICK (MCK) 138kV customer substation looped into Ckt.60A Orchard/Rosenberg |  | Orchard | Rosenberg | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 4 |  |  |  | 44520, 44540, 44541, 44615 | Y | N |  | 0 | 52377 | 52376
54755 | This is related to GINR19INR0081 | This is a switching station to interconnect new generation project 19INR0081 Anson Solar Project. |  |  |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2020-12-31 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 68004, 68000, 68001 | Y |  |  | 0 | 54756 | 54755
56109 | McDonough Substation Removal | Remove 69kV McDonough substation from CNP service |  | McDonough |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 69 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 41040, 40352, 40800 | Y | N |  | 0 | 56110 | 56109
57422 | Brown Substation Removal | Remove 69kV Brown substation from CNP service |  | Brown |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 69 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47550, 47540, 47670 | Y | N |  | 0 | 57423 | 57422
48818 | Ballinger: Replace the 138/69 kV autotransformer | Replace the 138/69 kV autotransformer at Ballinger with a 130 MVA autotransformer |  | Ballinger |  | Planned | 1016 - 1194 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2777 | 2020-12-31 01:00 |  | 138 | 0 | 0 | 130 |  | Runnels |  | Tier 4 |  |  |  | 6338, 6340 | Y | N |  | 0 | 48819 | 48818
6938 | Leonard Road Substation 69 | Construct Leonard Rd Substation with Dual Voltage Transformer. Will be served at 69kV until completion of Smetana to Leonard Rd 138kV line. | [5 empty] | BRYN | James Tanneberger jtanneberger@btutilities.com 979-821-5763 |  | 2021-01-01 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 32851, 32864, 32850 | Y |  |  |  | 14758 | 6938
56581 | Kimbro Substation Addition | Provide transmission service to a generator by cutting -in a new substation between the LCRA TSC Gilleland Creek Substation and Oncor Elgin Switch. This is related to ERCOT Generation Interconnection or Change Request No. 15INR0090. |  | Kimbro |  | Under Construction |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017433 | 2021-01-19 |  | 138 | 0 | 0 | 0 |  | Travis |  | Tier 4 |  |  |  | 7337, 3650, 7336 | Y |  |  | 0 | 56582 | 56581
6167 | Harlingen SS - Raymondville #2: Convert to 138 kV | Harlingen SS - Raymondville #2: Convert to 138 kV |  | Harlingen SS | Raymondville #2 | Planned | 864 - 1042 | AEP TCC | Eric Scott bcogan@aep.com 918-599-2857 | 3650 | 2021-01-28 |  | 138 | 0 | 0 | 0 |  | Cameron | Willacy | Tier 4 |  |  |  | 8300, 8700, 80436, 8302, 8325, 8327 | Y | N |  |  | 13892 | 6167
4495 | Champlin: Station Reconfigure | Expand existing breaker configuration to a four (4) breaker ring bus expandable to a six (6) breaker ring bus configuration. |  | Champlin |  | Planned | 694 - 0864 | AEP TCC | John Pulay bcogan@aep.com 918-599-2857 | 3541 | 2021-01-30 |  | 138 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 8476 | Y | N |  |  | 12064 | 4495
4487 | Nueces Area 69kV Reinforcement | Expand and add new 138/69kV Auto at Valero East 69kV substation. Add 5th breaker to Champlin 138kV substation. Construct Champlin to Valero East 138kV Line. |  | Champlin | Valero East | Planned | 709 - 0879 | AEP TCC | John Pulay mlforcum@aep.com 918-599-2857 | 2903 | 2021-01-30 01:00 |  | 138 | 1.6 | 0 | 200 |  | Nueces |  | Tier 4 |  |  |  | 8528, 8476, 8859 | Y | N |  |  | 13570 | 4487
6345 | Yellowjckt to Menard Phillips T 69 kV line: Rebld 69 kV line | Rehab Yellowjacket to Menard Phillips Tap 69 kV line |  | Yellowjacket | Menard Phillips Tap | Planned | 786 - 0971 | AEP TNC | Brian Oyster mlforcum@aep.com 918-599-2674 | 2711 | 2021-01-31 |  | 69 | 0 | 15.3 | 0 |  | Menard | Kimble | Tier 4 |  |  |  | 6363, 6401 | Y | N |  |  | 14089 | 6345
6352 | Crckett Hghts to Sonora Atlntic 69 kV line: Rbld 69 kV line | Rehab Crockett Heights to Sonora Atlantic 69 kV line |  | Crockett Heights | Sonora Atlantic | Planned | 786 - 0971 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2706 | 2021-01-31 |  | 69 | 0 | 16.8 | 0 |  | Crockett | Sutton | Tier 4 |  |  |  | 6511, 6552 | Y | N |  |  | 14096 | 6352
6753 | Quihi: Build 138kV Station | Build new Quihi 138kV In and Out Station on Razorback to Castroville 138kV Line |  | Quihi |  | Planned | 900 -1078 | ETT/STEC | James Weaver bcogan@aep.com 918-599-2857 | 3684 | 2021-01-31 |  | 138 | 0.8 | 0 | 0 |  | Medina |  | Tier 4 |  |  |  | 8248, 88248, 5083, 8241 | Y | Y |  |  | 14546 | 6753
45508 | Pig Creek: Build 138 kV terminal | Interconnect Taygete I solar farm at the Pig Creek 138 kV station | Update Contact | Pig Creek |  | Planned | 981 - 1159 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2822 | 2021-01-31 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60393 | Y | N |  | 0 | 45509 | 45508
4505 | BRYN_4505_Smetana_Sub | Construction of a new Smetana Substation at 138kV |  |  |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2021-02-02 |  | 138 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32850, 32853, 32868, 32864 | Y |  |  |  | 12077 | 4505
4576 | BRYN_4576_Smetana_to_Steele_Store | Construct New 138kV line (Bundled 1033 ACSR - Curlew) to new Steele Store substation as part of the reliability project to loop in Steele Store |  | 32853 | 32852 | Planned |  | BRYN | James Tanneberger jtanneberger@btutilities.com 979-821-5763 |  | 2021-02-02 |  | 138 | 4.5 | 0 | 0 |  | Brazos | Burleson | Tier 4 | 2015-10-09 | 2015-11-06 |  | 32852, 32853 | Y |  |  |  | 12158 | 4576
50340 | Rebuild Markham Tap to Van Vleck Sw | Rebuilds 4/0 ACSR to 795 ACSR on double circuit 138 kV capable poles. NERC assessment and 2019 RTP |  | Markham Tap | Van Vleck Switch | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-02-15 |  | 69 | 0 | 4.65 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 5554, 5556 | Y | N |  | 0 | 50341 | 50340
5024 | Crane Loop: Rebuild 69 kV line | Rebuild Crane Loop 69 kV line |  | Crane | Crane | Planned | 738 - 0921 | AEP TNC | Jeremy Brazeal mlforcum@aep.com 918-599-2674 | 2619 | 2021-02-28 |  | 69 | 0 | 8.05 | 0 |  | Crane | Crane | Tier 4 |  |  |  | 6600, 6603, 6607, 6609, 6606, 6608, 6613 | Y | N |  |  | 12661 | 5024
6118 | Port Isabel - Causeway 138 kV Line | Rehab Port Isabel - Causeway 138 kV Line |  | Port Isabel | Causeway | Planned | 826 - 1010 | AEP TCC | Kenneth Haley bcogan@aep.com 918-599-2857 | 3626 | 2021-02-28 |  | 138 | 0 | 6.74 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8338, 8744 | Y | N |  |  | 13844 | 6118
49570 | Goodlett: Build 69 kV station | Build new Goodlett 69 kV station on the Childress to Quanah 69 kV line |  | Goodlett |  | Planned | 1021 - 1199 | AEP TNC | Alison Scribailo mlforcum@aep.com 918-599-2674 | 2783 | 2021-02-28 |  | 69 | 0 | 0 | 0 |  | Hardeman |  | Tier 4 |  |  |  | 60446, 6052, 6053 | Y | N |  | 0 | 49571 | 49570
50896 | Garnet: Build new 138 kV station | Interconnect Norton solar farm on the Ballinger to Oak Creek 138 kV line | Update Contact | Garnet |  | Planned | 1049 - 1222 | AEP TNC | Bryan Oyster mlforcum@aep.com 918-599-2674 | 2824 | 2021-02-28 |  | 138 | 0 | 0 | 0 |  | Runnels |  | Tier 4 |  |  |  | 60451, 6325, 6340 | Y | N |  | 0 | 50897 | 50896
51996 | Rebuild Markham Tap to AEP Markham Tap | Rebuild Markham Tap to AEP Markham Tap with 138 kV capable structures |  | Markham Tap | AEP MarkhamTap | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-02-28 |  | 69 | 0 | 1.5 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 5554, 8984 | Y | N |  | 0 | 51997 | 51996
56012 | PSARCO Fault Duty Upgrade with Bus Reactors | Install (2) 10-Ohm Reactors at PSARCO by splitting PSARCO bus as a fault duty upgrade |  | PSARCO |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-02-28 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 41300, 41305, 40190, 41021, 110579, 110571, 110572, 110573, 110574, 110577 | Y | N |  | 0 | 56103 | 56012
57350 | Lyons to Gay Hill T-line pole change out and reconductor | Replace existing structure with upgraded structures and replace existing 336.4 ACSR Linnet with 795 ACSR Drake on Lyons to Gay Hill transmission line. |  | Lyons | Gay Hill | Planned |  | BBEC | Curtis Fischer curtis.fischer@bluebonnet.coop curtis.fischer@bluebonnet (979) 716-0253 |  | 2021-02-28 |  | 138 | 0 | 11.51 | 0 |  | Burleson | Washington | Tier 4 |  |  |  | 7572, 7573 | Y |  |  | 0 | 57351 | 57350
48288B | BOGGY (BOG) 138kV Substation (SHELL Substation Replacement) | Install new customer-owned BOGGY 138kV substation. Loop from Ckt.85 to create new Ckt.85 DERICK to BOGGY to SHELL |  | BOGGY | DERICK/SHELL | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-02-28 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41460, 40981, 41320, 41380, 41450, 41580, 40089, 41620, 110950, 110951, 110953, 110947, 110948, 110952 | Y | N |  | Cost Included in 48288A | 58108 | 48288
48288C | BOGGY (BOG) 138kV Substation (SHELL Substation Replacement) | Install new customer-owned BOGGY 138kV substation. Loop from Ckt.88 to create new Ckt.88 PAIR to BOGGY to ESBELT |  | BOGGY | PAIR/ESBELT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-02-28 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40530, 41210, 41350, 41370, 41460 | Y | N |  | Cost Included in 48288A | 57334 | 48288
44426 | Foxtail: Add 345 kV reactor | Add new 345 kV reactor at Foxtail |  | Foxtail |  | Planned | 940 - 1118 | AEP TNC | Todd Siegert mlforcum@aep.com 918-599-2674 | 2754 | 2021-02-28 01:00 |  | 345 | 0 | 0 | 0 | -50,0 | Baylor |  | Tier 4 |  |  |  | 6076 | Y | N |  | 0 | 44427 | 44426
51216B | Ward Winkler RPG | Re-terminate existing IH20-Pecos 69kV line to 138kV buses. |  | TNMP IH20 (38040 / 38045) | TNMP Pecos (38090 /38091) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2021-03-01 |  | 138 | 0 | 0 | 0 |  | Reeves | Reeves | Tier 2 | 2019-03-19 | 2019-10-10 |  | 38045, 38091 | Y |  |  | 0 | 56657 | 51216
52284 | This adds a capacitor to Bell County |  |  | BellCounty | BellCounty | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2021-03-01 |  | 69 | 0 | 0 | 0 | 0,16 | Bell | Bell | Tier 4 |  |  |  | 133 | Y |  |  | 0 | 52285 | 52284
49812 |  |  |  | 5945059410 | 79689 |  |  | BPUB | Javier Martinez jamartinez@brownsville-pub.com 956-083-6530 |  | 2021-03-10 |  | 138 | 0 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 5962, 59410, 59450, 79689 | Y |  |  | 0 | 49813 | 49812
6833 | Vineyard 138 kV Switching Station | Establish new 138 kV switching station | Project Deferral | Vineyard Switch |  | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M3211 | 2021-03-15 |  | 138 | 4.2 | 0 | 0 |  | Tarrant | Tarrant | Tier 2 |  |  |  | 2025, 555, 648, 2015, 12013, 2031 | Y | N |  |  | 14635 | 6833
57957 | Construct Copperhead 138 kV Switch | Construct Copperhead 138 kV Switch for new solar interconnection |  | Copperhead Switch |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5288 | 2021-03-15 01:00 |  | 138 | 0 | 0 | 0 |  | Fannin |  | Tier 4 |  |  |  | 11809, 1808, 11808, 143424 | Y | N |  | 0 | 57958 | 57957
47539 | Frelsburg Circuit Breaker Addition | Increase the reliability of transmission facilities on the T176 Fayetteville - Glidden 20.0-mile 138-kV transmission line. LCRA TSC will add three 138-kV, 3000A, 40kAIC circuit breakers in ring-bus configuration next to Frelsburg Substation. |  | Frelsburg Substation | Frelsburg Substation | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-03-16 |  | 138 | 0 | 0 | 0 |  | Colorado | Colorado | Tier 4 |  |  |  | 7263 | Y | N |  | 0 | 47540 | 47539
5218B | San Miguel 345/138 kV autotransformer replacements | Replace T2 300 MVA autos with much larger autos |  | San Miguel |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-03-30 |  | 345 | 0 | 0 | 675 |  | Atascosa |  | Tier 4 |  |  |  | 5909, 5901, 5902 | Y | N |  | Delayed from 2018 to 2019 in the 2016 RTP. | 45091 | 5218
44395 | Dupont SW: Connect 138 kV Gen Tie Line | Connect 138 kV Victoria Port Generation Tie Line into Dupont SW |  | Dupont SW | Rupley | In-Service | 950 - 1128 | AEP TCC | Tommy Vannoy bcogan@aep.com 918-599-2857 | 3714 | 2021-03-30 |  | 138 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  | 88142, 88143, 8143, 8172, 111343 | Y | N |  | 0 | 44396 | 44395
48109 | Dolan Creek: Construct 138 kV Box Bay | Dolan Creek: Construct 138 kV Box Bay |  | Dolan Creek |  | Planned | 930 - 1108 | AEP TCC/PEC | Alison Scribailo bcogan@aep.com 918-599-2857 | 3706 | 2021-03-30 |  | 138 | 0 | 0 | 0 |  | Val Verde | Sutton | Tier 4 |  |  |  | 8991, 88991, 8259, 8261, 72194 | Y | Y |  | 0 | 48147 | 48109
52064 | Bay City - Lane City: 138 kV Line Rebuild | Rebuild the Bay City - Magill - Lane City 138 kV Line |  | Bay City | Lane City | Planned | 1078 - 1251 | AEP TCC | Marc E. Wilson bcogan@aep.com 918-599-2857 | 3803 | 2021-03-30 |  | 138 | 0 | 16 | 0 |  | Matagorda | Wharton | Tier 4 |  |  |  | 8111, 8113, 8127 | Y | N |  | 0 | 52065 | 52064
52688 | Angleton Substation Expansion | Expand Angleton substation for the Myrtle Solar generator interconnection (19INR0041). |  | Angleton |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-03-30 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42110, 111533 | Y | N |  | 0 | 55842 | 52688
5205 | Carrizo Springs-Crystal City 69 kV Line: Rebuild | Rebuild Carrizo Spring to Crystal City 69 kV Line |  | Carrizo Springs | Crystal City | Under Construction | 761-0945 | AEP | Jeremy Brazeal bcogan@aep.com 918-599-2857 | 3569 | 2021-03-31 |  | 69 | 0 | 13.9 | 0 |  | Dimmit | Zavala | Tier 3 | 2017-07-12 | 2017-08-07 | 2017-08-21 | 8244, 8242 | Y | N |  |  | 12864 | 5205
5967 | Burma: Build new 69 kV station | Construct a new 69 kV station near the exsiting Grape Creek tap and reterminate the College Hills to Sterling City and Grape Creek to North San Angelo 69 kV lines into Burma |  | Burma |  | Planned | 845 - 1029 | AEP TNC | John Pulay mlforcum@aep.com 918-599-2674 | 2688 | 2021-03-31 |  | 69 | 0 | 0 | 0 |  | Tom Green |  | Tier 4 |  |  |  | 6416, 60411, 6437, 6460, 6468 | Y | N |  |  | 13682 | 5967
44393 | Zapata: Add 138 kV Reactor | Add 138 kV Reactor at Zapata |  | Zapata |  | Under Construction | 949 - 1127 | ETT | Jeremy Brazeal bcogan@aep.com 918-599-2857 | 3713 | 2021-03-31 |  | 138 | 0 | 0 | 0 | -10,0 | Zapata |  | Tier 4 |  |  |  | 8299 | Y | N |  | 0 | 44394 | 44393
44858 | Luna 138 kV Station | Rayos Del Sol Solar interconnection |  | Mesquite | STEC Rangerville | Planned | 964 - 1142 | AEP TCC | James Weaver bcogan@aep.com 918-599-2857 | 3722 | 2021-03-31 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8656, 88656, 8554, 80103 | Y | N |  | 0 | 44859 | 44858
47434 | Zorn Auto Replacement | Increase the reliability of substation equipment at Zorn Substation through replacement of the Zorn AT1 autotransformer. |  | Zorn | Zorn | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-03-31 |  | 345 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7042 | Y | N |  | 0 | 47435 | 47434
55270 | Stillman: Reterminate two AEP 138 kV lines | Stillman: Reterminate two AEP 138 kV lines |  | PUB Loma Alto | Stillman | Planned | 1036 - 1214 | AEP TCC | William Loveless bcogan@aep.com 918-599-2698 | 3775 | 2021-03-31 |  | 138 | 0 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 5962, 8333, 8337, 79689 | Y | Y |  | 0 | 55271 | 55270
55959 | Crosby to Highlands Ckt.08G Upgrades | Upgrade Crosby to Highlands Ckt.08G as a clearance project |  | Crosby | Highlands | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-03-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40390, 40811 | Y | N |  | 0 | 55960 | 55959
45015 | Barnhart to Cassava: Rebuild 69 kV line | Rebuild the Barnhart to Cassava 69 kV line |  | Barnhart | Cassava | Planned | 942 - 1120 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2756 | 2021-03-31 01:00 |  | 69 | 0 | 6.021 | 0 |  | Irion | Irion | Tier 4 |  |  |  | 6532, 6530, 6537, 60359 | Y | N |  | 0 | 45016 | 45015
45032 | Brant: Build 69 kV station | Construct new 69 kV box bay on the Rock Springs to Sonora 69 kV line |  | Brant |  | Planned | 977 - 1155 | AEP TNC | Michael Glueck mlforcum@aep.com 918-599-2674 | 2762 | 2021-03-31 01:00 |  | 69 | 0 | 0 | 0 |  | Sutton |  | Tier 4 |  |  |  | 60438, 6570, 8239 | Y | N |  | 0 | 45033 | 45032
45155 | Ollin: Build 138 kV station | Construct new Ollin 138 kV station |  | Ollin |  | Planned | 939 - 1117 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2752 | 2021-03-31 01:00 |  | 138 | 0.1 | 0 | 0 |  | Crane |  | Tier 4 |  |  |  | 6600, 6605, 6606, 6668, 6669, 60428, 60429, 60432, 60441, 6604, 6610, 6613, 6607, 6611, 60431, 76615 | Y | N |  | 0 | 45156 | 45155
45506 | Coulomb: Build 345 kV terminal | Interconnect TG East wind farm on the Clear Crossing to Edith Clarke 345 kV line |  | Coulomb |  | Planned | 980 - 1158 | ETT | Michael Macias mlforcum@aep.com 918-599-2674 | 2821 | 2021-03-31 01:00 |  | 345 | 0 | 0 | 0 |  | Hardeman |  | Tier 4 |  |  |  | 60722 | Y | N |  | 0 | 45507 | 45506
3821 | Pearsall to Palo Duro 138 kV line upgrade | Upgrade Pearsall to Palo Duro 138 kV line as recommended in 2013 RTP. Will investigate using a reconductor on existing structures with ACCC and other high temperature conductors. |  | Pearsall | Paloduro | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-04-01 |  | 138 | 0 | 10.8 | 0 |  | Frio | Frio | Tier 4 |  |  |  | 5866, 5895 | Y | N |  |  | 11278 | 3821
50336 | Rebuild Pleasanton to Mccoy | Rebuilds 4/0 ACSR to 795 ACSR on double circuit 138 kV capable poles. NERC assessment and 2019 RTP |  | Pleasanton | McCoy | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-04-01 |  | 69 | 0 | 10.9 | 0 |  | Atascosa | Atascosa | Tier 4 |  |  |  | 5714, 5721 | Y | N |  | 0 | 50337 | 50336
50338 | Rebuild Van Vleck Sw to Bay City | Rebuilds 4/0 ACSR to 795 ACSR on double circuit 138 kV capable poles. NERC assessment |  | Van Vleck Switch | Bay City | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-04-01 |  | 69 | 0 | 1.23 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 5556, 5560 | Y | N |  | 0 | 50339 | 50338
57081 | Elara 138 bus and line to Palo Duro | Adds new Elara station to connect Elara Solar plant and a line to Palo Duro |  | Palo Duro | Elara | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-04-01 |  | 138 | 2.77 | 0 | 0 |  | Frio | Frio | Tier 4 |  |  |  | 5890, 5866 | Y | N |  | 0 | 57082 | 57081
6382 | Stewart Road: Construct 345 kV cut-in | Hairpin the North Edinburg to SU Palmito 345 kV line into new Stewart Rd 345 station. The hairpin will be constructed in a double circuit configuration, approximately 5 miles long. |  | Stewart Road | North Edinburg, SU Palmito | Planned | 874 - 1052 | ETT | Teresea Trotman bcogan@aep.com 918-599-2857 | 3661 | 2021-04-02 |  | 345 | 5 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 2 | 2015-07-10 | 2016-05-19 | 2016-06-14 | 80137, 5966, 8383 | Y | N |  |  | 14126 | 6382
51041 | Rio Pecos: Add bus breakers and bus differential | Add 138 kV bus tie circuit breakers | Update Contact & Cost | Rio Pecos |  | Planned | 1043 - 1216 | AEP TNC | Thomas Neils mlforcum@aep.com 918-599-2674 | 2790 | 2021-04-06 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60452, 60453, 6601, 60014, 76595, 76600, 76615 | Y | N |  | 0 | 51042 | 51041
7077 | Horse Crossing - Rio Pecos Transmission Line Addition | Construct a new 138-kV transmission line to a new radially connected generator-serving substation called Horse Crossing from Rio Pecos using double 795 26/7 ACSR Drake OPGW static. The planned transmission circuit rating will be (MVA): Rate A=439, Rate B=448, Rate C=448. |  | Horse Crossing | Rio Pecos | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018600 | 2021-04-09 |  | 138 | 0.9 | 0 | 0 |  | Crane | Crockett | Tier 4 |  |  |  | 76601, 76602, 6601 | Y | N |  |  | 14909 | 7077
57882 | Add Vancourt POI for Vancourt Solar | Add Vancourt POI for Vancourt Solar at Luna |  | Luna | Vancourt | Planned | 1121 - 1299 | AEP | J Randy Weaver jrweaver@aep.com 918-599-2253 | 3840 | 2021-04-11 |  | 138 | 0.25 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 88657, 8656 | Y |  |  | 0 | 57883 | 57882
5286B | Fayette Area Upgrades | Upgrade existing Plum - Flatonia (T133) TL with a minimum rating of 380 MVA and with OPGW. Upgrade terminal equipment at Plum to achieve a planned static normal and emergency rating of 530 MVA on Piney Creek - Plum (T535). | Planning In-Service Date Change. Updated to a phased project, the original TPIT project number is 5286. | Flatonia | Plum | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1019026, 1019024 | 2021-04-19 |  | 138 | 0 | 19.6 | 0 |  | Fayette | Fayette | Tier 4 | 2017-06-29 | 2017-07-28 |  | 7248, 7274, 7307 | Y | N |  |  | 14584 | 5286
57343 | Rosita Creek Substation 138-kV T2 Power Transformer Addition | Add second 138/12.47-kV power transformer bay with new 138-kV transmission switch and circuit switcher interconnected at LCRA Switch# 12669. New power transformer capacity will be 15/20/25 MVA. | No immediate projected load increase. Justification is to provide backup power source for critical medical center loads and to accommodate potential future load increases. | Pueblo | Escondido | Conceptual |  | RGEC | Larry T. Powell lpowell@rgec.coop 830-563-6178 |  | 2021-04-25 |  | 138 | 0 | 0 | 0 |  | Maverick | Maverick | Tier 4 |  |  |  |  | Y | N |  | 0 | 57344 | 57343
54115 | Lockhart Circuit Breaker Addition | Increase transmission service reliability to the Lockhart Substation. LCRA TSC will install two (2) 4000-A circuit breakers and associated terminal equipment such that Lockhart T2 has breakered connections to both 138-kV operating buses. |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2021-04-27 |  | 138 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  | 7216 | Y | N |  | 0 | 54116 | 54115
47448 | Motorman Substation Addition | Construct a new 138-kV Motorman substation. Motorman Substation is located in west Texas approximately 0.25 miles west of the LCRA TSC Crane East Substation. Construct a 3-breaker ring bus cut in to the existing Crane East to LCRA Crane transmission line. |  | Motorman | Motorman | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-04-28 |  | 138 | 0 | 0 | 0 |  | Crane | Crane | Tier 4 |  |  |  | 7869, 11238, 76615, 11239, 71214 | Y | N |  | 0 | 52822 | 47448
53953 | Eckert - Nebo Transmission Line Overhaul | LCRA TSC will perform an overhaul of T126 with replacement structures that are capable of operating at 138-kV and supporting a single 795 ACSR Drake conductor. The replacement conductor on T126 will be 795 ACSR Drake. This overhaul will include the installation of a 72-count optical ground wire (OPGW). |  | Eckert | Nebo | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2021-04-28 |  | 69 | 0 | 0 | 0 |  | Gillespie | Gillespie | Tier 4 |  |  |  | 7122, 7124 | Y | N |  | 0 | 53954 | 53953
54086 | Fort Mason Circuit Breaker Addition | Provide transmission service to a generator. Upgrade 138-kV ring bus to accommodate new circuit termination. ERCOT Generation Interconnection or Change Request No. 21INR0365. |  | Fort Mason Substation | Fort Mason Substation | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2021-04-28 |  | 138 | 0 | 0 | 0 |  | Mason | Mason | Tier 4 |  |  |  | 76390 | Y | N |  | 0 | 54087 | 54086
6201 | Alice - North Ella 69 kV Line | Rehab Alice - North Ella 69 kV Line |  | Alice | North Ella | Planned | 818 - 1002 | AEP TCC | Joe Yeagler bcogan@aep.com 918-599-2857 | 3614 | 2021-04-30 |  | 69 | 0 | 11.56 | 0 |  | Jim Wells |  | Tier 4 |  |  |  | 8500, 8878 | Y | N |  |  | 13926 | 6201
47432 | LULING - ZORN Transmission Line OverHaul | Increase the reliability of transmission facilities on the T158 Luling - Zorn 28.3-mile 138-kV transmission line. Increase the reliability and capacity of transmission facilities on the T158 Luling - Zorn 28.3-mile 138-kV transmission line. Tear down and rebuild all existing wood structures on the SC section from Seguin split to Luling and replace with 795 ACSR Drake conductor. Add OPGW. |  | Luling | Zorn | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-04-30 |  | 138 | 0 | 0 | 0 |  | Caldwell | Guadalupe | Tier 4 |  |  |  | 7180, 7222, 7224 | Y | N |  | 0 | 47433 | 47432
48784 | Rowe: Construct New Distribution Station | Rowe: Construct New Distribution Station |  | North McAllen | West McAllen | Planned | 1030 - 1208 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3769 | 2021-04-30 |  | 138 | 0 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8041, 8367, 8631 | Y | N |  | 0 | 48785 | 48784
50670 | Angstrom: Add new 345 kV Station | Angstrom: Add new 345 kV Station to serve SDI |  | Angstrom |  | Planned | 1050 - 1223 | AEP TCC | Teresa Trotman bcogan@aep.com 918-599-2857 | 3776 | 2021-04-30 |  | 345 | 0.5 | 0 | 0 |  | San Patricio | Matagorda | Tier 4 |  |  |  | 8249, 5915, 8956 | Y | N |  |  | 50671 | 50670
51645 | Sand Crab: Add New Distribution Station | Sand Crab: Add New Distribution Station |  | Joslin | North Carbide | Planned | 1064 - 1237 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3799 | 2021-04-30 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 8155, 8135, 8140, 8190 | Y |  |  | 0 | 51646 | 51645
52089 | Red Creek: Add new 345 kV terminal | Interconnect Bravepost Solar at the Red Creek 345 kV station |  | Red Creek |  | Planned | 1067 - 1240 | AEP TNC | Michael Glueck mlforcum@aep.com 918-599-2674 | 2828 | 2021-04-30 |  | 345 | 0 | 0 | 0 |  | Tom Green |  | Tier 4 |  |  |  | 6444 | Y | N |  | 0 | 52090 | 52089
55596 | Clear Crossing: Install 345 kV terminal | Install 345 kV terminal at Clear Crossing to interconnect Azure Sky Solar & BESS |  | Clear Crossing |  | Planned | 1097 - 1275 | ETT | Glen Reed gareed@aep.com 918-599-2664 | 1865 | 2021-04-30 |  | 345 | 0 | 0 | 0 |  | Haskell |  | Tier 4 |  |  |  | 60464, 60515 | Y | N |  | 0 | 57651 | 55596
57645 | Hillje 345kV Danish Fields Solar (21INR0069) | Expand Hillje 345kV substation and install one generator lead for new interconnection to Danish Fields Solar |  | Hillje |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-04-30 |  | 345 | 0 | 0 | 0 |  | Wharton |  | Tier 4 |  |  |  |  | Y | N |  | 0 | 57646 | 57645
57752 | West Columbia Roughneck Storage (19INR0176) | Install generator lead from CNP West Columbia substation to customer NORTCO substation for interconnection to Roughneck Battery Storage (19INR0176) |  | West Columbia |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-04-30 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  |  | Y | N |  | 0 | 57753 | 57752
45174 | Ollin to LCRA Crane: Partial build, partial rebuild, and con | Build new Ollin 138 kV station; partial build, rebuild, and conversion to 138 kV of Ollin to LCRA Crane; and rebuild McElroy to Sage | Update Description | Ollin | LCRA Crane | Planned | 939 - 1117 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2767 | 2021-04-30 01:00 |  | 138 | 0.52 | 0 | 0 |  | Crane | Crane | Tier 4 |  |  |  | 6600, 6605, 6606, 6669, 60428, 60429, 60431, 60432, 60441, 6610, 6613, 6668, 76615 | Y | N |  | 0 | 45175 | 45174
45421 | McElroy to Sage: Rebuild 69 kV line | Build new Ollin 138 kV station with a 138/69 kV auto; partial build, rebuild, and conversion to 138 kV of Ollin to LCRA Crane; and rebuild McElroy to Sage |  | McElroy | Sage | Planned | 939 - 1117 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2768 | 2021-04-30 01:00 |  | 69 | 0 | 1.99 | 0 |  | Crane | Crane | Tier 4 |  |  |  | 6604, 6607 | Y | N |  | 0 | 45422 | 45421
47936 | Pleasant Grove Rebuilds | Pleasant Grove Rebuilds |  | Midway (bus 185) | Calvert Switch (bus 73) | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2021-05-01 |  | 69 | 0 | 20.4 | 0 |  | Falls | Milam | Tier 4 |  |  |  | 73, 81, 185 | Y |  |  | 0 | 47937 | 47936
51216C | Ward Winkler RPG | Re-conductor Pecos to Cedarvale (both lines D & E). |  | Pecos (38091) | Cedarvale (38145) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2021-05-01 |  | 138 | 0 | 15.12 | 0 |  | Reeves | Ward | Tier 2 | 2019-03-19 | 2019-10-10 |  | 38091, 38145 | Y |  |  | 0 | 56658 | 51216
51216D | Ward Winkler RPG | Re-conductor TNMP Wink - Oncor Wink 138kV line. Convert existing TNMP Wink - Oncor Wink 69kV line to 138kV. |  | TNMP Wink (37900) | Oncor Wink (1074) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2021-05-01 |  | 138 | 0 | 2.66 | 0 |  | Winkler | Winkler | Tier 2 | 2019-03-19 | 2019-10-10 |  | 1074, 1075, 37900, 37920 | Y |  |  | 0 | 56659 | 51216
51216E | Ward Winkler RPG | Construct two 138kV tie-lines between TNMP Cedarvale and Oncor Sand Lake. |  | TNMP Cedarvale (38145) | Oncor Sand Lake (11097) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2021-05-01 |  | 138 | 1.56 | 0 | 0 |  | Ward | Ward | Tier 2 | 2019-03-19 | 2019-10-10 |  | 11097, 38145 | Y |  |  | 0 | 56660 | 51216
51740 | Buttercup Bus Upgrade | Upgrade the Buttercup bus from operate/transfer to double-bus double-breaker |  | Buttercup |  | Planned |  | PEC | Ryan Morlino ryan.morlino@peci.com 830-868-5166 |  | 2021-05-01 |  | 138 | 0 | 0 | 0 |  | Williamson |  | Tier 4 |  |  |  | 7531 | Y | N |  | 0 | 51750 | 51740
51742 | Pipeline Breaker Addition | Convert existing tap substation to ring bus |  | Pipeline |  | Planned |  | PEC | Ryan Morlino ryan.morlino@peci.com 830-868-5166 |  | 2021-05-01 |  | 138 | 0 | 0 | 0 |  | Williamson |  | Tier 4 |  |  |  | 7390 | Y | N |  | 0 | 51751 | 51742
51744 | Buda Bus Upgrade | Upgrade the Buda bus from operate/transfer to breaker-and-a-half |  | Buda |  | Planned |  | PEC | Ryan Morlino ryan.morlino@peci.com 830-868-5166 |  | 2021-05-01 |  | 138 | 0 | 0 | 0 |  | Hays |  | Tier 4 |  |  |  | 7498 | Y | N |  | 0 | 51752 | 51744
4567 | BRYN_4567_Smetana_to_Leonard | Build Smetana to Leonard Rd 138 line in existing 69KV ROW of old Annex to Atkins line |  | 32897 | 32863 | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2021-05-05 |  | 138 | 0.75 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32853, 32851 | Y |  |  |  | 12149 | 4567
5792 | Leonard Road Substation 138 | Upgrade Leonard Rd from 69kV to 138kV and construct 138 from Leonard to Atkins |  |  |  | Planned |  | BRYN | James Tanneberger jtanneberger@btutilities.com 979-821-5763 |  | 2021-05-05 |  | 138 | 0 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32851, 32862, 32864 | Y |  |  | 0 | 53867 | 5792
47422 | Homestead Substation Addition | Construct a new 138-kV Homestead substation.The Homestead substation will be located approximately ½ mile from the existing Tarbush substation (owned by TNMP) and will include three-PWTs with RGEC distribution (express feeders) to the load. |  | Homestead | Homestead | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-05-05 |  | 138 | 0 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 7868, 38295 | Y |  |  | 0 | 47423 | 47422
07TPIT0050 | Dunlap to Techridge 138kV Circuit Relocation | This project will reroute the existing Ckt 975 Dunlap-Techridge from near the intersection of Howard Lane and Dessau Road to the Techridge substation. The reroute will use 3000 amp bundled 795 ACSS Drake conductor. |  | Dunlap Substation | Techridge Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | PLAN_117_P071 | 2021-05-07 |  | 138 | 0 | 2.7 | 0 |  | Travis | Travis | Tier 2 | 2009-01-26 | 2009-07-21 |  | 9045, 9190 | Y | N |  |  | 8189 | 1013
5939 | Cooks Point Substation and Transmission Line Addition | Construct a load serving 138-kV substation in Northern Burleson County called Cooks Point. Construct a 16.7-mile single circuit 138-kV transmission line from Lyle Wolz to Cooks Point 138-kV transmission line with bundled 795 ACSR Drake (440 MVA). Bryan Texas Utilities will construct a 138-kV transmission line from Steele Store Substation to Cooks Point bundled 1033 ACSR Curlew (495 MVA). |  | Cooks Point | Lyle Wolz | Planned | 6666 | LCRATSC/BBEC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017348 | 2021-05-07 |  | 138 | 16.7 | 0 | 0 |  | Burleson | Burleson | Tier 4 | 2016-07-07 |  |  | 7569, 7567 | Y | N |  |  | 13650 | 5939
54084 | King Mountain Circuit Breaker Addition | Provide transmission service to a generator. Add a 138-kV bay and associated circuit breaker to the existing substation. ERCOT (ERCOT Generation Interconnection or Change Request No. 20INR0226) |  | King Mountain Sub | King Mountain Sub | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2021-05-07 |  | 138 | 0 | 0 | 0 |  | Upton | Upton | Tier 4 |  |  |  | 76635 | Y | N |  | 0 | 54085 | 54084
5277 | Glidden Area Transmission Line Upgrade | Convert existing 69-kV lines (T544) from Glidden to Altair and (T545) from Altair to Nada to 138-kV transmission lines. Relocate existing 45 MVA auto from Glidden to Altair. Add a second new 45 MVA auto at Altair substation. |  | Glidden | Nada | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1016219 | 2021-05-10 |  | 138 | 0 | 0.77 | 45 |  | Colorado | Colorado | Tier 4 |  |  |  | 78107, 78111, 78115, 78118, 78170, 78171, 78520, 5536, 7258, 78103, 78106 | Y | N |  | 0 | 46205 | 5277
54092 | Sheriff's Posse Substation Upgrade | Increase transmission service reliability to the Sheriff¿s Posse Substation. Increase the reliability of substation equipment at the Sheriff¿s Posse Substation. Note: NBU is adding a third power transformer at Sheriff¿s Posse and reconfiguring the substation to a ring bus arrangement. LCRA TSC will complete this project to support the NBU substation reconfiguration. LCRA TSC will ultimately own a section of the ring bus at Sheriff¿s Posse where an existing LCRA TSC transmission line terminates. |  | Sheriff's Posse | Sheriff's Posse | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2021-05-11 |  | 138 | 0 | 0 | 0 |  | Comal | Comal | Tier 4 |  |  |  | 7460 | Y | N |  | 0 | 54093 | 54092
56098 | Turtle Creek Substation Upgrade | LCRA TSC will change the SB/SB configuration to a four-breaker ring bus and replace all three existing CBs (8810, 8820, and 8830) at Turtle Creek Substation. |  | Turtle Creek |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018970 | 2021-05-13 |  | 138 | 0 | 0 | 0 |  | Kerr |  | Tier 4 |  |  |  | 7442 | Y |  |  | 0 | 56099 | 56098
6972 | Dimmit Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Dimmit Substation. |  | Dimmit |  |  |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-05-14 |  | 138 | 0 | 0 | 0 |  | Dimmit |  | Tier 4 |  |  |  | 78281 | Y | N |  |  | 14789 | 6972
6978 | Ranch Road 12 Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Ranch Road 12 Substation. |  | Ranch Road 12 |  | Planned | 1018923 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018923 | 2021-05-14 |  | 138 | 0 | 0 | 0 |  | Hays |  | Tier 4 |  |  |  | 7186 | Y | N |  |  | 14795 | 6978
7115 | Quarry Field - Kyle Ranch 138 kV Line | Quarry Field - Kyle Ranch 138 kV Line |  | Quarry Field | Kyle Ranch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8384 | 2021-05-14 |  | 138 | 12 | 0 | 0 |  | Loving |  | Tier 4 |  |  |  | 11089, 11189 | Y |  |  |  | 14951 | 7115
45573 | Hayter Ranch Substation Addition | Construct a new 138-kV Hayter Ranch substation. The Hayter Ranch Substation will be located on the Alamito Creek to Solstice 138-kV transmission line. The total length of the line is 68.12 miles and the Hayter Ranch substation will be approximately 8.5 miles from Solstice. |  | Alamito Creek | Solstice | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2021-05-14 |  | 138 | 0 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 78925, 60444 | Y | N |  | 0 | 45574 | 45573
47034 | Gabriel- Rivery Transmission Line Storm Hardening | Overhaul and upgrade the 138-kV Gabriel - Rivery transmission line with bundled 795 ACSR capable structures, bundled 795 ACSR conductor (440 MVA), and OPGW static. |  | Gabriel | Rivery | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-05-14 |  | 138 | 2.4 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 7346, 7347 | Y | N |  | 0 | 47035 | 47034
47513 | Pooley Road Circuit Breaker Addition | LCRA TSC will convert Pooley Road Substation to ring bus configuration by installing three 138-kV, 3000A, 40kAIC circuit breakers. |  | Pooley Road Substation | Pooley Road Substation | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-05-14 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7222 | Y | N |  | 0 | 47514 | 47513
50452 | LCRATSC_Clear Springs AT1 | Replacing the failed Auto-transformer with like and kind Auto-transformer. |  | Clear Springs | Clear Springs | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-05-14 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 77683 | Y | N |  | 0 | 50453 | 50452
5408 | Herty N Sw. Sta. 138 kV Rebuild | Rebuild existing 138 kV switching station, it will be named Redland Switch after the completion of the project | Project Deferral | Herty North | Herty North | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6069 | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Angelina | Angelina | Tier 4 |  |  |  | 3317, 3319 | Y | N |  |  | 13094 | 5408
5491 | Whitestone - Leander 138kV Transmission Line Upgrade | Upgrade the Whitestone - Blockhouse (T469) and the Blockhouse - Leander (T326) 138kV Line to 441MVA. |  | Whitestone | Leander | Under Construction |  | PEC | Charles Dewitt Charles.Dewitt@peci.com (830) 868-5041 |  | 2021-05-15 |  | 138 | 0 | 5.4 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 7525, 7527, 7529 | Y | N |  | 0 | 51769 | 5491
44944 | Burnet-Bertram-Andice 138kV Conversion | Rebuild Burnet to Bertram to Andice 69 kV line and convert to 138 kV. |  | Burnet | Andice | Under Construction |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 |  | 2021-05-15 |  | 138 | 0 | 21.9 | 0 |  | Burnet | Williamson | Tier 3 |  |  |  | 7520, 7521, 7097, 7100, 7522 | Y | N |  | 0 | 51770 | 44944
47450 | Naruna Circuit Breaker Addition | LCRA TSC will increase the reliability of transmission facilities along T219 Burnet - Lampasas by adding three 138-kV, 3000A, 40kAIC circuit breakers in a ring bus configuration at Naruna Substation. |  | Naruna | Naruna | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Lampasas | Lampasas | Tier 4 |  |  |  | 7063 | Y | N |  | 0 | 47451 | 47450
51228B | Construct Kennedale 138 kV Substation and Burleson 138 kV Sw | Construct Burleson 138 kV Sw |  | Burleson |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5294 | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Tarrant |  | Tier 4 |  |  |  | 1967, 1969, 2205, 2209, 12205 | Y |  |  | 0 | 52342 | 51228
52062 | Blackjack Creek POI | Blackjack Creek: Install POI for new Blackjack Creek WF |  | Grissom | Blackjack Creek | Planned | 1075 - 1248 | AEP TCC | Darren O'Hare bcogan@aep.com 918-599-2857 | 3800 | 2021-05-15 |  | 345 | 0 | 0 | 0 |  | Bee |  | Tier 4 |  |  |  | 88670, 8624 | Y | Y |  | 0 | 52063 | 52062
52151 | Upgrade Elkton - Tyler Switch 138 kV Line | Upgrade Elkton - Tyler Switch 138 kV Line |  | Elkton | Tyler | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6079 | 2021-05-15 |  | 138 | 0 | 5.3 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3106, 3107, 3196, 3197 | Y |  |  | 0 | 52152 | 52151
52253 | Wink Switch 138 kV Terminal Addition | Add a 138 kV terminal at Wink Switch |  | Wink |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8503 | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Winkler |  | Tier 4 | 2019-03-01 | 2019-09-01 | 2019-10-01 | 1074 | Y |  |  | 0 | 52254 | 52253
52255 | Sand Lake Switch 138 kV Terminal Addition | Add 2-138 kV terminals at Sand Lake Switch |  | Sand Lake |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8504 | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Ward |  | Tier 4 | 2019-03-01 | 2019-09-01 | 2019-10-01 | 11097 | Y |  |  | 0 | 52256 | 52255
52295 | Natural Dam 138 kV Switch | Upgrade the existing 138 kV Switch |  | Natural Dam | Natural Dam | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8308 | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Howard | Howard | Tier 4 |  |  |  | 11355, 11322, 11331, 23836 | Y |  |  | 0 | 52347 | 52295
52303 | Quarry Field 345/138 kV Switch | Construct a new 345/138 kV Switch |  | Quarry Field | Quarry Field | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8481 | 2021-05-15 |  | 345 | 0 | 0 | 0 |  | Loving | Loving | Tier 3 |  |  |  | 11188, 11194, 11216, 11010, 11084, 11189 | Y |  |  | 0 | 52494 | 52303
52309 | Horseshoe Springs Switch - Riverton Switch 138 kV Second Cir | Install a 2nd circuit on existing 138 kV structures |  | Horseshoe Springs | Riverton | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8526, R8452 | 2021-05-15 |  | 138 | 0 | 55 | 0 |  | Culberson | Reeves | Tier 3 |  |  |  | 11266, 11267, 11268, 11269, 11271, 11272, 11083, 11090, 11112, 11183, 11190 | Y |  |  | 0 | 56599 | 52309
52827 | Keller Wall Price 138 kV Capacitor Banks | Upgrade the existing 138 kV capacitor banks at Keller Wall Price |  | Keller Wall Price |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5223 | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Tarrant |  | Tier 4 |  |  |  | 2037, 2038 | Y |  |  | 0 | 52828 | 52827
54098 | Warda Winchester - Transmission Line Upgrade | Increase the transmission capacity of T170: Warda ¿ Winchester 138-kV transmission circuit. LCRA TSC will upgrade T170: Warda - Winchester transmission line to a minimum 105 degree F ambient temperature rating of 580 MVA at 138-kV using single 1433 Merrimack ACSS conductor with OPGW fiber addition. |  | Warda | Winchester | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Fayette | Fayette | Tier 4 |  |  |  | 7306, 7312 | Y | N |  | 0 | 54099 | 54098
54436 | Kent Street Substation Upgrade | LCRA TSC will remove the capacitor bank at the Buttercup Substation, and add a new capacitor bank to the Kent Street Substation. |  | Kent Street |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Williamson |  | Tier 4 |  |  |  | 7530, 7531 | Y | N |  | 0 | 54437 | 54436
57165 | Red Gate138/69 autotransformer and lines to McCook and Faysv | Adds 69 kV bus at Red Gate, a 138/69 autotransformer at Red Gate, and connects 69 kV lines to McCook#1 and Faysville Switch. |  | Redgate | McCook and Faysville Switch | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-05-15 |  | 69 | 1 | 0 | 50 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 5780, 5782, 5783, 8377, 161031 | Y | N |  | 0 | 57166 | 57165
57754 | Install Quinlan Tap 138/69 kV Autotransformer | Install Quinlan Tap 138/69 kV Autotransformer |  | Quinlan Tap |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M3058 | 2021-05-15 |  | 138 | 0 | 0 | 47 |  |  |  | Tier 4 |  |  |  | 12729, 2471, 6583, 6665, 7046, 12470, 60708, 60710, 60618, 60621, 76003, 76583, 76668, 2729 | Y |  |  | 0 | 57755 | 57754
57857 | Ennis West Switch 138 kV Reconfiguration | Reconfigure existing 138 kV Switch |  | Ennis West |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4311 | 2021-05-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | Y |  |  | 0 | 57858 | 57857
6792 | Anna - Anna Tap 138 kV Line | Upgrade existing Anna Switch - Anna Tap 138 kV Line |  | Anna Switch | Anna Tap | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4314 | 2021-05-15 01:00 |  | 138 | 8.3 | 8.3 | 0 |  | Collin | Collin | Tier 3 |  |  |  | 12705, 2340, 2374, 2520, 2528, 2704, 12704 | Y | N |  | 0 | 49821 | 6792
49834 | Fullerton 138 kV Switch Terminal Addition | Fullerton 138 kV Switch Terminal Addition |  | Fullerton | Fullerton | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9037 | 2021-05-15 01:00 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 1274, 11275, 1272, 11274, 11284 | Y |  |  | 0 | 49835 | 49834
45541 | Watermill Switch - Camp Wisdom 138 kV Line | Upgrade the Camp Wisdom - Witt Road 138 kV Line Section |  | Camp Wisdom | Witt Road | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4216 | 2021-05-15 12:00 |  | 138 | 0 | 6.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2988, 2989, 12990, 2990, 3068 | Y |  |  | 0 | 52172 | 45541
45545 | Norwood Switch - Denton Drive 138 kV DCKT Line | Upgrade the Norwood Switch - Denton Drive 138 kV DCKT Line |  | Norwood Switch | Denton Drive Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | m4245 | 2021-05-15 12:00 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2405, 2407, 2488, 2796, 2797, 12487, 2487, 2800, 2801 | Y |  |  | 0 | 45546 | 45545
49841 | Fullerton_to_NorthAndrews_138_kV_Conversion_East | Fullerton_to_NorthAndrews_138_kV_Conversion_East |  | Fullerton | North Andrews | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9038 | 2021-05-16 |  | 138 | 0 | 0 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 1285, 1159, 1160, 11274, 11275 | Y |  |  | 0 | 49842 | 49841
49858 | Fullerton_to_NorthAndrews_138_kV_Conversion_West | Fullerton_to_NorthAndrews_138_kV_Conversion_West |  | Fullerton | North Andrews | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9039 | 2021-05-17 |  | 138 | 0 | 0 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 1160, 1267, 1270, 11274, 1159, 1272, 11275 | Y |  |  | 0 | 49859 | 49858
6984 | Rim Rock - Turtle Creek Transmission Line Storm Hardening | Overhaul and upgrade the 138-kV Rim Rock - Turtle Creek transmission line supporting circuit T270 with single 795 ACSR capable structures, single 795 ACSR conductor, and OPGW static. The planned T270 circuit rating is (MVA): Rate A=220, Rate B=220, Rate C=220. |  | Rim Rock | Turtle Creek | Planned | 1018968 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018968 | 2021-05-21 |  | 138 | 0 | 7.6 | 0 |  | Kerr | Kerr | Tier 4 |  |  |  | 7143, 7442 | Y | N |  |  | 14801 | 6984
43284D | Baytown Area Upgrades | Upgrade portions of reconfigured Ckt.87 SR Bertron to TEXAS to increase thermal ratings |  | SR Bertron | TEXAS | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-28 |  | 138 | 0 | 0.99 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41405, 41540 | Y | N |  | 0 | 56065 | 43284
50658 | Upgrade Friendswood - Mustang Bayou ckt 04 to 440/525 MVA | Upgrade 138kV Ckt.04 Friendswood tap to Mustang Bayou to increase thermal ratings. |  | Friendswood Tap | Mustang Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-28 |  | 138 | 0 | 2.19 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42652, 42960 | Y | N |  | 0 | 50816 | 50658
4186F | University Area 138kV Conversions | Disconnect Ckt.12B and Ckt.30A at University and Reconnect 69kV circuits to create New Ckt.xx GENRAL to Garden Villas |  | Garden Villas | Genral | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1123 | 2021-05-30 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47755, 42690, 47560, 47670, 47762 | Y | N |  | Cost included in Phase D | 57373 | 4186
5717 | Waller 138kV Substation Reconfiguration | Convert Waller substation from single-circuit radial service to radial & tap service. Install new tap section from Ckt.65 Hockley to Peters. |  | Waller | Hockley/Peters | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-30 |  | 138 | 2.4 | 0 | 0 |  | Harris | Austin | Tier 4 |  |  |  | 46561, 46560, 45885, 46220 | Y | N |  |  | 13459 | 5717
6325 | Install two distribution transfomers at Jones Creek | Install two distribution transformers at Jones Creek. Tap Ckt.59 Jones Creek to Freeport/Surfside and Ckt.59 Jones Creek to CORTEZ |  | Jones Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-30 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42546, 42547, 42541, 42542, 42645, 43440 | Y | N |  | 0 | 51031 | 6325
6668A | Freeport - Master Plan | Upgrade Ckts. 18 & 27 DOW to Jones Creek to increase thermal limits |  | DOW | Jones Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-30 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 1 |  |  | 2017-12-12 | 42500, 42530 | Y | N |  | 0 | 58255 | 6668
43284F | Baytown Area Upgrades | Upgrade Ckt.87 TEXAS to Cedar Bayou tap to increase thermal ratings |  | TEXAS | Cedar Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-30 |  | 138 | 0 | 3.91 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40011, 40015, 41540 | Y | N |  | 0 | 56061 | 43284
43511 | Keystone Capbank in TNMP West Texas System | Transfer West Texas spare 69kV 10MVar capacitor bank to Keystone Substation. Project delayed. |  | East Toyah (Bus #38129) | Keystone (Bus #38290) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2021-05-30 |  | 69 | 0 | 0 | 0 | 0,10 | Reeves | Winkler | Tier 4 |  |  |  | 38290 | Y |  |  | 0 | 48418 | 43511
52181 | ENCO (ENC) 138kV Substation | Install new customer-owned 138kV ENCO (ENC) substation. Loop into existing Ckt.91A between PH Robinson and El Dorado |  | ENCO |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-30 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47780, 42015, 42561 | Y | N |  | 0 | 52182 | 52181
52197B | Jordan Auto A3 Addition (PLACID 138kV Sub) | Loop Ckt 97C-1 Chambers-King into Jordan 345kV |  | Chambers | King | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointe 713-207-2760 |  | 2021-05-30 |  | 345 | 0 | 0 | 0 |  | Chambers | Harris | Tier 3 | 2019-10-24 | 2019-11-18 |  | 40255, 40850, 40900 | Y | N |  | Cost included in Phase A | 57346 | 52197
52555 | Wallis to East Bernard Ckt.65C Upgrades | Upgrade Ckt.65C Wallis to East Bernard to increase thermal limits. |  | East Bernard | Wallis | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-30 |  | 138 | 0 | 8.17 | 0 |  | Wharton | Austin | Tier 4 |  |  |  | 44190, 44740 | Y | N |  | 0 | 52556 | 52555
4186D | University Area 138kV Conversions | Remove University Auto A1 from service |  | University |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1123 | 2021-05-30 |  | 138 | 0 | 0 | 0 | -200,0 | Harris |  | Tier 4 |  |  |  | 49030, 47755, 47760 | Y | N |  | Cost included in 4186A | 57371 | 4186
6022 | Stamford to Haskell Tap 1 69 kV line: Rebuild 69 kV line | Rehab Stamford to Haskell Tap 1 69 kV line |  | Stamford | Haskell Tap 1 | Planned | 786 - 0971 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2668 | 2021-05-31 |  | 69 | 0 | 12.22 | 0 |  | Jones | Haskell | Tier 4 |  |  |  | 6171, 6172 | Y | N |  |  | 13739 | 6022
6029 | Anson to Stamford 69 kV line: Rebuild 69 kV line | Rehab Anson to Stamford 69 kV line |  | Anson | Stamford | Planned | 786 - 0971 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2667 | 2021-05-31 |  | 69 | 0 | 16.08 | 0 |  | Jones | Jones | Tier 4 |  |  |  | 6173, 6175, 6172, 6180 | Y | N |  |  | 13753 | 6029
6573 | Reconductor Dunlavey to Heights Ckt. 31 | Reconductor the Dunlavy to Heights as identified in the 2015 RTP case |  | Dunlavy | Heights | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 69 | 0 | 2.4 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47581, 47682, 47580, 47680 | Y | N |  | 0 | 50777 | 6573
43284G | Baytown Area Upgrades | Upgrade Ckt.87 Cedar Bayou to Cedar Bayou tap to increase thermal ratings |  | Cedar Bayou | Cedar Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 2.39 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40011, 40015 | Y | N |  | Overall cost for 2020 project included in 6585E | 56060 | 43284
43454 | Gable Street Reconfigurations | Add 69kV breaker at Gable Street to mitigate P2 contingency load loss |  | Gable Street | Gable Street | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47640 | Y |  |  | 0 | 51311 | 43454
46938 | McCreeAdds600MVAAuto2 | McCreeAdds600MVAAuto2 |  | McCree | McCree | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2021-05-31 |  | 345 | 0 | 0 | 600 |  | Dallas | Dallas | Tier 4 |  |  |  | 983, 973, 834 | Y | N |  | 0 | 46939 | 46938
48774 | Fincas: Construct New Distribution Station | Fincas: Construct New Distribution Station |  | Gateway Tap West | Wormser | Planned | 1026 - 1204 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3765 | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Webb | Webb | Tier 4 |  |  |  | 8039, 8295, 8650 | Y | N |  | 0 | 48775 | 48774
48780 | Pantera: Construct New Distribution Station | Pantera: Construct New Distribution Station |  | Wesmer | Weslaco SW | Planned | 1027 - 1205 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3766 | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8033, 8347, 8348 | Y | N |  | 0 | 48781 | 48780
49576 | Hayter: Build 138 kV box bay | Construct new 138 kV box bay on the Alamito Creek to Solstcie 138 kV line | Updated Contact | Hayter |  | Planned | 1025 - 1203 | AEP TNC | Michael Glueck mlforcum@aep.com 918-599-2674 | 2788 | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 6680, 60385, 60444 | Y | N |  | 0 | 49577 | 49576
52068 | Pleasanton to Three Rivers: Rebuild 69 kV line | Rebuild Pleasanton to Three Rivers 69 kV line |  | Pleasanton | Three Rivers | Planned | 1077 - 1250 | AEP TCC | Nathan Cowan bcogan@aep.com 918-599-2857 | 3802 | 2021-05-31 |  | 69 | 0 | 0.06 | 0 |  | Atascosa | Live Oak | Tier 4 |  |  |  | 8200, 8400, 8406, 8507, 8600 | Y | N |  | 0 | 52069 | 52068
52141 | Cedar Bayou 138kV - West Bus In-Series 10-Ohm Reactor | Cedar Bayou 138kV - West Bus In-Series 10-Ohm Reactor |  | Cedar Bayou | Cedar Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  | 40015, 40020 | Y | N |  | 0 | 52142 | 52141
52167B | El Dorado 10.8 MVar Cap Bank | Install old harrisburg cap bank at El Dorado (Electrically connected to Ckt.91) |  | El Dorado/Harrisburg |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 | 0,10.8 | Harris |  | Tier 4 |  |  |  | 42561 | Y | N |  | 0 | 55385 | 52167
52173 | Spencer 7.2MVar Cap Bank | Install Spencer 7.2MVar Distribution Cap Bank (Electrically connected to Ckt.91) |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 | 0,7.2 | Harris |  | Tier 4 |  |  |  | 43272 | Y | N |  | 0 | 52174 | 52173
52197E | Jordan Auto A3 Addition (PLACID 138kV Sub) | Upgrade Ckt.86J Bender to Jordan to increase thermal limits. |  | Bender | Jordan | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointe 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2019-10-24 | 2019-11-18 |  | 40155, 40856, 40855 | Y | N |  | 0 | 57349 | 52197
52197A | Jordan Auto A3 Addition (PLACID 138kV Sub) | Install 800 MVA Jordan Auto A3 |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointe 713-207-2760 |  | 2021-05-31 |  | 345 | 0 | 0 | 800 |  | Chambers | Chambers | Tier 3 | 2019-10-24 | 2019-11-18 |  | 49079, 40850, 40855 | Y | N |  | 0 | 57345 | 52197
52519C | Jones Creek Area Reconfigurations | Unbundle existing Ckt.02G Velasco to Jones Creek to create parallel circuits Ckt.02G and Ckt.36y Velasco to Jones Creek. This project entry is for Ckt.36y. Reconnect existing Jones Creek cap bank #2 to this line position (Should be installed as fixed 120MVAr cap bank #2). Reconnect existing Jones Creek cap bank #1 to the 48JCKCTZ line position at Jones Creek (Should be installed as switched 160MVAr cap bank #1). |  | Velasco | Jones Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42541, 42542, 42540, 42546, 42547, 43360 | Y | N |  | Cost included in Phase A. | 52522 | 52519
52519B | Jones Creek Area Reconfigurations | Unbundle existing Ckt.02G Velasco to Jones Creek to create parallel circuits Ckt.02G and Ckt.36y Velasco to Jones Creek. This project entry is for Ckt.02G. Existing Jones Creek fixed cap bank #3 will remain on this line with no expected change in capacity. |  | Velasco | Jones Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42543, 43360 | Y | N |  | Cost Included in Phase A. | 52521 | 52519
52519A | Jones Creek Area Reconfigurations | Reconfigure existing Ckt.02H COPPER to Velasco to create new Ckt.36x COPPER to Jones Creek. |  | Copper | Jones Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42195, 42215, 42540, 43211, 43360, 43222, 48006 | Y | N |  | 0 | 52520 | 52519
52529 | Jordan to Cities to Dalton Ckt.86I |  |  | Jordan | Dalton | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  | 40340, 40855, 40740, 40857 | Y | N |  | 0 | 52530 | 52529
53854 | Avenger: Build 69 kV station | Construct new 69 kV station on the Putnam to Cross Plains 69 kV line |  | Avenger |  | Planned | 1084 - 1257 | AEP TNC | Michael Glueck mlforcum@aep.com 918-599-2674 | 1854 | 2021-05-31 |  | 69 | 0 | 0 | 0 |  | Callahan |  | Tier 4 |  |  |  | 60457, 6312, 6357 | Y | N |  | 0 | 53855 | 53854
55628 | Rio Hondo: Upgrade 138 kV terminal | Upgrade 138 kV STEC East Rio Hondo terminal at Rio Hondo |  | Rio Hondo |  | Planned | 1103 - 1281 | AEP TCC | Bill Roberts bcogan@aep.com 918-599-2857 | 3821 | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8319 | Y |  |  | 0 | 55629 | 55628
55630 | Lobo: Install 345 kV terminal | Install terminal at Lobo to interconnect Corazon Solar, build 345 kV line from Lobo to Corazon Solar |  | Lobo | Corazon Solar | Planned | 1098 - 1214 | ETT | Adam Wells bcogan@aep.com 918-599-2857 | 3775 | 2021-05-31 |  | 345 | 4.5 | 0 | 0 |  | Webb | Webb | Tier 4 |  |  |  | 80599, 80219 | Y | Y |  | 0 | 55631 | 55630
55789 | Rebuild 138 kV line from Big Foot to Moore SW | Big Foot to Moore SW: Rebuild 138 kV line |  | Big Foot | Moore | Planned | 1108 - 1286 | AEP TCC/STEC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3828 | 2021-05-31 |  | 138 | 0 | 6.09 | 0 |  | Frio | Frio | Tier 2 | 2019-11-19 | 2020-04-19 |  | 8221, 5827 | Y | Y |  | 0 | 55790 | 55789
55957 | COUGAR to Gulfgate Ckt.91 Upgrades | Upgrade Ckt.91 COUGAR to Gulfgate tap to minimum 478MVA emergency rating |  | COUGAR | Gulfgate | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42741, 47560 | Y | N |  | 0 | 55958 | 55957
55963 | Pearland 40 MVAr Cap Bank | Install Pearland 40 MVAr Cap Bank tapped on Ckt.06K |  | Pearland |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 | 0,40 | Brazoria |  | Tier 4 |  |  |  | 43051 | Y | N |  | 0 | 55964 | 55963
57514 | Jeanetta Auto A1 Upgrade | Upgrade Jeanetta Auto A1 |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 345 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47300, 47310, 49024 | Y | N |  | 0 | 57515 | 57514
57518A | Wortham 138kV Distribution Substation | New Ckt.21G CAMRON to Wortham tap to TH Wharton. |  | Wortham | CAMRON/TH Wharton | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45102, 45515, 45700 | Y | N |  | 0 | 57520 | 57518
57518B | Wortham 138kV Distribution Substation | New Ckt.76A Gertie tap to Wortham tap to Satsuma tap |  | Wortham | Gertie/Satsuma | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45101, 45802, 46302 | Y | N |  | 0 | 57519 | 57518
57534A | Heights and White Oak Upgrades | Install New 200MVA White Oak 138-69kV Auto A4. |  | White Oak |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 200 |  | Harris |  | Tier 4 |  |  |  | 49021, 46615, 46620 | Y | N |  | 0 | 57535 | 57534
57534B | Heights and White Oak Upgrades | Upgrade Ckt.34A Heights - White Oak |  | Heights | White Oak | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 46620, 47680 | Y | N |  | 0 | 57536 | 57534
57642A | Hayes Ckt.09A Loop Upgrade | Upgrade Ckt.09A Britmoore to Hayes to increase thermal limits |  | Britmoore | Hayes | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0.1 | 0 |  |  |  | Tier 4 |  |  |  | 44120, 44310 | Y | N |  | 0 | 57644 | 57642
57647 | Hillje 345kV Ramsey Solar (20INR0130) | Expand Hillje 345kV substation and install one generator lead for new interconnection to Ramsey Solar. Reposition existing Ckt.72 Hillje to Bailey |  | Hillje |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 345 | 0 | 0 | 0 |  | Wharton |  | Tier 4 |  |  |  |  | Y | N |  | 0 | 57648 | 57647
57859 | West Galveston New Distribution Transformer | Install 3rd distribution transformer at West Galveston substation. Tap from Ckt.01B to create new Galveston 26th Street to West Galveston tap to Webster |  | West Galveston | Galveston 26th Street/Webster | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 43403, 42670, 43500, 43400, 43401 | Y | N |  | 0 | 57860 | 57859
57642B | Hayes Ckt.09A Loop Upgrade | Upgrade Ckt.09A Hayes to Alief to increase thermal limits |  | Hayes | Alief | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0.1 | 0 |  |  |  | Tier 4 |  |  |  | 44020, 44310 | Y | N |  | Cost included in main entry | 57643 | 57642
4323 | CPSE_Braunig to Brooks_MLSE | Upgrade terminal at Brooks and ensure a rating of 2000 A (minimum) at both Braunig and Brooks terminals |  | Braunig | Brooks | In-Service |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0669 | 2021-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5030, 5045 | Y | Y |  |  | 11875 | 4323
4895 | CPSE_Capitol Cement Transmission Reconfiguration | Re-configurate Capitol Cement by loop into the existing Dresden to Skyline 138 kV transmission line and removing the existing Captiol Cement to Tuttle 138 kV transmission line. |  | Capitol Cement | Dresden/Skyline | Planned | S-0767 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0246 | 2021-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5075, 5130, 5370, 5435 | Y | N |  |  | 12507 | 4895
5417 | Buckeye to LA_HTS Rebuild | Rebuild 1.8 mile 138 kV t-line from Buckeye to LA_Hts. Upgrade line terminal at Buckeye Station for Buckeye to LA_HTS t-line. |  | Buckeye | LA_Hts | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0266, S-0899a | 2021-06-01 |  | 138 | 0 | 1.8 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5050, 5285 | Y |  |  |  | 13105 | 5417
6281 | CPSE_Harlandal_Sommers_MLSE | Upgrade terminals at Harlandale and Sommers Substation. | [5 empty] | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0732 | 2021-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5190, 5395 | Y |  |  |  | 14013 | 6281
6931 | New Tres Lagos Substation | Adds new station and short line from W Edinburg-Alton line |  | West Edinburg | Alton | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-06-01 |  | 138 | 1.8 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 5770, 5771, 5772 | Y | N |  |  | 14750 | 6931
44963 | USAA Rebuild 138 kV Station | CPSE_USAA 138 kV Substation Rebuild and Line Reconfiguration. |  |  |  | Planned | S-0896 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0285 | 2021-06-01 |  | 138 | 0.6 | 0 | 0 |  | Bexar | Bexar | Tier 4 | 2019-01-10 |  |  | 5450, 5451, 5452, 5125, 5170, 5208, 5300, 5453 | Y |  |  | 0 | 44964 | 44963
45125 | Quintana Rd to South San Rebuild | Rebuild 1.3 miles of 138 kV transmission line form Quintana Rd substation to South San substation. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0271 | 2021-06-01 |  | 138 | 0 | 1.29 | 0 |  | Bexar | Bexar | Tier 4 | 2019-01-15 |  |  | 5350, 5385 | Y |  |  | 0 | 45126 | 45125
50643 | CPSE_Spruce_Skyline MLSE | Upgrade terminals at Spruce and Skyline to ensure a 3000 A rating (minimum). |  | Skyline | Spruce | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0899b/S-0899c | 2021-06-01 |  | 345 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5371, 5400 | Y |  |  | 0 | 50644 | 50643
52245 | CONSTRUCT OGALLALA TO BLACKWATER DRAW 345 KV LINE | REBUILD ABERNATHY SW AND RENAME BLACKWATER DRAW. CONSTRUCT OGALLALA TO BLACKWATER 345 KV LINE, LPL INTEGRATION |  | OGALLALA | BLACKWATER DRAW | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R3002, R3003, R3005 | 2021-06-01 |  | 345 | 0 | 0 | 0 |  | Castro | Hale | Tier 1 | 2015-12-29 | 2016-06-09 |  | 23920, 23912 | Y |  |  | 0 | 52246 | 52245
50672 | Black Cat: New 138 kV Distribution Station | Black Cat: In & Out capable bus with manual bus tie switch for double bank station |  | Bay City | Conoco | Planned |  | AEP TCC | Nathan Cowan bcogan@aep.com 918-599-2857 |  | 2021-06-02 |  | 138 | 0 | 0 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 80124, 8547, 8549, 8113, 8114 | Y | N |  |  | 50673 | 50672
52258 | CONSTRUCT BLACKWATER DRAW TO FOLSOM POINT345 KV LINE | CONSTRUCT FOLSOM POINT SWITCH AND BLACKWATER DRAW TO FOLSOM POINT 345 KV LINE, LPL INTEGRATION |  |  |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R3007, R3011 | 2021-06-02 |  | 345 | 23.3 | 0 | 0 |  | Hale | Lubbock | Tier 1 | 2015-12-29 | 2016-06-09 |  | 23926, 23920, 59156 | Y |  |  | 0 | 52259 | 52258
52299 | CONSTRUCT BLACKWATER DRAW TO DOUBLE MOUNTAIN | CONSTRUCT DOUBLE MOUNTAIN SWITCH AND BLACKWATER DRAW TO DOUBLE MOUNTAIN 345 KV LINE, LPL INTEGRATION |  | BLACKWATER DRAW | DOUBLE MOUNTAIN | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R3001, R3008 | 2021-06-03 |  | 345 | 33 | 0 | 0 |  | Hale | Lubbock | Tier 1 | 2015-12-29 | 2016-06-09 |  | 23928, 23920, 59178 | Y |  |  | 0 | 52300 | 52299
52307 | CONSTRUCT DOUBLE MOUNTAIN TO FIDDLEWOOD TO FARMLAND 345 KV L | CONSTRUCT FIDDLEWOOD SWITCH AND DOUBLE MOUNTAIN TO FIDDLEWOOD TO FARMLAND 345 KV LINE, LPL INTEGRATION |  | DOUBLE MOUNTAIN | FARMLAND | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R3004, R3006, R3009, R3010 | 2021-06-04 |  | 345 | 49.3 | 0 | 0 |  | Lubbock | Lynn | Tier 1 | 2015-12-29 | 2016-06-09 |  | 23930, 23924, 23928, 59196 | Y |  |  | 0 | 52308 | 52307
52570 | INSTALL 75MVAR REACTOR |  |  | DOUBLE MOUNTAIN | DOUBLE MOUNTAIN | Planned |  | ONCOR | CHARLES SAKER | R3016 | 2021-06-05 |  | 345 | 0 | 0 | 0 | -75,0 | Lubbock | Lubbock | Tier 4 |  |  |  | 23928 | Y |  |  | 0 | 52571 | 52570
52587 | INSTALL 75MVAR REACTOR |  |  | FIDDLEWOOD | FIDDLEWOOD | Planned |  | ONCOR | CHARLES SAKER | R3017 | 2021-06-05 |  | 345 | 0 | 0 | 0 | -75,0 | Lubbock | Lubbock | Tier 4 |  |  |  | 23930 | Y |  |  | 0 | 52588 | 52587
57904 | Brightside Temporary Connection | Build Brightside Temporary Connection | NEW | Beeville | Three Rivers | Planned | 1113 - 1291 | AEP TCC | Nathan Cowan bcogan@aep.com 918-599-2674 | 3832 | 2021-06-11 |  | 138 | 0 | 0 | 0 |  | Bee | Live Oak | Tier 4 |  |  |  | 84006, 8199, 8400 | Y | N |  | 0 | 57905 | 57904
54757 | This is related to GINR20INR0083 | This is a switching station to interconnect new generation project 20INR0083 Baird North Wind Project |  |  |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2021-06-15 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 68008, 68006, 68010 | Y |  |  | 0 | 54758 | 54757
55873 | Upgrade Moore to Hondo Creek 138 kV line | Replace the 336 ACSR with 1020 ACCC conductor while keeping the existing structures that still meet our standards. |  | Moore | Hondo Creek | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-06-15 |  | 138 | 0 | 13.5 | 0 |  | Medina | Frio | Tier 2 | 2019-11-20 | 2020-05-21 |  | 5819, 5827 | Y | N | Field engineering is still occurring due to short timeline for this upgrade. Details may change. | Current plan is to upgrade the line using mostly existing structures. Detailed field engineering is underway and could change the plan. | 55874 | 55873
47541 | Crane Circuit Breaker Addition | Provide transmission service to American Electric Power at Crane Substation. Adding one (1) breaker and associated equipment needed to connect the AEP-owned Crane to Kinnison 138-kV transmission line. |  | Crane Substation | Crane Substation | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-06-22 |  | 138 | 0 | 0 | 0 |  | Crane | Crane | Tier 4 |  |  |  | 76615 | Y | N |  | 0 | 47542 | 47541
6971 | Magnolia Mercer Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Magnolia Mercer Substation. |  | Magnolia Mercer |  | Planned | 1018915 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018915 | 2021-06-24 |  | 69 | 0 | 0 | 0 |  | Caldwell |  | Tier 4 |  |  |  | 7218, 7215, 7220 | Y | N |  |  | 14788 | 6971
44372 | Geronimo T1 Replacement | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Geronimo |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2021-06-25 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 7606 | Y |  |  | 0 | 44373 | 44372
5838 | New Katz Auto to Benjamin 138 kV | Joint project with AEP to add autotransformer from Katz (bus# 774) to Katz8 (bus #798) and new line to Benjamin (bus # 6088) when AEP converts to 138 kV and builds line from the new Tardis switching station | [5 empty] | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 15016 | 2021-06-28 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 2 | 2016-02-03 | 2016-05-30 |  | 790, 798, 33798, 745, 774, 6088, 6087 | Y |  |  |  | 14961 | 5838
5274 | Camp Wood - Leakey Transmission Line Overhaul | Rebuild T269 Camp Wood to Leakey to be 138-kV capable with a nominal conductor rating of 223 MVA at 138-kV (Single Drake) with OPGW and operated at 69-kV. |  | Camp Wood | Leakey | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1016183 | 2021-06-30 |  | 69 | 0 | 17.3 | 0 |  | Real | Real | Tier 4 | 2015-12-16 | 2016-01-27 |  | 7426, 8633 | Y | N |  |  | 12950 | 5274
5604 | Stewart Road: Construct 345 kV cut-in | Construct new 345 kV 4 breaker ring bus station at AEP Stewart Rd, with two 675 MVA 345/138 autotransformers connected to Stewart Rd 138 station. Hairpin the North Edinburg to SU Palmito 345 kV line into new Stewart Rd 345 station. The hairping will be constructed in a double circuit configuration, approximately 5 miles long. Also install 100 Mvar shunt reactor at the new Stewart Rd 345 kV station. |  | Stewart Road |  | Planned | 792 - 0977 | AEP TCC | Teresa Trotman bcogan@aep.com 918-599-2857 | 3582 | 2021-06-30 |  | 345 | 0 | 0 | 1350 | -100,0 | Hidalgo | Hidalgo | Tier 2 | 2015-07-10 | 2016-05-19 | 2016-06-14 | 80137, 8951 | Y | N |  |  | 13334 | 5604
6121 | Sunchase - South Padre Island 138 kV Line | Rebuild Sunchase - South Padre Island 138 kV Line |  | Sunchase | South Padre Island | Planned | 826 - 1010 | AEP TCC | Kenneth Haley bcogan@aep.com 918-599-2857 | 3625 | 2021-06-30 |  | 138 | 0 | 3.33 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8335, 8917 | Y | N |  |  | 13847 | 6121
6974 | New Bremen Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at New Bremen Substation. |  | New Bremen |  | Planned | 1018919 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018919 | 2021-06-30 |  | 138 | 0 | 0 | 0 |  | Austin |  | Tier 4 |  |  |  | 7271, 7270, 7273 | Y | N |  |  | 14791 | 6974
6988 | Sheriff's Posse to Marion Transmission Line Upgrade | Replace existing T-340 795 ACSR with 959 ACSS. At Sheriff Posse - Upgrade/Replace underrated switches 2967, 2969, 2971 to 3,000 Amp Switches. Replace and increase fault interrupting rating of breaker 2970 to 63kA, and its continuous rating to 3,000 Amp. Replace CS 2965 and CS 2975 to 40kA units. |  | Sheriff's Posse | Marion | Planned |  | NBU | Gregory Thomas gthomas@nbutexas.com 830-608-8953 |  | 2021-07-01 |  | 138 | 0 | 3.35 | 0 |  | Comal | Guadalupe | Tier 4 |  |  |  | 7178, 7460 | Y | N |  |  | 14806 | 6988
11TPIT0011 | East_Village138kV Substation | East_Village 138kV Substation |  | Techridge | East_Village SUB |  |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2021-08-02 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9195, 9045, 9190 | Y |  |  |  | 13043 | 5357
6540 | LCRA Gonzales to GVEC Gonzales Transmission Line Upgrade | Replace 0.98 miles of 4/0 ACSR 69 kV T-line, with double circuit 138kV structures, 795 ACSR "Drake", initially operate one circuit at 69 kV; plus terminal improvements |  | LCRA Gonzales | GVEC Gonzales | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2021-08-31 |  | 69 | 0 | 0.98 | 0 |  | Gonzales | Gonzales | Tier 4 |  |  |  | 7592, 7626 | Y | N |  |  | 14280 | 6540
52638 | Solanum: Build 138 kV station | Construct new 138 kV box bay on the Abilene South to Putnam 138 kV line |  | Solanum |  | Planned | 1074 - 1247 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2835 | 2021-08-31 |  | 138 | 0 | 0 | 0 |  | Callahan |  | Tier 4 |  |  |  | 61015, 6309, 60365 | Y | N |  | 0 | 52639 | 52638
56372 | This is related to GINR19INR0117 | This is a brand new substation named Reata Station to accommodate GINR19INR0117 Roadrunner Crossing Wind project and Sheep Creek Wind Project later. |  |  |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2021-09-15 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 68051, 68005, 68050 | Y |  |  | 0 | 56373 | 56372
58292 | This is related to GINR21INR0031 | Jordan station will be interconnected project GINR 21INR0031 Indigo Solar Project |  |  |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2021-09-15 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 68013, 68000, 68001 | Y |  |  | 0 | 58293 | 58292
47424 | Clear Fork - Lockhart Transmission Line Overhaul | Increase the reliability and capability of circuit T601 on the Clear Fork - Lockhart 3.0-mile 69-kV transmission line.Upgrade all structures to 138-kV class and bundled Suwannee capable. Upgrade conductor to bundled 959 ACSS Suwannee. Add OPGW. |  | ClearFork | Lockhart | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-09-27 |  | 69 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  | 7195, 7215 | Y |  |  | 0 | 47425 | 47424
6666 | BRYN_6666_Steele_Store_to_Cooks_Point | Construct 138kV line from BTU Steele Store to LCRA Cooks Point (Bundled 1033 ACSR - Curlew) |  | 32852 | 7569 | Planned |  | BRYN | James Tanneberger jtanneberger@btutilities.com 979-821-5763 |  | 2021-09-30 |  | 138 | 6 | 0 | 0 |  | Brazos | Burleson | Tier 4 | 2016-07-07 | 2017-07-07 |  | 32852, 7569 | Y |  |  |  | 14422 | 6666
7013 | NASA Substation Upgrades | Upgrade substation equipment at NASA substation to increase thermal limits |  | NASA | NASA | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-09-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42970, 42610 | Y | N |  |  | 14835 | 7013
44868 | McKenzie - Westside 138 kV Line: Rebuild | Rebuild McKenzie - Westside 138 kV Line |  | McKenzie Road | Westside | Under Construction | 968 - 1146 | ETT | James Weaver bcogan@aep.com 918-599-2857 | 3726 | 2021-09-30 |  | 138 | 0 | 11.48 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8485, 8858 | Y | N |  | 0 | 44869 | 44868
48248 | BrandToCollegeLineUpgrade | Brand to College Line Upgrade to Cumberland |  | Brand | College | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2021-09-30 |  | 138 | 0 | 4.16 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 827, 829 | Y |  |  | 0 | 48249 | 48248
52469 | Scout: Build 69 kV station | Construct new 69 kV box bay on the Abilene South to Steamboat 69 kV line |  | Scout |  | Planned | 1072 - 1245 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2833 | 2021-09-30 |  | 69 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  | 60456, 6328, 6331 | Y | N |  | 0 | 52470 | 52469
57797 | Athey: Build 138 kV Station | Build new 138 kV Station on the Ft Stockton to Rio Pecos 69 kV line | NEW | Athey |  | Planned | 1109 - 1287 | AEP TNC | Michael Glueck mlforcum@aep.com 918-599-2674 | 1866 | 2021-09-30 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60792, 60718, 60798 | Y | N |  | 0 | 57798 | 57797
58004 | Katoen: Build 345 kV station | Build 345 kV station Katoen to interconnect El Algodon, cut-in Katoen station to the Lon Hill to Goddard 345 kV line |  | Katoen |  | Planned | 1110 - 1288 | AEP TCC | Raza S Ansari bcogan@aep.com 918-599-2857 | 3829 | 2021-09-30 |  | 345 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 8579, 88579, 8455, 8606 | Y |  |  | 0 | 58005 | 58004
10TPIT0025 | Bluff Spring 138kV substation | Establish 138kV Bluff Spring substation with (2) 30MVA transformers and will cut into existing Ckt 987 (Lytton Springs to Slaughter Lane). | Changing name of substation from Rinard Creek to Bluff Springs | Lytton Springs substation | Bluff Springs Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | PLAN_117_P151 PLAN_117_P152 | 2021-10-12 |  | 138 | 0.1 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9262, 9075, 9267 | Y | N |  |  | 8206 | 1030
53999 | ElCampo - Ricebird Transmission Line Strom Hardening | Increase the reliability of transmission facilities on the T589 El Campo ¿ Ricebird 4.6-mile 138-kV transmission line. |  | El Campo | Ricebird | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@lcra.org 512-578-4514 |  | 2021-10-20 |  | 138 | 0 | 0 | 0 |  | Wharton | Wharton | Tier 4 |  |  |  | 8102, 78104 | Y | N |  | 0 | 54000 | 53999
52066 | Blessing to Bay City Pumps: Rebuild 69 kV Line | Rebuild Blessing to Markham Tap and retire the radial line servicing Bay City Pumps |  | Blessing | Markham Tap | Planned | 1076 - 1249 | AEP TCC | Marc E. Wilson bcogan@aep.com 918-599-2857 | 3801 | 2021-10-30 |  | 69 | 0 | 10.78 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 8546, 8547, 8549, 8119, 8550, 8984 | Y | N |  | 0 | 52067 | 52066
52197C | Jordan Auto A3 Addition (PLACID 138kV Sub) | PLACID (PLA) Substation Looped into Ckt.86D RIGBY to Crosby |  | Rigby | Crosby | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointe 713-207-2760 |  | 2021-10-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Harris | Tier 3 | 2019-10-24 | 2019-11-18 |  | 40680, 40155, 40390, 40670, 40665 | Y | N |  | 0 | 57347 | 52197
54698 | Perigee: Build 345 kV station | Interconnect Apogee wind farm on the Foxtail to Mulberry Creek 345 kV line |  | Perigee |  | Planned | 1038 - 1265 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 1855 | 2021-10-31 |  | 345 | 0 | 0 | 0 |  | Haskell |  | Tier 4 |  |  |  | 60791, 6076, 6235 | Y | N |  | 0 | 54699 | 54698
55971 | Eagle Nest (EGL) Sub for Brazoria West Solar (20INR0101) | Install new 138kV Eagle Nest substation for generator interconnection to Brazoria West Solar. Loop Ckt.02 into Eagle Nest substation to create new Ckt.02 BURKE to Eagle Nest to West Columbia |  | Eagle Nest | BURKE/ West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-10-31 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42430, 42410, 43380 | Y | N |  | 0 | 56717 | 55971
48814 | Albany Foundry to Fort Griffin: Rebuild 69 kV line | Rebuild 69 kV line from Albany Foundry to Fort Griffin, install box bay at Salt Prong POD, install capacitor banks at Albany Foundry | Update Description | Albany Foundry | Fort Griffin | Planned | 1014 - 1192 | AEP TNC | Nathan Cowan mlforcum@aep.com 918-599-2674 | 2775 | 2021-10-31 01:00 |  | 69 | 0 | 4.66 | 0 | 0,14.4 | Shackelford | Shackelford | Tier 4 |  |  |  | 6208, 6213, 60445, 6202, 6212, 60398, 6214 | Y | N |  | 0 | 48815 | 48814
47929 | Rising Star Area Rebuilds | Rising Star Area Rebuilds |  | Downing (281) | Nimrod (289) | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2021-11-01 |  | 69 | 0 | 50.04 | 60 |  | Comanche | Eastland | Tier 3 | 2019-04-04 | 2019-04-30 |  | 281, 285, 289, 293, 277, 1649 | Y |  |  | 0 | 47930 | 47929
47440 | Rattler Substation Addition | Construct a new load-serving 138-kV substation. Rattler substation will be located on T262 transmission line between Redwood and McCarty Lane. |  | Rattler | Rattler | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2021-11-03 |  | 138 | 0 | 0 | 0 |  | Hays | Hays | Tier 4 |  |  |  | 7184, 7182, 7188 | Y | N |  | 0 | 47441 | 47440
46259 | Big Spring - Buzzard Draw 69 kV Line Conversion | Big Spring - Buzzard Draw 69 kV Line Conversion |  | Big Spring | Buzzard Draw | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9015 | 2021-11-15 23:00 |  | 138 | 0 | 21.3 | 0 |  | Howard | Howard | Tier 4 |  |  |  | 1357, 1358, 1359, 1361, 1365, 1322, 1323, 1355, 1356, 11324 | Y |  |  | 0 | 46262 | 46259
3948 | Steamboat to Tuscola: Rebuild 69 kV line | Rebuild Winters to Steamboat and Steamboat to Tuscola |  | Steamboat | Tuscola | Planned | 685 - 0855 | ETT | Nathan Cowan mlforcum@aep.com 918-599-2674 | 1851 | 2021-11-30 |  | 69 | 0 | 9.856 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6328, 6331, 60332 | Y | N |  |  | 11441 | 3948
3949 | Steamboat to Winters: Rebuild 69 kV line | Rebuild Winters to Steamboat and Steamboat to Tuscola |  | Steamboat | Winters | Planned | 685 - 0855 | ETT | Nathan Cowan mlforcum@aep.com 918-599-2674 | 1850 | 2021-11-30 |  | 69 | 0 | 9.944 | 0 |  | Taylor | Runnels | Tier 4 |  |  |  | 6333, 60332 | Y | N |  |  | 11442 | 3949
6668B | Freeport - Master Plan | New 345 kV double-circuit line from Bailey Substation to Jones Creek Substation | Accelerated Project Schedule | Bailey | Jones Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-11-30 |  | 345 | 55.2 | 0 | 0 |  | Wharton | Brazoria | Tier 1 |  |  | 2017-12-12 | 5568, 5915, 42400, 42500, 42530, 43011, 43120, 44000, 44005, 44040, 43221, 43380, 44200, 47531, 47532 | Y | N |  | 0 | 58254 | 6668
6749 | Rosata: Build 138kV Substation | Build new Rosata 138kV POD Switch on Coleto Creek to Kenedy 138kV Line |  | Rosata |  | Planned | 898 - 1076 | AEP TCC | James Lutz bcogan@aep.com 918-599-2857 | 3682 | 2021-11-30 |  | 138 | 0 | 0 | 0 |  | Goliad |  | Tier 4 |  |  |  | 8153, 88153, 7241, 8162, 8186 | Y | Y |  |  | 14542 | 6749
46513 | Port Isabel: Rebuild As GIS Station | Rebuild Port Isabel as a GIS |  | Port Isabel |  | Planned | 958 - 1136 | AEP TCC | James Nivens bcogan@aep.com 918-599-2857 | 3716 | 2021-11-30 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8338, 8744 | Y | N |  | 0 | 50322 | 46513
49556 | Ozona: Rebuild 69 kV station | Replace existing Ozona 69 kV station with a new 69 kV ring bus |  | Ozona |  | Planned | 1018 - 1196 | AEP TNC | Nathan Cowan mlforcum@aep.com 918-599-2674 | 2780 | 2021-11-30 |  | 69 | 0 | 0 | 0 |  | Crockett |  | Tier 4 |  |  |  | 6550, 6560 | Y | N |  | 0 | 49557 | 49556
50160 | Beeville - Goliad: Rebuild 69 kV Line | Beeville - Goliad: Rebuild 69 kV Line |  | Beeville | Goliad | Planned | 961 - 1139 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3719 | 2021-11-30 |  | 69 | 0 | 22.21 | 0 |  | Bee | Goliad | Tier 3 | 2019-04-30 | 2019-05-30 |  | 8584, 8586, 8587 | Y | N |  | 0 | 50161 | 50160
50870 | Coleto Creek - Rosata: Line Rebuild | Coleto Creek - Kenedy SS: Line Rebuild |  | Coleto Creek | Rosata | Planned | 1052 - 1225 | AEP TCC | Curtis Brown bcogan@aep.com 918-599-2857 | 3778 | 2021-11-30 |  | 138 | 0 | 15.3 | 0 |  | Goliad | Goliad | Tier 3 |  |  |  | 8162, 88153 | Y | N |  | 0 | 50871 | 50870
50878 | North Edinburg: 345 kV Reconfigure | North Edinburg: 345 kV Reconfigure |  | North Edinburg |  | Planned | 1056 - 1229 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3786 | 2021-11-30 |  | 345 | 0 | 0 | 0 | -100,0 | Hidalgo |  | Tier 4 |  |  |  | 8341, 8383 | Y | N |  | 0 | 50879 | 50878
50898 | Alamito Creek to Paisano to Alpine: Rebuild 69 kV line | Rehab Alamito Creek to Paisano to Alpine 69 kV line |  | Alamito Creek | Alpine | Planned | 1045 - 1218 | AEP TNC | Nathan Cowan mlforcum@aep.com 918-599-2674 | 2793 | 2021-11-30 |  | 69 | 0 | 22.26 | 0 |  | Presidio | Brewster | Tier 4 |  |  |  | 60449, 6666, 6667, 6672 | Y | N |  | 0 | 50899 | 50898
52072 | Conan: Build new 69 kV box bay | Construct new 69 kV box bay on the Santa Anna to Cross Plains 69 kV line and install capacitor bank |  | Conan |  | Planned | 1066 - 1239 | AEP TNC | Michael Glueck mlforcum@aep.com 918-599-2674 | 2827 | 2021-11-30 |  | 69 | 0 | 0 | 0 | 0,7.2 | Callahan |  | Tier 4 |  |  |  | 6356, 60455, 6350, 6352, 6357 | Y | N |  | 0 | 52073 | 52072
52100 | Bradshaw to Steamboat: Rebuild 69 kV line | Rebuild Bradshaw to Steamboat 69 kV line | Update Contact | Bradshaw | Steamboat | Planned | 1069 - 1242 | ETT | Glen Reed gareed@aep.com 918-599-2664 | 2830 | 2021-11-30 |  | 69 | 0 | 0.25 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6331, 60332, 6328, 60456 | Y | N |  | 0 | 52101 | 52100
55367 | Wolfcamp: Build 138 kV box bay | Build new 138 kV box bay on the Big Lake to North McCamey line |  | Wolfcamp |  | Planned | 1087 - 1270 | AEP TNC | Michael Glueck mlforcum@aep.com 918-599-2674 | 1860 | 2021-11-30 |  | 138 | 0 | 0 | 0 |  | Upton |  | Tier 4 |  |  |  | 60799, 60361, 60723 | Y | N |  | 0 | 55368 | 55367
57908 | North Edinburg: Station Work | North Edinburg: Station Work |  | North Edinburg |  | Planned | 1112 - 1290 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3831 | 2021-11-30 |  | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  | 88381, 88382, 8380, 8383, 8341 | Y | N |  | 0 | 57909 | 57908
48288A | BOGGY (BOG) 138kV Substation (SHELL Substation Replacement) | Remove existing customer-owned SHELL (_SL) 138kV Substation |  | SHELL |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-11-30 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 41450, 40070, 40530, 41460, 41210 | Y | N |  | 0 | 57332 | 48288
55969 | Cedar Creek (CCK) Substation for Old 300 Solar (21INR0406) | New 138kV Cedar Creek substation for generator interconnection to Old 300 Solar. Loop Ckt.02 into substation to create new Ckt.72 BAILEY to Cedar Creek to WAP |  | Cedar Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-11-30 |  | 345 | 0 | 0 | 0 |  | Fort Bend |  | Tier 4 |  |  |  | 44090, 44005, 44040 | Y | N |  | 0 | 56664 | 55969
17TPIT0005 | St. Jo Autos | Replace 40 MVA autos with 60 MVA autos |  | St. Jo | St. Jo | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 12005 | 2021-12-01 |  | 138 | 0 | 0 | 60 |  | Cooke |  | Tier 4 |  |  |  | 750, 746 | Y | N |  |  | 9491 | 2243
3818 | Rebuild Calallen to Robstown | Rebuild 4-0 ACSR 69 kV to higher rated and 138 kV capable line, as originally recommended in 2013 RTP. |  | Calallen | Robstown | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-12-01 |  | 69 | 0 | 6.26 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 5626, 5634 | Y | N |  |  | 11275 | 3818
4010 | Rebuild Magnolia - Seminole 138 kV line. | *Project pushed back to 2021. |  | Magnolia Sub | Seminole Sub | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | STE07216 | 2021-12-01 |  | 138 | 0 | 3.3 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 38950, 38990 | Y |  |  |  | 11530 | 4010
6685 | Van Vleck substation loop | Replaces single circuit radial line connected to a pole mounted switch with a double circuit transmission loop to the Van Vleck substation and upgrades the 4/0 ACSR to 795 ACSR on 138 kV capable poles. |  | Van Vleck Substation | Van Vleck Switch | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-12-01 |  | 69 | 2 | 2 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 5556, 5554, 5558, 5560 | Y | N |  |  | 14456 | 6685
6934B | Elm Creek - New 345 kV Reactor | Install new 345 kV 60 Mvar Reactor at Elm Creek Substation. | [5 empty] | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0873 | 2021-12-01 |  | 345 | 0 | 0 | 0 | 60,0 | Guadalupe |  | Tier 4 |  |  |  | 5133 | Y |  |  |  | 14754 | 6934
43623 | McCreeCristBenDavisLinesUpgrade | McCree to Crist to Ben Davis 138kV Lines Upgrade to Cumberland Conductor |  | McCree | Ben Davis | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2021-12-01 |  | 138 | 0 | 6.95 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 834, 850, 968 | Y | N |  | 0 | 43624 | 43623
51216F | Ward Winkler RPG | Convert & re-conductor existing TNMP Wickett - Oncor Yucca 69kV line to 138kV, construct line extension (~1.3 miles) and re-terminate line to Oncor Wolf 138kV station. |  | TNMP Wickett (37980 / 37981) | Oncor Wolf (1013) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2021-12-01 |  | 138 | 1.3 | 4.7 | 0 |  | Ward | Ward | Tier 2 | 2019-03-19 | 2019-10-10 |  | 1013, 1015, 37940, 37960, 37980, 37981 | Y |  |  | 0 | 56661 | 51216
51990 | AEN_New_Dunlap_345kV_Auto_AT2_PMCR |  |  | 9044 | 9045 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2021-12-01 |  | 345 | 0 | 0 | 672 |  |  | Travis | Tier 4 |  |  |  | 9045, 9044 | Y |  |  | 0 | 51991 | 51990
54088 | Hortontown Substation Upgrade | Increase the reliability of substation equipment at the Hortontown Substation. LCRA TSC will change the existing high-side configuration at Hortontown substation from Single Bus/Single Breaker to Ring Bus. |  | Hortontown Substation | Hortontown Substation | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2021-12-12 |  | 138 | 0 | 0 | 0 |  | Comal | Comal | Tier 4 |  |  |  | 7175 | Y | N |  | 0 | 54089 | 54088
14TPIT0056 | Northaven - Morrison 138 kV line | Upgrade existing double-circuit line |  | Northaven | Morrison | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4088-E | 2021-12-15 |  | 138 | 0 | 12 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2655, 2656, 2660, 2661, 2662, 2663, 2782, 2783 | Y | N |  |  | 9773 | 2493
5310 | Everman - Venus 345 kV Double-circuit line | Upgrade existing line |  | Everman | Venus | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1735 | 2021-12-15 |  | 345 | 0 | 34.6 | 0 |  | Tarrant | Ellis | Tier 4 |  |  |  | 1882, 1886, 1906, 1907 | Y | N |  |  | 12986 | 5310
6273 | Saginaw-Eagle Mountain 138 kV DCKT | Upgrade the Saginaw - Eagle Mountain 138 kV Double Circuit Line |  | Saginaw | Eagle Mountain | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5274 | 2021-12-15 |  | 138 | 0 | 28 | 0 |  | Tarrant | Tarrant | Tier 3 |  |  |  | 1864, 2066, 2067, 2074, 1860, 2069, 2070, 11860 | Y | N |  | 0 | 52331 | 6273
7020 | Cedar Hill - Camp Wisdom 138 kV Line | Upgrade existing Cedar Hill - Camp Wisdom 138 kV Line |  | Cedar Hill | Camp Wisdom | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4250 | 2021-12-15 |  | 138 | 0 | 9.1 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2421, 2990, 2993, 2994, 2992, 2999 | Y | N |  |  | 14842 | 7020
7025 | Renner Sw. Sta. - Plano Tennyson Sw. Sta. 138 kV Line | Upgrade existing Renner Sw. Sta. - Plano Tennyson Sw. Sta. 138 kV Line |  | Renner Sw. Sta. | Plano Tennysson Sw. Sta. | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M3047 | 2021-12-15 |  | 138 | 0 | 10.6 | 0 |  | Collin | Collin | Tier 4 |  |  |  | 2352, 2353, 2521, 2523, 2524 | Y | N |  |  | 14847 | 7025
7118 | Everman 345 kV Sw. Sta. | Rebuild Everman 345 kV Sw. Sta. |  | Everman |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5278 | 2021-12-15 |  | 345 | 0 | 0 | 0 |  | Tarrant |  | Tier 3 |  |  |  | 1882 | Y |  |  |  | 14954 | 7118
45517 | Waco West - Waco East 138 kV Line | Upgrade the Waco West Switch - Waco East Switch (Via Baylor Tap) 138 kV Line to 2071 A |  | Waco West | Waco East | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R463 | 2021-12-15 |  | 138 | 0 | 10.6 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  | 3434, 3436, 3438, 3563 | Y | N |  | 0 | 45518 | 45517
52149 | Upgrade Elm Mott - Bosque 138 kV Line | Upgrade Elm Mott - Bosque 138 kV Line |  | Elm Mott | Bosque | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1721 | 2021-12-15 |  | 138 | 0 | 19.3 | 0 |  | McLennan | Bosque | Tier 4 |  |  |  | 249, 252, 3407 | Y |  |  | 0 | 52150 | 52149
52153 | Upgrade Eustace SE - Mabank 138 kV Line | Upgrade Eustace SE - Mabank 138 kV Line |  | Eustace Southeast | Mabank | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6097 | 2021-12-15 |  | 138 | 0 | 9.3 | 0 |  | Henderson | Henderson | Tier 4 |  |  |  | 3176, 3177, 3179, 6951 | Y |  |  | 0 | 52154 | 52153
52234 | Calmont 138 kV Emergency Capacitors | Install new 55.2 Mvar capacitor bank |  | Calmont |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5134 | 2021-12-15 |  | 138 | 0 | 0 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1955 | Y |  |  | 0 | 52235 | 52234
52247 | Marrs - Handley 69 kV Line Conversion to 138 kV | Convert the existing Marrs-Handley 69 kV line to 138 kV operation |  | Marrs SW | Handley | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5222 | 2021-12-15 |  | 138 | 2.2 | 13 | 0 |  | Tarrant | Tarrant | Tier 3 |  |  |  | 1952, 1968, 2158, 2159, 2160, 2161, 11952, 1951, 1969 | Y |  |  | 0 | 52248 | 52247
52251 | Mountain Creek Switch 138 kV Breaker Installation | install two 138 kV breakers |  | Mountain Creek |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4093 | 2021-12-15 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 12457, 12458, 2411, 2412, 3014, 3015 | Y |  |  | 0 | 52252 | 52251
52305 | Cedar Hill Switch-Cedar Hill 138 kV Line Upgrade | rebuild the existing Cedar Hill Switch-Cedar Hill 138 kV Line |  | Cedar Hill SW | Cedar Hill | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4131 | 2021-12-15 |  | 138 | 5.9 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2422, 3049, 3051, 3052, 3053, 3050, 3055 | Y |  |  | 0 | 52306 | 52305
52728 | Add NS Crane 138 kV Switch | Oncor's portion of AEP's Crane Area Transmission Project |  | LCRA Arco Crane | Navajo Tap | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8502 | 2021-12-15 |  | 138 | 0 | 0 | 0 |  | Crane | Crane | Tier 4 | 2019-06-01 | 2019-07-22 |  | 10002, 11202, 60448, 71199 | Y |  |  | 0 | 52730 | 52728
54118 | Rebuild Alvin-Mainland-Freeway Park (795 ACSS) | Rebuild Alvin - Mainland - Freeway Park 138 kV line with 795 ACSS conductor. |  | Freeway Park 138 kV Substation (Bus # 38820) | Alvin 138 kV Substation (Bus # 39030) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | STE09517 | 2021-12-15 |  | 138 | 0 | 17.3 | 0 |  | Galveston | Brazoria | Tier 4 |  |  |  | 38820, 38830, 39030 | Y |  |  | 0 | 54119 | 54118
54120 | Rebuild Tejas-Commanche (Bundled 795 ACSS) | Rebuild Tejas - Commanche 138 kV line with Bundled 795 ACSS conductor. Project status changed to Planned but not in case until confirmation of effective date (4/2/2020). |  | Tejas 138 kV Substation (Bus # 38530) | Commanche 138 kV Substation (Bus # 38560) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | STE07318 | 2021-12-15 |  | 138 | 0 | 0.95 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 38530, 38560 | N |  |  | 0 | 54121 | 54120
57758 | Carrollton Northwest 345/138 kV Autotransformer | Carrollton Northwest 345/138 kV Autotransformer |  | Carrollton Northwest |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4247 | 2021-12-15 |  | 345 | 0 | 0 | 600 |  |  |  | Tier 3 |  |  |  | 2360, 2362, 2363, 2361, 12360 | Y |  |  | 0 | 57759 | 57758
57853 | Palmer and Rice 69 kV Substations Conversion to 138 kV | Convert Palmer and Rice 69 kV Substations to 138 kV |  | Palmer | Rice | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4317 | 2021-12-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 2344, 2345, 2346, 2347, 221, 2326, 2329, 2342, 3468 | Y |  |  | 0 | 57854 | 57853
57855 | Ennis Switch 138 kV Rebuild | Rebuild Ennis 138 kV Switch |  |  |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4302 | 2021-12-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | Y |  |  | 0 | 57856 | 57855
57915 | Tall City - Telephone Road 138 kV Line Rebuild | Tall City - Telephone Road 138 kV Line Rebuild |  | Tall City | Telephone Road | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8552 | 2021-12-15 |  | 138 | 0 | 11.9 | 0 |  | Midland | Midland | Tier 3 | 2020-09-11 |  |  | 23855, 23862 | Y |  |  | 0 | 57916 | 57915
52316 | Anna Tap - Princeton 138 kV Line | Upgrade the Anna Tap - Princeton 138 kV Line |  | Anna Tap | Princeton Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4275 | 2021-12-15 01:00 |  | 138 |  | 9.6 | 0 |  | Collin | Collin | Tier 3 |  |  |  | 2527, 2707, 2528, 2708 | Y |  |  | 0 | 52317 | 52316
14TPIT0010 | Handley - Sherry 138 kV line | Upgrade existing line |  | Handley | Sherry | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5155-E | 2021-12-15 12:00 |  | 138 | 0 | 8.9 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1919, 1920, 1950, 1951, 2245, 2246, 2247, 2251, 2252 | Y | N |  |  | 11813 | 2582
45527 | Plano West - Richardson Collins 138 kV Line | Upgrade the Plano West - Richardson Collins 138 kV Line |  | Plano West Switch | Richardson Collins Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M364 | 2021-12-15 12:00 |  | 138 | 0 | 0 | 0 |  | Collin | Dallas | Tier 4 |  |  |  | 2685, 2628, 2673, 2683, 2684, 2686, 12684 | Y |  |  | 0 | 45528 | 45527
5230 | Sonne Substation Addition | Provide transmission service for a generator off T554 radial 138-kV line between North McCamey and Tippet Substations. |  | North McCamey | Tippet | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1015964 | 2021-12-16 |  | 138 | 0 | 0 | 0 |  | Upton | Pecos | Tier 4 |  |  |  | 76020, 76021, 76595 | Y | N |  |  | 12903 | 5230
52239 | Lake Hubbard SW | Install two 138 kV breakers |  | Lake Hubbard |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4134 | 2021-12-16 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 12401, 12402, 2401, 2402, 2441, 2939 | Y |  |  | 0 | 52240 | 52239
52322 | Establish Courtney Creek Switch | Establish Courtney Creek 138/69 kV Switch |  | Courtney Creek Switch | Athey (AEP) | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8479 | 2021-12-16 |  | 138 |  |  | 82 |  | Pecos | Pecos | Tier 4 |  |  |  | 11242, 11258, 1240, 1242, 60792 | Y |  |  | 0 | 56445 | 52322
6786 | Schumansville T2 Replacement | Replace T2, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Schumansville |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2021-12-17 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7609 | Y |  |  |  | 14580 | 6786
51736 | Cibolo to McQueeney Transmission Line | Install 10.62 miles of 1192 Bunting to existing transmission structures, circuit to help with load flows per the TPA and will be source for Santa Clara Substation. |  | Cibolo | McQueency | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2021-12-23 |  | 138 | 10.62 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7608, 7606 | Y | N |  | 0 | 51737 | 51736
3774 | Olinger-Ben Davis Line Upgrade | Olinger to Ben Davis 138 kV line upgrade to Cumberland conductor |  | Olinger | Ben Davis | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2021-12-25 |  | 138 | 0 | 17.25 | 0 |  | Collin | Dallas | Tier 4 |  |  |  | 818, 968 | Y | N |  |  | 11194 | 3774
52640 | HO Clarke Auto A3 Replacement | Replace existing HO Clarke Auto A3 with removed University Auto A1 |  | HO Clarke |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-12-30 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47175, 47165, 49009 | Y | N |  | 0 | 52641 | 52640
6572 | Ballinger to Eden 69 kV line: Rebuild taps | Ballinger to Eden 69 kV line: Rebuild taps |  | Ballinger | Eden | Planned | 890 - 1068 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2814 | 2021-12-31 |  | 69 | 0 | 2.8 | 0 |  | Runnels | Concho | Tier 4 |  |  |  | 6338, 6369, 6370, 6372, 6376 | Y | N |  |  | 14323 | 6572
6687 | Rebuild Rio Hondo to East Rio Hondo | Rebuild the 138 kV line from Rio Hondo to East Rio Hondo. |  | Rio Hondo | East Rio Hondo | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-12-31 |  | 138 | 0 | 8.19 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 5764, 8319 | Y | N |  |  | 14458 | 6687
45543 | Everman Switch - Marrs Switch 138 kV DCKT Line | Upgrade the Everman Switch - Marrs Switch 138 kV Double-Circuit Line |  | Everman Switch | Marrs Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5279 | 2021-12-31 |  | 138 | 0 | 8 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1883, 1884, 1969, 2211, 11968, 11967 | Y |  |  | 0 | 51248 | 45543
57414 | BEARLE (BER) 138kV Customer Substation | BEARLE (BER) 138kV customer substation looped into Ckt.96C Philip to South Channel |  | BEARLE | Philip/South Channel | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41230, 41250, 41370 | Y | N |  | 0 | 57415 | 57414
57582 | Cedar Bayou Auto A1 Upgrade | Upgrade Cedar Bayou auto A1 to increase thermal limits |  | Cedar Bayou |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-12-31 |  | 345 | 0 | 0 | 0 |  | Chambers |  | Tier 4 |  |  |  | 40000, 40015, 49005 | Y | N |  | 0 | 57583 | 57582
57586 | Cedar Bayou to Center Ckt.97D Upgrade | Upgrade Cedar Bayou to Center Ckt.97D |  | Cedar Bayou | CENTER | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-12-31 |  | 345 | 0 | 0 | 0 |  | Chambers | Harris | Tier 4 |  |  |  | 40000, 40240 | Y | N |  | 0 | 57587 | 57586
58540 | Rebuild 16th St - Soaptree |  |  | TNMP 16th Street (38310) | TNMP Soaptree (38450) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2021-12-31 |  | 138 | 0 | 31.83 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 38310, 38450 | Y |  |  | 0 | 58541 | 58540
44511 | Aransas_Pass-Seawall: Rebuild and re-conductor with 795 ACSS | Rebuild and re-conductor Aransas Pass - Seawall with 795 ACSS (2000 A conductor). This will relieve overload seen in the 2025 SSWG Summer Peak case for loss of Naval Base- North Padre. |  | Aransas Pass | Seawall | Planned | 947 - 1125 | AEP | Michael Glueck bcogan@aep.com 918-599-2857 | 3711 | 2022-01-30 |  | 69 | 0 | 3.2 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8427, 8435 | Y | N |  | 0 | 44512 | 44511
44866 | Dilley - Jourdanton 69 kV Line | Rebuild Dilley - Jourdanton 69 kV Line |  | Dilley | Jourdanton | Under Construction | 967 - 1145 | AEP | Brian Oyster bcogan@aep.com 918-599-2857 | 3725 | 2022-01-30 |  | 69 | 0 | 44.8 | 0 |  | Frio | Atascosa | Tier 3 | 2019-05-23 | 2019-05-24 | 2019-06-17 | 8206, 8208, 8607 | Y | N |  | 0 | 44867 | 44866
49546 | Resnik: Construct New Distribution Station | Resnik: Construct New Distribution Station |  | Resnik |  | Planned | 996 - 1174 | AEP TCC | Dave Goetz bcogan@aep.com 918-599-2857 | 3749 | 2022-01-31 |  | 138 | 0 | 0 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  | 8580, 8422, 8565, 80470 | Y | N |  | 0 | 49547 | 49546
50950 | Whitepoint Area Improvements | Whitepoint Area Improvements |  | Whitepoint | Hecker | Planned | 1061 - 1234 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3792 | 2022-01-31 |  | 138 | 0 | 12 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  | 8418, 8565, 8961 | Y | N |  | 0 | 50951 | 50950
50954 | Whitepoint: Add Second Auto | Whitepoint: Add Second Auto |  | Whitepoint |  | Planned | 1085 - 1258 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3805 | 2022-01-31 |  | 345 | 0 | 0 | 500 |  | San Patricio |  | Tier 4 |  |  |  | 8956, 8961 | Y | N |  | 0 | 50955 | 50954
57756 | WOLF 345kV for Fighting Jays Solar (21INR0278) | New 345kV CNP WOLF (WLF) substation for generator interconnection to Fighting Jays Solar. Loop Ckt.64C into substation to create new Ckt.64 Hillje to WOLF to WA Parish. |  | WOLF | Hillje/WA Parish | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-01-31 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 44160, 44000, 44200 | Y | N |  | 0 | 57757 | 57756
6873 | Support 69kV to 138kV East Loop Conversion Projects | Upgraded lines Apollo to Naaman to Walnut to Newman to support 69kV to 138kV East Loop Conversion Projects |  | Apollo | Newman | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2022-02-09 |  | 138 | 0 | 10.1 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 800, 814, 825, 826, 802, 849, 823, 806 | Y | N |  |  | 14682 | 6873
46968 | Gabriel Substation Upgrade | LCRA TSC will upgrade the configuration of the 138-kV bus from single bus/single breaker to a breaker and a half bus configuration and replace five existing CBs at Gabriel Substation and provide for future Georgetown PWT addition. |  | Gabriel | Gabriel | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2022-02-15 |  | 138 | 0 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | Y | N |  | 0 | 46969 | 46968
47426 | Clear Fork - Robert Brown Transmission Line Overhaul | Increase the reliability and capability of circuit T519 on the Clear Fork - Robert Brown Jr 8.8-mile 69-kV transmission line. Upgrade all structures to 138-kV class and bundled Suwannee capable. Upgrade conductor to bundled 959 ACSS Suwannee. Add OPGW. |  | Clear Fork | Robert Brown Jr | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2022-03-01 |  | 69 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  | 7194, 7195 | Y | N |  | 0 | 47427 | 47426
58002 | Foxtrot: Construct new 345 kV Station |  |  |  |  | Planned | 1120 - 1298 | AEP | Glen Reed gareed@aep.com 918-599-2664 | 3839 | 2022-03-01 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 8689, 88689, 5725, 8606 | Y |  |  | 0 | 58003 | 58002
6980 | Weimar Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Weimar Substation. |  | Weimar |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2022-03-03 |  | 138 | 0 | 0 | 0 |  | Colorado |  | Tier 4 |  |  |  | 7254, 7258 | Y | N |  |  | 14797 | 6980
43212B | Caymus Capbanks in TNMP West Texas System | Expands Caymus Capacitor bank by 1 block of 20 Mvar. |  | Caymus (Bus #38410) | Caymus (Bus #38410) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07819 | 2022-03-15 |  | 138 | 0 | 0 | 0 | 0,20 | Reeves | Reeves | Tier 4 |  |  |  | 38410 | Y |  |  | 0 | 48414 | 43212
48415B | TransPecos Capbank in TNMP West Texas System | Expands TransPecos Capacitor bank by 1 block of 20 Mvar. |  | TransPecos (Bus #38377) | TransPecos (Bus #38377) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07919 | 2022-03-15 |  | 138 | 0 | 0 | 0 | 0,20 | Reeves | Reeves | Tier 4 |  |  |  | 38377 | Y |  |  | 0 | 48417 | 48415
49574 | Tesla: Build 345 kV terminal | Interconnect Misae II solar farm at Tesla |  | Tesla |  | Planned | 1023 - 1201 | AEP | Michael Glueck mlforcum@aep.com 918-599-2674 | 2785 | 2022-03-24 |  | 345 | 0 | 0 | 0 |  | Childress |  | Tier 4 |  |  |  | 60501 | Y | N |  | 0 | 49575 | 49574
55464 | Adds new Morrow sub near Pearsall | Adds new Morrow substation and short line from Morrow to the Pearsall substation |  | Pearsall | Morrow | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2022-03-30 |  | 138 | 0.91 | 0 | 0 |  | Frio | Frio | Tier 4 |  |  |  | 5896, 5895 | Y | N |  | 0 | 55465 | 55464
6571 | Lake Pauline to Vernon 69 kV line: Rebuild taps | Lake Pauline to Vernon 69 kV line: Rebuild taps |  | Lake Pauline | Vernon Main | Planned | 891 - 1069 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2815 | 2022-03-31 |  | 69 | 0 | 2.5 | 0 |  | Hardeman | Wilbarger | Tier 4 |  |  |  | 6048, 6056, 6057, 6058 | Y | N |  |  | 14322 | 6571
6791 | Lake Pauline: Replace 138/69 kV Auto | Replace the 138/69 kV autotransformer at Lake Pauline with a 130 MVA autotransformer |  | Lake Pauline |  | Planned | 906 - 1084 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2730 | 2022-03-31 |  | 138 | 0 | 0 | 130 |  | Hardeman |  | Tier 4 |  |  |  | 6048, 6050 | Y | N |  |  | 14589 | 6791
44399 | South Padre Island: Rebuild as GIS station | Rebuild South Padre Island as a GIS |  | South Padre Island | - | Planned | 948 - 1126 | AEP | James Nivens bcogan@aep.com 918-599-2857 | 3712 | 2022-03-31 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8335, 8917 | Y | N |  | 0 | 44400 | 44399
45399 | Bearkat Loop - Bearkat to Longshore | Adds 345 KV line from Bearkat to Longshore. |  | Bearkat | Longshore | Planned |  | WETT/ONCOR | Christina Minchew christina.minchew@windene 512-436-9469 |  | 2022-03-31 |  | 345 | 27 | 0 | 0 |  | Glasscock | Howard | Tier 1 | 2017-08-15 | 2018-09-19 | 2018-10-09 | 1058, 59903 | Y | N |  | 0 | 45473 | 45399
46456 | LookoutAddsSVC&Capbanks | Lookout adds SVC&Capbanks for voltage reliability |  | Lookout | Lookout | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2022-03-31 |  | 138 | 0 | 0 | 0 | 0,180 | Dallas | Dallas | Tier 4 |  |  |  | 828 | Y | N |  | 0 | 46457 | 46456
49948 | McCreeShilohLineUpgrades | McCree to Shiloh Line Upgrades to Cumberland |  | McCree | Shiloh | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2022-03-31 |  | 138 | 0 | 2.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 830, 834 | Y | N |  | 0 | 49949 | 49948
50843 | Heron: Build 138 kV station | Build Heron 138 kV station with a 138/69 kV auto, expand the Kinnison 138 kV station, expand the Sage 69 kV station, rebuild Heron to Ollin and convert to a 138 kV line, and rebuild Kinnison to Sage 69 kV line | Update Contact | Heron |  | Planned | 1048 - 1221 | AEP TNC | Gregory Crane mlforcum@aep.com 918-599-2674 | 2796 | 2022-03-31 |  | 138 | 0 | 0 | 90 |  | Crane |  | Tier 3 |  |  |  | 60447, 60448, 6610 | Y | N |  | 0 | 50844 | 50843
50845 | Kinnison: Expand 138 kV station | Build Heron 138 kV station with a 138/69 kV auto, expand the Kinnison 138 kV station, expand the Sage 69 kV station, rebuild Heron to Ollin and convert to a 138 kV line, and rebuild Kinnison to Sage 69 kV line | Updated Contact | Kinnison |  | Planned | 1048 - 1221 | AEP TNC | Gregory Crane mlforcum@aep.com 918-599-2674 | 2797 | 2022-03-31 |  | 138 | 0 | 0 | 130 |  | Crane |  | Tier 3 |  |  |  | 60431, 60432 | Y | N |  | 0 | 50846 | 50845
50847 | Sage: Expand 69 kV station | Build Heron 138 kV station with a 138/69 kV auto, expand the Kinnison 138 kV station, expand the Sage 69 kV station, rebuild Heron to Ollin and convert to a 138 kV line, and rebuild Kinnison to Sage 69 kV line | Update Contact | Sage |  | Planned | 1048 - 1221 | AEP TNC | Gregory Crane mlforcum@aep.com 918-599-2674 | 2799 | 2022-03-31 |  | 69 | 0 | 0 | 0 |  | Crane |  | Tier 3 |  |  |  | 6604 | Y | N |  | 0 | 50848 | 50847
50892 | Seawall to Port Aransas: Replace 69 kV undersea cable | Replace Seawall to Port Aransas 69 kV undersea cable |  | Seawall | Port Aransas | Planned | 1058 - 1231 | AEP | Bill Roberts bcogan@aep.com 918-599-2857 | 3789 | 2022-03-31 |  | 69 | 0 | 0.5 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8435, 8442 | Y | N |  | 0 | 50893 | 50892
50900 | Mason to North Brady: Rebuild 69 kV line | Rehab Mason to North Brady 69 kV line |  | Mason | North Brady | Planned | 1046 - 1219 | AEP TNC | David Baker mlforcum@aep.com 918-599-2674 | 2794 | 2022-03-31 |  | 69 | 0 | 30.24 | 0 |  | Mason | McCulloch | Tier 3 | 2019-10-01 | 2019-11-01 |  | 6006, 6381, 6393, 6406, 60386 | Y | N |  | 0 | 50901 | 50900
51010 | Heron to Ollin: Rebuild and convert to 138 kV line | Build Heron 138 kV station with a 138/69 kV auto, expand the Kinnison 138 kV station, expand the Sage 69 kV station, rebuild Heron to Ollin and convert to a 138 kV line, and rebuild Kinnison to Sage 69 kV line |  | Heron | Ollin | Planned | 1048 - 1221 | AEP TNC | Gregory Crane mlforcum@aep.com 918-599-2674 | 2798 | 2022-03-31 |  | 138 | 0 | 2 | 0 |  | Crane | Crane | Tier 3 |  |  |  | 60448, 60441 | Y | N |  | 0 | 51011 | 51010
51012 | Kinnison to Sage: Rebuild 69 kV line | Build Heron 138 kV station with a 138/69 kV auto, expand the Kinnison 138 kV station, expand the Sage 69 kV station, rebuild Heron to Ollin and convert to a 138 kV line, and rebuild Kinnison to Sage 69 kV line | Update Contact | Kinnison | Sage | Planned | 1048 - 1221 | AEP TNC | Gregory Crane mlforcum@aep.com 918-599-2674 | 2823 | 2022-03-31 |  | 69 | 0 | 0.25 | 0 |  | Crane | Crane | Tier 3 |  |  |  | 60431, 6604 | Y | N |  | 0 | 51013 | 51012
57161 | Rebuild Vanderbilt to VanHumble | Rebuild 4/0 ACSR with 795 ACSR on 138 kV capable poles |  | Vanderbilt | Van Humble Switch | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2022-04-01 |  | 69 | 0 | 0.97 | 0 |  | Jackson | Jackson | Tier 4 |  |  |  | 5580, 5582 | Y | N |  | 0 | 57162 | 57161
5621 | South McAllen-Bentsen and North Edinburg-West Edinburg | Replace MLSE equipment at North Edinburg and South McAllen |  | North Edinburg | North McAllen | Planned | 795 - 0980 | AEP TCC | Michael Richardson bcogan@aep.com 918-599-2857 | 3585 | 2022-04-07 |  | 138 | 0 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 5771, 8367, 8371, 8368, 8380, 8758, 8822 | Y | N |  |  | 13351 | 5621
7161 | Naval_Base-North_Padre: Rebuild and re-conductor | For Naval Base-North Padre Tap: Rebuild line to 138 kV standards with 2000A conductor (795 ACSS). For North Padre Tap - North Padre station, double ckt. line is already built to 138 kV standards with 477 ACSR. Re-conductor both circuits with largest possible conductor to achieve maximum rating. The 2nd ckt. is part of the North Padre - Mustang Island branch |  | Naval Base | North Padre Tap | Planned | 909 - 1087 | AEP TCC | Bill Roberts bcogan@aep.com 918-599-2857 | 3690 | 2022-04-30 |  | 69 | 0 | 12.7 | 0 |  | Nueces | Nueces | Tier 3 |  |  |  | 8495, 8847, 8856 | Y | N |  |  | 15002 | 7161
48776 | Tidehaven: Construct New Distribution Station | Tidehaven: Construct New Distribution Station |  | Blessing | Lolita | Planned | 1028 - 1206 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3767 | 2022-04-30 |  | 138 | 0 | 0 | 0 |  | Matagorda | Jackson | Tier 4 |  |  |  | 8044, 8121, 8125 | Y | N |  | 0 | 48777 | 48776
51005 | Rocksprings to Friess Ranch: Rebuild 69 kV line | Rebuild Rocksprings to Sonora 69 kV line | Update Cost | Rocksprings | Friess Ranch | Planned | 1044 - 1217 | AEP TNC | Nathan Cowan mlforcum@aep.com 918-599-2674 | 2792 | 2022-04-30 |  | 69 | 0 | 22.6 | 0 |  | Edwards | Sutton | Tier 3 |  |  |  | 8238, 8239 | Y | N |  | 0 | 51006 | 51005
55217 | Putnam to Leon: Rebuild 138 kV line | Rehab Putnam to Leon 138 kV line |  | Putnam | Leon | Planned | 1042 - 1269 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 1859 | 2022-04-30 |  | 138 | 0 | 21.93 | 0 |  | Callahan | Eastland | Tier 3 |  |  |  | 1624, 6310 | Y | N |  | 0 | 55218 | 55217
55421 | Ballinger to Concho: Rebuild 69 kV line | Rebuild 69 kV line from Ballinger to Concho, install POD box bay for Rowena, install CB at Miles, install POP switches for Harriett REA and Warbler |  | Ballinger | Concho | Planned | 1088 - 1271 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 1861 | 2022-04-30 |  | 69 | 0 | 20.45 | 0 |  | Runnels | Tom Green | Tier 3 |  |  |  | 6409, 60800, 6338, 6410, 6412, 6413, 6450, 6411 | Y | N |  | 0 | 55422 | 55421
51001 | Friess Ranch to Sonora: Rebuild 69 kV line | Rebuild Rocksprings to Sonora 69 kV line | Updated Description, Contact, Schedule & Cost | Friess Ranch | Sonora | Planned | 1044 - 1217 | AEP TNC | Nathan Cowan mlforcum@aep.com 918-599-2674 | 2791 | 2022-04-30 12:00 |  | 69 | 0 | 24.3 | 0 |  | Sutton | Sutton | Tier 3 |  |  |  | 8238, 8239, 60438, 6513, 6570 | Y | N |  | 0 | 51002 | 51001
58542 | Texas City RPG | Texas City RPG |  | Cat Tail (38580), Cherokee (39075) & Greenbelt (38575) | Texas City Main (39140,39141) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2022-05-01 |  | 138 | 4.1 | 0 | 200 |  | Galveston | Galveston | Tier 2 | 2020-04-16 | 2020-09-16 |  | 38580, 39141, 38575, 39075, 39140 | Y |  |  | 0 | 58543 | 58542
47537 | Kempner Circuit Breaker Addition | LCRA TSC will add three 138kV, 3000A, 40kAIC circuit breakers in a ring bus configuration at Kempner Substation. |  | Kempner Substation | Kempner Substation | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2022-05-11 |  | 138 | 0 | 0 | 0 |  | Lampasas | Lampasas | Tier 4 |  |  |  | 260 | Y | N |  | 0 | 47538 | 47537
47436 | ROBERT BROWN JR ¿ SAN MARCOS Transmission Line OverHaul | Increase the reliability and capability of circuit T220 on the Robert Brown Jr ¿ San Marcos 4.9-mile 69-kV transmission line. Upgrade all structures to 138-kV class and bundled Suwannee capable. Upgrade conductor to bundled 959 ACSS Suwannee. Add OPGW. |  | Robert Brown JR | San Marcos | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2022-05-13 |  | 138 | 0 | 0 | 0 |  | Hays | Caldwell | Tier 4 |  |  |  | 7191, 7194, 7196 | Y | N |  | 0 | 47437 | 47436
47442 | Graphite Mine Circuit Breaker Addition | LCRA TSC will increase the reliability of transmission facilities along T109 by adding three 138-kV, 3000A, 40kAIC circuit breakers in ring-bus configuration at the Graphite Mine Substation. |  | Graphite Mine | Graphite Mine | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2022-05-13 |  | 138 | 0 | 0 | 0 |  | Burnet | Burnet | Tier 4 |  |  |  | 7084 | Y | N |  | 0 | 47443 | 47442
53965 | Red Rock - Tahitian Transmission Line Overhaul | LCRA TSC will perform an overhaul of T153 with replacement structures that are capable of operating at 138-kV and supporting a single 959 ACSR Suwannee conductor. The replacement conductor on T153 will be 595 ACSR Suwannee. This overhaul will include the installation of a 72-count optical ground wire (OPGW). |  | Red Rock | Tahitian Village | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2022-05-13 |  | 138 | 0 | 0 | 0 |  | Bastrop | Bastrop | Tier 4 |  |  |  | 7560, 7575, 7576 | Y | N |  | 0 | 53966 | 53965
5466 | Redland Switch 345/138 kV Autotransformer | Install new 345/138 kV Autotransformer at Redland Switch previously known as Herty North |  | Redland | Redland | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6076 | 2022-05-15 |  | 345 | 0 | 0 | 600 |  | Angelina | Angelina | Tier 3 |  |  |  | 3319, 3321, 3322 | Y | N |  |  | 13170 | 5466
5467 | Nacogdoches Southeast_Redland 345kV Line | Establish a new 345kV Line between Nacogdoches Southeast Switch and Redland Switch |  | Nacogdoches Southeast | Redland | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6075 | 2022-05-15 |  | 345 | 13.4 | 0 | 0 |  | Nacogdoches | Angelina | Tier 2 |  |  |  | 3119, 3321 | Y | N |  |  | 13171 | 5467
47428 | Bellville South - Prairie View Transmission Line Upgrade | The proposed project converts the existing 69-kV transmission line T283 from Bellville South - Quanex Switch - Sunnyside Prairie View Substation to 138-kV. The proposed project improves the reliability of transmission facilities on the 26.1-mile transmission line and increases the line capacity for long term system growth. |  | Bellville South | Prairie View | Conceptual |  | SBEC | James Jouett jjouett@sbec.org 979-413-7714 |  | 2022-05-15 |  | 69 | 0 | 0 | 0 |  | Austin | Waller | Tier 3 |  |  |  | 7269, 7660, 7664, 7666 | N | N |  | 0 | 47429 | 47428
53962 | Turtle Creek - Verde Creek Transmission Line Overhaul | LCRA TSC will perform an overhaul of T221 with replacement structures that are capable of operating at 138-kV and supporting a single 795 ACSR Drake conductor. The replacement conductor on T221 will be 795 ACSR Drake. This overhaul will include the installation of a 72-count optical ground wire (OPGW). |  | Turtle Creek | Verde Creek | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2022-05-15 |  | 138 | 0 | 0 | 0 |  | Kerr | Kerr | Tier 4 |  |  |  | 7146, 7442 | Y | N |  | 0 | 53963 | 53962
54101 | Ranch Road - Hilltop Transmission Line Upgrade | Increase the reliability of transmission facilities on the T375: Hilltop-Ranch Road 12 3.95-mile 138-kV transmission line by upgrading the conductor and increasing the transmission capacity. |  | Ranch Road 12 | Hilltop | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2022-05-15 |  | 138 | 0 | 0 | 0 |  | Hays | Hays | Tier 4 |  |  |  | 7186, 7190 | Y | N |  | 0 | 54102 | 54101
54105 | McCarty Lane - Ranch Road 12 Transmission Line Upgrade | Increase the reliability of transmission facilities on the T699 McCarty Lane ¿ Ranch Road 12 6.7-mile 138-kV transmission line by upgrading the conductor and increasing the transmission capacity. |  | McCarty Lane | Ranch Road 12 | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2022-05-15 |  | 138 | 0 | 0 | 0 |  | Hays | Hays | Tier 4 |  |  |  | 7182, 7186 | Y | N |  | 0 | 54106 | 54105
54109 | Fayetteville - Substation Upgrade | Increase the reliability of substation equipment at Fayetteville Substation through the replacement of the Fayetteville AT2 autotransformer and installation of two 138-kV shunt reactors. |  | Sayetteville Substation | Sayetteville Substation | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2022-05-15 |  | 138 | 0 | 0 | 0 |  | Fayette | Fayette | Tier 4 |  |  |  | 7057, 7286, 7853 | Y | N |  | 0 | 54110 | 54109
56350A | Burnett-Ringgold Magnolia Tap 69 kV Line |  |  | Burnett | Ringgold Magnolia Tap | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4015 | 2022-05-15 |  | 69 | 0 | 21 | 100 |  | Wichita | Clay | Tier 3 |  |  |  | 1452, 1523, 1543, 1544, 1426, 1491, 1545 | Y | N |  | 0 | 56861 | 56350
57163 | Rebuild VanHumble to Olivia Switch | Rebuild 4/0 ACSR with 795 ACSR on 138 kV capable poles |  | Van Humble Switch | Olivia Switch | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2022-05-15 |  | 69 | 0 | 14.4 | 0 |  | Jackson | Jackson | Tier 4 |  |  |  | 5580, 5582 | Y | N |  | 0 | 57164 | 57163
57167 | Faysville substation conversion from 69 to 138 kV | The lines from North Edinburg to Faysville Switch to Faysville will be rebuilt to 138 kV. Faysville substation will be built to 138 kV. |  | Faysville | North Edinburg | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2022-05-15 |  | 138 | 0 | 8.46 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 5782, 5786, 5787, 5788, 5780, 8380 | Y | N |  | 0 | 57168 | 57167
57731B | Hornsby Substation Addition | Construct a new 345-kV substation between Clear Springs to Gilliland Creek 345-kV transmission line to provide transmission service to a load-serving substation. Restore 138-kV transmission line from Decker to Sand Hill by removing temporary substation/arrangements made in first phase to serve load. |  | Clear Springs | Gilleland Creek | Planned |  | ERCOT |  |  | 2022-05-15 |  | 345 | 0 | 0 | 960 |  | Travis | Travis | Tier 4 |  |  |  | 7047, 7916, 7050, 9187, 7340, 9216 | Y | N |  | 0 | 57740 | 57731
57928 | Wolf Switch 138 kV Terminal Addition | Add Wolf Switch 138 kV Terminal Addition |  | Wolf Switch | Wolf Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8505 | 2022-05-15 |  | 115 | 0 | 0 | 0 |  | Ward | Ward | Tier 4 |  |  |  | 1013 | Y |  |  | 0 | 57930 | 57928
57919 | Add Buzzard Draw 138 kV Terminal Additions | Add Buzzard Draw 138 kV Terminal Additions |  | Buzzard Draw | Buzzard Draw | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8555 | 2022-05-15 01:00 |  | 138 | 0 | 0 | 0 |  | Howard | Howard | Tier 4 |  |  |  | 1355, 23829, 23838 | Y |  |  | 0 | 57921 | 57919
57925 | Add Midland County NW - Mockingbird 138 kV Line Rebuild | Add Midland County NW - Mockingbird 138 kV Line Rebuild |  | Midland County Northwest | Mockingbird | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8558 | 2022-05-15 01:00 |  | 138 | 0 | 7.5 | 0 |  | Midland | Midland | Tier 4 |  |  |  | 1182, 1183 | Y |  |  | 0 | 57927 | 57925
6979 | Lexington Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Lexington Substation. |  | Lexington |  | Planned | 1018928 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018928 | 2022-05-16 |  | 138 | 0 | 0 | 0 |  | Burleson |  | Tier 4 |  |  |  | 7571 | Y | N |  |  | 14796 | 6979
6875 | Support 69kV to 138kV West Loop Conversion Projects | Upgraded line Apollo to Jupiter to support 69kV to 138kV West Loop Conversion Projects |  | Apollo | Jupiter | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2022-05-27 |  | 138 | 0 | 3.1 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 803, 806, 802, 815, 829 | Y | N |  |  | 14684 | 6875
50880 | Medio Creek to Warburton (STEC) | Lon Hill - STEC Warburton: Line Rebuild |  | Medio Creek | STEC Warburton | Planned | 1055 - 1228 | AEP TCC | Bill Roberts bcogan@aep.com 918-599-2857 | 3783 | 2022-05-30 |  | 138 | 0 | 32.7 | 0 |  | San Patricio | Refugio | Tier 3 | 2019-09-05 | 2019-10-07 |  | 5607, 8912 | Y | Y |  | 0 | 50881 | 50880
4465 | Wirtz to FlatRock to Paleface Transmission Line Upgrade | Upgrade the 17.34 mile Wirtz (7104) - Flat Rock (7111) - Paleface (7477) 138-kV transmission line to bundled 795 ACSR Drake, 441 MVA. |  | Wirtz | Paleface | Planned |  | PEC | Charles Dewitt Charles.Dewitt@peci.com (830) 868-5041 |  | 2022-05-31 |  | 138 | 0 | 17.34 | 0 |  | Burnet | Travis | Tier 4 |  |  |  | 7104, 7111, 7477 | Y | N |  |  | 12026 | 4465
5244 | Hardy to Northside Ckt.91 Thermal Uprate | Upgrade Ckt.91 Hardy to Northside to increase thermal ratings | - Overall Date Update | Hardy | Northside | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45840, 47711 | N | N |  |  | 12919 | 5244
5945 | Howard Lane to Wells Branch Transmission Line Upgrade | Rebuild the 0.9-mile 138-kV line from Wells Branch (7288) to Howard Lane Tap (7335) in Travis county such that the new 2-hour emergency rating is at least 710 MVA. |  | Howard Lane | Wells Branch | Conceptual |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2022-05-31 |  | 138 | 0 | 0.9 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 7288, 7335 | N | N |  |  | 13656 | 5945
5949 | Study Butte Substation and Transmission Line Addition | Rebuild Altuda - Persimmon Gap to 138-kV capable structures. Establish a new transmission line 138-kV capable operated at 69-kV from Persimmon Gap to Study Butte Substation. | Scope of project redefined | Persimmon Gap | Study Butte | Conceptual |  | LCRATSC/RGEC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017405 | 2022-05-31 |  | 69 | 61 | 0 | 0 |  | Presidio | Brewster | Tier 4 |  |  |  | 76667, 76668, 76669 | N | N |  |  | 13660 | 5949
52197D | Jordan Auto A3 Addition (PLACID 138kV Sub) | Upgrade Ckt.86J Connor to Bender to increase thermal limits. |  | Connor | Bender | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointe 713-207-2760 |  | 2022-05-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2019-10-24 | 2019-11-18 |  | 40155, 40665 | Y | N |  | 0 | 57348 | 52197
54811 | Winecup: Build 69 kV station | Construct new 69 kV box bay on the North San Angelo to San Angelo Grape Creek Tap 69 kV line | NEW | Winecup |  | Planned | 1041 - 1268 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 1858 | 2022-05-31 |  | 69 | 0 | 0 | 0 |  | Tom Green |  | Tier 4 |  |  |  | 60796, 6459, 6465 | Y | N |  | 0 | 54812 | 54811
55550 | Brushline: Construct New Distribution Station | Brushline: Construct New Distribution Station | NEW |  |  | Planned | 1106 - 1284 | AEP | Rick Garcia bcogan@aep.com 918-599-2857 | 3826 | 2022-05-31 |  | 138 | 0 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8972, 5754, 8963 | Y |  |  | 0 | 55551 | 55550
55961 | PSARCO to Highlands Ckt.08G Upgrades | Upgrade Ckt.08G PSARCO to Highlands with minimum 427MVA Continuous Rating |  | Highlands | PSARCO | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40811, 41300 | Y | N |  | 0 | 55962 | 55961
57735A | Mykawa 138kV Switching Station | Install new CNP-owned 138kV switching station |  | Pearland |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42750 | Y | N |  | 0 | 57736 | 57735
57750 | Seabrook 138kV Distribution Substation | Build new 138kV Seabrook distribution substation. Double tap from Ckt.79F PH Robinson to Hanna and Ckt.96A PH Robinson to Bayou. |  | Seabrook |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-05-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 42851, 42852, 42013, 42014, 42160, 42780 | Y | N |  | 0 | 57751 | 57750
57912 | Champlin to Weil Tract: Rebuild 138 kV Line | Champlin to Weil Tract Line Rebuild | New | Champlin | Weil Tract | Planned | 1111 - 1289 | ETT | Nathan Cowan mlforcum@aep.com 918-599-2674 | 3830 | 2022-05-31 |  | 138 | 0 | 1.37 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8476, 8482 | Y | N |  | 0 | 57913 | 57912
58006 | Magnolia Cap Bank | Install Cap bank (14.4 Mvar ) at Magnolia |  | Kosciusko |  | Planned | 1115 - 1293 | AEP | Glen Reed gareed@aep.com 918-599-2664 | 3834 | 2022-05-31 |  | 138 | 0 | 0 | 0 | 0,14.4 |  |  | Tier 4 |  |  |  | 8583 | Y |  |  | 0 | 58007 | 58006
58008 | Laredo VFT North to North Laredo Switch: Rebuild 138 kV Line | Rebuild 11.691 miles of the Laredo VFT North to North Laredo Switch 138 kV transmission line and upgrade any limiting elements. |  | Laredo | Laredo | Planned | 1116 - 1294 | AEP | Glen Reed gareed@aep.com 918-599-2664 | 3835 | 2022-05-31 |  | 138 | 11.68 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 8112, 8643, 80481, 8909, 8918, 80013, 88909 | Y |  |  | 0 | 58009 | 58008
57735B | Mykawa 138kV Switching Station | Loop Ckt.06K into new CNP-owned 138kV switching station to create new Ckt.06 Gulfgate to Mykawa to Pearland |  | Mykawa | Gulfgate/Pearland | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42742, 42750, 43051 | Y | N |  | Cost include in main project | 57737 | 57735
57735C | Mykawa 138kV Switching Station | Loop Ckt.91A into new CNP-owned 138kV switching station to create new Ckt.91 Gulfgate to Mykawa to Pearland |  | Mykawa | Gulfgate/Pearland | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42741, 42750, 43052 | Y | N |  | Cost include in main project | 57738 | 57735
11TPIT0008 | RAINEY_ST 138kV substation | Establish a new 138kV Rainey St. Substation with (2) 50MVA transformers and cut into existing Ckt 1015 (Pedernales to Seaholm). |  | Rainey St Substation | Rainey St Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | PLAN_117_P158 PLAN_117_P166 PLAN_117_P167 | 2022-06-01 |  | 138 | 0.1 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9261, 9118, 9132 | Y | N |  |  | 8208 | 1032
13TPIT0124 | Airport 69 kV Substation | Build new load serving station in the 69 kV line from Lone Tree to Twin Pines Switch. |  | Airport |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2022-06-01 |  | 69 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  | 5601, 5600, 5602 | Y | N |  |  | 8729 | 1538
17TPIT0002 | Hunt Lane to Pinn Road - 138 kV Transmission Line Rebuild | Rebuild approximately eight circuit miles of 138 kV transmission from Hunt Lane to Pinn Road |  | Hunt Lane | Pinn Rd | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0190 | 2022-06-01 |  | 138 | 0 | 8 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5054, 5305, 5324, 5345, 5427 | Y | N |  | There are no transformers associated with this project | 9558 | 2307
17TPIT0001 | 36th St to Merida - 138 kV Transmission Line Rebuild | Rebuild approximately four circuit miles of 138 kV transmission from 36th Street to Merida |  | 36th Street | Merida | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0196 | 2022-06-01 |  | 138 | 0 | 4 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5310, 5427 | Y | N |  | There are no transformers associated with this project | 9559 | 2308
15TPIT0044 | Fowlerton Capacitor | Add 19.2 MVAR capacitor |  | Fowlerton |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2022-06-01 |  | 138 | 0 | 0 | 0 | 0,19.2 | La Salle |  | Tier 4 |  |  |  | 5705 | Y | N |  |  | 9835 | 2554
45084B | Braunig to Highland Rebuild | Rebuild approximately sixteen circuit miles of 138kV transmission from Braunig to Highland Hills/Brooks. This rebuild is between 'Schillers Tap to Braunig'. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0194, T-0238 | 2022-06-01 |  | 138 | 0 | 16 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5030, 5095, 5205 | Y |  |  | 0 | 45086 | 45084
45084A | Braunig to Highland Rebuild | Rebuild approximately six circuit miles of 138kV transmission from Braunig to Highland Hills/Brooks. This rebuild is between 'Highland Hills to Schillers Tap'. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0194, T-0238 | 2022-06-01 |  | 138 | 0 | 6 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5030, 5095, 5205 | Y |  |  | 0 | 45085 | 45084
45101 | Chavaneaux_Chavaneaux Tap (Chavaneaux to Palo Alto)- 138 kV | CPSE_Chavaneaux_Chavaneaux 138 kV Tap Rebuild (Chavaneaux to Palo Alto). |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0256 | 2022-06-01 |  | 138 | 0 | 0.9 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5085, 5330 | Y |  |  | 0 | 45102 | 45101
48327 | Reconductor 138kV ckt 972 Howard Lane to McNeil to 3000A. |  |  | 9079 | 9217 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinene (512) 322-6740 |  | 2022-06-01 |  | 138 | 0 | 2.81 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9079, 9217 | Y |  |  | 0 | 48328 | 48327
54568 | CPSE_New_Navistar_Substation | CPSE_New_Navistar_Substation |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2022-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5317, 5007, 5297 | Y |  |  | 0 | 54569 | 54568
4577 | BRYN_4577_Dansby_Rebuild | Convert Dansby 69kV bus to Double Bus, Double Breaker configuration |  |  |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2022-06-29 |  | 69 | 0 | 0 | 200 |  | Brazos |  | Tier 4 |  |  |  | 32875, 32897 | Y |  |  | 0 | 45636 | 4577
5154 | Holford 138 kV new load substation and connections | Holford 138 kV new substation and its connections to CampbellSW and to Firewheel as well as some load growths at Holford |  | CampbellSW | Firewheel | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2022-06-30 |  | 138 | 0 | 1.5 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 835, 821, 838 | Y |  |  |  | 12810 | 5154
50440 | Delhi Substation Addition | Add a new load serving substation 10 miles north of IH-10 along 304, w/30 MVA PWT. |  | Delhi | Delhi | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2022-06-30 |  | 69 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  | 7896 | Y | N |  | 0 | 50441 | 50440
51734 | Blue Stem to Delhi Transmission Line | Build new 9.5 mile 138/69 kV transmission. |  | BlueStem | Delhi | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2022-06-30 02:00 |  | 69 | 9.5 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  | 7895, 7230, 7231, 7896 | Y | N |  | 0 | 51843 | 51734
5457 | Load serving | New station to aid in DME's load serving |  | Brinker |  | Planned |  | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2022-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 927, 906, 907, 913, 921 | Y | N |  |  | 13160 | 5457
6072 | Eldorado to Ft. McKavitt 69 kV line: Rebuild 69 kV line | Rehab Eldorado to Ft. McKavitt 69 kV line |  | Eldorado Tap | Ft. McKavitt | Planned | 786 - 0971 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2677 | 2022-07-31 |  | 69 | 0 | 19.41 | 0 |  | Schleicher | Schleicher | Tier 4 |  |  |  | 6505, 6506, 6507, 6508 | Y | N |  |  | 13794 | 6072
57169 | Rebuilds Faysville Switch to Redgate 138 kV | Rebuilds Faysville SW to Redgate from 69 kV to 138 kV and opens the current Redgate tap |  | Redgate | Faysville Switch | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2022-08-01 |  | 138 | 0 | 3.45 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 5787, 88380, 161031 | Y | N |  | 0 | 57170 | 57169
5165 | Borglum: Construct a new 138/69 kV station | Construct a new 138/69 kV Borglum station and install an 138/69 kV autotransformer with 130 MVA capacity at Borglum station. Rebuild and convert Beeville - Three Rivers 69 kV line to 138 kV and reterminate into Borglum. Construct the new 138/69 kV double circuit transmission line from Tuleta - Beeville. | Schedule Update | Borglum |  | Under Construction | 742 - 0925 | AEP TCC | Dave Goetz bcogan@aep.com 918-599-2857 | 2914 | 2022-08-30 |  | 138 | 0 | 0 | 130 |  | Bee |  | Tier 1 | 2015-03-01 | 2015-09-01 | 2015-10-01 | 8196, 8197, 8205, 8107, 8198, 8199, 8904 | Y | N |  |  | 13315 | 5165
5166 | Borglum to Three Rivers: Rebuild 69 kV line | Construct a new 138/69 kV Borglum station and install an 138/69 kV autotransformer with 130 MVA capacity at Borglum station. Rebuild and convert Beeville - Three Rivers 69 kV line to 138 kV and reterminate into Borglum. Construct the new 138/69 kV double circuit transmission line from Tuleta - Beeville. | Schedule Update | Borglum | Three Rivers | Under Construction | 742 - 0925 | AEP TCC | Dave Gotez bcogan@aep.com 918-599-2857 | 2915 | 2022-08-30 |  | 138 | 6 | 22 | 0 |  | Bee | Live Oak | Tier 1 | 2015-03-01 | 2015-09-01 | 2015-10-01 | 8156, 84006, 8142, 8199, 8196, 8400, 8403 | Y | N |  | 0 | 57889 | 5166
5167 | Borglum to Tuleta: Build new double circuit 138/69 kV line | Construct a new 138/69 kV Borglum station and install an 138/69 kV autotransformer with 130 MVA capacity at Borglum station. Rebuild and convert Beeville - Three Rivers 69 kV line to 138 kV and reterminate into Borglum. Construct the new 138/69 kV double circuit transmission line from Tuleta - Beeville. | Schedule Update | Borglum | Tuleta | Under Construction | 742 - 0925 | AEP TCC | Dave Goetz bcogan@aep.com 918-599-2857 | 2916 | 2022-08-30 |  | 138 | 23.5 | 23.5 | 0 |  | Bee | Bee | Tier 1 | 2015-03-01 | 2015-09-01 | 2015-10-01 | 8584, 8629, 88198, 8196, 8197, 8198, 8585, 8586, 8592, 8590, 8593 | Y | N |  |  | 13317 | 5167
6719 | Twelvemile Substation Addition | Construct a new substation named Twelvemile off the Bakersfield to Schneeman Draw transmission line to support a generation interconnection request (16INR0104). |  | Bakersfield | Schneeman Draw | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018769 | 2022-09-21 |  | 345 | 0 | 0 | 0 |  | Pecos | Crockett | Tier 4 |  |  |  | 76008, 7053, 76015 | Y | N |  | 0 | 58408 | 6719
3505 | Cibolo Substation, T3 transformer addition | Add T3, 40 MVA 138-26.18 kV power transformer, CSW and low side |  | Cibolo |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2022-10-14 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7608 | Y | N |  |  | 10887 | 3505
49572 | Goodlett to Quanah: Build a new portion of 69 kV line | Build new section of 69 kV line between Goodlett and Quanah |  | Goodlett | Quanah | Planned | 1022 - 1200 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2784 | 2022-10-31 |  | 69 | 0 | 0 | 0 |  | Hardeman |  | Tier 4 |  |  |  | 6052, 6051, 60446 | Y | N |  | 0 | 49573 | 49572
50952 | Whitepoint: Replace reactors | Replace the 10 ohm reactors with 19.08 ohm reactors at Whitepoint |  | Whitepoint |  | Planned | 1086 - 1259 | AEP | Michael Glueck bcogan@aep.com 918-599-2857 | 3806 | 2022-10-31 |  | 138 | 0 | 0 | 0 | -18.16,0 | San Patricio |  | Tier 4 |  |  |  | 8961, 80128, 80129 | Y | N |  | 0 | 50953 | 50952
50866 | Structure 31/8 - Kenedy SS: Line Rebuild | Coleto Creek - Kenedy SS: Line Rebuild |  | Rosata | Kenedy SS | Planned | 1052 - 1225 | AEP TCC | Curtis Brown bcogan@aep.com 918-599-2857 | 3779 | 2022-11-30 |  | 138 | 0 | 14.3 | 0 |  | Karnes | Karnes | Tier 3 |  |  |  | 8186, 88153 | Y | N |  | 0 | 50867 | 50866
50868 | Rosata - Structure 31/8: Line Rebuild | Coleto Creek - Kenedy SS: Line Rebuild |  | Rosata | Kenedy SS | Planned | 1052 - 1225 | AEP TCC | Curtis Brown bcogan@aep.com 918-599-2857 | 3780 | 2022-11-30 |  | 138 | 0 | 15.5 | 0 |  | Goliad | Karnes | Tier 3 |  |  |  | 8186, 88153 | Y | N |  | 0 | 50869 | 50868
55470 | Bison to Ozona: Rebuild 69 kV line | Rehab 69 kV line from Bison to Ozona |  | Bison | Ozona | Planned | 1095 - 1273 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 1863 | 2022-11-30 |  | 69 | 0 | 27 | 0 |  | Reagan | Crockett | Tier 4 |  |  |  | 6549, 6560, 60395 | Y | N |  | 0 | 55471 | 55470
55603 | Big Foot to Pearsall: Rebuild 69 kV line | Rebuild 69 kV line from Big Foot to Dilley |  | Big Foot | Pearsall | Planned | 1104 - 1282 | AEP | Bill Roberts bcogan@aep.com 918-599-2857 | 3821 | 2022-11-30 |  | 69 | 0 | 14.79 | 0 |  | Frio | Frio | Tier 3 |  |  |  | 8218, 8216 | Y |  |  | 0 | 55604 | 55603
45136 | CPSE_New Midtown Substation | New Mid Town substation looped into Comal St to Olmos transmission line. |  |  |  |  | S-0910 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0283 | 2022-12-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5311, 5096, 5325 | Y |  |  | 0 | 45137 | 45136
50647 | CPSE_Merida to Westside MLSE | Upgrade terminal at Merida to ensure a 2000 A rating. |  | Merida | Westside | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0773 | 2022-12-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5310, 5490 | Y |  |  | 0 | 50648 | 50647
57890 | Brightside Permanent Connection | Construct Charter Station |  | Beeville | Three Rivers | Planned | 1114 - 1292 | AEP | Glen Reed gareed@aep.com 918-599-2664 | 3833 | 2022-12-11 |  | 138 | 0 | 0 | 0 |  | Bee |  | Tier 4 |  |  |  | 8156 | Y |  |  | 0 | 57891 | 57890
5492 | Venus - Webb/Cedar Hill Sw. Sta. 345 kV DCKT Line | Upgrade existing Venus - Webb/Cedar Hill Sw. Sta. 345 kV Double Ckt Line |  | Ellis | Tarrant | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4230 | 2022-12-15 |  | 345 | 0 | 27 | 0 |  | Ellis | Tarrant | Tier 4 |  |  |  | 1904, 1906, 2420, 11901 | Y | N |  |  | 13230 | 5492
7126 | Renner TPL 138 kV Capacitors | Upgrade existing capacitor banks |  | RENNER SWITCH | RENNER SWITCH | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M3048 | 2022-12-15 |  | 138 | 0 | 0 | 0 | 0,110.4 | Dallas | Dallas | Tier 4 |  |  |  | 2352, 2353 | Y | N |  |  | 14964 | 7126
7127 | East Levee 138 kV Emergency Capacitors | Upgrade East Levee 138 kV Emergency Capacitors |  | EAST LEVEE | EAST LEVEE | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4290 | 2022-12-15 |  | 138 | 0 | 0 | 0 | 0,110.4 | Dallas | Dallas | Tier 4 |  |  |  | 2481, 2482 | Y | N |  |  | 14965 | 7127
57934 | Midland East - Spraberry 138 kV Line Rebuild | Add Midland East - Spraberry 138 kV Line Rebuild |  | Midland East | Spraberry | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8147 | 2022-12-15 |  | 138 | 0 | 18.9 | 0 |  | Midland | Midland | Tier 4 |  |  |  | 1023, 1329, 11123, 11134, 1132, 11361 | Y |  |  | 0 | 57952 | 57934
52318 | Royse Switch - Greenbriar Switch 138 kV Line | Upgrade the Royse Switch - Greenbriar Switch 138 kV Line |  | Royse | Greenbriar | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4292 | 2022-12-15 01:00 |  | 138 | 0 | 0 | 0 |  | Collin | Rockwall | Tier 3 |  |  |  | 2472, 2707, 12527 | Y |  |  | 0 | 52319 | 52318
57726 | Commerce - Royse 69 kV Line Conversion to 138 kV | Convert existing 69 kV Line to 138 kV |  | Commerce | Royse | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R985 | 2022-12-15 01:00 |  | 138 | 0 | 0 | 0 |  | Hunt | Rockwall | Tier 3 |  |  |  | 1818, 1821, 1824, 1826, 1827, 1828, 1829, 1830, 1831, 6944, 1820, 2463, 2472 | Y |  |  | 0 | 57727 | 57726
50446 | Santa Clara Substation Addition | Add a new load serving substation 10 miles west of City of Seguin, of IH-10, w/ twin 40 MVA PWTs. |  | Santa Clara Substation | Santa Clara Substation | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2022-12-16 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7891 | Y | N |  | 0 | 50447 | 50446
51841 | H-Pole to Santa Clara Transmission Line Addtition | Build 5 onmiles of new double circuit 138kV t-line loop, 1192 ACSR Bunting, from H-pole structure to Santa Clara Substation |  | H-pole ( Structure/Tap) | Santa Clara | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2022-12-23 |  | 69 | 10 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7890, 7892, 7606, 7608, 7891 | Y | N |  | 0 | 57331 | 51841
5940B | Mountain Home Substation and Transmission Line Addition | Construct a 138-kV transmission line from Harper substation to Mountain Home substation. | For total project cost please see 5940_C | Mountain Home | Harper | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017394 | 2022-12-27 |  | 138 | 11.5 | 0 | 0 |  | Kerr | Gillespie | Tier 1 | 2016-11-18 |  |  | 74100, 7410, 7750 | Y | N |  | 0 | 46981 | 5940
5940A | Mountain Home Substation and Transmission Line Addition | Construct new Mountain Home substation and construct a 138-kV transmission line from Hunt substation to Mountain Home substation. | For total project cost please see 5940_C | Hunt | Mountain Home | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017394 | 2022-12-27 |  | 138 | 7.5 | 0 | 0 |  | Kerr | Kerr | Tier 1 | 2016-11-18 |  |  | 7750, 7144 | Y | N |  | 0 | 46980 | 5940
5940C | Mountain Home Substation and Transmission Line Addition | Add one(1) 138/69-kV autotransformer at Harper substation |  | Harper | Live Oak | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017394 | 2022-12-27 00:10 |  | 138 | 0 | 21.7 | 45 |  | Gillespie | Gillespie | Tier 1 | 2016-11-18 |  |  | 7412, 7130, 7132, 7149, 7410, 7413, 74100 | Y | N |  | 0 | 46982 | 5940
43460 | Moody to Stewart Ckt.63 Upgrades | Upgrade Ckt.63 Moody to Stewart |  | Moody | Stewart | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-30 |  | 138 | 0 | 0 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 42950, 43290 | Y |  |  | 0 | 43461 | 43460
52183 | EXTER 69kV Substation Removal | Remove EXTER 69kV Substation from Ckt.53B |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-30 |  | 138 | 0 | 0 | 0 |  | Galveston | Harris | Tier 4 |  |  |  | 42600, 42080, 43510 | Y | N |  | Cost included in MOD 52181 - ENCO new customer sub | 52184 | 52183
6876 | Support 69kV to 138kV West Loop Conversion Projects | Upgraded line Jupiter to College to support 69kV to 138kV West Loop Conversion Projects |  | Jupiter | College | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2022-12-31 |  | 138 | 0 | 2.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 806, 829 | Y |  |  |  | 14685 | 6876
52218 | Alvin 69kV Substation Bypass | Alvin 69kV Substation Bypass |  | Webster | Manvel | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 69 | 0 | 0 | 0 |  | Galveston | Brazoria | Tier 4 |  |  |  | 42080, 43510, 44440 | Y | N |  | 0 | 52225 | 52218
52267F | SR Bertron 138/69kV Conversions | ReMove 100 MVAr Cap Bank from HOC |  | HO Clarke |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47155, 47151, 47175 | Y | N |  | Cost included in Phase A | 52291 | 52267
52267D | SR Bertron 138/69kV Conversions | Disconnect Ckt.16A and Ckt.23A at SRB and Reconnect to Create New Ckt.xx South Channel to Deepwater |  | South Channel | Deepwater | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40089, 40470, 41380, 41410, 41415 | Y | N |  | Cost included in Phase A. | 52289 | 52267
52267B | SR Bertron 138/69kV Conversions | Remove SRB Auto A1 |  | SR Berton | SR Berton | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  |  | 0 | 0 | -200 |  | Harris | Harris | Tier 4 |  |  |  | 110005, 41400, 41415 | Y | N |  | Cost included in Phase A. | 52287 | 52267
52267E | SR Bertron 138/69kV Conversions | De-Energize Ckt.55D SRB to SRB |  | SR Bertron | SR Bertron | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41410, 41415, 41419, 40089, 40470, 41400, 49004, 110005 | Y | N |  | Cost included in Phase A. | 52290 | 52267
52267C | SR Bertron 138/69kV Conversions | Remove SRB Auto A2 |  | SR Bertron | SR Bertron | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  |  | 0 | 0 | -192 |  | Harris | Harris | Tier 4 |  |  |  | 49004, 41400, 41410 | Y | N |  | Cost Included in Phase A. | 52288 | 52267
52267A | SR Bertron 138/69kV Conversions | Deenergize 69kV SRB substation and connect 138kV Buses |  | SR Bertron | SR Bertron | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  |  | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41405, 41415, 40290, 40480, 40540, 41400, 41540 | Y | N |  |  | 52286 | 52267
52267G | SR Bertron 138/69kV Conversions | Install cap bank removed from HOC at SRB. |  |  | SR Bertron | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 0 | 0 | 0,100 | Harris | Harris | Tier 4 |  |  |  | 41400 | Y | N |  | Cost included in Phase A | 52292 | 52267
56003A | Mont Belvieu Reliability Project | Expand Jordan and Mont Belvieu with new line positions |  | Jordan | Winfre | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2020-09-01 |  |  | 40500, 40764, 40857, 40740, 40855 | Y | N |  | 0 | 56075 | 56003
57521A | Stone Lake New Sub Ckt66 | Install Stone Lake Distribution Substation AP2022 to create new Ckt..66 Hockley to Stone Lake to Tomball. |  | Stone Lake | Hockley/Tomball | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 44840, 45880, 46511 | Y | N |  | 0 | 57530 | 57521
52523A | Hayes to WA Parish Ckt.09A Upgrades | Upgrade Ckt.09A Hayes to Alief as a Clearance upgrade |  | Hayes | Alief | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 1.7 | 0 |  | Harris | Harris | Tier 3 | 2019-12-18 | 2020-01-16 |  | 44020, 44120, 44310 | Y | N |  | 0 | 57335 | 52523
56003B | Mont Belvieu Reliability Project | Remove existing Jordan TR1 tap from Ckt.86I Jordan to Cities. Reconnect at new Ckt.52A Jordan to Winfre |  | Jordan | Cities | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2020-09-01 |  |  | 40340, 40855, 40740, 40857 | Y | N |  | Cost included in main entry | 56076 | 56003
52523B | Hayes to WA Parish Ckt.09A Upgrades | Upgrade Ckt.09A Alief to Stafford as a Clearance upgrade |  | Alief | Stafford | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 4.67 | 0 |  | Harris | Harris | Tier 3 | 2019-12-18 | 2020-01-16 |  | 44020, 44671 | Y | N |  | Cost included in main entry | 57336 | 52523
56003C | Mont Belvieu Reliability Project | Reconfigure existing 86B/86H/86K to create new Ckt.52B Winfre to Eagle with minimum 360/440 MVA |  | Winfre | Eagle | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2020-09-01 |  |  | 40220, 40300, 40500, 40764 | Y | N |  | Cost included in main entry | 56077 | 56003
52523C | Hayes to WA Parish Ckt.09A Upgrades | Upgrade Ckt.09A Stafford to WA Parish as a Clearance upgrade |  | Stafford | WA Parish | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 11.75 | 0 |  | Harris | Harris | Tier 3 | 2019-12-18 | 2020-01-16 |  | 44015, 44671 | Y | N |  | Cost included in main entry | 57337 | 52523
56003D | Mont Belvieu Reliability Project | Expand Jordan and Mont Belvieu with new line positions |  | Eagle | Mont Belvieu | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2020-09-01 |  |  | 40500, 41111 | Y | N |  | Cost included in main entry | 56078 | 56003
56003E | Mont Belvieu Reliability Project | Expand Jordan and Mont Belvieu with new line positions |  | Dalton | BRINE/Mont Belvieu | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2020-09-01 |  |  | 40220, 40775, 40740, 41111, 41113 | Y | N |  | Cost included in main entry | 56079 | 56003
56003F | Mont Belvieu Reliability Project | Reconfigure existing 86B/86H/86K to create new Ckt.86B Chevron to Langston with minimum 440/525 MVA |  | Chevron | Langston | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Chambers | Tier 3 | 2020-09-01 |  |  | 40300, 40775 | Y | N |  | Cost included in main entry | 56080 | 56003
56003G | Mont Belvieu Reliability Project | Upgrade Ckt.84D Cedar Bayou Plant to Cedar Bayou Tap to HOPSON with minimum 682MVA Emergency Rating |  | Cedar Bayou Plant | Cedar Bayou/HOPSON | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2020-09-01 |  |  | 40012, 40015, 41690 | Y | N |  | Cost included in main entry | 56081 | 56003
56003H | Mont Belvieu Reliability Project | Upgrade Ckt.86A Cedar Bayou Plant to Chevron with minimum 669MVA Emergency Rating |  | Cedar Bayou Plant | Chevron | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Harris | Tier 3 | 2020-09-01 |  |  | 40015, 40300 | Y | N |  | Cost included in main entry | 56082 | 56003
50872 | Structure 25/7 - Medio Creek: Line Rebuild | Lon Hill - STEC Warburton: Line Rebuild |  | Haisley | Medio Creek | Planned | 1055 - 1228 | AEP TCC | Bill Roberts bcogan@aep.com 918-599-2857 | 3784 | 2023-01-31 |  | 138 | 0 | 14.9 | 0 |  | San Patricio | Refugio | Tier 3 |  |  |  | 8912, 8920 | Y | N |  | 0 | 50873 | 50872
45397 | Lion: 138 kV Station & Transmission Line | Lion: 138 kV Station with new line to Stewart Road |  | Lion | Stewart Road | Planned | 885 - 1063 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3672 | 2023-02-23 |  | 138 | 2.71 | 0 | 40 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8969, 8758, 8951 | Y | N |  | 0 | 50139 | 45397
6373 | Hamilton Road to Picacho ckt #2, rebuild 138 kV line | Rebuild Hamilton Road to Picacho 138 kV line ckt #2 |  | Hamilton Road | Picacho | Planned | 870-1051 | AEP TCC | Nathan Cowan bcogan@aep.com 918-599-2857 | 3660 | 2023-03-30 |  | 138 | 0 | 8.4 | 0 |  | Val Verde | Val Verde | Tier 4 |  |  |  | 8186, 8255, 8690, 8688, 8684 | Y | N |  |  | 14117 | 6373
5648 | Hamilton Road to Picacho Ckt #2 138 kV Line: Rebuild | Rebuild Hamilton Road to Picacho 138 kV line ckt #1 | Update Schedule | Hamilton Road | Del Rio | Under Construction | 869-1050 | AEP | Jeremy Brazeal bcogan@aep.com 918-599-2857 | 3659 | 2023-03-31 |  | 138 | 0 | 8.7 | 0 |  | Val Verde | Val Verde | Tier 4 |  |  |  | 8255, 8684 | Y | N |  |  | 13382 | 5648
45501 | Eldorado Live Oak to Sonora: Rebuild 69 kV line | Rehab Eldorado Live Oak to Sonora 69 kV line | Update Title, Contact, Schedule, Cost, Miles Rebuilt & RPG Dates | Eldorado Live Oak | Sonora | Planned | 982 - 1160 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2769 | 2023-03-31 01:00 |  | 69 | 0 | 23.92 | 0 |  | Schleicher | Sutton | Tier 3 | 2018-12-18 | 2019-01-17 |  | 6498, 6505, 6509, 6510, 6513 | Y | N |  | 0 | 45502 | 45501
55572 | Burma to Sterling City: Rebuild 69 kV line | Rehab 69 kV line from Burma to Sterling City |  | Burma | Sterling City | Planned | 1096 - 1274 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 1864 | 2023-04-30 |  | 69 | 0 | 32 | 0 |  | Tom Green | Sterling | Tier 3 |  |  |  | 6439, 6445, 6460, 61016, 61017, 6435, 6446, 6461, 60411 | Y | N |  | 0 | 55573 | 55572
55622 | Dilley to Pearsall: Rebuild 69 kV line | Rebuild 69 kV line from Big Foot to Dilley |  | Dilley | Pearsal | Planned | 1104 - 1282 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3822 | 2023-05-01 |  | 69 | 0 | 17.7 | 0 |  | Frio | Frio | Tier 3 |  |  |  | 8216, 8208 | Y |  |  | 0 | 55623 | 55622
54103 | Hilltop - Strahan Transmission Line Upgrade | Increase the reliability of transmission facilities on the T445: Hilltop ¿ Strahan 1.25-mile 138-kV transmission line by upgrading the conductor and increasing the transmission capacity. |  | Hilltop | Strahan | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2023-05-12 |  | 138 | 0 | 0 | 0 |  | Hays | Hays | Tier 4 |  |  |  | 7190, 7193 | Y | N |  | 0 | 54104 | 54103
54204 | Gonzales - Hochheim Transmission Line Overhaul | Increase the reliability and capacity of transmission facilities on the T542 Luling ¿ Cuero 19.6-mile 69-kV transmission line from Gonzales (structure #33) to Hochheim Tap. LCRA TSC will perform an overhaul of T542 with replacement structures that are capable of operating at 138-kV and supporting a single 795 ACSR Drake conductor. The replacement conductor on T542 will be 795 ACSR Drake. This overhaul will include the installation of a 72-count optical ground wire (OPGW). |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2023-05-12 |  | 69 | 0 | 0 | 0 |  | Gonzales | DeWitt | Tier 4 |  |  |  | 7223, 78577 | Y | N |  | 0 | 54205 | 54204
12TPIT0080 | Forney Sw. Sta. Second 600 MVA, 345/138 kV Autotransformer | Add second 345/138 autotransformer | Project Deferral | Forney Sw. Sta. |  | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4037 | 2023-05-15 |  | 345 | 0 | 0 | 600 |  | Kaufman |  | Tier 3 | 2008-06-01 | 2008-07-01 |  | 2437, 2438 | Y | N | 2007-R2 |  | 9769 | 2489
4270 | Handley - Hemphill 138 kV Line | Upgrade existing line | Project Deferral | Handley | Hemphill | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5214 | 2023-05-15 |  | 138 | 0 | 7.4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1950, 2164, 2167 | Y | N |  |  | 11818 | 4270
4804 | Wichita Falls South 345/138 kV autotransformer | Install autotransformer |  | Wichita Falls South |  | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4010 | 2023-05-15 |  | 345 | 0 | 0 | 600 |  | Archer |  | Tier 4 |  |  |  | 11464, 11465, 1422, 1425, 1464 | Y | N |  |  | 12410 | 4804
4834 | Cresson - Rocky Creek 138 kV Line | Construct new line |  | Cresson | Rocky Creek | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5228 | 2023-05-15 |  | 138 | 3 | 0 | 0 |  | Tarrant | Parker | Tier 2 |  |  |  | 1881, 2202 | Y | N |  |  | 12436 | 4834
5436 | Morgan Creek - McDonald 138 kV Line | Upgrade existing line | Project Deferral | Morgan Creek | McDonald Rd | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8360 | 2023-05-15 |  | 138 | 0 | 31.8 | 0 |  | Howard | Mitchell | Tier 3 |  |  |  | 1032, 1333 | Y | N |  |  | 13139 | 5436
5475 | Lufkin Switch - Redland Switch 345 kV Line | Construct a new 345 kV Line from Lufkin Switch to Redland Switch |  | Lufkin Switch | Redland Switch | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6077 | 2023-05-15 |  | 345 | 8.1 | 0 | 0 |  | Angelina | Angelina | Tier 2 |  |  |  | 3117, 3321 | Y | N |  |  | 13180 | 5475
5525 | Forney - Lake Hubbard 345 kV Line | Construct new 345 kV line |  | Forney | Lake Hubbard | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4233 | 2023-05-15 |  | 345 | 0 | 7.5 | 0 |  | Kaufman | Dallas | Tier 2 |  |  |  | 2455, 2467 | Y | N |  |  | 13252 | 5525
5526 | Forney 345 kV Switching Station | Reconstruct existing 345 kV switching station |  | Forney |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4114 | 2023-05-15 |  | 345 | 0 | 0 | 0 |  | Kaufman |  | Tier 3 |  |  |  | 2467, 2433, 2437, 2470, 2478, 150189, 2438, 12438 | Y | N |  | 0 | 49916 | 5526
5624 | Killeen Sw. Sta. 345/138 kV Autotransformer Replacement | Replace existing autotransformer |  | Killeen Sw. Sta. | Killeen Sw. Sta | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R797 | 2023-05-15 |  | 345 | 0 | 0 | 600 | -75,0 | Bell | Bell | Tier 3 |  |  |  | 3422, 3423, 13423 | Y | N |  |  | 13354 | 5624
5981 | Shamburger North 345/138 kV Sw. Sta. | Establish Shamburger North 345/138 kV Sw. Sta. |  | Shamburger North | Shamburger North | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6083 | 2023-05-15 |  | 345 | 0 | 0 | 600 |  | Smith | Smith | Tier 3 |  |  |  | 3217, 3223, 3226, 2478, 3103, 3201, 3206 | Y | N |  |  | 13696 | 5981
7023 | Hicks Sw. Sta. - Roanoke Sw. Sta. 345 kV Double-circuit Line | Upgrade existing Hicks Sw. Sta. - Roanoke Sw. Sta. 345 kV Double-circuit Line |  | Hicks Sw. Sta. | Roanoke Sw. Sta. | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5256 | 2023-05-15 |  | 345 | 0 | 19.4 | 0 |  | Tarrant | Denton | Tier 3 |  |  |  | 1855, 2081, 1845, 1851 | Y | N |  | 0 | 52815 | 7023
7125 | Greenville Ave 138 kV Capacitors | Upgrade existing capacitor banks |  | Greenville Ave | Greenville Ave | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4177 | 2023-05-15 |  | 138 | 0 | 0 | 0 | 0,110.4 | Dallas | Dallas | Tier 4 |  |  |  | 2882, 2883 | Y | N |  |  | 14963 | 7125
51243 | Keller Wall Price 138 kV Switch | Upgrade Roanoke - Keller Wall Price Switch 138 kV Double-Circuit Line |  | Keller Wall Price |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5251 | 2023-05-15 |  | 138 | 0 | 0 | 0 |  | Denton | Tarrant | Tier 4 |  |  |  | 2037, 12038, 12307, 566, 679, 1852, 1854, 1856, 1857, 2027, 2033, 2034, 2036, 2038, 2058, 11857, 15100, 15101 | Y |  |  | 0 | 52845 | 51243
53956 | Coronado - Fairland Transmission Line Upgrade | Increase the reliability of transmission facilities on the T110 Coronado - Fairland 12.4-mile 138-kV transmission line by replacing the existing Condor conductor with Drake conductor. |  | Coronado | Fairland | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2023-05-15 |  | 138 | 0 | 0 | 0 |  | Burnet | Llano | Tier 4 |  |  |  | 7087, 7518 | Y | N |  | 0 | 53957 | 53956
53958 | Fairland - Lago Vista Transmission Line Upgrade | Increase the reliability of transmission facilities on the T414 Fairland - Lago Vista 21-mile 138-kV transmission line by replacing the existing Condor conductor with Drake conductor. |  | Fairland | Lago Vista | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2023-05-15 |  | 138 | 0 | 0 | 0 |  | Burnet | Travis | Tier 4 |  |  |  | 7352, 7518 | Y | N |  | 0 | 53959 | 53958
53968 | Fayetteville - Salem Transmission Line Upgrade | Increase the reliability of transmission facilities on the T177 Fayetteville - Salem 138-kV and T211 FPP Yard #1 - Salem 345-kV 19.3-mile double-circuit transmission line by replacing the existing Condor conductor from Fayetteville Substation to Salem Substation. |  | Fayetteville | Salem | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2023-05-15 |  | 345 | 0 | 0 | 0 |  | Fayette | Washington | Tier 4 |  |  |  | 7056, 7286, 7058, 7289 | Y | N |  | 0 | 53969 | 53968
54080 | Lockhart - Lulig Transmission Line Overhaul | LCRA TSC will perform an overhaul of T184 (from Lockhart structure #301 to Luling) with replacement structures that are capable of operating at 138-kV and supporting a single 795 ACSR Drake conductor. The replacement conductor on T184 will be 795 ACSR Drake. Note: Condor conductor replacement (from Lockhart to structure #301) will be taken into account on Lockhart - Split Transmission Line Upgrade project with ISD of May 15, 2023. |  | Lockhart (structure #301) | Luling | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2023-05-15 |  | 138 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  | 7216, 7224 | Y | N |  | 0 | 54081 | 54080
54082 | Lockhart - Red Rock Transmission Line Overhaul | LCRA TSC will perform an overhaul of T578 (from Lockhart structure #301 to Red Rock) with replacement structures that are capable of operating at 138-kV and supporting a single 959 ACSR Suwannee conductor. The replacement conductor on T578 will be 959 ACSR Suwannee. This overhaul will include the installation of a 72-count optical ground wire (OPGW). Note: Condor conductor, new OPGW and any structure replacement (from Lockhart to structure #301) will be taken into account on Lockhart - Split Transmission Line Upgrade project with ISD of May 15, 2023. |  | Lockhart (structure #301) | Red Rock | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2023-05-15 |  | 138 | 0 | 0 | 0 |  | Caldwell | Bastrop | Tier 4 |  |  |  | 7216, 7560 | Y | N |  | 0 | 54083 | 54082
56350B | Burnett-Ringgold Magnolia Tap 69 kV Line |  |  | Bowie | Ringgold Magnolia Tap | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4015 | 2023-05-15 |  | 69 | 0 | 21 | 0 |  | Montague | Clay | Tier 3 |  |  |  | 1540, 1545, 1547, 1548, 1550, 33770 | Y | N |  | 0 | 56862 | 56350
6777 | Cedar Hill - Liggett 138 kV Line | Loop Cedar Hill - Liggett 138 kV line in to Home Run Substation | Project Deferral | Grand Prairie West | Mayfield Tap | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4270 | 2023-05-15 02:01 |  | 138 | 7 | 0 | 0 |  | Dallas | Tarrant | Tier 4 |  |  |  | 2143, 1912, 1919, 2138, 2265 | Y | N |  | 0 | 51988 | 6777
7124 | Johnson Draw - Barr Ranch 138 kV line | Johnson Draw - Barr Ranch 138 kV line |  | Johnson Draw | Barr Ranch | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8373 | 2023-05-16 |  | 138 | 6 | 0 | 0 |  | Midland | Midland | Tier 4 |  |  |  | 11235, 11344 | Y |  |  |  | 14962 | 7124
5522 | Lake Hubbard 345/138 kV Switching Station | Construct new 345/138 kV switching station |  | Lake Hubbard |  | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4139 | 2023-05-17 |  | 345 | 0 | 0 | 600 |  | Dallas |  | Tier 3 |  |  |  | 12455, 12456, 2401, 2402, 2455 | Y | N |  |  | 13249 | 5522
18TPIT0001 | Wiederstein Substation Transformer Replacement | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Wiederstein |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2023-05-26 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7461 | Y | N |  |  | 10675 | 3319
48816 | Mulberry Creek: Rebuild 345 kV station | Rebuild Mulberry Creek 345 kV station | Update Cost | Mulberry Creek |  | Planned | 1015 - 1193 | AEP TNC | Michael Glueck mlforcum@aep.com 918-599-2674 | 2776 | 2023-05-30 01:00 |  | 345 | 0 | 0 | 0 |  | Jones |  | Tier 3 |  |  |  | 6230, 1435, 6235, 60040, 6232, 60788 | Y | N |  | 0 | 48817 | 48816
50874 | Smith - Mathis: Line Rebuild | Smith - Mathis: Line Rebuild |  | Smith | Mathis | Planned | 1053 - 1226 | AEP TCC | Joseph Page bcogan@aep.com 918-599-2857 | 3781 | 2023-05-31 |  | 69 | 0 | 22.47 | 0 |  | San Patricio | San Patricio | Tier 3 |  |  |  | 8407, 8408, 8424, 8866 | Y | N |  | 0 | 50875 | 50874
52464 | Alamito Creek to Ft. Davis: Rebuild 69 kV line | Rehab Alamito Creek to Ft. Davis 69 kV line | NEW | Alamito Creek | Ft Davis | Planned | 1070 - 1243 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2831 | 2023-05-31 |  | 69 | 0 | 20.5 | 0 |  | Presidio |  | Tier 4 |  |  |  | 6676, 6677, 6691, 6678, 6692 | Y | N |  | 0 | 52465 | 52464
52533 | Gebhardt to Sealy Ckt.65A Upgrades | Upgrade Ckt.65A Gebhardt to Sealy to increase thermal limits (Transmission Design Hardening Project) |  | Gebhardt | Sealy | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2023-05-31 |  | 138 | 0 | 2.46 | 0 |  | Austin | Austin | Tier 4 |  |  |  | 44640, 44700 | Y | N |  | 0 | 52534 | 52533
52553 | Wallis to Gebhardt Ckt.65C Upgrades | Upgrade Ckt.65C Wallis to Gebhardt to increase thermal limits. |  | Wallis | Gebhardt | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2023-05-31 |  | 138 | 0 | 9.58 | 0 |  | Austin | Austin | Tier 4 |  |  |  | 44700, 44740 | Y | N |  | 0 | 52554 | 52553
57521D | Stone Lake New Sub Ckt66 | Add Cap Bank #1 at Stone Lake Substation |  | Stone Lake |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2023-05-31 |  | 138 | 0 | 0 | 0 | 0,14.4 | Harris |  | Tier 4 |  |  |  | 44840 | Y | N |  | 0 | 57533 | 57521
57521C | Stone Lake New Sub Ckt66 | Add Cap Bank #1 at Stone Lake Substation |  | Stone Lake |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2023-05-31 |  | 138 | 0 | 0 | 0 | 0,14.4 | Harris |  | Tier 4 |  |  |  | 44840 | Y | N |  | 0 | 57532 | 57521
57521B | Stone Lake New Sub Ckt66 | Upgrade Ckt.66 Hockley to Stone Lake BP2023 as a transmission project. |  | Stone Lake | Hockley/Tomball | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2023-05-31 |  | 138 | 0 | 15.7 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 44840, 45880 | Y | N |  | 0 | 57531 | 57521
57584 | Cedar Bayou Auto A1 and A3 Position Swaps at 138kV | Swap Cedar Bayou Auto A1 and A3 Positions on the 138kV side to address fault concerns |  | Cedar Bayou |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2023-05-31 |  | 345 | 0 | 0 | 0 |  | Chambers |  | Tier 4 |  |  |  | 40000, 40010, 40015, 49005, 49008 | Y | N |  | 0 | 57585 | 57584
57906 | Laredo to University: Rebuild 138 kV Line | Rebuild the 5.19 mile Laredo to University 138 kV transmission line and upgrade any limiting elements. | NEW | Laredo | University | Planned | 1119 - 1297 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3838 | 2023-05-31 |  | 138 | 0 | 5.19 | 0 |  | Webb | Webb | Tier 4 |  |  |  | 8293, 8645, 8647 | Y | N |  | 0 | 57907 | 57906
14TPIT0038 | Northland to Mag Plant Circuit 979 Upgrade | Reconductor the existing Northland to Mag Plant circuit from single 795SCAR to bundle 795 ACSR Drake and increase rating to 2000 Amp |  | Northland Substation | Mag Plant Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | NEW | 2023-06-01 |  | 138 | 0 | 4.11 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9128, 9238 | Y | N |  | Will add the project to the base case | 9723 | 2443
3297 | Tezel Road - New 138kV Substation | Loop new 138 kV substation into the existing 138 kV Helotes to Bandera line. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2023-06-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 5421, 5020, 5200 | Y |  |  | There are no transformers associated with this project | 10840 | 3297
6253 | AEN_New_Kramer_Lane_Substation |  |  | 9238 | 9276 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2023-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9276, 9077, 9238 | Y |  |  |  | 13981 | 6253
50645 | CPSE_Rafter 138kV Cap Bank | [6 empty] | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2023-06-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 5355 | Y |  |  | 0 | 50646 | 50645
20TPIT0000 | Parkway Substation T1 Replacement | Replace T1, 20 MVA with a 40 MVA 138-13.09 kV transformer |  | Parkway |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2023-06-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7611 | Y | N |  |  | 10679 | 3323
44513 | Concho to Live Oak: Rebuild 69 kV line | Rebuild remaining portions of the Concho to Live Oak 69 kV line | Update Contact & Schedule | Concho | Live Oak | Planned | 941 - 1119 | AEP TNC | Jim Nivens mlforcum@aep.com 918-599-2674 | 2755 | 2023-06-30 01:00 |  | 69 | 0 | 3.3 | 0 |  | Tom Green | Schleicher | Tier 4 |  |  |  | 6450, 6494, 6495, 6496, 6497, 6498, 6527 | Y | N |  | 0 | 44514 | 44513
5430K | Conversion to 138kV | Construct new 138kV Hickory substation and terminate the existing Bonnie Brae - Hickory (which is already insulated for 138kV) at the new 138kV Hickory substation. |  | Bonnie Brae | Hickory | Planned | N/A | DENTON | Chuck Sears Chuck.Sears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 922, 931 | Y | N | N/A | 0 | 55205 | 5430
5430G | Conversion to 138kV | Reconstruct the 69kV Bonnie Brae - North Lakes to 138kV and terminate it at the new 138kV North lakes substation after the 69kV Bonnie Brae substation is converted to 138kV. Reconstruction will be completed by 12/19/2016. Cost already accounted for in the Reconstruct 69kV BonnieBrae-NLakes sub-phase. |  | Bonnie Brae | North Lakes | Planned | N/A | DENTON | Chuck Sears Chuck.Sears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 905, 915 | Y | N | N/A | 0 | 55201 | 5430
5430I | Conversion to 138kV | Retire the existing 69kV North Lakes substation together with the transformer relocated from Denton North |  | North Lakes |  | Planned | N/A | DENTON | Chuck Sears Chuck.Sears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 915, 928 | Y | N | N/A | 0 | 55203 | 5430
5430J | Conversion to 138kV | Line already insulated for 138kV. Line will be terminated at the new 138kV Hickory substation |  | Bonnie Brae | Hickory | Planned | N/A | DENTON | Chuck Sears Chuck.Sears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 905, 910 | Y | N | N/A | 0 | 55204 | 5430
5430H | Conversion to 138kV | Reconstruct the 69kV Bonnie Brae - North Lakes to 138kV and terminate it at the new 138kV North lakes substation after the 69kV Bonnie Brae substation is converted to 138kV. Reconstruction will be completed by 12/19/2016. Cost already accounted for in the Reconstruct 69kV BonnieBrae-NLakes sub-phase. |  | Bonnie Brae | North Lakes | Planned | N/A | DENTON | Chuck Sears Chuck.Sears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 138 | 0 | 1.521 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 928, 931 | Y | N | N/A | 0 | 55202 | 5430
5461 | Load serving |  |  | Puckrus | Mayhill | Planned |  | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 138 | 1.9 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 929, 917 | N | N |  |  | 13164 | 5461
5559 | Add new 138kV Bonnie Brae Substation and retire the 69kV sta |  |  | Bonnie Brae |  | Planned | N/A | DENTON | Charles Sears cxsears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 138 | 0 | 0 | 0 |  | Denton |  | Tier 4 |  |  |  | 905, 931 | Y | N | N/A |  | 13291 | 5559
44416 | Add a 2nd circuit at Brinker - Denton Steam |  |  | Brinker | Denton Steam | Planned |  | DENTON | Chuck Sears |  | 2023-07-01 |  | 138 | 0.63068 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 927, 982 | Y | N |  | 0 | 44417 | 44416
45511 | Laredo - Del Mar: 138 kV Line Rebuild | Rebuild Laredo - Del Mar 138 kV Line with 795 ACSS |  | Laredo | Del Mar | Conceptual | 992 - 1170 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3746 | 2023-07-01 |  | 138 | 0 | 2.73 | 0 |  | Webb | Webb | Tier 4 |  |  |  | 8293, 8645 | Y | N |  | 0 | 45512 | 45511
45513 | Santo Nino - Wormser: 138 kV Line Rebuild | Rebuild Santo Nino - Wormser 138 kV line with 795 ACSS |  | Santo Nino | Wormser | Conceptual | 991 - 1169 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3745 | 2023-07-01 |  | 138 | 0 | 0 | 0 |  | Webb | Webb | Tier 4 |  |  |  | 8295, 8649, 8653 | Y | N |  | 0 | 45514 | 45513
45566 | Holly - Southside: 138 kV Line Rating Increase | Increase MOT for Holly - Southside 138 kV Line |  | Holly | Southside | Planned | 994 - 1172 | AEP | Michael Glueck bcogan@aep.com 918-599-2857 | 3747 | 2023-07-01 |  | 138 | 0 | 1.8 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8483, 8486, 8496 | Y | N |  | 0 | 45567 | 45566
5206 | Brackettville to Escondido: Construct 138 kV line | Build a single circuit capable 138 kV circuit from Brakettville to Escondido station | Update Schedule | Brackettville | Escondido | Planned | 762-0947 | AEP | James Weaver bcogan@aep.com 918-599-2857 | 3570 | 2023-07-30 |  | 138 | 45 | 0 | 0 |  | Kinney | Maverick | Tier 2 | 2016-01-05 | 2017-01-20 | 2017-02-08 | 8252, 8260 | Y | N |  |  | 12865 | 5206
52147 | Rising Star Area Conversions | Converts voltage to 138 KV from Holder to Nimrod to Rising Star. |  | Holder | Rising Star | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2023-09-01 |  | 138 | 0 | 0 | 0 |  | Brown | Comanche | Tier 4 |  |  |  | 285, 289, 293, 292, 281 | Y |  |  | 0 | 52148 | 52147
52169 | Rising Star Area Conversions | This converts the voltage to 138 following Rising Star Substation Voltage Conversion |  | Rising Star | Downing | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2023-10-01 |  | 138 | 0 | 0 | 0 |  | Comanche | Comanche | Tier 4 |  |  |  | 281, 277, 285, 294 | Y |  |  | 0 | 52170 | 52169
5889 | MIRAGE - 138kV Substation Removal | Remove 138kV MIRAGE customer-owned substation from CNP service. |  | MIRAGE | MCCABE/BIMONT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2023-10-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42360, 40209, 42351, 40200 | Y | N |  |  | 13606 | 5889
55605 | New Barksdale to Rocksprings: Rebuild 69 kV line | Rebuild 69 kV line from Campwood to Rocksprings |  | New Barksdale | Rocksprings | Planned | 1102 - 1280 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3819 | 2023-11-01 |  | 69 | 0 | 19.51 | 0 |  | Edwards | Edwards | Tier 3 |  |  |  | 8365, 8238 | Y |  |  | 0 | 55606 | 55605
6712 | Soda Lake Substation Addition | Construct a new substation named Soda Lake off the LCRA Crane to Rio Pecos (T451) transmission line to support a generation interconnection request (18INR0040). |  | LCRA Crane | Rio Pecos | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018761 | 2023-11-07 |  | 138 | 0 | 0 | 0 |  | Crane | Crockett | Tier 4 |  |  |  | 76026, 6601, 60014 | Y | N |  |  | 14495 | 6712
14TPIT0098 | Cost Substation Addition | Upgrade the existing 69-kV substation |  | Cost |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2023-11-17 |  | 69 | 0 | 0 | 0 |  | Gonzales |  | Tier 4 |  |  |  | 7622 | Y | N |  |  | 10677 | 3321
50882 | Lon Hill - Structure 25/4: Line Rebuild | Lon Hill - STEC Warburton: Line Rebuild |  | Lon Hill | Haisley | Planned | 1055 - 1228 | AEP TCC | Bill Roberts bcogan@aep.com 918-599-2857 | 3785 | 2023-11-30 |  | 138 | 0 | 10.2 | 0 |  | San Patricio | San Patricio | Tier 3 |  |  |  | 8027, 8452, 8920 | Y | N |  | 0 | 50883 | 50882
55299 | Munday to Throckmorton: Rebuild 69 kV line | Rehab 69 kV line from Munday to Throckmorton |  | Munday | Throckmorton | Planned | 1094 - 1272 | AEP TNC | Charity Kreher mlforcum@aep.com 918-599-2857 | 1862 | 2023-11-30 |  | 69 | 0 | 34.55 | 0 |  | Knox | Throckmorton | Tier 3 |  |  |  | 6107, 6204, 6205 | Y | N |  | 0 | 55300 | 55299
6755 | Stratton: Add Cap Bank | Add 14.4Mvar Cap Bank at Stratton 138kV Substation |  | Stratton |  | Planned | 903 - 1081 | AEP TCC | Bill Roberts bcogan@aep.com 918-599-2857 | 3687 | 2023-12-31 |  | 138 | 0 | 0 | 0 | 0,14.4 | Nueces |  | Tier 4 |  |  |  | 8514 | Y | N |  |  | 14548 | 6755
52260 | India to DWU Rebuild | India to DWU Rebuild |  | India | Dallas Water Utilities | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2024-01-01 |  | 69 | 0 | 0 | 0 |  | Ellis | Dallas | Tier 4 |  |  |  | 230, 2351 | Y |  |  | 0 | 52261 | 52260
52670 | BEPC_20TPITXXXX_DowningStephenville |  |  | Stephenville | Carlton Switch | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2024-02-05 |  | 138 | 0 | 0 | 0 |  | Erath | Erath | Tier 4 |  |  |  | 286, 299, 295, 297, 294 | Y |  |  | 0 | 52671 | 52670
54523 | BEPC_20TPIT54523_Moffat_Hasse | At some later point, this will be broken up into phases. The submission to RPG is being prepared and will be submitted in April 2020. |  | Moffat | Hasse | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2024-02-05 |  | 138 | 0 | 17.5 | 0 |  | Bell | Comanche | Tier 2 |  |  |  | 142, 145, 149, 152, 153, 157, 158, 159, 250, 254, 258, 262, 265, 268, 269, 273, 277, 126, 141, 3583, 1649, 3586, 37580 | Y |  |  | 0 | 54524 | 54523
50948 | Angstrom - Grissom: Build New Line | Angstrom - Grissom: Build New Line |  | Angstrom | Grissom | Planned | 1063 - 1236 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3797 | 2024-04-01 |  | 345 | 17 | 0 | 0 |  | San Patricio | Bee | Tier 1 |  |  |  | 8249, 8624 | Y | N |  | 0 | 50949 | 50948
50966 | North Shore: 345 kV (Chienere LNG) RPG | Corpus North Shore RPG |  | Angstrom | Resnik | Planned | 1063 - 1236 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3798 | 2024-04-01 |  | 345 | 50 | 0 | 1350 |  | San Patricio | San Patricio | Tier 1 |  |  |  | 8659, 8660, 8249, 8580 | Y | N |  | 0 | 50970 | 50966
52175 | Rising Star Area Conversions | This continues the Rising Star Area Conversions with Carlton Switch to Downing | Carlton to Downing 138 kV Conversion | Carlton | Downing | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2024-04-01 |  | 138 | 0 | 0 | 0 |  | Erath | Comanche | Tier 4 |  |  |  | 294, 281, 286, 297 | Y |  |  | 0 | 52176 | 52175
54892 | Eden to North Brady: Rebuild 69 kV line | Rehab Eden to North Brady 69 kV line | NEW | Eden | North Brady | Planned | 1039 - 1266 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 1856 | 2024-04-30 |  | 69 | 0 | 32.7 | 0 |  | Concho | McCulloch | Tier 3 |  |  |  | 6384, 60797, 6006, 6372, 6380, 6385 | Y | N |  | 0 | 54893 | 54892
5496 | Forney - Royse 345 kV Line | Upgrade existing Royse - Forney 345 kV Line |  | Royse | Forney | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4235 | 2024-05-10 |  | 345 | 0 | 30 | 0 |  | Rockwall | Kaufman | Tier 3 |  |  |  | 2437, 2467, 2470, 2474, 2478 | Y | N |  | 0 | 49917 | 5496
17TPIT0031 | Elkton 345/138 kV autotransformer | Replace existing autotransformer |  | Elkton | Elkton | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6032-E | 2024-05-15 |  | 345 | 0 | 0 | 600 |  | Smith | Smith | Tier 3 |  |  |  | 3105, 3106, 29150 | Y | N |  |  | 10501 | 3155
5479 | Trinidad_TriC_Watermill_345kV_DCKT | Upgrade existing DCKT line |  | Trinidad Sw. Sta | TriCorner/Watermill | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4045 | 2024-05-15 |  | 345 | 0 | 92.1 | 0 |  | Henderson | Dallas | Tier 3 |  |  |  | 2432, 3123, 3124 | Y | N |  |  | 13184 | 5479
5982 | Relocate existing Shamburger North - Shamburger 138 kV Line | Establish 138 kV Line |  | Shamburger North | Shamburger | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6084 | 2024-05-15 |  | 138 | 10 | 0 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3104, 3206, 3226 | Y | N |  |  | 13697 | 5982
5524 | Royse South 345/138 kV Switching Station | Establish new 345/138 kV switching station |  | Royse | Forney | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4234 | 2024-05-15 12:00 |  | 345 | 0 | 0 | 0 |  | Rockwall |  | Tier 3 |  |  |  | 2469, 2470, 12471, 2437, 2467, 2471, 2478, 2702, 2474, 2710, 3223, 12702 | Y | N |  | 0 | 49918 | 5524
22TPIT0000 | Parkway Substation | Replace T2, 20 MVA with a 40 MVA 138-13.09 kV transformer |  | Parkway |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2024-05-24 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7611 | Y | N |  |  | 10680 | 3324
6304 | Shamburger North - Shamburger 345 kV Line | Upgrade existing 345 kV Line |  | Shamburger North | Shamburger | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6085 | 2024-05-28 |  | 345 | 10 | 10 | 0 |  | Smith | Smith | Tier 3 |  |  |  | 3103, 3223 | Y | N |  |  | 14033 | 6304
55626 | Ganso to Hamilton Road: Rebuild 138 kV line | Rebuild 138 kV line from Ganso to Hamilton Road |  | Maverick | Hamilton Road | Planned | 1105 - 1283 | AEP | Bill Roberts bcogan@aep.com 918-599-2857 | 3824 | 2024-05-30 |  | 138 | 0 | 41.1 | 0 |  | Maverick | Val Verde | Tier 3 |  |  |  | 8267, 8692, 8255 | Y |  |  | 0 | 55627 | 55626
4477 | Austrop to Sandow Double 345-kV Transmission Line Upgrade | Upgrade 33.98-mile Austrop (7040) to Sandow (13429) 345-kV double circuit transmission lines to bundled 959 Suwannee conductor (1921 MVA). |  | Austrop | Sandow | Conceptual |  | LCRATSC/Oncor | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2024-05-31 |  | 345 | 0 | 67.96 | 0 |  | Travis | Milam | Tier 1 |  |  |  | 7040, 13429 | N | N |  |  | 12038 | 4477
4479 | Cut T511 Gilleland Creek to Clear Springs into AEN Dunlap | Cut-In the existing Gilleland Creek (7340) to Clear Springs (7050) T511 345kV transmission line into Austin Energy's Dunlap (9044) substation. |  | Gilleland Creek | Clear Springs | Conceptual |  | LCRATSC/AEN | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2024-05-31 |  | 345 | 4 | 0 | 0 |  | Travis | Guadalupe | Tier 1 |  |  |  | 7050, 7340, 9044 | N | N |  |  | 12043 | 4479
5287 | Buda to Turnersville Transmission Line Addition | Construct a second 138-kV transmission line between Buda and Turnersville Substations. |  | Buda | Turnersvile | Conceptual |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2024-05-31 |  | 138 | 0 | 0 | 0 |  | Hays | Hays | Tier 3 |  |  |  | 7498, 7500 | N | N |  |  | 12963 | 5287
57910 | Uvalde - West Batesville: Rebuild 138 kV Line | Rebuild the 20.61 mile Uvalde to West Batesville 138 kV line |  | Uvalde | West Batesville | Planned | 1117 - 1295 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3836 | 2024-05-31 |  | 138 | 0 | 20.6 | 0 |  | Uvalde | Zavala | Tier 4 |  |  |  | 8234, 8236 | Y | N |  | 0 | 57911 | 57910
16TPIT0007 | McNeil to MagPlant Ckt 977 Upgrade | Reconductor existing McNeil to MagPlant circuit from 2000 to 3000 Amp. Relocate McNeil to Summit Circuit 907 and McNeil to MagPlant Circuit 977 to separate structures |  | McNeil Substation | Mag Plant Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | P396 | 2024-06-01 |  | 138 | 0 | 3.24 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9077, 9238 | Y | N |  | Will add the ptoject to the base case. | 8207 | 1031
45029 | Grandview Highland Hills Rebuild | CPSE_Rebuild of 138 kV double circuit line Line between Grandview to Highland Hills. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0273 | 2024-06-01 |  | 138 | 0 | 11.6 | 0 |  | Bexar | Bexar | Tier 4 | 2019-01-11 |  |  | 5030, 5175, 5095, 5205 | Y |  |  | 0 | 45030 | 45029
48854 | Adds Annova and Port South Bus and lines | Adds Annova and Port South buses, lines to connect Annova to Port South, line from HWY 511 to Port South, and reconnects line from S Carbide to HWY 511 into Port South |  | Annova LNG | Port South | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2024-06-01 |  | 138 | 22.1 | 0 | 0 | 0,120 | Cameron | Cameron | Tier 4 |  |  |  | 5775, 5776, 5767, 8337 | Y | N |  | 0 | 48855 | 48854
44946 | CPSE_New_Scenic_Loop_138kV_Load_Serving_Station | The new Scenic Loop 138 kV load serving station will be looped into existing Ranchtown to LCRA (Menger Creek) 138 kV transmission line. The substation should be located south west of the existing Fair Oaks Ranch and north east of the existing Ranchtown substation. |  |  |  | Planned | S-0885 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0275 | 2024-06-01 20:00 |  | 138 | 9 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5363, 5358, 7665 | Y |  |  | 0 | 44947 | 44946
19TPIT0000 | Weser Substation | Replace 5.6 MVA with 69-13.09 kV, 20 MVA transformer |  | Weser |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2024-06-28 |  | 69 | 0 | 0 | 0 |  | Goliad |  | Tier 4 |  |  |  | 7239 | Y | N |  |  | 10694 | 3336
5430M | Conversion to 138kV | Construct a new 138kV Eagle substation along the 138kV Hickory - Locust line |  | Eagle |  | Planned | N/A | DENTON | Chuck Sears Chuck.Sears@cityofdenton.com 940-349-7111 |  | 2024-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 926, 924 | Y | N | N/A | 0 | 55207 | 5430
5430P | Conversion to 138kV | Transfer the 69kV Hickory - RD Wells to the 138kV Hickory and RD Wells substations. Line is already insulated for 138kV. |  | Hickory | RD Wells | Planned | N/A | DENTON | Chuck Sears Chuck.Sears@cityofdenton.com 940-349-7111 |  | 2024-07-01 |  | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 910, 932 | Y | N | N/A | 0 | 55210 | 5430
5430O | Conversion to 138kV | Reconnect the 69kV Hickory - RD Wells to the 138kV Hickory and RD Wells substations. Line is already insulated for 138kV. |  | Hickory | RD Wells | Planned | N/A | DENTON | Chuck Sears Chuck.Sears@cityofdenton.com 940-349-7111 |  | 2024-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 922, 930 | Y | N | N/A | 0 | 55209 | 5430
5430Q | Conversion to 138kV | Retire the existing 69kV RD Wells substation together with the autotransformers |  | RD Wells |  | Planned | N/A | DENTON | Chuck Sears Chuck.Sears@cityofdenton.com 940-349-7111 |  | 2024-07-01 |  | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 932, 930 | Y | N | N/A | 0 | 55211 | 5430
5430N | Conversion to 138kV | Construct a new 138kV Eagle substation along the 138kV Hickory - Locust line |  | Eagle |  | Planned | N/A | DENTON | Chuck Sears Chuck.Sears@cityofdenton.com 940-349-7111 |  | 2024-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 922, 926 | Y | N | N/A | 0 | 55208 | 5430
6930 | New Paloma Substation | Adds new station and short line from Midstream |  | Midstream | Paloma | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2024-08-30 |  | 138 | 0.9 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 5644, 5643 | Y | N |  |  | 14749 | 6930
52179 | Rising Star Area Conversions | This converts Hasse to Downing to 138 KV |  | Downing | Hasse | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2024-10-01 |  | 138 | 0 | 0 | 0 |  | Comanche | Comanche | Tier 4 |  |  |  | 277, 281, 1649 | Y |  |  | 0 | 52180 | 52179
52070 | Carver - Maxwell: Line Rebuild | Carver - Maxwell: Line Rebuild | Update Contact & Schedule | Carver | Maxwell | Planned | 1079 - 1252 | AEP | Charity Kreher bcogan@aep.com 918-599-2853 | 3804 | 2024-10-31 |  | 138 | 0 | 60.24 | 0 |  | Sutton | Val Verde | Tier 3 |  |  |  | 8259, 8261, 60412, 8991, 8998, 60440 | Y | N |  | 0 | 52071 | 52070
55617 | Campwood to New Barksdale: Rebuild 69 kV line | Rebuild 69 kV line from Campwood to Rocksprings |  | New Barksdale | Campwood | Planned | 1102 - 1280 | AEP | Glen Reed gareed@aep.com 918-599-2664 | 3820 | 2024-11-01 |  | 69 | 0 | 7.73 | 0 |  | Edwards | Edwards | Tier 3 |  |  |  | 8633, 8365 | Y |  |  | 0 | 55618 | 55617
55624 | Escondido to Ganso: Rebuild 138 kV line | Rebuild 138 kV line from Escondido to Hamilton Road |  | Escondido | Ganso | Planned | 1105 - 1283 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3825 | 2024-11-30 |  | 138 | 0 | 10.198 | 0 |  | Maverick | Maverick | Tier 4 |  |  |  | 8260, 8267 | Y |  |  | 0 | 55625 | 55624
3334 | Fort Sam to Kirby and Fort Sam to Tenth Street MLSE Upgrade | Upgrade entire bus and terminals at Fort Sam and ensure a rating of 2000 A. |  | Fort Sam | Kirby/Tenth Street | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0744 | 2024-12-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5160, 5250, 5420 | Y | N |  | There are no transformers associated with this project | 10692 | 3334
13TPIT0070 | Nash Creek Substation | Replace existing PWT with new 69kVx13.09 kV, new Control House, CSW, structures, containment foundations, bus, panels, etc |  | Nash Creek |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2024-12-16 |  | 69 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7596 | Y | N |  |  | 10678 | 3322
54521 | Weatherford_Peaster |  |  | Advance | Shady Grove | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2024-12-26 |  | 138 | 0 | 0 | 60 |  | Parker | Parker | Tier 4 |  |  |  | 510, 515, 517, 33517, 516, 518, 543, 1585, 1589 | Y |  |  | 0 | 54522 | 54521
4320 | CPSE_Brooks to Chavaneaux MLSE | Upgrade terminals at Brooks and Chavaneaux to ensure a 1364 A rating (minimum) |  | Brooks | Chavaneaux |  |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0733 | 2024-12-31 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5045, 5085 | Y | Y |  |  | 11872 | 4320
6287 | Sherry Sw. - Webb/Kennedale 345 kV DCKT Line | Upgrade the existing 345 kV Line |  | Sherry | Webb/Kennedale | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4252 | 2025-05-15 |  | 345 | 0 | 11.2 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1911, 1918, 1930, 1929, 1932, 1934 | Y |  |  |  | 14016 | 6287
58010 | North McAllen: Rebuild 138 kV Station | North McAllen Station Rebuild |  | McAllen |  | Planned | 1118 - 1296 | AEP | Glen Reed gareed@aep.com 918-599-2664 | 3837 | 2025-05-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 8368, 8631, 8632 | Y |  |  | 0 | 58011 | 58010
15TPIT0031 | Chavaneaux_Chavaneaux Tap Rebuild (Brooks to Chavaneaux ckt) | Rebuild 138 kV transmission from Chavaneaux to Chavaneaux Tap. This rebuild is for Brooks to Chavaneaux ckt. |  | Brooks | Chavaneaux | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0260 | 2025-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5045, 5085 | Y |  |  | There are no transformers associated with this project | 9555 | 2304
4084 | Barton-Vega: Upgrade Ckt 928 | Reconductor to 2000 amps |  | Barton | Vega | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2025-06-01 |  | 138 | 0 | 4.05 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9158, 9285 | Y |  |  |  | 11609 | 4084
4425 | New TR-AW Ckt 1032 AW-JV Ckt 961 | Old Description in Planbook Add 2nd Ckt from TR to HL to tie-in to HL-JV Ckt 961 bypassing HL and creating TR-JV Ckt. New description Ckt 1032 from TR-AW and CKT 961 from AW - JV |  | Techridge 9190 AshtonWoods 9224 | AshtonWoods 9226 Jollyville 9223 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2026-06-01 |  | 138 | 1.7 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9190, 9223, 9224, 9226 | Y | N |  |  | 11984 | 4425
4490 | LaPalma: Add 2nd 345/138 kV autotransformer | Add 345/138 kV autotransformer capacity at LaPalma |  | LaPalma |  | Planned | 710 - 0880 | AEP TCC | Teresa Trotman bcogan@aep.com 918-599-2857 | 2904 | 2027-09-30 |  | 345 | 0 | 0 | 675 |  | Cameron |  | Tier 4 |  |  |  | 8356, 8317, 8314 | Y | N |  |  | 12067 | 4490
6774 | Marina: Add New Distribution Station | Add New Marina Distribution Station |  | Highway 9 | Nueces Bay | Planned | 878 - 1056 | AEP TCC | Teresa Trotman bcogan@aep.com 918-599-2857 | 3665 | 2028-01-30 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8026, 8441, 8470, 8474 | Y | N |  |  | 14780 | 6774
15TPIT0004 | Converse - New 138kV Substation | Loop new 138kV substation into future 138kV Martinez to Skyline transmission line |  | Converse | Martinez-Skyline | Planned | T-0177 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0601 | 2028-06-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5098, 5294, 5368 | Y | N |  | There are no transformers associated with this project | 8143 | 967
1549 | Devine Switch breaker addition | Adds breakers to Devine Switch to allow closing of normally open Devine Switch to Devine. Creates 3- terminal switching station |  | Devine Switch |  | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2028-06-01 |  | 69 | 0 | 0 | 0 |  | Medina |  | Tier 4 |  |  |  | 5857, 58570 | N | N |  |  | 8754 | 1549
2161 | Oaks to Loxley | Build new 138 kV 795 ACSR circuit from Oaks to a new AEP switching station Loxley in the Leon Creek to Pleasanton line | Load forecasts have changed since project was RPG approved | Oaks | Loxley | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2028-06-01 |  | 138 | 6 | 0 | 0 |  | Atascosa | Atascosa | Tier 3 | 2011-12-16 | 2012-04-25 |  | 5713, 80491 | N | N |  | This new line was part of Karnes Electric Cooperative Project that was approved in 2012. While much of the projected load is now on the system, not all of the projected load materialized. Studies with newer load projections have not shown the need for this line. STEC recommends evaluating this project as an option when studies show the need for a project in this area of the transmission system. | 9408 | 2161
12TPIT0009 | Masterson Rd - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to Howard line. |  | Masterson Rd. | Cagnon-Howard | Planned | T-0910 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0538 | 2028-06-01 |  | 138 | 8 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5296, 5054, 5230 | Y | N |  | There are no transformers associated with this project | 9466 | 2218
12TPIT0004 | Sulpher Springs - New 138kV Substation | Loop new 138kV substation into the existing 138kV OW Sommers to Kirby line |  | Sulpher Springs | OW Sommers-Kirby | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0385 | 2028-06-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5416, 5250, 5395 | Y | N |  | There are no transformers associated with this project | 10365 | 3021
3595 | Bevo to AEP Carrizo Springs 69 kV line | Add 2 mile line by double circuiting two existing circuits, as recommended in 2013 RTP. |  | Bevo | Carrizo Springs | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2028-06-01 |  | 69 | 0 | 2 | 0 |  | Dimmit | Dimmit | Tier 1 | 2012-04-12 | 2012-08-12 | 2012-09-12 | 5871, 8244 | N | N |  | This new line was part of Karnes and Medina Electric Cooperatives Project that was approved in 2012. This also helped voltage on AEP transmission under contingencies. While much of the projected load is now on the system, not all of the projected load materialized. Studies with newer load projections have not shown the need for this line. STEC recommends evaluating this project as an option when studies show the need for a project in this area of the transmission system. | 10984 | 3595
3822 | San Miguel to Sigmor 138 kV line upgrade | Upgrade San Miguel to Sigmor 138 kV line as recommended in 2013 RTP. Will investigate re-conductoring on existing structures with ACCC and other high temperature conductors. |  | San Miguel | Sigmor | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2028-06-01 |  | 138 | 0 | 26.3 | 0 |  | Atascosa | Live Oak | Tier 3 |  |  |  | 5689, 5902, 8404 | N | N |  | Studies after the 2013 RTP have shown that AEP's approved project to rebuild the 69 kV Beeville to Three Rivers to 138 kV, TPIT 5166, reduces the loading on this line. STEC believes that rebuilding San Miguel to Sigmor is likely to be justified in the future by load growth and or generation additions. STEC recommends evaluating this project as an option when studies show the need for a project in this area of the transmission system. | 11279 | 3822
5220 | Move Orange Grove load to 138 kV bus | Move load from the 69 KV to the 138 KV instead of replacing auto. 2015 RTP |  | Orange Grove |  | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2028-06-01 |  | 138 | 0 | 0 | 0 |  | Jim Wells |  | Tier 4 |  |  |  | 5660 | N | N |  |  | 12887 | 5220
45068 | Merida to Harlandale Rebuild | CPSE_Merida to Harlandale Rebuild |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0233 | 2028-06-01 |  | 138 | 0 | 10 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5190, 5310, 5385, 5395 | Y |  |  | 0 | 45069 | 45068
45535 | Valley_to_ValleyTap_Rebuild | Rebuild an approximate four circuits miles of 138 kV Transmission line from Valley Tap to Valley Road substation. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0279 | 2028-06-01 |  | 138 | 0 | 4 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5025, 5053, 5465 | Y |  |  | 0 | 45536 | 45535
15TPIT0033 | Randolph - 138 kV Substation Equipment Upgrade | Upgrade the Weiderstein and Tuttle terminals and ensure a 2000 A rating (minimum). Reconfigure and-or upgrade the main bus to ensure a 2000 A rating (minimum). |  | Randolph | Tuttle-Weiderstein | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0645b | 2028-06-01 12:00 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5360, 5435 | Y | N |  | There are no transformers associated with this project | 9557 | 2306
6743 | Magellan Tank Farm: LCRA Interconnect | Add 138kV Tie Line between Navigation 138kV substation and Magellan's 138kV substation. Add Metering at Magellan's Substation. |  | Navigation | Magellan | Planned | 905 - 1083 | AEP TCC/LCRA | Michael Glueck bcogan@aep.com 918-599-2857 | 3689 | 2028-07-01 |  | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 78460 | Y | Y |  |  | 14536 | 6743
5763C | CHORIN to STRANG Ckt.87 | STRANG to Cedar Bayou Ckt.87 |  | STRANG | Cedar Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2031-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40010, 41500 | Y | N |  | 0 | 45414 | 5763
4997E | Deepwater Area Conversions | Upgrade Harrisburg substation for Ckt.33 loop service. | - Project cancelled...Breakers will remain at Harrisburg substation | Harrisburg | TEXPET/ Reed | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 986 | 2099-10-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40470, 40800, 41040, 41560 | Y |  |  | 0 | 43263 | 4997

## CompletedTPIT100120NoCost
OCTOBER BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 10/1/2020
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar ) (-Reactor, +Capacitor ) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number
5429B | Phase 3 of the conversion to 138kV | Retire the existing 69kV line from the existing 69kV locust substation to Spencer Switch |  | Locust | Spencer Switch | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2019-01-01 | 2017-07-01 | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 904, 914 | Y | N | N/A | 0 | 45743 | 5429
4186E | University Area 138kV Conversions |  |  | University |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1123 | 2019-01-14 00:03 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47760, 47752, 49030 | Y |  |  | 0 | 48946 | 4186
5223B | 2015 RTP rebuild 4 sections from George West through Mathis | Rebuild 4/0 ACSR from George West Switching Station to Kittie West Substation with 795 ACSR that is 138 capable. Removes the GOAB at West George West Switch. 2015 RTP |  | George West Switching Station | Kittie West | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-01-18 | 2019-06-15 | 69 | 0 | 4.25 | 0 |  | Live Oak | Live Oak | Tier 4 |  |  |  | 5685, 5683, 5684, 5686 | Y | N |  | 0 | 43337 | 43336
6583 | Del Sol-Cenizo: Create Temporary Tap | Install temporary tap on the Del Sol - Cenizo 345 kV line for the Rio Bravo windfarm temporary itnerconnection. The windfarm will build and own the gen-tie line from their collector station up to the tap point. The collector station name is CABEZON. |  | Del Sol | Cenizo | Planned | 895 - 1073 | ETT | Rich Haley dnlyons@aep.com 918-599-2698 | 3679 | 2019-01-22 |  | 345 | 0 | 0 | 0 |  | Starr |  | Tier 4 |  |  |  | 80380, 80225, 80307 | Y | N |  |  | 14337 | 6583
5763A | CHORIN to STRANG Ckt.87 | Upgrade 138kV Ckt.87 CHORIN to STRANG to increase thermal ratings. | - Transmission upgrade portion now on hold...Substation upgrades still expected | CHORIN | STRANG | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-01-23 | 2019-01-22 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40320, 41500 | Y | N |  | 0 | 45412 | 5763
5763B | CHORIN to STRANG Ckt.87 | STRANG to Cedar Bayou Ckt.87 |  | STRANG | Cedar Bayou | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-01-23 00:01 | 2019-04-30 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40010, 41500 | Y | N |  | 0 | 45413 | 5763
6242 | Pinto Creek Substation Addition | Install a new motor operated 138-kV load serving substation on T464 between Brackettville and Hamilton Road. |  | Pinto Creek |  | Planned |  | LCRATSC/RGEC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017994 | 2019-01-25 |  | 138 | 0 | 0 | 0 |  | Kinney |  | Tier 4 |  |  |  | 78255, 8252, 8255 | Y | N |  |  | 13967 | 6242
6109 | Stadium - Banquete 69 kV Line | Rehab Stadium - Banquete 69 kV Line |  | Stadium | Banquete | Planned | 816 - 1000 | AEP TCC | Andrew Garlick dnlyons@aep.com 918-599-2698 | 3610 | 2019-01-31 |  | 69 | 0 | 16.43 | 0 |  | Jim Wells | Nueces | Tier 4 |  |  |  | 8031, 8888, 8889 | Y | Y |  |  | 13835 | 6109
5535 | Lynx to Rio Pecos: Rebuild 138 kV line | Rebuild Lynx to Rio Pecos 138 kV line |  | Lynx | Rio Pecos | Planned | 788 - 0973 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2648 | 2019-01-31 |  | 138 | 0 | 2.23 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6601, 60400 | Y | N |  |  | 13263 | 5535
6636 | CELNES 138kV Substation | Install 138kV customer-owned CELWST substation. Loop from Ckt.94 BAYWAY to HIMONT |  | Himont | Bayway | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-02-14 | 2019-02-14 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42250, 42170, 42790 | Y |  |  | 0 | 43475 | 6636
5217 | Rebuild Cotulla to Big Wells 69 kV line | Rebuild 69 kV line with 795 ACSR on 138 kV and double circuit capable structures 2015- NERC assessment |  | Cotulla | Big Wells | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-02-15 12:00 | 2019-02-18 | 69 | 0 | 22.2 | 0 |  | La Salle | Dimmit | Tier 4 |  |  |  | 5868, 5876 | Y | N |  |  | 12882 | 5217
5966 | College Hills to Grape Crk T 69 kV line: Rebuild 69 kV line | Rehab College Hills to Grape Creek Tap 69 kV line | IN SERVICE | College Hills | Burma | In-Service | 786 - 0971 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2664 | 2019-02-18 | 2019-02-18 | 69 | 0 | 10.45 | 0 |  | Tom Green | Tom Green | Tier 4 |  |  |  | 6468, 6416 | Y | N |  |  | 13681 | 5966
6358 | Christoval to Arrott 69 kV line: Rebuild 69 kV line | Rehab Christoval to Arrott 69 kV line | IN SERVICE | Christoval | Arrott | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2721 | 2019-02-20 | 2019-02-20 | 69 | 0 | 8.17 | 0 |  | Tom Green | Schleicher | Tier 4 |  |  |  | 6495, 6496 | Y | N |  |  | 14102 | 6358
5766A | Knight to BUNKER to HOC Ckt.08 Upgrades | Upgrade Ckt.08 Knight to BUNKER to increase thermal ratings |  | Knight | BUNKER | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-02-28 | 2019-05-23 | 138 | 0 | 1.6 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47331, 47340 | Y | N |  |  | 13512 | 5766
5972 | Benjamin Tap to Munday 69 kV line: Rebuild 69 kV line | Rehab Benjamin Tap to Munday 69 kV line | IN SERVICE | Benjamin Tap | Munday | In-Service | 786 - 0971 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2661 | 2019-02-28 | 2019-02-28 | 69 | 0 | 13.12 | 0 |  | Knox | Knox | Tier 4 |  |  |  | 790, 6086, 6087, 6107 | Y | N |  |  | 13687 | 5972
5766B | Knight to BUNKER to HOC Ckt.08 Upgrades | Upgrade Ckt.08 HOC to BUNKER to increase thermal ratings |  | HO Clarke | BUNKER | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-02-28 00:01 | 2019-05-23 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47150, 47340 | Y | N |  | Cost is Reflected in Phase A of TPIT Project 5766 | 13536 | 5766
5223C | 2015 RTP rebuild 4 sections from George West through Mathis | Rebuild 4/0 ACSR from Kittie West Substation to George West Substation to Mathis with 795 ACSR that is 138 capable. 2015 RTP |  | Kittie West | George West Substation | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-03-01 | 2019-04-15 | 69 | 0 | 6.44 | 0 |  | Live Oak | Live Oak | Tier 4 |  |  |  | 5684, 5683 | Y | N |  | 0 | 43338 | 43336
5634 | Rebuild Danevang to Clemville Sw 69 kV line | Rebuild the Danevang Sub to Clemville Switch 4/0 ACSR 69 kV line with 795 ACSR 138 capable. 2016 RTP |  | Danevang | Clemville | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-03-01 12:00 | 2019-03-08 | 69 | 0 | 5.1 | 0 |  | Wharton | Matagorda | Tier 4 |  |  |  | 5548, 5550 | Y | N |  |  | 13368 | 5634
44389 | Torrecillas POI | [6 empty] | ETT | Terry Weeks dnlyons@aep.com 918-599-2698 |  | 2019-03-02 | 2018-11-14 | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 80210, 80219, 161257 | Y |  |  | 0 | 44390 | 44389
6011 | Laredo Plant: Replace 138/69 kV autotransformer | Upgrade 138/69 kV autotransformer capacity at Laredo Plant |  | Laredo Plant | - | In-Service | 806 - 0991 | AEP | Randy Weaver dnlyons@aep.com 918-599-2698 | 3595 | 2019-03-02 | 2018-12-20 | 138 | 0 | 0 | 180 |  | Webb |  | Tier 4 |  |  |  | 8530, 8290, 8642, 8293, 8298, 8303 | Y | N |  |  | 13728 | 6011
6119 | Rockport - Fulton 69 kV Line | Rehab Rockport - Fulton 69 kV Line |  | Rockport | Fulton | Planned | 827 - 1011 | AEP TCC | Dave Goetz dnlyons@aep.com 918-599-2698 | 3628 | 2019-03-02 | 2019-07-31 | 69 | 0 | 7.66 | 0 |  | San Patricio | Aransas | Tier 4 |  |  |  | 8431, 8432, 8841 | Y | N |  |  | 13845 | 6119
6000 | Banquete - Calallen 69 kV line | Rehab Banquete - Calallen 69 kV line |  | Calallen | Banquete | Planned | 816 - 1000 | AEP TCC/STEC | Andrew Garlick dnlyons@aep.com 918-599-2698 | 3609 | 2019-03-02 | 2019-05-23 | 69 | 0 | 12.7 | 0 |  | Nueces |  | Tier 4 |  |  |  | 5626, 8888 | Y | Y |  |  | 13717 | 6000
2979 | Melon Creek: Build new 138 kV station | Construct new Melon Creek station near Refugio, cut-in Airco to Rincon 138 kV line into Melon Creek, and cut-in Refugio to Tatton 69 kV line into Melon Creek. | Company Contact Update | Melon Creek | - | In-Service | 100 - 0100 | AEP | Bill Roberts dnlyons@aep.com 918-599-2698 | 2021 | 2019-03-02 | 2018-11-15 | 138 | 3 | 0 |  |  | Refugio |  | Tier 3 | 2017-03-31 | 2017-04-21 | 2017-06-01 | 8144, 8437, 8800, 8811, 80065, 8410, 8412, 80066 | Y | N |  |  | 10323 | 2979
6110 | Blessing - Palacios 69 kV Line | Rehab Blessing - Palacios 69 kV Line |  | Blessing | Palacios | Planned | 817 - 1001 | AEP TCC | Jason Bryant dnlyons@aep.com 918-599-2698 | 3611 | 2019-03-02 | 2019-06-20 | 69 | 0 | 9.27 | 0 |  | Matagorda |  | Tier 4 |  |  |  | 8119, 8131 | Y | N |  |  | 13836 | 6110
7006A | CNP_18TPIT7006_HOC_Reactor_Upgrades | Remove cap bank C1 from HOC Ckt.05 to WAP (position between HOC breakers H850 & H810) |  | HOC | HOC | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-03-07 | 2019-03-07 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47171, 44081, 47170 | Y |  |  |  | 14828 | 7006
45342 | Lemay: Build 138 kV Hard Tap | Lemay: Build 138 kV Hard Tap on North Laredo SS - Reveille Line |  | Encinal | Reveille | Planned |  | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 |  | 2019-03-11 | 2019-05-09 | 138 | 0 | 0 | 0 |  | La Salle | La Salle | Tier 4 |  |  |  | 88088, 88627, 8619, 8612 | Y | N |  | 0 | 47935 | 45342
6355 | Robert Lee to Bronte 69 kV line: Rebuild 69 kV line | Rehab Robert Lee to Bronte 69 kV line | IN SERVICE | Robert Lee | Bronte | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2716 | 2019-03-11 |  | 69 | 0 | 8.72 | 0 |  | Coke | Coke | Tier 4 |  |  |  | 6414, 6419, 6420 | Y | N |  |  | 14099 | 6355
44814 | Ollin: Build 69 kV temporary tap | Build new Ollin 69 kV temporary tap on the Crane 69 kV loop | IN SERVICE | Ollin |  | In-Service | 955 - 1131 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2753 | 2019-03-14 01:00 | 2019-03-14 | 69 | 0 | 0 | 0 |  | Crane |  | Tier 4 |  |  |  | 6668, 6606, 6610, 6611 | Y | N |  | 0 | 44815 | 44814
44816 | Ollinphi: Build 69 kV temporary tap | Build new Ollinphi 69 kV temporary tap on the Crane 69 kV loop | IN SERVICE | Ollinphi |  | In-Service | 953 - 1132 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2758 | 2019-03-14 02:00 | 2019-03-14 | 69 | 0 | 0 | 0 |  | Crane |  | Tier 4 |  |  |  | 6669, 6606, 6610, 6668, 6611 | Y | N |  | 0 | 44817 | 44816
5931 | Shiner Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Shiner (S183). |  | Shiner |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017402 | 2019-03-21 |  | 138 | 0 | 0 | 0 |  | Lavaca |  | Tier 4 |  |  |  | 7238 | Y | N |  |  | 13639 | 5931
4531 | Solstice to Clovis: Build 138 kV line | Interconnect Roserock solar farm with a new 138 kV line from Solstice to Clovis | IN SERVICE | Solstice | Clovis | In-Service | 705 - 0875 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2811 | 2019-03-25 | 2019-03-25 | 138 | 4.5 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6630, 60383, 60385 | Y | N |  |  | 12106 | 4531
6246 | Masterson Fld to Pecos Valley 69 kV line: Rebuild 69 kV line | Rehab Masterson Field to Pecos Valley 69 kV line | IN SERVICE | Masterson Field | Pecos Valley | In-Service | 786 - 0971 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2701 | 2019-03-26 | 2019-03-26 | 69 | 0 | 8.84 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6642, 6643 | Y | N |  |  | 13974 | 6246
4185 | HO Clarke Partial Load Conversion (TR1) | Convert HO Clarke TR1 load to 138kV. Tap off of Ckt.90 HO Clarke to Garrott | - Delayed project schedule | HO Clarke |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1112 | 2019-03-27 | 2019-03-27 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47155, 47160, 47150, 47322 | Y | N |  |  | 11715 | 4185
4996 | HO Clarke Load Conversion | Convert HO Clarke TR2 & TR3 to 138kV service. Tap off of Ckt.25 HO Clarke to Fondren. | - Delayed project schedule | HO Clarke | Fondren | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-03-27 | 2019-03-27 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 47151, 47152, 47160, 47100, 47150, 47412 | Y |  |  |  | 12629 | 4996
6750 | Quihi: Build 138kV Tap | Quihi Temprary 138kV Hard Tap on Razorback to Castroville 138kV Line |  | Quihi Tap | - | Planned | 899 - 1077 | AEP TCC/STEC | Daniel Lyons dnlyons@aep.com 918-599-2698 | 3683 | 2019-03-28 08:00 | 2019-02-18 | 138 | 0 | 0 | 0 |  | Medina |  | Tier 4 |  |  |  | 88248, 5083, 8241 | Y | Y |  |  | 14543 | 6750
5970 | Wolfgang to Rotan 69 kV line: Rebuild 69 kV line | Rehab Wolfgang to Rotan 69 kV line | IN SERVICE | Wolfgang | Rotan | In-Service | 786 - 0971 | AEP TNC | David Baker mlforcum@aep.com 918-599-2674 | 2659 | 2019-03-30 | 2019-03-30 | 69 | 0 | 12.41 | 0 |  | Kent | Fisher | Tier 4 |  |  |  | 6162, 6196 | Y | N |  |  | 13685 | 5970
4186A | University Area 138kV Conversions | Convert University TR2 load to 138kV. |  | University | COUGAR | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1123 | 2019-03-30 | 2019-03-30 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47750, 47751, 47752, 47755, 47760, 47762, 47764, 42690, 47560, 47600, 47670, 47700, 47763, 49030 | Y | N |  | 0 | 48942 | 4186
4186B | University Area 138kV Conversions | Convert University TR3 load to 138kV. |  | University | Eastside | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1123 | 2019-03-31 | 2019-03-30 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47763, 47755, 47600, 47760 | Y | N |  | Cost included in 4186A | 48943 | 4186
6106 | Woodsboro - Bonniview 69 kV Line | Rehab Woodsboro - Bonniview 69 kV line |  | Woodsboro | Bonniview | Planned | 834 - 1018 | AEP | Jason Bryant dnlyons@aep.com 918-599-2698 | 3640 | 2019-03-31 | 2019-02-10 | 69 | 0 | 5.37 | 0 |  | Refugio |  | Tier 4 |  |  |  | 8804, 8805 | Y | N |  |  | 13832 | 6106
6328A | REED - Substation Removal | Outage REED load |  | REED |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-03-31 00:01 |  | 69 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 41340 | Y |  |  | 0 | 45475 | 6328
6009 | Kenedy Switch: Replace 138/69 kV autotransformer | Upgrade 138/69 kV autotransformer capacity at Kenedy Switch |  | Kenedy Switch | - | Planned | 837 - 1021 | AEP TCC | James Nivens dnlyons@aep.com 918-599-2698 | 3639 | 2019-04-03 | 2019-04-16 | 138 | 0 | 0 | 130 |  | Karnes |  | Tier 4 |  |  |  | 8184, 8186 | Y | N |  |  | 13726 | 6009
6889 | GSEC_6889_69kV_Add_Enterprise_Lake_Ivey_Sub | [6 empty] | GOLDENSPREAD | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2019-04-03 16:00 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 9431, 6377 | Y |  |  |  | 14704 | 6889
6781 | Leakey - Utopia Transmission Line Overhaul | Rebuild T281 Leakey to Utopia to be 138 kV capable with a nominal conductor rating of 223 MVA at 138 kV (Single Drake) with ADSS and operated at 69 kV. | Accelerating Schedule | Leakey | Utopia | Under Construction |  | BANDERA | Tyler Pansing t.pansing@banderaelectric.com 866-226-3372 Ext 6078 | 353985 | 2019-04-05 |  | 69 | 0 | 17.95 | 0 |  | Real | Bandera | Tier 4 |  |  |  | 7426, 7428 | Y | N |  |  | 14575 | 6781
6341 | Lake Pauline to Chillicothe 69 kV line: Rebuild 69 kV line | Rehab Lake Pauline to Chillicothe 69 kV line | IN SERVICE | Lake Pauline | Chillicothe | In-Service | 786 - 0971 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2704 | 2019-04-09 | 2019-04-09 | 69 | 0 | 9.4 | 0 |  | Hardeman | Hardeman | Tier 4 |  |  |  | 6048, 6057 | Y | N |  |  | 14085 | 6341
4538 | Add new 138kV line from Tall City to Glass Ranch |  |  | Tall City | Glass Ranch | Planned |  | SHRY | Brad Schwarz 512-289-7425 |  | 2019-04-10 |  | 138 | 10 | 0 | 0 |  | Midland | Martin | Tier 2 |  |  |  | 79507, 79558 | Y | N |  |  | 12115 | 4538
6359 | Arrott to Pave Paws 69 kV line: Rebuild 69 kV line | Rehab Arrott to Pave Paws 69 kV line | IN SERVICE | Arrott | Pave Paws | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2722 | 2019-04-11 | 2019-04-11 | 69 | 0 | 6.47 | 0 |  | Schleicher | Schleicher | Tier 4 |  |  |  | 6494, 6496, 6497 | Y | N |  |  | 14103 | 6359
5259 | Lotebush: Add dynamic reactive device | Rebuild Solstice to Yucca Drive 138 kV line and add dynamic reactive devices at Lotebush | IN SERVICE | Lotebush |  | In-Service | 713 - 0946 | AEP TNC | John Pulay mlforcum@aep.com 918-599-2674 | 2638 | 2019-04-12 | 2019-04-12 | 138 | 0 | 0 | 0 | -100100 | Reeves |  | Tier 1 | 2015-12-15 | 2016-09-21 | 2016-10-26 | 60392, 60439 | Y | N |  |  | 14312 | 5259
5887B | RUSSEL 138kV Substation (ARITEK Substation Removal) | Install 138kV customer-owned RUSSEL substation (ARITEK substation replacement). Loop from Ckt.84 DOWLAP to Morgans Point. |  | RUSSEL | DOWLAP/Morgans Point | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-04-13 | 2019-04-13 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40125, 40070, 40120, 40490, 41310, 41391, 41410, 41415, 41631, 40320, 41100, 41400, 41419, 41450, 42610 | Y | N |  |  | 13613 | 5887
5831 | Rebuild Gustine to Energy SW | Rebuild Gustine (Bus #273) to Energy SW (Bus #265) per RTP study results |  |  |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 16013 | 2019-04-18 |  | 69 | 0 | 5.05 | 0 |  | Comanche | Comanche | Tier 4 |  |  |  | 265, 273 | Y |  |  |  | 13573 | 5831
5930 | Robbins Switch Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Robbins Switch (S547). |  | Robbins Switch |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017400 | 2019-04-22 |  | 138 | 0 | 0 | 0 |  | Upton |  | Tier 4 |  |  |  | 76597 | Y | N |  |  | 13638 | 5930
4960 | Adding Nat Dam to Sales 17 miles 138 kV line |  |  | Sales Ranch | Natural Dam | Planned |  | SHRY | Brad Schwarz 512-289-7425 |  | 2019-04-25 |  | 138 | 17 | 0 | 0 |  | Martin | Howard | Tier 4 | 2015-06-29 | 2015-07-29 |  | 79508, 79509 | Y | N |  |  | 12593 | 4960
5715B | Red Bluff - 138kV Substation | Construct service to new 138kV Red Bluff distribution substation. Loop through Ckt.79 Terminal to Bayway |  | Red Bluff | Terminal/Bayway | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-04-29 | 2019-04-29 | 138 | 1.1 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42930, 42931, 905210, 42170, 42955, 43225 | Y | N |  |  | 13455 | 5715
6101 | Lon Hill: Replace 345/138 kV autotransformers | Replace 345/138 kV autotransformers at Lon Hill | Formerly TPIT project 6040 | Lon Hill | - | Planned | 829 - 1013 | AEP | Bill Roberts dnlyons@aep.com 918-599-2698 | 3630 | 2019-04-30 | 2019-04-24 | 345 | 0 | 0 | 1350 |  | Nueces |  | Tier 4 |  |  |  | 8455, 8452, 8499, 8502 | Y | N |  | Formerly TPIT project 6040 | 13826 | 6101
6715 | Noelke Substation Addition | Construct a new substation named Noelke off the Bakersfield to Schneeman Draw transmission line to support a generation interconnection request (20INR0011). |  | Bakersfield | Schneeman Draw | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018746 | 2019-04-30 |  | 345 | 0 | 0 | 0 |  | Pecos | Crockett | Tier 4 |  |  |  | 7053, 76004, 76002, 76005 | Y | N |  |  | 14498 | 6715
6120 | Sabinal - Knippa 69 kV line | Rehab Sabinal - Knippa 69 kV line |  | Sabinal | Knippa | Planned | 811 - 0996 | AEP | James Nivens dnlyons@aep.com 918-599-2698 | 3602 | 2019-04-30 | 2019-04-23 | 69 | 0 | 2.655 | 0 |  | Uvalde |  | Tier 4 |  |  |  | 8628, 8630 | Y | N |  |  | 13846 | 6120
10TPIT0062 | Marion Power Transformer Addition (Formerly Weil Road) | Expand the Marion substation 138-kV bus. Install a 138-26.18 kV 40 MVA power transformer at Marion 138 kV bus. | Delayed due to ERCOT outage restrictions | Marion |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org | 1015120 | 2019-04-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7178 | Y | N |  |  | 9648 | 2384
7165 | T505 Geronimo - Clear Springs MLSE Upgrade | Upgrade terminal equipment at Geronimo and Clear Springs to achieve a planned static normal and emergency rating of 492 MVA on T505. |  | Geronimo | Clear Springs | Planned | 1019370 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1019370 | 2019-04-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7604, 7680 | Y | N |  |  | 15006 | 7165
6021 | Haskell Tap 1 to Paint Creek 69 kV line: Rebuild 69 kV line | Rehab Haskell Tap 1 to Paint Creek 69 kV line | IN SERVICE | Haskell Tap 1 | Paint Creek | In-Service | 786 - 0971 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2669 | 2019-04-30 | 2019-04-30 | 69 | 0 | 14 | 0 |  | Haskell | Haskell | Tier 4 |  |  |  | 6005, 6159, 6171, 6174 | Y | N |  |  | 13738 | 6021
7163 | T180 Lakeway - Marshall Ford MLSE Upgrade | Upgrade terminal equipment at Lakeway and Marshall Ford to achieve a planned static normal and emergency rating of 217 MVA on T180. |  | Lakeway | Marshall Ford | Planned | 1019367 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1019367 | 2019-04-30 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 7356, 7538 | Y | N |  |  | 15004 | 7163
43212A | Caymus Capbanks in TNMP West Texas System | Install 60 Mvar Capacitor bank at TNMP Caymus Substation (NOMCR # 57482-1). |  | Caymus (Bus #38410) | Caymus (Bus #38410) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07819 | 2019-05-01 |  | 138 | 0 | 0 | 0 | 0,60 | Reeves | Reeves | Tier 4 |  |  |  | 38410 | Y |  |  | 0 | 48413 | 43212
6387A | Greenville Arera System Enhancements | [6 empty] | RYBRN | Alfonso Galindo agalindo@epeconsulting.co 512-886-2139 |  | 2019-05-01 | 2019-05-01 | 138 | 0 | 0 | 0 |  | Hunt |  | Tier 3 | 2015-12-15 | 2016-02-15 |  | 6883 | Y | N |  | 0 | 47082 | 6387
48685 | This adds capacitance to Hamilton | This adds capacitance to Hamilton NOMCR 56568 |  |  |  | Under Construction |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2019-05-01 |  | 69 | 0 | 0 | 0 | 0,7.6 | Comanche | Comanche | Tier 4 |  |  |  | 258 | Y |  |  | 0 | 48686 | 48685
6834A | IH20 STATCOM RPG | Re-conductor Collie Field Tap-Collie Field with 795 ACSR. Construct Collie Yard Tap and Collie Capacitor Station. Install three initial 20 MVAR MSCs at Collie Capacitor Station (38035). |  | Collie Field Tap (38037) | Collie Capacitor Station (38035) & Collie Field (38038) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-05-01 |  | 138 | 0.085227 | 0.056818 | 0 | 0,60 | Reeves | Reeves | Tier 3 | 2017-10-10 | 2017-12-06 |  | 38035, 38036, 38037, 38038 | Y |  |  | 0 | 46206 | 6834
47971 | Rebuild Friendswood-Seminole 138kV line with 795 ACSS | NOMCR # 58045-1 |  | TNMP Friendswood (Bus #38980) | TNMP Seminole (Bus #38990) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | STE07219 | 2019-05-01 |  | 138 | 0 | 2.9 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 38980, 38990 | Y |  |  | 0 | 48411 | 47971
6328B | REED - Substation Removal | Remove 69kV REED substation from CNP transmission service |  | REED |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-02 00:01 | 2019-05-02 | 69 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 41340, 40352, 40800, 41040 | Y |  |  | 0 | 45474 | 6328
6640 | PARKES 138kV Substation | Install 138kV customer-owned PARKES substation. Loop from Ckt.84 Channelview to HADEN |  | PARKES | Channelview/ HADEN | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-03 | 2019-05-03 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40881, 40280, 40780 | Y |  |  |  | 14397 | 6640
5917 | Desert Mesa Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Desert Sky Tap #1 (S566). |  | Desert Sky Tap #1 |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017353 | 2019-05-09 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 76022 | Y | N |  |  | 13625 | 5917
4758 | Sand Lake 138 kV Switching Station | Construct new switching station |  | Sand Lake |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8340 | 2019-05-14 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  | 11097, 1086, 11086, 11104, 11197 | Y | N |  |  | 12353 | 4758
6764 | Round Rock Capacitors | Upgrade existing capacitor banks at Round Rock Switching Station |  | Round Rock | Round Rock | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R764 | 2019-05-15 |  | 138 | 0 | 0 | 0 | 0,110.4 | Williamson | Williamson | Tier 4 |  |  |  | 3668 | Y | N |  |  | 14558 | 6764
5927 | King Mountain Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at King Mountain West Tap (S563). |  | King Mountain |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017391 | 2019-05-15 |  | 138 | 0 | 0 | 0 |  | Crane |  | Tier 4 |  |  |  | 76635 | Y | N |  |  | 13635 | 5927
7099 | Yucca - Moss 138 kV Series Reactor | Yucca - Moss 138 kV Series Reactor |  | Yucca | Moss | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8447 | 2019-05-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 11015, 1009, 1019, 37980 | Y |  |  | 0 | 49925 | 7099
45809 | Add Yucca Drive 138 kV Capacitors | Add Yucca Drive 138 kV Capacitors |  | Yucca | Yucca | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8466 | 2019-05-15 |  | 138 | 0 | 0 | 0 |  | Ward | Ward | Tier 4 |  |  |  | 1009, 1010 | Y |  |  | 0 | 45811 | 45809
5488 | Northwest Carrollton - LakePointe TNP 138 kV Line | Upgrade existing NW Carrollton - LakePointe 138 kV Line | Construction schedule change | Northwest Carrollton | LakePointe | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5156 | 2019-05-15 |  | 138 | 0 | 2.1 | 0 |  | Dallas | Denton | Tier 4 |  |  |  | 2362, 37010 | Y | N |  |  | 13226 | 5488
17TPIT0024 | Payne - Anna Switch 138 kV Line | Upgrade existing line | Project Deferral | Payne | Anna Switch | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R938-E | 2019-05-15 |  | 138 | 0 | 20.8 | 0 |  | Grayson | Collin | Tier 4 |  |  |  | 1713, 1748, 1754, 1839, 2374 | Y | N |  |  | 10561 | 3213
4274 | Navarro - Corsicana 69 kV Line | Upgrade existing line |  | Navarro | Corsicana | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R793 | 2019-05-15 |  | 69 | 0 | 12.5 | 0 |  | Navarro | Navarro | Tier 4 |  |  |  | 3468, 3475, 3479, 3480, 13468 | Y | N |  |  | 11823 | 4274
7092 | Moss Sw. Sta. 345/138 kV Autotransformer #2 | Moss Sw. Sta. 345/138 kV Autotransformer #2 |  | Moss |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8275 | 2019-05-15 |  | 345 | 0 | 0 | 600 |  | Ector |  | Tier 4 |  |  |  | 18526, 1018, 1019 | Y |  |  |  | 14926 | 7092
7102 | Wink - Yukon 138 kV Second Circuit | Wink - Yukon 138 kV Second Circuit |  | Wink | Yukon | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8449 | 2019-05-15 |  | 138 | 26.6 | 0 | 0 |  | Winkler | Ector | Tier 4 |  |  |  | 1251, 1253, 1258, 11237, 1074, 1250, 1252, 1254, 11253, 11260, 11252 | Y |  |  | 0 | 49707 | 7102
5805 | Holland 69 kV Capacitors | Install 69 kV Capacitors |  | Holland | Holland | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R772 | 2019-05-15 |  | 69 | 0 | 0 | 0 | 0,9.2 | Bell | Bell | Tier 4 |  |  |  | 3646 | Y | N |  |  | 13545 | 5805
2941B | North Main Switch third transmission source |  |  | North Main Tap | North Main Sw | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5161-E | 2019-05-15 |  | 138 | 0 | 0.1 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2093, 2106 | Y | N |  |  | 14910 | 2941
7100 | Wolf - General Tire 138 kV Series Reactor | Wolf - General Tire 138 kV Series Reactor |  | Wolf | General Tire | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8448 | 2019-05-15 |  | 138 | 0 | 0 | 0 |  | Ward | Ector | Tier 4 |  |  |  | 11018, 1013, 1103 | Y |  |  |  | 14934 | 7100
6759 | Ranger Gulf 69 kV Emergency Capacitors | Install 18.4 MVar Cap Bank at Ranger Gulf |  | Ranger Gulf | Ranger Gulf | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1746 | 2019-05-15 |  | 69 | 0 | 0 | 0 | 0,18.4 | Eastland | Eastland | Tier 4 |  |  |  | 1628 | Y | N |  |  | 14553 | 6759
5801 | Hutto - Rnd Rck SE - Gil | Upgrade138 kV line | Project Deferral | Hutto | Gilleland | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R2005 | 2019-05-15 |  | 138 | 0 | 7.5 | 0 |  | Williamson | Travis | Tier 4 |  |  |  | 3654, 3666, 7336 | Y | N |  |  | 13541 | 5801
6763 | Round Rock switching station | Reconfigure existing 138 kV Round Rock switching station |  | Round Rock | Round Rock | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R767 | 2019-05-15 |  | 138 | 0 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | Y | N |  |  | 14557 | 6763
5484 | Royse-Terrell 138 kV Line | Upgrade existing Royse - Terrell 138 kV line |  | Royse | Terrell Sw | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4224 | 2019-05-15 |  | 138 | 0 | 28 | 0 |  | Rockwall | Kaufman | Tier 4 |  |  |  | 2715, 2472, 2713, 2717, 2718, 2719, 2721, 2723 | Y | N |  |  | 13222 | 5484
13TPIT0059 | Cedar Crest - Industrial 138 kV line | Upgrade existing line | Construction schedule change | Cedar Crest | Industrial | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4072-E | 2019-05-15 |  | 138 | 0 | 3.2 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2494, 2976, 2981 | Y | N | 2009-R23 |  | 9775 | 2495
16TPIT0061 | Norwood - Record Crossing - East Levee 138 kV Line | Upgrade existing line | Construction schedule change | Norwood | East Levee | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4107-E | 2019-05-15 12:00 |  | 138 | 0 | 7.6 | 0 |  | Dallas | Dallas | Tier 4 |  | 2016-08-22 |  | 2405, 2407, 2482, 2811, 2812, 2813, 2815, 2816, 2814, 2819, 2823, 2824 | Y | N |  |  | 11846 | 3067
46280 | Screwbean Tap - Screwbean 138 kV Line | Rebuild Screwbean Tap - Screwbean 138 kV Line |  | Screwbean Tap | Screwbean | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8465 | 2019-05-15 23:00 |  | 138 | 0 | 0.8 | 0 |  | Culberson | Culberson | Tier 4 |  |  |  | 1079, 1090, 1095 | Y |  |  | 0 | 46282 | 46280
45118 | Add Dune Switch | Add Dune Switch |  | Dune Switch | Dune Switch | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9050 | 2019-05-16 |  | 138 | 2 | 0 | 0 |  | Winkler | Winkler | Tier 4 |  |  |  | 11260, 1251, 11253, 182301 | Y |  |  | 0 | 45407 | 45118
6945 | Horseshoe Spring 138 kV Sw. Sta. | Horseshoe Spring 138 kV Sw. Sta. |  | Horseshoe Springs Switch |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8408 | 2019-05-16 |  | 138 | 0 | 0 | 0 |  | Culberson | Culberson | Tier 4 |  |  |  | 11190, 1096, 1097, 11079, 11097, 11103, 11191 | Y |  |  | 0 | 45510 | 6945
5234 | Cibolo to Schertz T-Line (T303), Breaker upgrades | Add 138kV Breaker at Schertz, replace 138 breaker at Cibolo; upgrad associated 138 switches relaying to achieve 277 MVA rating on the Cibolo to Schertz Cirtcuit #2. | Construction Schedule | Cibolo | Schertz | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2019-05-17 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7608, 7610 | Y | N |  |  | 12907 | 5234
6946 | Add Horseshoe Draw 138 kV Dynamic Reactive Devices | Construct Horseshoe Draw 138 kV -250/+250 MVAR STATCOM |  | Horseshoe Spring | Horsehsoe Draw | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8418 | 2019-05-17 |  | 138 | 0 | 0 | 0 | -250250 | Culberson |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11172, 11190 | Y |  |  |  | 14768 | 6946
17TPIT0008 | Marion to Cibolo T-Line (T-302) Circuit Addition | Add another 138 kV circuit, to existing Marion to Cibolo T-Line (T-302), 1192 ACSR, 4.81 miles; Replace 3-138 breakers to 63 kA rating at Marion; Add 138 terminal w 138 breaker and associated relaying at Cibolo sub | Construction Schedule | Marion | Cibolo | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2019-05-17 |  | 138 | 4.81 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7178, 7608 | Y | N |  |  | 10137 | 2792
7097 | Add Horseshoe Springs 138 kV Capacitors | Add 4 blocks of 36.8 MVAR capacitors at Horseshoe Springs Sw. Sta. |  | Horseshoe Springs |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8410 | 2019-05-18 |  | 138 | 0 | 0 | 0 | 0,147.2 | Culberson |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11079, 11103, 11190 | Y |  |  |  | 14931 | 7097
44902 | Marion Switch Upgrades and Replacement | Upgrade/Replace underrated switches 5679, 5681, 5689, 5691, 5699, 5701 to 3000 Amp Switches. Replace and increase fault interrupting rating of breakers 5680, 5690, 5700 to 63kA, and continuous rating to 3,000Amp. |  | Marion | Marion | Under Construction |  | NBU | Gregory Thomas gthomas@nbutexas.com 830-608-8953 |  | 2019-05-19 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7178 | Y | N |  | 0 | 44903 | 44902
5242 | Clodine to Barker Ckt.73 Thermal Uprate | Upgrade Ckt.73 Clodine to Barker to increase thermal ratings | Delay in project schedule | Clodine | Barker | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-05-20 | 2019-05-20 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 44052, 44140 | Y | N |  |  | 12917 | 5242
6397 | Treadwell: Build new 138 kV station | Interconnect Cactus Flats wind farm on the SAPS to Yellowjacket 138 kV line | IN SERVICE | Treadwell |  | In-Service | 875 - 1053 | AEP TNC | Tom Reynolds mlforcum@aep.com 918-599-2674 | 2727 | 2019-05-22 | 2019-05-22 | 138 | 0 | 0 | 0 |  | Concho |  | Tier 4 |  |  |  | 60423, 6365, 6480 | Y | Y |  |  | 14156 | 6397
5978 | Tankersley to Mathis Field 69 kV line: Rebuild 69 kV line | Rehab Tankersley to Mathis Field 69 kV line | IN SERVICE | Tankersley | Mathis Field | In-Service | 786 - 0971 | AEP TNC | Bill Roberts mlforcum@aep.com 918-599-2674 | 2663 | 2019-05-23 | 2019-05-23 | 69 | 0 | 9.99 | 0 |  | Irion | Tom Green | Tier 4 |  |  |  | 6477, 6528 | Y | N |  |  | 13693 | 5978
44445 | Riley: Interconnect Electra Wind phase two | Interconnect Electra wind farm phase two, Lockett Station, into the Electra wind farm phase one, Digby substation | IN SERVICE | Riley |  | In-Service | 935 - 1113 | ETT | Dave Goetz mlforcum@aep.com 918-599-2674 | 2748 | 2019-05-23 | 2019-05-23 | 345 | 0 | 0 | 0 |  | Foard |  | Tier 4 |  |  |  | 6101 | Y | N |  | 0 | 44446 | 44445
5916 | Darst Creek Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Darst Creek Substation (138-kV capable). |  | Darst Creek |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017352 | 2019-05-30 |  | 69 | 0 | 0 | 0 |  |  | Guadalupe | Tier 4 |  |  |  | 78195 | Y | N |  |  | 13624 | 5916
6745 | Reading: New Distribution Station | Add New Reading Distribution Station |  | Uvalde | STEC Downie | Planned | 876 - 1054 | AEP TCC | Guillermo Taylor dnlyons@aep.com 918-599-2698 | 3663 | 2019-05-30 | 2019-06-04 | 138 | 0 | 0 | 0 |  | Uvalde |  | Tier 4 |  |  |  | 8024, 5885, 8234 | Y | N |  |  | 14538 | 6745
7006B | CNP_18TPIT7006_HOC_Reactor_Upgrades | Install (1) 5-Ohm Reactor at HO Clarke as a fault duty upgrade |  | HOC | HOC | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47175, 42041, 47150, 47155, 47170, 47165, 49009 | Y |  |  |  | 14827 | 7006
6115 | Melon Creek - Tatton 69 kV Line | Rehab Melon Creek - Tatton 69 kV Line |  | Melon Creek | Tatton | Under Construction | 815 - 0999 | AEP | Bill Roberts dnlyons@aep.com 918-599-2698 | 3608 | 2019-05-30 | 2019-01-18 | 69 | 0 | 7.75 | 0 |  | Refugio | Aransas | Tier 4 |  |  |  | 80065, 8811 | Y | N |  |  | 13841 | 6115
6314A | BASF-HOFMAN-LakeJackson_Ckt.02_Upgrades | Upgrade 138kV Ckt.02 BASF to HOFMAN to increase thermal ratings. |  | BASF | HOFMAN | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-30 | 2019-04-22 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42150, 42810 | Y | N |  | 0 | 44960 | 6314
3938C | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.82 Angleton to Richwood to increase thermal ratings. | - Overall change in schedule | Angleton | Richwood | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-05-30 00:03 | 2019-08-08 | 138 | 0 | 14.2 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42110, 43150 | Y | N |  | Cost Included in TPIT Project 3938E | 45096 | 3938
3938E | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.26 Angleton to STRATT to increase thermal ratings. | - Overall change in schedule | Angleton | STRATT | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-05-30 00:04 | 2019-08-08 | 138 | 0 | 13.8 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42110, 43300 | Y | N |  |  | 45094 | 3938
3938D | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.82 Richwood to Cavern to increase thermal ratings. | - Overall change in schedule | Richwood | Cavern | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-05-30 00:04 | 2019-08-08 | 138 | 0 | 5.4 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43150, 43330 | Y | N |  | Cost Included in TPIT Project 3938E | 45097 | 3938
3938B | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.26 STRATT to SINTEK to increase thermal ratings. |  | STRATT | SINTEK | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-05-30 00:04 | 2019-08-08 | 138 | 0 | 6.4 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43240, 43300 | Y | N |  | Cost Included in TPIT Project 3938E | 45095 | 3938
4844 | 2nd Marion Autotransformer | Add a Second 345/138-kV Autotransformer at Marion. Part of the CPS Tie Project |  | Marion | Marion | Planned | 4473 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1015208 | 2019-05-31 |  | 345 | 0 | 0 | 478 |  | Guadalupe | Guadalupe | Tier 1 | 2014-06-29 | 2015-03-26 | 2015-04-14 | 77044, 7044, 7178 | Y | N |  |  | 12446 | 4844
6314B | BASF-HOFMAN-LakeJackson_Ckt.02_Upgrades | Upgrade 138kV Ckt.02 HOFMAN to Lake Jackson to increase thermal ratings. | - Delayed project schedule | HOFMAN | Lake Jackson | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-31 | 2019-04-22 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42215, 42810, 42880, 48006 | Y | N |  | Cost included in 18TPIT6314A | 44961 | 6314
6986 | Upton County Capacitor Bank Additions | Install two (2) 31.2 MVAR capacitor banks at Benedum Substation. |  | Benedum |  | Planned | 6717 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1019103, 1019103 | 2019-05-31 |  | 138 | 0 | 0 | 0 | 0,31.2 | Upton |  | Tier 4 |  |  |  | 71213 | Y | N |  |  | 14803 | 6986
5555A | Clodine-Obrien Ckt25 & Ck73 Thermal Uprate | Upgrade Ckt.25 Clodine to Obrien to increase thermal ratings | Delay in project schedule | Clodine | Obrien | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1118 | 2019-05-31 | 2019-06-13 | 138 | 0 | 0 | 0 |  | Harris | Fort Bend | Tier 4 |  |  |  | 44145, 44510, 44511 | Y | N |  |  | 13283 | 5555
4473 | Zorn to Marion 2nd 345-kV Transmission Line Addition | Add 345-kV Zorn (7042) to Marion (7044) 2nd circuit using bundled Suwannee. Portion of the CPS-Tie Project. |  | Zorn | Marion | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1015208 | 2019-05-31 |  | 345 | 18 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 1 | 2014-06-29 | 2015-03-26 | 2015-04-14 | 7042, 7044 | Y | N |  |  | 12034 | 4473
6314C | BASF-HOFMAN-LakeJackson_Ckt.02_Upgrades | Upgrade 138kV Ckt.02 Lake Jackson to Retrieve to increase thermal ratings. |  | Lake Jackson | Retrieve | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-31 | 2019-04-22 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42880, 43172 | Y | N |  | Cost included in 18TPIT6314A | 44962 | 6314
5555B | Clodine-Obrien Ckt25 & Ck73 Thermal Uprate | Upgrade Ckt.73 Clodine to Obrien to increase thermal ratings | Delay in project schedule | Clodine | Obrien | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1118 | 2019-05-31 00:01 | 2019-06-13 | 138 | 0 | 0 | 0 |  | Harris | Fort Bend | Tier 4 |  |  |  | 44140, 44512 | Y | N |  |  | 13284 | 5555
4703A | Bellaire to San Felipe Ckt.09 & Bellaire tap Ckt.24 | Reconductor Ckt.09 Bellaire to San Felipe and upgrade substation equipment to increase thermal ratings. |  | Bellaire | San Felipe | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1132 | 2019-05-31 00:01 | 2019-05-23 | 138 | 0 | 2 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 46600, 47010, 47013, 47165, 47300, 47380, 47381, 47680 | Y | N |  | 0 | 48255 | 4703
4083 | CPSE_Merida to Westside Rebuild | Rebuild approximately four miles of 138 kV transmission circuit from Merida to Westside. |  | Merida | Westside | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0235 | 2019-06-01 |  | 138 | 0 | 4 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5310, 5490 | Y | N |  |  | 11608 | 4083
44687 | New 345kV substation |  |  |  |  | Planned |  | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2019-06-01 |  | 345 | 0 | 0 | 0 |  | Deaf Smith | Deaf Smith | Tier 4 |  |  |  | 79513, 79502, 79504 | Y |  |  | 0 | 44688 | 44687
3273A | Southton - New 138kV Substation | Rebuild Brooks to Brooks Tap |  |  |  | Under Construction | S-0750 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0217 | 2019-06-01 |  | 138 | 0 | 1.6 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5045, 5030, 5085 | Y |  |  | 0 | 45521 | 3273
11TPIT0084 | Hidden Lakes - New Substation | Build a new 138-12.47 kV substation to accommodate new subdivision growth along the FM 517 and FM 646 corridors in Dickinson, Texas. Project delayed until 2019 RMC. |  | Leave blank | Leave blank | Planned |  | TNMP | Anthony Hudson Anthony.Hudson@tnmp.com. 281-581-4712 | STE02416 | 2019-06-01 |  | 138 | 0 | 0 | 0 |  | Galveston |  | Tier 4 |  |  |  | 38900, 38890, 38920, 42015 | Y | N |  |  | 8439 | 1261
5144 | CPSE_Pleasanton Rd Transmission Rebuild | Rebuild approximately seven circuit miles of 138 kV transmission on Pleasanton Road from Loop 410 to Harlandale Tap. This project includes partial rebuild of the Sommers to Harlandale and Sommers to Merida 138 kV transmission circuits. |  | Sommers | Harlandale/Merida | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0192 | 2019-06-01 |  | 138 | 0 | 7 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5190, 5310, 5395 | Y | N |  |  | 12797 | 5144
6377 | Pave Paws to Eldorado Live Oak 69 kV line: Rbld 69 kV line | Rehab Pave Paws to Eldorado Live Oak 69 kV line | IN SERVICE | Pave Paws | Eldorado Live Oak | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2723 | 2019-06-21 | 2019-06-21 | 69 | 0 | 7.71 | 0 |  | Schleicher | Schleicher | Tier 4 |  |  |  | 6494, 6498 | Y | N |  |  | 14121 | 6377
44428 | Edith Clarke: Build 345 kV terminal | Interconnect Foard City wind farm at Edith Clarke | IN SERVICE | Edith Clarke |  | In-Service | 934 - 1112 | ETT | Eric Blind mlforcum@aep.com 918-599-2674 | 2747 | 2019-06-28 | 2019-06-28 | 345 | 0 | 0 | 0 |  | Foard |  | Tier 4 |  |  |  | 60500 | Y | N |  | 0 | 44429 | 44428
44495 | Edith Clarke to Foard City: Build 345 kV line | Interconnect Foard City wind farm at Edith Clarke | IN SERVICE | Edith Clarke | Foard City | In-Service | 934 - 1112 | ETT | Eric Blind mlforcum@aep.com 918-599-2674 | 2746 | 2019-06-28 01:00 | 2019-06-28 | 345 | 4 | 0 | 0 |  | Foard | Foard | Tier 4 |  |  |  | 60500, 142563 | Y | N |  | 0 | 44496 | 44495
6746 | Valadez: Add New Distribution Station | Add New Valadez Distribution Station |  | Wooldridge | Barney Davis | Planned | 879 - 1057 | AEP TCC | Brad Duvall dnlyons@aep.com 918-599-2698 | 3666 | 2019-06-30 | 2019-05-14 | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8028, 8458, 8492 | Y | N |  |  | 14539 | 6746
6107 | Bonniview - Rincon 69 kV Line | Rehab Bonniview - Rincon 69 kV line |  | Bonniview | Rincon | Planned | 834 - 1018 | AEP TCC | Jason Bryant dnlyons@aep.com 918-599-2698 | 3641 | 2019-06-30 | 2019-07-18 | 69 | 0 | 11.97 | 0 |  | Refugio | San Patricio | Tier 4 |  |  |  | 8416, 8805 | Y | N |  |  | 13833 | 6107
5915 | Cypress Creek Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Cypress Creek Substation (This is a two year project). |  | Cypress Creek |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017351 | 2019-06-30 |  | 138 | 0 | 0 | 0 |  | Kendall |  | Tier 4 |  |  |  | 7156 | Y | N |  |  | 13623 | 5915
6387E | Greenville Arera System Enhancements | [6 empty] | RYBRN | Alfonso Galindo agalindo@epeconsulting.co 512-886-2139 |  | 2019-07-01 | 2019-07-01 | 138 | 0 | 0 | 0 |  | Hunt |  | Tier 3 | 2015-12-15 | 2016-02-15 |  | 6750, 6879, 6882 | Y | N |  | 0 | 47081 | 6387
6536 | T-283 Bellville South to Quanex Switch | Rebuild transmission line to 138-kV capable 959.6 ACSS-TW conductor due to maintenance on old 69 KV wood pole line and the future conversion to 138 KV. |  | Bellville South | Quanex Switch Structure | Under Construction |  | SBEC | James Jouett jjouett@sbec.org 979-413-7714 | WO# 17-6071 | 2019-07-01 |  | 69 | 0 | 3.33 | 0 |  | Austin | Austin | Tier 4 |  |  |  | 7269, 7660 | Y | N |  |  | 14276 | 6536
6387B | Greenville Arera System Enhancements |  |  |  |  | Planned |  | RYBRN | Alfonso Galindo agalindo@epeconsulting.co 512-886-2139 |  | 2019-07-01 | 2018-10-01 | 138 | 0 | 0 | 100 |  | Hunt | Hunt | Tier 3 | 2015-12-15 | 2016-02-15 |  | 837 | Y | N |  | 0 | 47083 | 6387
5222 | Rebuild Dilley to Cotulla 69 kV line | Rebuild 4/0 ACSR 69 kV line with 138 kV capable 795 ACSR. 2015 RTP |  | Dilley | Cotulla | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-07-01 | 2019-07-17 | 69 | 0 | 15.8 | 0 |  | La Salle | Frio | Tier 4 |  |  |  | 5863, 5876 | Y | N |  |  | 12889 | 5222
43447 | T-283 Quanex Switch yard | LCRA Quanex Switch 69 KV lattice Tower with 3-way GOAB Switch to be replaced with switch yard. Installing three A-Frames with 2000 amp connected bus with 138 KV switches with interupterson each A-Frame plus a midpoint switch with interrupter. This is to be built in 2019 in conjuction with the Project Number 6536 |  | Quanex | Quanex switch | In-Service |  | SBEC | James Jouett jjouett@sbec. |  | 2019-07-10 |  | 69 | 0 | 0 | 0 |  | Austin | Austin | Tier 4 |  |  |  | 7660 | Y |  |  | 0 | 43448 | 43447
5794 | Mason to Fort Mason: Rebuild 69 kV line | Rebuild Mason to Fort Mason 69 kV line and convert to 138 kV | IN SERVICE | Mason | Ft. Mason | In-Service | 646 - 0815 | AEP TNC | Michael Richardson mlforcum@aep.com 918-599-2674 | 1810 | 2019-07-12 | 2019-07-12 | 69 | 0 | 0.15 | 0 |  | Mason | Mason | Tier 4 |  |  |  | 6393, 60410, 76388, 76390 | Y | N |  |  | 13533 | 5794
4454 | Henne to Comal Transmission Line Upgrade | Upgrade the 7.6 mile Henne (7174) - Comal (7176) 138-kV transmission line from 159 MVA to 380 MVA using single 959 ACSS Suwannee conductors. |  | Henne | Comal | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1015116 | 2019-07-16 |  | 138 | 0 | 7.6 | 0 |  | Comal | Comal | Tier 4 |  |  |  | 7172, 7174, 7176 | Y | N |  |  | 12014 | 4454
5980 | Bison: Build 69 kV station | Construct new 69 kV ring bus at Powell Field Junction Tap | IN SERVICE | Bison |  | In-Service | 840 - 1024 | AEP TNC | Brad Duvall mlforcum@aep.com 918-599-2674 | 2680 | 2019-07-19 | 2019-07-19 | 69 | 0 | 0 | 0 |  | Crockett |  | Tier 4 |  |  |  | 6548, 60395, 6545, 6547, 6549 | Y | N |  |  | 13695 | 5980
6064 | Anson to Exxon Hawley Tap 69 kV line: Rebuild 69 kV line | Rehab Anson to Exxon Hawley Tap 69 kV line | IN SERVICE | Anson | Exxon Hawley Tap | In-Service | 786 - 0971 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2674 | 2019-07-29 | 2019-07-29 | 69 | 0 | 10.39 | 0 |  | Jones | Jones | Tier 4 |  |  |  | 6175, 6176, 6238 | Y | N |  |  | 13784 | 6064
6834B | IH20 STATCOM RPG | Install +/- 190 MVAR STATCOM at IH20. |  | IH20 138 kV (38045) | IH20 STATCOM 138 kV (38046) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-08-01 |  | 138 | 0 | 0 | 0 | -190190 | Reeves | Reeves | Tier 3 | 2017-10-10 | 2017-12-06 |  | 38046, 38045 | Y |  |  | 0 | 46207 | 6834
46246 | Monument Draw Interconnection | Monument Draw Interconnection (NOMCR # 57718-1). (Cost estimate needs to be verified) |  | All American Tap (Bus #38230) | Lone Star Tap (Bus #38180) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-08-01 |  | 69 | 0.04 | 0 | 0 |  | Winkler | Ward | Tier 4 |  |  |  | 38210, 38211, 38212, 38180, 38230 | Y |  |  | 0 | 48423 | 46246
5962 | Mason: Add new 138/69 kV autotransformer | Add 138/69 kV autotransformer capacity at Mason | IN SERVICE | Mason |  | In-Service | 646 - 0815 | AEP TNC | Michael Richardson mlforcum@aep.com 918-599-2674 | 2687 | 2019-08-15 | 2019-08-15 | 138 | 0 | 0 | 130 |  | Mason |  | Tier 4 |  |  |  | 60410, 6393 | Y | N |  |  | 13677 | 5962
45336 | Corichi Tap: Build 138 kV Hard Tap | Corichi Tap: Build 138 kV Hard Tap on El Campo - Victoria Line |  | El Campo | Ganado | In-Service |  | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 |  | 2019-08-16 | 2019-07-03 | 138 | 0 | 0 | 0 |  | Wharton | Jackson | Tier 4 |  |  |  | 88099, 8102, 8117 | Y | N |  | 0 | 45337 | 45336
45338 | Dobbin Tap: Build 138 kV Hard Tap | Dobbin Tap: Build 138 kV Hard Tap on Bunsen - Lon Hill Line |  | Bunsen | Lon Hill | Planned |  | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 |  | 2019-08-19 | 2019-08-06 | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 88463, 8452, 8459 | Y | N |  | 0 | 45339 | 45338
44856 | Lipton 138 kV Hard Tap | New Lipton 138 kV Hard Tap |  | Asherton | West Batesville | In-Service | 972 - 1150 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3730 | 2019-08-21 | 2019-03-27 | 138 | 0 | 0 | 0 |  | Zavala |  | Tier 4 |  |  |  | 88285, 8236, 8283 | Y | N |  | 0 | 44857 | 44856
47927 | Tesla to Misae: Build new 345 kV line | Interconnect Misae Solar at Tesla | IN SERVICE | Tesla | Misae | In-Service | 936 - 1114 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2773 | 2019-08-22 01:00 | 2019-08-22 | 345 | 0.5 | 0 | 0 |  | Childress | Childress | Tier 4 |  |  |  | 60501, 142815 | Y | N |  | 0 | 47928 | 47927
44460 | Tesla: Build 345 kV terminal | Interconnect Misae Solar at Tesla | IN SERVICE | Tesla |  | In-Service | 936 - 1114 | ETT | Eric Blind mlforcum@aep.com 918-599-2674 | 2749 | 2019-08-22 12:00 | 2019-08-22 | 345 | 0 | 0 | 0 |  | Childress |  | Tier 4 |  |  |  | 60501 | Y | N |  | 0 | 44461 | 44460
7153 | Fort Stockton Plant to Solstice: Raise Structures on 138 kV | Raise Structures on the Fort Stockton Plant to Solstice 138 kV line | IN SERVICE | Fort Stockton Plant | Solstice | In-Service | 923 - 1101 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2820 | 2019-08-25 | 2019-08-25 | 138 | 0 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6630, 60385 | Y | N |  |  | 14992 | 7153
45027 | Brant: Build 69 kV temporary Tap | Build new Brant 69 kV temporary tap on the Rock Springs to Sonora 69 kV line | IN SERVICE | Brant |  | In-Service | 952 - 1130 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2757 | 2019-08-28 01:00 | 2019-08-28 | 69 | 0 | 0 | 0 |  | Sutton |  | Tier 4 |  |  |  | 60438, 6570, 8239 | Y | N |  | 0 | 45028 | 45027
6254 | Gomez to Fort Stockton Switch 69 kV line: Rebuild 69 kV line | Rehab TNMP Gomez to Fort Stockton Switch 69 kV line | IN SERVICE | Gomez | Fort Stockton Switch | In-Service | 786 - 0971 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2700 | 2019-08-30 | 2019-08-30 | 69 | 0 | 4.77 | 0 |  | Pecos | Reeves | Tier 4 |  |  |  | 6645, 38470 | Y | N |  |  | 13982 | 6254
6251 | Pecos Valley to TNMP Gomez 69 kV line: Rebuild 69 kV line | Rehab Pecos Valley to TNMP Gomez 69 kV line | IN SERVICE | Pecos Valley | Gomez | In-Service | 786 - 0971 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2699 | 2019-08-30 | 2019-08-30 | 69 | 0 | 14.2 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6643, 38470 | Y | N |  |  | 13979 | 6251
5552A | North Belt to Greens to Lockwood Ckt.90 Thermal Uprate | Upgrade Ckt.90 North Belt to Greens Road to increase thermal ratings |  | North Belt | Greens Road | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1126 | 2019-08-30 | 2019-06-13 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45822, 46112 | Y |  |  | 0 | 52129 | 5552
6387D | Greenville Arera System Enhancements |  |  |  |  | Planned |  | RYBRN | Alfonso Galindo agalindo@epeconsulting.co 512-886-2139 |  | 2019-08-30 | 2019-09-01 | 138 | 5 | 0 | 0 |  | Hunt | Hunt | Tier 3 | 2015-12-15 | 2016-02-15 |  | 837, 6750 | Y | N |  | 0 | 47080 | 6387
47973 | Interconnects Saddleback and Roy Bean to TNMP WTN | Interconnects Saddleback and Roy Bean to TNMP WTN system (NOMCR # 55847-1). |  | Salt Draw Tap (Bus #38055) | Barilla Draw Tap (Bus #38065) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE04018 | 2019-08-31 |  | 138 | 0.1 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38058, 38059, 38055, 38060 | Y |  |  | 0 | 48421 | 47973
5552B | North Belt to Greens to Lockwood Ckt.90 Thermal Uprate | Upgrade Ckt.90 Greens Road to Lockwood to increase thermal ratings |  | Greens Road | Lockwood | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1126 | 2019-08-31 | 2019-06-13 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45822, 46031 | Y |  |  | 0 | 52130 | 5552
43214 | Interconnects Calmity Jane to TNMP WTN | New Substation - Calamity Jane (Cost estimate needs to be verified) |  | Worsham (Bus #38021) | Calamity Jane (Bus #38020) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-09-01 |  | 138 | 0.5 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38020, 38021 | Y |  |  | 0 | 48426 | 43214
45114 | TNMP County Road Substation | New Substation - County Road |  | IH20 (Bus #38045) | County Road (Bus #38047) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-09-01 |  | 138 | 0 | 0.2 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38047, 38050, 38040, 38045 | Y |  |  | 0 | 48425 | 45114
6068 | Onyx to Nugent Tap 69 kV line: Rebuild 69 kV line | Rehab Onyx to Nugent Tap 69 kV line | IN SERVICE | Onyx | Nugent Tap | In-Service | 786 - 0971 | AEP TNC | Jeremy Brazeal mlforcum@aep.com 918-599-2674 | 2676 | 2019-09-02 | 2019-09-02 | 69 | 0 | 6.71 | 0 |  | Jones | Jones | Tier 4 |  |  |  | 6219, 6243, 6388 | Y | N |  |  | 13789 | 6068
5934 | Warda Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Warda (S407). |  | Warda |  | In-Service |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017411 | 2019-09-09 | 2019-02-14 | 138 | 0 | 0 | 0 |  | Fayette |  | Tier 4 |  |  |  | 7312 | Y | N |  |  | 13642 | 5934
47952 | New Coyote Springs Substation | New Coyote Springs Substation (Reeves County 138 kV Conversion) |  | Coyote Springs (Bus #38113) | Reeves County Tap (Bus #38114) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE02819 | 2019-09-15 |  | 138 | 0 | 0.1 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38113, 38114 | Y |  |  | 0 | 48412 | 47952
6296 | Cowden North - Odessa North 69 kV Line Conversion | Cowden North - Odessa North 69 kV Line Conversion |  | Cowden North | Odessa North | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9028 | 2019-09-15 |  | 138 | 0 | 10.5 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 11259, 1122, 1123, 1141, 1142, 1259 | Y |  |  |  | 14025 | 6296
5221 | Move Oaks load to 138 kV bus | Move the Oaks load from the 69 kV to the 138 kV instead of replacing auto. 2015 RTP |  | Oaks |  | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-09-15 | 2019-09-13 | 138 | 0 | 0 | 0 |  | Atascosa |  | Tier 4 |  |  |  | 5713 | Y | N |  |  | 12888 | 5221
7110 | Horseshoe Springs - Owl Hills 138 kV Line | Horseshoe Springs - Owl Hills 138 kV Line |  | Horseshoe Springs | Owl Hills | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8383 | 2019-09-15 |  | 138 | 10 | 0 | 0 |  | Culberson |  | Tier 4 |  |  |  | 11090, 11190 | Y |  |  |  | 14944 | 7110
6920 | Reconfigures Barilla Draw and Interconnects BD-AMI | Reconfigures Barilla Draw and Interconnects BD-AMI (NOMCR # 57681-1) |  | Barilla Draw Tap (Bus #38060) | Barilla Draw-AMI (Bus #38061) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07213 | 2019-09-18 |  | 138 | 0.06 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38060, 38061, 38062, 38065, 38058, 38069 | Y |  |  | 0 | 48422 | 6920
5920 | Fourmile Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Indian Mesa/Orion/NWP Tap (S564). |  | Indian Mesa/Orion/NWP Tap |  | In-Service |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017380 | 2019-09-24 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 76019 | Y | N |  |  | 13628 | 5920
6116 | Palacios - Carancahua 69 kV Line | Rehab Palacios - Carancahua 69 kV Line |  | Palacios | Carancahua | In-Service | 817 - 1001 | AEP TCC | Jason Bryant dnlyons@aep.com 918-599-2698 | 3612 | 2019-09-30 | 2019-05-22 | 69 | 0 | 13.36 | 0 |  | Matagorda | Jackson | Tier 4 |  |  |  | 8131, 8555 | Y | N |  |  | 13842 | 6116
6004 | Refugio - Melon Creek 69 kV line | Rehab Refugio - Melon Creek 69 kV line |  | Refugio | Melon Creek | In-Service | 815 - 0999 | AEP TCC | Bill Roberts dnlyons@aep.com 918-599-2698 | 3607 | 2019-09-30 | 2020-04-06 | 69 | 0 | 12.6 | 0 |  | Refugio | Calhoun | Tier 4 |  |  |  | 8410, 8800 | Y | N |  |  | 13721 | 6004
6387C | Greenville Arera System Enhancements |  |  |  |  | Planned |  | RYBRN | Alfonso Galindo agalindo@epeconsulting.co 512-886-2139 |  | 2019-10-01 | 2019-05-01 | 138 | 5 | 0 | 0 |  | Hunt | Hunt | Tier 3 | 2015-12-15 | 2016-02-15 |  |  | Y | N |  | 0 | 47079 | 6387
7160 | Jackie Howard: Create Interconnection for Mesteno WF | Create interconnection for Mesteno windfarm by interconnecting the the Mesteno gen-tie line permanently to the last ETT transmission line deadend structure on the existing Del Sol - Jackie Howard line. Windfarm owner will own an interconnecting station named "Charlie Egner". |  | Del Sol | Jackie Howard | In-Service | 924 - 1102 | ETT | Kenneth 'Rich' Haley dnlyons@aep.com 918-599-2698 | 3701 | 2019-10-01 | 2019-10-29 | 345 | 0 | 0 | 0 |  | Starr | Starr | Tier 4 |  |  |  | 80368, 80355, 162101, 161553, 162104 | Y | N |  |  | 15001 | 7160
48533 |  | New 138kV Substation with BPUB system. | [5 empty] | BPUB | Javier Martinez jamartinez@brownsville-pub.com 956-083-6530 |  | 2019-10-04 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 59550, 59300, 59480 | Y |  |  | 0 | 48534 | 48533
6342 | Cross Plains to Santa Anna T 69 kV line: Rebuild 69 kV line | Rehab Cross Plains to Santa Anna Tap 69 kV line | IN SERVICE | Cross Plains | Santa Anna Tap | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2719 | 2019-10-15 | 2019-10-15 | 69 | 0 | 14.72 | 0 |  | Callahan | Coleman | Tier 4 |  |  |  | 6352, 6356, 6357 | Y | N |  |  | 14086 | 6342
6344 | Harriett to Miles 69 kV line: Rebuild 69 kV line | Rehab Harriett to Miles 69 kV line | IN SERVICE | Harriett | Miles | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2713 | 2019-10-15 | 2019-10-15 | 69 | 0 | 5.71 | 0 |  | Tom Green | Runnels | Tier 4 |  |  |  | 6410, 6412 | Y | N |  |  | 14088 | 6344
5954 | Gillrina: Build new distribution station | Gillrina: Build new distribution station for STEC load |  | Banquette | Stadium | In-Service | 805 - 0990 | AEP TCC/STEC | Bill Roberts bcogan@aep.com 918-599-2857 | 3594 | 2019-10-19 | 2019-08-09 | 69 | 0 | 0 | 0 | 0,14.4 | Nueces |  | Tier 4 |  |  |  | 8031, 8889 | Y | Y |  | 0 | 51808 | 5954
6834C | IH20 STATCOM RPG | Install fourth 20 MVAR MSC at Collie Capacitor Station (38035). |  | Collie Capacitor Station (38035) | Collie Capacitor Station (38035) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-10-20 |  | 138 | 0 | 0 | 0 | 0,20 | Reeves | Reeves | Tier 3 | 2017-10-10 | 2017-12-06 |  | 38035 | Y |  |  | 0 | 46208 | 6834
6082 | Basin: Build 138 kV station | Construct new 138 kV box bay on the Solstice to Permian Basin 138 kV line | IN SERVICE | Basin |  | In-Service | 860 - 1038 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2696 | 2019-10-23 | 2019-10-23 | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60415, 60392, 60397 | Y | N |  |  | 13806 | 6082
48746 | Cedar Canyon Substation Addition | Construct a new substation named Cedar Canyon off the Bakersfield to Schneeman Draw transmission line to support a generation interconnection request (19INR0038). |  | Bakersfield | Schneeman Draw | In-Service |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1019501 | 2019-10-30 |  | 345 | 0 | 0 | 0 |  | Crockett | Pecos | Tier 4 |  |  |  | 76015, 7053, 76002 | Y |  |  | 0 | 48747 | 48746
6773 | Callicaotte: Add New Distribution Station | Add New Callicaotte Distribution Station |  | Lon Hill | Haisley | In-Service | 880 - 1058 | AEP TCC | Thomas Reynolds bcogan@aep.com 918-599-2857 | 3667 | 2019-10-30 | 2019-11-10 | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8027, 8452, 8920 | Y | N |  | 0 | 51797 | 6773
6823 | Goddard: Contruct a new 345 kV station | Interconnect Karankawa I Wind Farm at Goddard. Construct a three breaker ring in breaker and half configuration expandable to four rungs |  | Goddard |  | In-Service | 960 - 1138 | AEP TCC | Teresa Trotman dnlyons@aep.com 918-599-2698 | 3718 | 2019-10-30 | 2019-10-18 | 345 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 8606, 88606, 88607, 5725, 8455 | Y | N |  |  | 14624 | 6823
6067 | Belknap to Rainey Crk 69 kV line: Rebld 69 kV line | Rehab Belknap to Rainey Creek 69 kV line | IN SERVICE | Belknap | Rainey Creek | In-Service | 786 - 0971 | AEP TNC | Jeremy Brazeal mlforcum@aep.com 918-599-2674 | 2675 | 2019-10-30 | 2019-10-30 | 69 | 0 | 8.33 | 0 |  | Jones | Taylor | Tier 4 |  |  |  | 6215, 6220, 6221, 60409 | Y | N |  |  | 13788 | 6067
43284B | Baytown Area Upgrades | Upgrade equipment at EXXON substation to increase thermal ratings on Ckt.66 EXXON to Baytown |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-10-30 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40170, 40570 | Y |  |  | Overall Cost for 2018 Projects included in project 6585A | 56062 | 43284
6667 | Stewart and West Galveston 5MVAR Reactors | Remove existing 10MVAR reactor at Stewart 138kV substation and re-install 5MVAR reactor. Install 5MVAR reactor at West Galveston substation |  | Stewart & West Galveston |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-10-31 |  | 138 | 0 | 0 | 0 |  | Galveston |  | Tier 4 |  |  |  | 43290, 43401 | Y | N |  | 0 | 51048 | 6667
43677 | Add 138kV MASCH Branch Substation | [5 empty] | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2019-10-31 | 2019-07-01 | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 934, 901, 985 | Y | N | N/A | 0 | 43678 | 43677
6578B | Rebuild Ckt.66 Katy-Freeman-Betka-Hockley | Rebuild Ckt.66 Katy to Freeman to address clearance issues (Phase 2 of overall Katy to Hockley upgrades) |  | Katy | Freeman | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-10-31 |  | 138 | 0 | 0 | 0 |  | Harris | Waller | Tier 4 |  |  |  | 44422, 45770, 45675 | Y |  |  | 0 | 52133 | 6578
43536 | RIGBY (RIG) - New 138kV Substation | Construct service to new 138kV customer-owned RIGBY (RIG) substation. Loop through Ckt.86 Crosby to CONNOR |  | RIGBY | Crosby/CONNOR | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-10-31 | 2020-03-05 | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  | 40670, 40155, 40390, 40480, 40665, 41090, 41405 | Y | N |  | 0 | 50152 | 43536
7015 | REFUGE (REF) 345kV Substation - Generator Interconnection fo | Loop new 345kV REFUGE substation and install one generator lead for new generator interconnection to PEYTON substation (Peyton Creek Wind). Loop new 345kV REFUGE substation on Ckt.27 between DOW and STP |  | REFUGE | DOW/ STP | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-10-31 |  | 345 | 0 | 0 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 42400, 5915, 42500 | Y | N |  |  | 14837 | 7015
6113 | Coy City Tap - Sunniland 69 kV Line | Rehab Coy City Tap - Sunniland 69 kV Line |  | Coy City Tap | Sunniland | In-Service | 814 - 0998 | AEP TCC | James Nivens bcogan@aep.com 918-599-2857 | 3605 | 2019-10-31 | 2019-10-03 | 69 | 0 | 16.5 | 0 |  | Atascosa | Live Oak | Tier 4 |  |  |  | 8406, 8600 | Y | N |  |  | 13839 | 6113
5558C | Proposed Substation |  |  |  |  | Planned |  | RYBRN | Alfonso Galindo agalindo@epeconsulting.co 512-886-2139 |  | 2019-11-01 | 2019-11-01 | 138 | 0 | 0 | 0 |  | Fannin |  | Tier 4 |  |  |  | 6817, 1807 | Y | N |  |  | 13289 | 5558
5882 | Blackland - Weilande 345/138kV additional source | [6 empty] | RYBRN | Alfonso Galindo agalindo@epeconsulting.co 512-886-2139 |  | 2019-11-01 | 2020-07-01 | 138 | 0.42 | 0 | 600 |  | Hunt |  | Tier 4 |  |  |  | 6878, 6879, 2464 | Y | N |  |  | 13598 | 5882
6166 | Carbide - Greenlake: Rebuild 69 kV Line | Carbide - Greenlake: Rebuild 69 kV Line |  | Carbide | Greenlake | In-Service | 868 - 1046 | AEP TCC | Brad Duvall bcogan@aep.com 918-599-2857 | 3655 | 2019-11-02 | 2019-11-22 | 69 | 0 | 2.2 | 0 |  | Calhoun | Calhoun | Tier 4 |  |  |  | 8149, 8159 | Y | N |  |  | 13891 | 6166
5533 | Lynx: Build a 138 kV station | Construct a new 138 kV ring bus near Woodward #1 Tap on the Fort Stockton to Rio Pecos Line and terminate Woodward 1 and 2 wind farms into Lynx | IN SERVICE | Lynx |  | In-Service | 788 - 0973 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2647 | 2019-11-05 13:35 | 2019-11-05 | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 6632, 60400, 6601, 6671, 130432, 130431 | Y | N |  |  | 13261 | 5533
5275 | Esperanza Substation Addition | Add a new load serving substation (ring bus) at Esperanza. The station will be built between Boerne an Fair Oaks Ranch off T503. |  | Boerne | Fair Oaks Ranch | In-Service |  | LCRATSC/PEC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1016187 | 2019-11-11 |  | 138 | 0 | 0 | 0 |  | Kendall |  | Tier 4 |  |  |  | 7710, 5470, 7168 | Y | N |  |  | 12951 | 5275
7166 | T535 Plum - Piney Creek MLSE Upgrade | Upgrade terminal equipment at Plum and Piney Creek to achieve a planned static normal and emergency rating of 530 MVA on T535. |  | Plum | Piney Creek | In-Service | 1019371 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1019371 | 2019-11-13 |  | 138 | 0 | 0 | 0 |  | Fayette | Fayette | Tier 4 |  |  |  | 7274, 7307 | Y | N |  |  | 15007 | 7166
48320 | Add Nelson 138 kV Switch | Add Nelson 138 kV Switch |  | Andrews County South Switch | Fullerton Switch | In-Service | R8457 | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2019-11-15 |  | 138 | 0.3 | 0 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 11273, 1134, 1135 | Y |  |  | 0 | 48322 | 48320
44631 | Adds Palmas station and line to E Rio Hondo | Add 138 kV Palmas station to connect a wind farm and the 138 kV line that connects to E Rio Hondo. |  | Palmas | E Rio Hondo | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-11-15 | 2020-02-14 | 138 | 6.3 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 5760, 5764 | Y | N |  | 0 | 44632 | 44631
50573 | Add Blackbird Switch | Add Blackbird Switch for Lapetus Energy Project |  | Fullerton Switch | Shafterlake Sub | In-Service | R8460 | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2019-11-15 |  | 138 | 0 | 0 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 11284, 1272, 1284, 134441, 134443 | Y |  |  | 0 | 50576 | 50573
45408 | Add Red Lakes Switch | Add Red Lakes Switch |  | Red Lakes Switch | Red Lakes Switch | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8461 | 2019-11-15 23:00 |  | 138 | 0 | 0 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 11293, 1292, 11292, 134093 | Y |  |  | 0 | 45410 | 45408
45579 | Hayter: Build 138 kV temporary tap | Build new Hayter 69 kV temporary tap on the Alamito Creek to Solstice 138 kV line | IN SERVICE | Hayter |  | In-Service | 1024 - 1202 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2787 | 2019-11-18 01:00 | 2019-11-18 | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60444, 6680, 60385 | Y | N |  | 0 | 45580 | 45579
5887A | RUSSEL 138kV Substation (ARITEK Substation Removal) | Remove ARITEK 138kV substation from CNP service |  | ARITEK | SR Bertron/CHORIN | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-11-30 | 2019-11-01 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40120, 40125, 40320, 41391 | Y | N |  |  | 13612 | 5887
6741 | Closner: Add New Distribution Station | Add New Closner Distribution Station |  | Azteca | South East Edinburg | In-Service | 883 - 1061 | AEP TCC | William Loveless bcogan@aep.com 918-599-2857 | 3670 | 2019-11-30 | 2019-11-11 | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  | 8029, 8374, 8708 | Y | N |  |  | 14534 | 6741
6123 | Turtle Creek - La Pryor 69 kV Line | Rehab Turtle Creek - La Pryor 69 kV Line |  | Turtle Creek | La Pryor | In-Service | 810 - 0995 | AEP TCC | James Nivens bcogan@aep.com 918-599-2857 | 3599 | 2019-11-30 | 2019-11-19 | 69 | 0 | 14.603 | 0 |  | Zavala | Zavala | Tier 4 |  |  |  | 8243, 8672 | Y | N |  |  | 13849 | 6123
5961 | Tardis: Build new 138 kV station | Construct new 138 kV ring bus Tardis on the Munday to Paducah 138 kV line, rebuild existing Benjamin Tap to 138 kV, terminate into Tardis, convert Benjamin to 138 kV operation and build new 138 kV line from Benjamin to Katz (BEC) | IN SERVICE | Tardis |  | In-Service | 769 - 0954 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2683 | 2019-11-30 | 2019-11-30 | 138 | 0 | 0 | 0 |  | Knox |  | Tier 2 | 2016-02-03 | 2016-05-01 | 2016-05-01 | 6320, 6117, 6135 | Y | N |  |  | 13676 | 5961
5932 | Jim Briley Substation Addition | Construct a motor operated load serving 138-kV substation off T499 between Geronimo and Seguin. | Substation name change from Strempel to Jim Briley | Seguin | Geronimo | In-Service |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017707 | 2019-11-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7695, 7228, 7604 | Y | N |  |  | 13640 | 5932
44391 | Victoria: Connect 138 kV Generator | Rupley Tap for Victoria Port Generation Interconnection |  | Victoria | Leupold | In-Service | 951 - 1129 | AEP TCC | Tommy Vannoy bcogan@aep.com 918-599-2857 | 3715 | 2019-11-30 | 2019-06-30 | 138 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  | 8174, 8172, 111363 | Y | N |  | 0 | 51798 | 44391
4706E | HO Clarke to Webster Ckt.05 | Restore Southwyck to Friendswood Tap after upgrades |  | Southwyck | Friendswood Tap | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-11-30 | 2019-12-16 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42015, 42651, 42652, 44361, 47150, 42061, 42960, 43260, 43500 | Y |  |  | 0 | 52138 | 4706
5885 | Tardis to Benjamin Tap: Rebuild 69 kV line | Construct new 138 kV ring bus Tardis on the Munday to Paducah 138 kV line, rebuild existing Benjamin Tap to 138 kV, terminate into Tardis, convert Benjamin to 138 kV operation and build new 138 kV line from Benjamin to Katz (BEC) | IN SERVICE | Benjamin | Tardis | In-Service | 769 - 0954 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2656 | 2019-11-30 | 2019-11-30 | 138 | 1.67 | 5.99 | 0 |  | Knox | Knox | Tier 2 | 2016-02-03 | 2016-05-01 | 2016-05-01 | 790, 6086, 6087, 6088, 6320, 6085, 6117, 6135, 6107 | Y | N |  |  | 13601 | 5885
6261 | Velasco Cap Bank #3 | Install capacitor bank #3 at Velasco substation (120MVAR). |  | Velasco | SURFSI | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-11-30 12:00 | 2019-06-13 | 138 | 0 | 0 | 0 | 0,120 | Brazoria | Brazoria | Tier 4 |  |  |  | 43363, 43360, 42510, 43315, 43362, 43155 | Y | N |  | 0 | 44948 | 6261
997 | Highway 32-Wimberley | Upgrade and convert the Highway 32 (7546) to Wimberley (7496) transmission line to 138-kV and 795 ACSR (220-MVA). |  | Highway 32 | Wimberley | In-Service |  | PEC | Ryan Morlino ryan.morlino@peci.com 830-868-5166 |  | 2019-12-01 | 2020-12-20 | 138 | 0 | 4 | 0 |  | Hays | Hays | Tier 4 |  |  |  | 7496, 7545, 7546 | Y | N |  |  | 8173 | 997
43129 | This adds capacitance to Rising Star |  |  | Rising Star (285) | Rising Star (285) | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2019-12-01 |  | 69 | 0 | 0 | 0 | 0,15 | Comanche | Comanche | Tier 4 |  |  |  | 285 | Y |  |  | 0 | 43130 | 43129
5558D | Proposed Substation |  |  |  |  | Planned |  | RYBRN | Alfonso Galindo agalindo@epeconsulting.co 512-886-2139 |  | 2019-12-01 | 2019-12-01 | 138 | 0 | 0 | 0 |  | Fannin |  | Tier 4 |  |  |  | 6807, 1835 | Y | N |  |  | 13288 | 5558
44397 | Continental: Rebuild 69 kV Station | Rebuild Continental 69 kV Station |  | Continental |  | In-Service | 946 - 1128 | AEP TCC | Todd Siegert dnlyons@aep.com 918-599-2698 | 3710 | 2019-12-01 | 2019-11-20 | 69 | 0 | 0 | 0 |  | Starr |  | Tier 4 |  |  |  | 8799 | Y | N |  | 0 | 44398 | 44397
48415A | TransPecos Capbank in TNMP West Texas System | Install 60 Mvar Capacitor bank at TNMP TransPecos Substation. |  | TransPecos (Bus #38377) | TransPecos (Bus #38377) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07919 | 2019-12-01 |  | 138 | 0 | 0 | 0 | 0,60 | Reeves | Reeves | Tier 4 |  |  |  | 38377 | Y |  |  | 0 | 48416 | 48415
6537 | T-283 Quanex Switch Structure - Sunnyside | Rebuild transmission line to 138-kV capable 959.6 ACSS-TW conductor due to maintenance on old 69 KV wood pole line and the future conversion to 138 KV. |  | Quanex Switch Structure | Sunnyside | In-Service |  | SBEC | James Jouett jjouett@sbec.org 979-413-7714 | WO# 17-6072 | 2019-12-01 | 2019-11-14 | 69 | 0 | 9.75 | 0 |  | Austin | Austin | Tier 4 |  |  |  | 7660, 7664 | Y | N |  |  | 14277 | 6537
6981 | Highway 36 Substation Upgrade | Upgrade the Highway 36 138-kV substation bus to a breaker and a half configuration. |  | Highway 36 |  | In-Service | 1019094 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1019094 | 2019-12-13 |  | 138 | 0 | 0 | 0 |  | Washington |  | Tier 4 |  |  |  | 7291 | Y | N |  |  | 14798 | 6981
48312 | Add Holstein Solar 345 kV POI | Add Holstein Solar 345 kV POI |  | Central Bluff 345 kV Switch | Central Bluff 345 kV Switch | In-Service | R8471 | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2019-12-15 |  | 345 | 0.2 | 0 | 0 |  | Nolan | Nolan | Tier 4 |  |  |  | 11405, 11406 | Y |  |  | 0 | 48314 | 48312
48932 | Mabank Tap - Eustace Southeast Switch 138 kV Line Section | R6098 Trinidad Switch - 138 kV Line (Mabank Tap - Eustace Southeast Switch line section) |  | Mabank Tap | Eustace Southeast | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6098 | 2019-12-15 |  | 138 | 0 | 6.7 | 0 |  | Henderson | Henderson | Tier 4 |  |  |  | 3131, 6951, 29266 | Y |  |  | 0 | 48933 | 48932
4759 | Riverton - Sand Lake 138 kV Line | Construct new 138 kV line | Construction schedule change | Riverton | Sand Lake | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8341 | 2019-12-15 |  | 138 | 25 | 0 | 0 |  | Reeves | Reeves | Tier 2 | 2016-02-01 | 2016-11-11 |  | 1011, 11097 | Y | N |  | 0 | 46055 | 4759
6276 | Northaven 138 kV Sw Sta | Rebuild the existing 138 kV Switching Station |  | Northaven Switch |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4243 | 2019-12-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 2646, 2649, 2650, 2655, 2656, 2657, 2658, 2659, 2596, 2597, 2651, 2652, 2660, 2661 | Y |  |  | 0 | 49532 | 6276
7111 | Quarry Field 138 kV Sw. Sta. | Quarry Field 138 kV Sw. Sta. |  | Quarry Field |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8412 | 2019-12-15 |  | 138 | 0 | 0 | 0 |  | Loving |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11189, 1093, 11091, 11094, 11100 | Y |  |  |  | 14946 | 7111
45533 | Palestine South - Palestine 138 kV Line | Upgrade the Palestine South - Palestine 138 kV Line to 1033 A |  | Palestine South | Palestine | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6100 | 2019-12-15 |  | 138 | 0 | 1.3 | 0 |  | Anderson | Anderson | Tier 4 |  |  |  | 3271, 3272 | Y | N |  | 0 | 45534 | 45533
48820 | Village Creek-Bowen 138 kV Tap | Village Creek-Bowen 138 kV Tap |  | Bowen Tap | Bowen | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5285 | 2019-12-15 12:00 |  | 138 | 1.2 | 1.2 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2219, 2233, 2248, 2232, 2250 | Y | N |  | 0 | 48821 | 48820
4802 | Lake Wichita Sw. Sta. Holliday 69 kV Line conversion | Convert existing 69 kV line to 138 kV operation |  | Lake Wichita Sw. Sta. | Holliday | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4009 | 2019-12-15 23:00 |  | 138 | 0 | 10.1 | 0 |  | Wichita | Archer | Tier 4 |  |  |  | 1447, 11527, 1423, 1424, 1446, 1449, 1527 | Y | N |  |  | 12408 | 4802
45493 | Rebuild Garden City Substation to Midkiff Switch 69 kV Line | Rebuild Garden City Substation to Midkiff Switch 69 kV Line |  | Garden City Substation | Midkiff Switch | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8445 | 2019-12-16 |  | 69 |  | 16 | 0 |  | Glasscock | Glasscock | Tier 4 |  |  |  | 1217, 1218, 1225, 1333, 1352, 11218, 11226 | Y |  |  | 0 | 45497 | 45493
6776 | Sherry - Brookhollow Tap 138 kV Line Upgrade | Upgrade existing line |  | SHERRY | BROOKHOLLOW TAP | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5247 | 2019-12-16 |  | 138 | 0 | 16 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1919, 2134, 2138, 2142, 2143 | Y | N |  |  | 14570 | 6776
6357 | Spence Pump to Robert Lee 69 kV line: Rebuild 69 kV line | Rehab Spence Pump to Robert Lee 69 kV line | IN SERVICE | Spence Pump | Robert Lee | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2715 | 2019-12-17 | 2019-12-17 | 69 | 0 | 8.55 | 0 |  | Coke | Coke | Tier 4 |  |  |  | 6420, 6421 | Y | N |  |  | 14101 | 6357
3776 | Big Lake to Powell Field Junction Tap: Rebuild 69 kV line | Rebuild Big Lake to Powell Field Junction Tap 69 kV line | IN SERVICE | Big Lake | Powell Field Junction Tap | In-Service | 667 - 0836 | AEP TNC | Michael Richardson mlforcum@aep.com 918-599-2674 | 2593 | 2019-12-17 | 2019-12-17 | 69 | 0 | 11.7 | 0 |  | Reagan | Crockett | Tier 4 |  |  |  | 6533, 6546, 6547, 60395 | Y | N |  |  | 11196 | 3776
7114 | Rondo 138 kV Dynamic Reactive Devices | Rondo 138 kV Dynamic Reactive Devices |  | Quarry Field | Rondo | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8454 | 2019-12-17 |  | 138 | 0 | 0 | 0 | -250250 | Loving |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11173, 11189 | Y |  |  |  | 14949 | 7114
44802 | Tinsley: Build 138 kV temporary tap | Build new Tinsley 138 kV temporary tap on the Carver to Maxwell 138 kV line | IN SERVICE | Tinsley |  | In-Service | 956 - 1134 | AEP TNC | Michael Glueck dnlyons@aep.com 918-599-2698 | 2760 | 2019-12-17 01:00 | 2019-12-17 | 138 | 0 | 0 | 0 |  | Sutton |  | Tier 4 |  |  |  | 60440, 8259, 60412, 6515 | Y | N |  | 0 | 44803 | 44802
6784 | Schumansville T1 Replacement | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Schumansville |  | In-Service |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2019-12-18 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7609 | Y |  |  |  | 14578 | 6784
7112 | Quarry Field 138 kV Capacitors | Quarry Field 138 kV Capacitors |  | Quarry Field |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8453 | 2019-12-18 |  | 138 | 0 | 0 | 0 | 0,147.2 | Loving |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11189 | Y |  |  |  | 14947 | 7112
6354 | Acme Bestwall to Quanah 69 kV line: Rebuild 69 kV line | Rehab Acme Bestwall to Quanah 69 kV line | IN SERVICE | Acme Bestwall | Quanah | In-Service | 786 - 0971 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2718 | 2019-12-18 | 2019-12-18 | 69 | 0 | 5.72 | 0 |  | Hardeman | Hardeman | Tier 4 |  |  |  | 6051, 6052 | Y | N |  |  | 14098 | 6354
6851 | Saragosa to Solstice: Rebuild 138 kV line | Build Saragosa to Solstice 138 kV line, retire existing Barrilla Junction to Saragosa 69 kV line, add new auto and capacitor bank at Saragosa. | IN SERVICE | Saragosa | Solstice | In-Service | 922 - 1100 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2736 | 2019-12-19 | 2019-12-19 | 138 | 0 | 19 | 90 | 0,7.2 | Pecos | Ward | Tier 4 |  |  |  | 60716, 6652, 6649, 6650, 60385, 6653 | Y | N |  |  | 14659 | 6851
6343 | Dressy Tap to Santa Anna Tap 69 kV line: Rebuild 69 kV line | Rehab Dressy Tap to Santa Anna Tap 69 kV line | IN SERVICE | Dressy Tap | Santa Anna Tap | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2720 | 2019-12-20 | 2019-12-20 | 69 | 0 | 13.6 | 0 |  | Callahan | Coleman | Tier 4 |  |  |  | 6352, 6356 | Y | N |  |  | 14087 | 6343
5048 | Falfurius: Upgrade | Replace DSTATCOM with SVC Plus at Falfurius station +50 & -40 MVAR capability |  | Falfurrias | Falfurrias | Under Construction | 873-1049 | ETT | Kenneth 'Rich' Haley 918-599-2664 dnlyons@aep.com | 3658 | 2019-12-20 |  | 69 | 0 | 0 | 0 | -40,50 | Brooks | Brooks | Tier 4 |  |  |  | 8625 | Y | N |  | 0 | 51790 | 5048
44818G | Fort Bend to West Columbia 138kV Conversion | Remove TEXWES customer from CNP service |  | West Columbia | TEXWES | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-29 00:06 |  | 69 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2018-10-30 | 2018-11-26 |  | 43350, 43390 | Y |  |  | 0 | 52196 | 44818
49560 | Jim Treece: Interconnect Blue Summit 3 | Interconnect Blue Summit 3 wind farm at Jim Treece 345 kV station | IN SERVICE | Jim Treece |  | In-Service | 1019 - 1197 | ETT | Michael Glueck mlforcum@aep.com 918-599-2674 | 2781 | 2019-12-30 | 2019-12-30 | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 61001 | Y |  |  | 0 | 49561 | 49560
6673A | Freeport - Bridge the Gap | Install capacitor bank #4 at Jones Creek substation (120MVAR). |  | Jones Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-30 |  | 138 | 0 | 0 | 0 | 0,120 | Brazoria |  | Tier 1 |  |  | 2017-12-12 | 42540 | Y | N |  | 0 | 56733 | 6673
4871 | Webster Breaker Addition | Install breaker at Webster 138kV substation to connect ring buses | - Delay in project schedule | Webster |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1134 | 2019-12-30 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 43505, 42651, 42970, 43082, 43500, 43507 | Y | N |  |  | 12481 | 4871
6578A | Rebuild Ckt.66 Katy-Freeman-Betka-Hockley | Rebuild Ckt.66 Freeman-Betka-Hockley to address clearance issues (Phase 1 of overall Katy to Hockley upgrades) |  | Freeman | Hockley | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45675, 45880 | Y |  |  | 0 | 52132 | 6578
17TPIT0019 | Forney - Royse 138 kV Line | Upgrade existing line |  | Forney | Royse | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4111-E | 2019-12-31 |  | 138 | 0 | 18.32 | 0 |  | Kaufman | Rockwall | Tier 4 |  |  |  | 2438, 2471, 2709, 2710, 2711, 2712 | Y | N |  |  | 11839 | 3086
4426A | Aritek to Chorin to SR Bertron Ckt. 87 Upgrades | Upgrade 138kV Ckt.87 Alexander Island to CHORIN to increase thermal ratings. (Previously known as 'Ckt.87 ARITEK to CHORIN Upgrades') |  | ARITEK | CHORIN | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 | 2019-05-13 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40120, 40320 | Y | N |  |  | 48257 | 4426
50922 | Replace failed Garden Villas C1 with 106.67 MVAR | Use removed HOC cap bank to replace failed Garden Villas cap bank. Garden Villas Cap bank will now be 106.67 MVAR |  | Garden Villas |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 |  | 138 | 0 | 0 | 0 | 0,6.67 | Harris |  | Tier 4 |  |  |  | 42680, 42681 | Y | N |  | 0 | 50923 | 50922
7004 | CNP_18TPIT7004_New_Garth_Distribution_Sub | Construct service to new 138kV Garth distribution substation. Loop through Ckt.66 Baytown to Highlands tap |  | Baytown | Highlands | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 | 2020-03-05 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 44630, 40010, 40011, 40170, 40171, 40172, 40391, 40439, 40790, 40812, 40871, 41540, 41610, 40015, 40130, 40390, 40430 | Y |  |  |  | 14825 | 7004
43462 | Northside Distribution Substation Expansion | Install third new 138/12 kV, 100 MVA distribution transformer |  | Northside | Northside | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 | 2020-01-29 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47711, 47712, 40962, 47570, 47630, 40710, 45840 | Y |  |  | 0 | 43463 | 43462
43245 | HOPSON - New 138kV Substation | Construct service to new 138kV HOPSON customer-owned substation. Loop through Ckt.84 WARVUE to Cedar Bayou |  | HOPSON | WARVUE/Cedar Bayou | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 | 2019-11-18 | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  | 41690, 40012, 40015, 40070, 40220, 40300, 40320, 40764, 40500, 40775, 41391, 41450, 41700 | Y |  |  | 0 | 56317 | 43245
6260 | Install 3rd 120MVAR capacitor bank at Jones Creek substation | Install capacitor bank #3 at Jones Creek substation (120MVAR). |  | Jones Creek | Velasco | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 | 2019-12-04 | 138 | 0 | 0 | 0 | 0,120 | Brazoria | Brazoria | Tier 4 |  |  |  | 42543, 40000, 40850, 40900, 42540, 43360, 46100 | Y | N |  | 0 | 56344 | 6260
50458 | Line rebuild from 336 to 959 conductor and Scurry station up |  |  |  |  | Planned |  | RYBRN | Alfonso Galindo agalindo@epeconsulting.co 512-886-2139 | 19T03 | 2019-12-31 |  | 138 | 0 | 3.75 | 0 |  | Kaufman | Kaufman | Tier 4 |  |  |  | 6896, 6908 | Y |  |  | 0 | 50817 | 50458
6754 | Bunsen: Add Breakers | Add Breakers at Bunsen 138kV Substation for customer Interconnect. Build 0.75 mile of 138kV Line between Bunsen and Customer. |  | Bunsen |  | In-Service | 902 - 1080 | AEP TCC | James Weaver bcogan@aep.com 918-599-2857 | 3686 | 2019-12-31 | 2019-12-31 | 138 | 0.8 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8459, 88614, 88615 | Y | N |  |  | 14547 | 6754
5836 | Rebuild Shady Grove to Advance | Rebuild Shady Grove (Bus #515) to Advance (Bus #518) |  |  |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 16017 | 2019-12-31 |  | 69 | 0 | 11.34 | 0 |  | Parker | Parker | Tier 4 |  |  |  | 515, 518 | Y |  |  |  | 13578 | 5836
6002 | Gregory - Rincon 69 kV line | Rehab Gregory - Rincon 69 kV line |  | Gregory | Rincon | Planned | 833 - 1017 | AEP TCC | Joseph Page dnlyons@aep.com 918-599-2698 | 3634 | 2019-12-31 |  | 69 | 0 | 4.34 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 8416, 8421 | Y | N |  |  | 13719 | 6002
43458 | Heights Cap Bank #1 | Relocate Harrisburg cap bank #1 to Heights substation and reduce size to 7.2 MVAR |  | Heights |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 |  | 69 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 40800, 47680 | Y | N |  | 0 | 43459 | 43458
7101 | Wink Sw. Sta. - No Trees Sw. Sta. 138 kV Line | Rebuild Wink Sw. Sta. - No Trees Sw. Sta. 138 kV Line |  | Wink | No Trees | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8406 | 2019-12-31 |  | 138 | 0 | 27.8 | 0 |  | Winkler | Winkler | Tier 3 |  | 2018-09-06 |  | 1074, 1147, 11135, 131853 | Y |  |  |  | 14935 | 7101
5979 | Carver: Build new 138 kV station | Construct a new 138 kV ring bus station to replace the 138 kV portion of the Sonora 138/69 kV station | IN SERVICE | Carver |  | In-Service | 838 - 1022 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2678 | 2019-12-31 | 2019-12-31 | 138 | 0 | 0 | 90 |  | Sutton |  | Tier 4 |  |  |  | 60412, 60433, 6500, 6513, 6515, 6562, 60440 | Y | N |  |  | 13694 | 5979
4426B | Aritek to Chorin to SR Bertron Ckt. 87 Upgrades | Upgrade 138kV Ckt.87 Alexander Island to SR Bertron to increase thermal ratings. |  | Alexander Island | SR Bertron | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 | 2019-05-09 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41391, 41400 | Y | N |  | Cost included in project 4426A | 48256 | 4426
45021 | Pershing: Build 138 kV temporary tap | Build new Pershing 138 kV temporary tap on the Abilene Northwest to Oak Creek 138 kV line | IN SERVICE | Pershing |  | In-Service | 978 - 1156 | AEP TNC | Michael Glueck 918-599-2674 | 2763 | 2019-12-31 01:00 | 2019-12-31 | 138 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  | 9460, 60724, 6229, 6335 | Y | N |  | 0 | 45022 | 45021
44385 | Victoria: Connect 138 kV Generator | Connect 138 kV Victoria City generator tie line into new breakers at Victoria. |  | Victoria | Leupold | In-Service | 951 - 1129 | AEP TCC | Tommy Vannoy bcogan@aep.com 918-599-2857 | 3715 | 2020-01-01 | 2019-12-03 | 138 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  | 8174, 8172, 111363 | Y | N |  | 0 | 44386 | 44385
7172 | Refugio: Install 138/69 kV Auto | Install 90 MVA 138/69 kV autotransformer and a 138 kV breaker |  | Refugio |  | In-Service | 100-0100 | AEP TCC | Bill Roberts bcogan@aep.com 918-599-2857 | 2021 | 2020-01-01 | 2019-10-24 | 138 | 0 | 0 | 90 |  | Refugio |  | Tier 3 | 2017-03-31 | 2017-04-21 | 2017-06-01 | 8412, 89634, 8410 | Y | N |  |  | 15013 | 7172
50674 | Chocolate Bayou: Upgrade Distribution Transformer | Chocolate Bayou: Upgrade Distribution Transformer |  | Chocolate Bayou |  | Planned |  | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 |  | 2020-01-01 |  | 138 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  | 80064 | Y | N |  | 0 | 50675 | 50674
7036 | Forest Grove Sw. Sta. to Eustace SE 138 kV line section | Rebuild the Forest Grove Sw. Sta. to Eustace SE 138 kV line section |  | Forest Grove Sw. Sta. | Eustace SE | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6014 | 2020-01-01 |  | 138 | 0 | 4.3 | 0 |  | Henderson | Henderson | Tier 4 |  |  |  | 3131, 6951 | Y | N |  |  | 14858 | 7036
6785 | Leakey Substation Upgrade | Replace 69/25 kV and 69/12.5 kV Power Transformers with dual-rated 138-69/25-12.5 kV Power Transformers and add one 138 kV Circuit Breaker to be operated at 69 kV. | Accelerating Schedule | Leakey |  | Planned |  | BANDERA | Tyler Pansing t.pansing@banderaelectric.com 866-226-3372 Ext 6078 | 353985 | 2020-01-08 |  | 69 | 0 | 0 | 0 |  | Bandera |  | Tier 4 |  |  |  | 7426 | Y | N |  |  | 14579 | 6785
45053 | Schottky 69 kV Hard Tap | Schottky 69 kV Hard Tap |  | Sunniland | Three Rivers | Under Construction | 970 - 1148 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3728 | 2020-01-16 | 2019-08-16 | 69 | 0 | 0 | 0 |  | Live Oak | Live Oak | Tier 4 |  |  |  | 88507, 8400, 8406 | Y | N |  | 0 | 51801 | 45053
6985 | Gonzales - Harwood Transmission Line Overhaul | Overhaul and upgrade the 69-kV Gonzales - Harwood transmission line supporting circuit T542 with 138-kV capable structures, 795 ASCR Drake, and OPGW static. The planned T542 circuit rating will be (MVA): Rate A=28, Rate B=28, Rate C=28. |  | Luling | Hochheim | Planned | 1018965 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018965 | 2020-01-24 |  | 69 | 0 | 10 | 0 |  | Gonzales | Gonzales | Tier 4 |  |  |  | 7223, 78577 | Y | N |  |  | 14802 | 6985
5195 | Rio Pecos: Build 138 kV terminal | Interconnect Pecos solar farm at Rio Pecos | IN SERVICE | Rio Pecos |  | In-Service | 758 - 0942 | AEP TNC | Randy Weaver mlforcum@aep.com 918-599-2674 | 2633 | 2020-01-24 | 2020-01-24 | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 6601 | Y | N |  |  | 12854 | 5195
43452A | Angleton to MONSAN Ckt.04 Upgrades | Upgrade Ckt.04 PETSON to MONSAN to increase thermal limits |  | Petson | Monsan | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-01-29 | 2020-01-21 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42940, 43070 | Y | N |  | Cost included in 43452C | 51007 | 43452
43452B | Angleton to MONSAN Ckt.04 Upgrades | Upgrade Ckt.04 Liverpool to PETSON to increase thermal limits |  | Liverpool | Petson | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-01-30 00:01 | 2020-01-21 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42870, 43070 | Y | N |  | Cost included in 43452C | 51008 | 43452
6255A | Rebuild BEVO to Brundage to Big Wells 69 kV lines. | Rebuild 69 kV line with 795 ACSR on 138 kV and double circuit capable structures 2015- NERC assessment |  | Brundage | Big Wells | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-01-31 | 2020-02-14 | 69 | 0 | 11.05 | 0 |  | Dimmit | Dimmit | Tier 4 |  |  |  | 5868, 5870 | Y | N |  | 0 | 45066 | 6255
50944 | Move Southwyck distribution 14.4MVAR to ckt 05 | Distribution 14.4 MVAR C1 moves from ckt 26 to ckt 05 |  |  |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-01-31 | 2020-03-31 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 43260, 43261 | Y |  |  | 0 | 50945 | 50944
43284E | Baytown Area Upgrades | Upgrade Ckt.21 DIABOX to MOMENT to increase thermal ratings |  | DIABOX | MOMENT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-01-31 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40480, 41090 | Y |  |  | 0 | 56063 | 43284
43452C | Angleton to MONSAN Ckt.04 Upgrades | Upgrade Ckt.04 Angleton to Liverpool to increase thermal limits |  | Angleton | Liverpool | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-01-31 00:02 | 2020-01-21 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42110, 42870, 44561 | Y | N |  | 0 | 51009 | 43452
48750 | Gibbs: Construct New 138 kV Station | Gibbs: Construct New 138 kV Station |  | McCampbell | Portland | In-Service | 846 - 1030 | AEP TCC | Thomas Reynolds bcogan@aep.com 918-599-2857 | 3642 | 2020-02-01 | 2019-10-30 | 138 | 0 | 0 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  | 8173, 88790, 8414, 80470 | Y | N |  | 0 | 48751 | 48750
4519 | Heartland: Build 69 kV station | Construct new 69 kV ring bus between MCEC Brady and Katemcy | IN SERVICE | Heartland |  | In-Service | 637 - 0806 | AEP TNC | Thomas Reynolds mlforcum@aep.com 918-599-2674 | 2609 | 2020-02-07 | 2020-02-07 | 69 | 0 | 0 | 0 |  | McCulloch |  | Tier 2 | 2014-01-23 | 2014-11-04 | 2014-11-17 | 60386 | Y | N |  |  | 12091 | 4519
4530 | Heartland to South Brady Tap: Rebuild existing & build new | Construct a new 69 kV line from Heartland to South Brady Tap and rebuild the existing line from Heartland to South Brady Tap | IN SERVICE | Heartland | South Brady Tap | In-Service | 637 - 0806 | AEP TNC | Thomas Reynolds mlforcum@aep.com 918-599-2674 | 2610 | 2020-02-07 | 2020-02-07 | 69 | 1.11 | 1.11 | 0 |  | McCulloch | McCulloch | Tier 2 | 2014-01-23 | 2014-11-04 | 2014-11-17 | 6379, 60386, 6378, 6381, 6406 | Y | N |  |  | 12105 | 4530
5956 | Young: Build new distribution station | Young: Build new distribution station |  | Polk Avenue | Pharr | In-Service | 804 - 0989 | AEP TCC | Thomas Reynolds bcogan@aep.com 918-599-2857 | 3593 | 2020-02-08 | 2020-02-18 | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  | 8030, 8372, 8373 | Y | N |  |  | 13669 | 5956
6077 | Bronte Atlantic to Miles 69 kV line: Rebuild 69 kV line | Rehab Bronte Atlantic to Miles 69 kV line | IN SERVICE | Bronte Atlantic | Miles | In-Service | 786 - 0971 | AEP TNC | Brian Oyster mlforcum@aep.com 918-599-2674 | 2691 | 2020-02-17 | 2020-02-17 | 69 | 0 | 17.44 | 0 |  | Coke | Runnels | Tier 4 |  |  |  | 6410, 6418 | Y | N |  |  | 13800 | 6077
7018 | Kleimann Substation Addition | Construct a 138-kV capable breakered substation, in a ring bus arrangement, between Columbus and Stafford Hill on circuit T544. The substation will provide transmission service to AEP load that will be transferred from Columbus Substation. Columbus Substation will be retired. ( Initially modelled at 69-kV until the completion of Glidden area upgrades project) |  | Columbus | Stafford Hill | Planned | 1018910 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018910 | 2020-02-26 |  | 138 | 0 | 0 | 0 |  | Colorado | Colorado | Tier 4 |  |  |  | 78111, 78115, 78107, 78520 | Y | N |  | 0 | 45505 | 7018
44381 | Causeway: Add 2nd Distribution Bank | Causeway: Add 2nd Distribution Bank |  | Causeway |  | Planned | 945 - 1123 | AEP TCC | James Weaver bcogan@aep.com 918-599-2857 | 3709 | 2020-02-28 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8744 | Y | N |  | 0 | 44382 | 44381
6683 | Del Sol-Cabezon: Create Permanent Interconnection for Rio Br | Construct 2nd circuit on Cenizo-Del Sol 345 kV line from the Rio Bravo Windfarm Collector Station (Cabezon) to Del Sol. |  | Del Sol | Cabezon | In-Service | 896 - 1074 | ETT | Kenneth Haley bcogan@aep.com 918-599-2857 | 3680 | 2020-02-28 | 2019-12-17 | 345 | 26.5 | 0 | 0 |  | Starr | Starr | Tier 4 |  |  |  | 80380, 80381, 80307, 80355, 80225, 161851, 161855 | Y | N |  |  | 14453 | 6683
6111 | Carancahua - Point Comfort 69 kV Line | Rehab Carancahua - Point Comfort 69 kV Line |  | Carancahua | Point Comfort | In-Service | 817 - 1001 | AEP TCC | Joseph Page bcogan@aep.com 918-599-2857 | 3613 | 2020-02-28 | 2019-12-13 | 69 | 0 | 9.18 | 0 |  | Jackson | Calhoun | Tier 4 |  |  |  | 8132, 8555 | Y | N |  |  | 13837 | 6111
6673C | Freeport - Bridge the Gap | Loop Ckt.27 STP-DOW into Jones Creek to create new Ckt.27 Jones Creek to STP |  | Jones Creek | STP | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-02-28 00:03 |  | 345 | 0.18 | 0 | 0 |  | Brazoria | Matagorda | Tier 1 |  |  | 2017-12-12 | 42400, 42500, 42530 | Y | N |  | 0 | 56736 | 6673
6673G | Freeport - Bridge the Gap | Install 7-Ohm in-series reactors at Jones Creek substation on Ckts.18 & 27 Jones Creek to STP |  | Jones Creek | STP | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-02-28 00:05 |  | 345 | 0 | 0 | 0 |  | Brazoria | Matagorda | Tier 1 |  |  | 2017-12-12 | 47531, 47532, 5915, 42400, 42530 | Y | N |  | 0 | 56738 | 6673
6673D | Freeport - Bridge the Gap | Loop Ckt.27 STP-DOW into Jones Creek to create new Ckt.27 Jones Creek to DOW |  | Jones Creek | DOW | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-02-28 00:06 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 1 |  |  | 2017-12-12 | 42400, 42500, 47531, 5915, 42530 | Y | N |  | Cost included in Phase C. | 56732 | 6673
45116 | TNMP Elm First Substation | New Substation - Elm First |  | IH20 (Bus #38045) | Reeves Tap (Bus #38114) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2020-03-01 |  | 138 | 0 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38049, 38090, 38040, 38045, 38114 | Y |  |  | 0 | 48424 | 45116
45344 | Pirate: Build 69 kV Station | Pirate: Build 69 kV Station on Beeville - Sinton Line |  | Skidmore | Sinton | In-Service | 882 - 1068 | AEP TCC | Terry Weeks bcogan@aep.com 918-599-2857 | 3669 | 2020-03-02 |  | 69 | 0 | 0 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  | 8652, 8405, 8413 | Y | N |  | 0 | 45345 | 45344
44368 | Amos Creek Substation Addition | Construct a 345-kV breakered substation, in a ring bus arrangement, between Red Creek and Bow Wood on circuit T424. The substation will provide transmission service for a generation interconnection (20INR0045) request. |  | Red Creek | Bow Wood | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1020230 | 2020-03-05 |  | 345 | 0 | 0 | 0 |  | Tom Green | McCulloch | Tier 4 |  |  |  | 7077, 6444, 76006 | Y | N |  | 0 | 44369 | 44368
43487 | Cryo to Saragosa: Build 138 kV line | Build new Cryo 138 kV station, build Cryo to Saragosa new 138 kV line, add capacitor banks at Cryo | IN SERVICE | Cryo | Saragosa | In-Service | 926 - 1104 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2739 | 2020-03-05 | 2020-03-05 | 138 | 5 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 60721, 60716 | Y | N |  | 0 | 43488 | 43487
43485 | Cryo: Build 138 kV station | Build new Cryo 138 kV station, build Cryo to Saragosa new 138 kV line, add capacitor banks at Cryo | IN SERVICE | Cryo |  | In-Service | 926 - 1104 | AEP TNC | Tom Reynolds mlforcum@aep.com 918-599-2674 | 2740 | 2020-03-05 | 2020-03-05 | 138 | 0 | 0 | 0 | 0,28.8 | Reeves |  | Tier 4 |  |  |  | 60721, 60716 | Y | N |  | 0 | 43486 | 43485
51240 | Add Wolf to Moss 138 kV Line High Temperature Upgrade | Wolf to Moss 138 kV Line High Temperature Upgrade |  | Wolf | Moss | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8494 | 2020-03-15 |  | 138 | 0 | 34.5 | 0 |  | Ward | Ector | Tier 3 | 2019-07-12 | 2019-09-06 |  | 1019, 1292 | Y |  |  | 0 | 51242 | 51240
7159 | Ajo-Stella: Create Permanent Interconnection for Stella WF | Convert Stella Windfarm temporary tap interconnection to a permanent interconnection. ETT will construct an extension of the gen tie-line by adding a second circuit on the Ajo-Zorillo line, therefore creating a dedicated circuit terminating at the Ajo station. |  | Ajo | Stella | In-Service | 894 - 1072 | ETT | Teresa Trotman bcogan@aep.com 918-599-2857 | 3678 | 2020-03-17 | 2020-03-03 | 345 | 0 | 7.85 | 0 |  | Kenedy | Kenedy | Tier 4 |  |  |  | 80070, 80071, 80072, 80076, 161591 | Y | N |  |  | 15000 | 7159
3894 | Fowlerton 345 station and 345/138 autotransformer | Add 345 kV bus and autotransformer |  | Fowlerton |  | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-03-20 12:00 | 2020-04-09 | 345 | 0 | 0 | 675 |  | McMullen |  | Tier 4 |  |  |  | 5706, 5709, 5901, 80219, 5705 | Y | N |  | 2017 RTP moved project up to 2019. Still studying size needed and possible relocation of existing autotransformer. | 44403 | 3894
6075 | Veribest T to Harriett 69 kV line: Rebuild 69 kV line | Rehab Veribest Tap to Harriett CVEC REA 69 kV line | IN SERVICE | Veribest Tap | Harriett CVEC REA | In-Service | 786 - 0971 | AEP TNC | Darren O'Hare mlforcum@aep.com 918-599-2674 | 2690 | 2020-03-24 | 2020-03-24 | 69 | 0 | 8.4 | 0 |  | Tom Green | Tom Green | Tier 4 |  |  |  | 6409, 6412 | Y | N |  |  | 13797 | 6075
44379 | Bonilla: Build new 345 kV Station | New Bonilla 345 kV Station to interconnect Raymond Wind |  | Bonilla |  | In-Service | 944 - 1122 | AEP TCC | Adam Wells bcogan@aep.com 918-599-2857 | 3708 | 2020-03-25 | 2020-01-27 | 345 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8573, 88573, 8318, 8383 | Y | N |  | 0 | 44380 | 44379
7164 | T195 Granite Mountain - Marble Falls MLSE Upgrade | Upgrade terminal equipment at Granite Mountain and Marble Falls to achieve a planned static normal and emergency rating of 221 MVA on T195. |  | Granite Mountain | Marble Falls | Planned | 1019369 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1019369 | 2020-03-26 |  | 138 | 0 | 0 | 0 |  | Burnet | Burnet | Tier 4 |  |  |  | 7348, 7474 | Y | N |  |  | 15005 | 7164
6711 | Castle Mountain Substation Addition | Construct a new substation named Castle Mountain off the LCRA Crane to Rio Pecos (T451) transmission line to support a generation interconnection request (18INR0039). |  | LCRA Crane | Rio Pecos | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018758 | 2020-03-27 |  | 138 | 0 | 0 | 0 |  | Crane | Crockett | Tier 4 |  |  |  | 76025, 60014, 76615 | Y | N |  |  | 14494 | 6711
44852 | Kelvin: Build new 138 kV station | Interconnect Chalupa wind farm on the La Palma to Rio Hondo 138 kV line |  | La Palma | Rio Hondo | In-Service | 965 - 1143 | AEP TCC | Joseph Page bcogan@aep.com 918-599-2857 | 3723 | 2020-04-01 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8640, 88640, 8314, 8319 | Y | N |  | 0 | 44853 | 44852
6783 | Utopia-Tarpley Re-Termination | Re-Termination of existing T281 Transmission Line, related to reconfiguration of Utopia and Tarpley Substations. | Change in schedule | Utopia | Tarpley | In-Service |  | BANDERA | Tyler Pansing t.pansing@banderaelectric.com 866-226-3372 Ext 6078 | 353985 | 2020-04-08 |  | 69 | 0 | 0.25 | 0 |  | Bandera | Bandera | Tier 4 |  |  |  | 7428, 7440 | Y | N |  |  | 14577 | 6783
6973 | Welcome Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement,at Welcome Substation. |  | Welcome |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018929 | 2020-04-13 |  | 138 | 0 | 0 | 0 |  | Austin |  | Tier 4 |  |  |  | 7577 | Y | N |  |  | 14790 | 6973
5914 | Crosswinds Substation Addition | LCRA TSC will construct a new three breaker ring bus substation to provide transmission service to PEC's planned distribution substation facility. |  | Turnersville | Goforth | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017349 | 2020-04-13 |  | 138 | 0 | 0 | 0 |  | Hays |  | Tier 4 |  |  |  | 7503, 7500, 7501 | Y | N |  |  | 13622 | 5914
4065 | Add Graham Road Substation |  |  | BTU South | BTU Greens Prairie | Planned |  | COCS | Tony Mickalsky tmichalsky@cstx.gov 979-764-3438 |  | 2020-04-15 10:00 |  | 138 | 0 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32007, 32878, 32880 | Y |  |  |  | 11590 | 4065
6347 | Ballinger to Paint Rock 69 kV line: Rebuild 69 kV line | Rehab Ballinger to Paint Rock 69 kV line | IN SERVICE | Ballinger | Paint Rock | In-Service | 786 - 0971 | AEP TNC | Brian Oyster mlforcum@aep.com 918-599-2674 | 2708 | 2020-04-20 | 2020-04-20 | 69 | 0 | 14.6 | 0 |  | Runnels | Concho | Tier 4 |  |  |  | 6338, 6369 | Y | N |  |  | 14091 | 6347
6353 | Kirkland to Acme Best Wall 69 kV line: Rebuild 69 kV line | Rehab Kirkland to Acme Best Wall 69 kV line | IN SERVICE | Kirkland | Acme Best Wall | Planned | 786 - 0971 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2717 | 2020-04-22 | 2020-04-22 | 69 | 0 | 14.6 | 0 |  | Childress | Hardeman | Tier 4 |  |  |  | 6052, 6053 | Y | N |  |  | 14097 | 6353
6983 | Fayetteville - Winchester Transmission Line Upgrade | Upgrade the 138-kV Fayetteville - Winchester transmission line supporting circuit T165 to single 1433 ACSS/TW conductor and OPGW static. The planned T165 circuit rating is (MVA): Rate A=470, Rate B=470, Rate C=470. |  | Fayetteville | Winchester | Planned | 1018933 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018933 | 2020-04-24 |  | 138 | 0 | 18.8 | 0 |  | Fayette | Fayette | Tier 4 |  |  |  | 7286, 7306 | Y | N |  |  | 14800 | 6983
44812 | Coulomb: Build new 345 kV station | Interconnect Vera wind farm on the Clear Crossing to Edith Clarke 345 kV line | Updated Contact & Cost | Coulomb |  | Planned | 933 - 1111 | ETT | Adam Wells mlforcum@aep.com 918-599-2674 | 2744 | 2020-04-27 01:00 |  | 345 | 4 | 0 | 0 |  | Knox |  | Tier 4 |  |  |  | 60722, 60500, 60702 | Y | N |  | 0 | 44813 | 44812
45415 | Coulomb to Vera: Build new 345 kV line | Interconnect Vera wind farm on the Clear Crossing to Edith Clarke 345 kV line | Updated Cost | Coulomb | Vera | Planned | 933 - 1111 | ETT | Eric Blind mlforcum@aep.com 918-599-2674 | 2745 | 2020-04-27 01:00 |  | 345 | 4 | 0 | 0 |  | Knox | Knox | Tier 4 |  |  |  | 143015, 60722 | Y | N |  | 0 | 45416 | 45415
6065 | Abilene Northwest to Anson 69 kV line: Rebuild 69 kV line | Rehab Abilene Northwest to Anson 69 kV line | IN SERVICE | Abilene Northwest | Anson | In-Service | 786 - 0971 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2673 | 2020-04-29 | 2020-04-29 | 69 | 0 | 14 | 0 |  | Taylor | Jones | Tier 4 |  |  |  | 6224, 6236 | Y | N |  |  | 13785 | 6065
5946 | Winchester Autotransformer Additions | Add two 672 MVA autotransformers at Winchester Substation. Cut the new 345-kV bus at Winchester into an existing Austin Energy owned 345-kV transmission line from FPP to Lost Pines. |  | FPP #1 | Lost Pines | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017413 | 2020-04-29 |  | 345 | 0 | 0 | 1344 |  | Fayette | Bastrop | Tier 3 | 2017-02-01 | 2017-03-20 |  | 77306, 77308, 77309, 7056, 9041, 7306 | Y | N |  |  | 13657 | 5946
52167A | El Dorado 10.8 MVar Cap Bank | Remove existing Harrisburg 10.8 MVAr cap bank CB2 |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-04-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40800 | Y | N |  | 0 | 55384 | 52167
4464A | Comal to Loop337 to GPI to Marion switchyard Transmission Up | Alter CTs to 2000:5 to remove CTs as MLSE elements. Utilize dynamic switch rating for Winter loading. | Switches may be dynamically rated during Winter peak conditions. | Comal | GPI Switchyard | In-Service |  | NBU | Gregory Thomas gthomas@nbutexas.com 830-608-8953 |  | 2020-04-30 |  | 138 | 0 | 0 | 0 |  | Comal | Comal | Tier 4 |  |  |  | 7176, 7456, 7459 | Y | N |  |  | 12380 | 4464
4464B | Comal to Loop337 to GPI to Marion switchyard Transmission Up | Upgrade/Replace underrated switches to 3000 Amp Switches. Replace and increase fault interrupting rating of breakers 430, 440, 3370, 3380, 5680, 5690, 5700, 2970, 5870 to 63kA. Replace and upgrade CS2965 and CS2975 to 3000 Amp 40kA. Replace and upgrade CS5395 and CS5405 to 40kA. | Switches may be dynamically rated during Winter peak conditions. | Comal | Marion | Planned |  | NBU | Gregory Thomas gthomas@nbutexas.com 830-608-8953 |  | 2020-04-30 |  | 138 | 0 | 0 | 0 |  | Comal | Comal | Tier 4 |  |  |  | 7176, 7178, 7456, 7459 | Y | N |  |  | 12381 | 4464
51746 | LagoVista Capacitor Switcher Upgrade | Upgrade interrupting capability of capacitor switcher from 8 kA to 40 kA and replace electromechanical relay panel with digital relay panel |  | Lago Vista |  | Planned |  | PEC | Ryan Morlino ryan.morlino@peci.com 830-868-5166 |  | 2020-05-01 |  | 138 | 0 | 0 | 0 |  | Travis |  | Tier 4 |  |  |  | 7352 | Y | N |  | 0 | 51753 | 51746
51748 | PEC Leander BusUpgrade | Upgrade the Leander bus from operate/transfer to breaker-and-a-half |  | Alamito Creek | Solstice | Planned |  | PEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2020-05-01 |  | 138 | 0 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 7525 | Y | N |  | 0 | 51754 | 51748
6074 | Concho to Veribest Tap 69 kV line: Rebuild 69 kV line | Rehab Concho to Veribest Tap 69 kV line | IN SERVICE | Concho | Veribest Tap | In-Service | 786 - 0971 | AEP TNC | Darren O'Hare mlforcum@aep.com 918-599-2674 | 2689 | 2020-05-04 | 2020-05-04 | 69 | 0 | 1.86 | 0 |  | Tom Green | Tom Green | Tier 4 |  |  |  | 6409, 6450 | Y | N |  |  | 13796 | 6074
5429A | Phase 3 of the conversion to 138kV | Add a new 138kV line from the new Locust station to Woodrow to Spencer Interchange via a three way tie at Woodrow. The section going from the 3way tie to Spencer Int. was added in phase 2. |  | Locust | Spencer Int. | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2020-05-05 | 2017-07-01 | 138 | 1.917 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 924, 99999, 921, 982 | Y | N | N/A | 0 | 45742 | 5429
5429C | Phase 3 of the conversion to 138kV | The three way tie will be retired and 138kV locust will tie directly to 138kV Woodrow. The Spencer Int. to the 3way tie will be reconfigured to terminate at the new 138kV Brinker substation. |  | Locust | Spencer Int. | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2020-05-05 | 2019-03-11 | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 99999, 921, 924, 982 | Y | N | N/A | 0 | 45744 | 5429
5428D | Phase 2 of the conversion to 138kV | Line will be reconfigured to through a 3way tie |  | Woodrow | Spencer Int | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2020-05-05 | 2017-07-01 | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 921, 982 | Y | N | N/A |  | 13116 | 5428
47444 | Divide Circuit Breaker Addition | Provide transmission service to a generator and add a 345-kV bay and circuit breaker at Divide Substation (19INR0156). |  | Divide | Divide | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2020-05-06 |  | 345 | 0 | 0 | 0 |  | Coke | Coke | Tier 4 |  |  |  | 76090 | Y | N |  | 0 | 47445 | 47444
6709 | Heines Substation Addition | Construct a new load-serving substation named Heines off the Airline to Naval Base (T476) transmission line. | [5 empty] | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018754 | 2020-05-07 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 78560, 8487, 8560 | Y |  |  | 0 | 45470 | 6709
6787 | Utopia Susbtation Upgrade | Add two 138 kV Circuit Breakers to Line Terminals to be operated at 69 kV. | Accelerating Schedule | Utopia |  | In-Service |  | BANDERA | Tyler Pansing t.pansing@banderaelectric.com 866-226-3372 Ext 6078 | 353985 | 2020-05-08 | 2020-06-20 | 69 | 0 | 0 | 0 |  | Bandera |  | Tier 4 |  |  |  | 7428, 7439, 7440 | Y | N |  |  | 14581 | 6787
6203 | Premont - Falfurrias 69 kV Line | Rehab Premont - Falfurrias 69 kV Line |  | Premont | Falfurrias | Planned | 818 - 1002 | AEP | Joe Yeagler bcogan@aep.com 918-599-2857 | 3616 | 2020-05-11 |  | 69 | 0 | 12.25 | 0 |  | Jim Wells | Brooks | Tier 4 |  |  |  | 8508, 8894 | Y | N |  |  | 13928 | 6203
6982 | Boerne Cico - Comfort - Kendall Transmission Line Upgrade | Upgrade the 138-kV Boerne Cico - Comfort transmission line supporting circuit T148 to bundled 795 ACSR conductor. The planned T148 circuit rating is (MVA): Rate A=440, Rate B=440, Rate C=440. Upgrade the 138-kV Comfort - Kendall transmission line supporting circuit T243 to bundled 959 ACSS/TW conductor. The planned T243 circuit rating is (MVA): Rate A=760, Rate B=760, Rate C=760. |  | Boerne Cico | Kendall | Planned | 1019089 | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1019089 | 2020-05-11 |  | 138 | 0 | 18.1 | 0 |  | Kendall | Kendall | Tier 4 |  |  |  | 7151, 7152, 7155 | Y | N |  |  | 14799 | 6982
44850 | Grissom: Build new 345 kV Station | Interconnect Cranell wind farm on the Coleto Creek to Lon Hill 345 kV line |  | Grissom |  | In-Service | 963 - 1141 | AEP TCC | Adam Wells bcogan@aep.com 918-599-2857 | 3721 | 2020-05-13 |  | 345 | 0 | 0 | 0 |  | Bee |  | Tier 4 |  |  |  | 8164, 8455, 8624, 88624 | Y | N |  | 0 | 51799 | 44850
16TPIT0050 | Northaven - Renner 138 kV Line | Upgrade existing line | Project Deferral | Northaven | Renner | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4108-E | 2020-05-14 |  | 138 | 0 | 8.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2356, 2357, 2596, 2597, 2613, 2614, 2615, 2616, 2657, 2658 | Y | N |  |  | 11845 | 3065
6778 | Tri Corner - Watermill 345 kV Line | Upgrade existing line |  | Watermill | Tri Corner | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4226 | 2020-05-14 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 12427, 2427, 2432 | Y | N |  | 0 | 49535 | 6778
5499 | Everman - Cedar Hill Sw. Sta. 345 kV Line | Upgrade existing Everman - Cedar Hill Sw. Sta. 345 kV Line | Construction schedule change | Everman | Cedar Hill | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5260 | 2020-05-14 11:52 |  | 345 | 0 | 39.14 | 0 |  | Tarrant | Dallas | Tier 4 | 2016-03-10 | 2016-07-22 |  | 1885, 1886, 1931, 1932, 2420 | Y | N |  |  | 13239 | 5499
51228A | Construct Kennedale 138 kV Substation and Burleson 138 kV Sw | Construct Kennedale 138 kV Substation |  | Kennedale | Burleson | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5294 | 2020-05-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 1933, 1883, 2208 | Y |  |  | Cost included in phase B | 52341 | 51228
6834D | IH20 STATCOM RPG | Install fifth and sixth 20 MVAR MSCs at Collie Capacitor Station (38035). |  | Collie Capacitor Station (38035) | Collie Capacitor Station (38035) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2020-05-15 |  | 138 | 0 | 0 | 0 | 0,40 | Reeves | Reeves | Tier 3 | 2017-10-10 | 2017-12-06 |  | 38035 | Y |  |  | 0 | 46209 | 6834
7021 | Collin 345/138 kV Autotransformer 2 Series Reactor | Install 2-ohm series reactor on Collin 345/138 kV Autotransformer 2 |  | Collin Sw. Sta. |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R960 | 2020-05-15 |  | 138 | 0 | 0 | 0 |  | Collin |  | Tier 4 |  |  |  | 2370, 29555 | Y | N |  |  | 14843 | 7021
50510 | Add Doghouse 345 kV Switch | Add Doghouse 345 kV Switch for Prospero Solar POI |  | Clearfork Switch | Doghouse Switch | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8482, R8284 | 2020-05-15 |  | 345 | 0 | 0 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 11270, 23876 | Y |  |  | 0 | 50512 | 50510
4829 | Hutto Switch second 345/138 kV autotransformer | Install new autotransformer |  | Hutto |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R750 | 2020-05-15 |  | 345 | 0 | 0 |  |  |  |  | Tier 4 |  |  |  | 13660, 3696, 3666 | Y |  |  | 0 | 49638 | 4829
51245 | Add Andrews County South 345/138 kV Autotransformer #2 | Andrews County South 345/138 kV Autotransformer #2 |  | Andrews County South | Andrews County South | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8495 | 2020-05-15 |  | 345 | 0 | 0 | 600 |  | Andrews | Andrews | Tier 3 | 2019-07-12 | 2019-09-16 |  | 11207, 1158, 1157 | Y |  |  | 0 | 51247 | 51245
11TPIT0034 | Sargent Road 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  | Sargent Road |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M486-E | 2020-05-15 |  | 345 | 0 | 0 | 600 |  | Dallas |  | Tier 4 |  |  |  | 2946, 2949 | Y | N |  |  | 9001 | 1784
7171 | Andrews County South Switch - No Trees Switch 138 kV Line | Andrews County South Switch - No Trees Switch 138 kV Line |  | Andrews Co South | No Trees | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8407 | 2020-05-15 |  | 138 | 0 | 8.8 | 0 |  | Andrews | Winkler | Tier 4 |  | 2018-09-06 |  | 1149, 1150, 1157, 131853 | Y |  |  |  | 15012 | 7171
44181 | 138kV Cooper Creek - Arco Line Reconstruction |  |  |  |  | Planned |  | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2020-05-15 | 2020-02-01 | 138 | 0 | 1.62 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 906, 923 | Y | N |  | Reconstruct 138kV Cooper Creek to Arco | 44182 | 44181
17TPIT0023 | Northwest Carrollton - Norwood 138 kV Line | Upgrade existing double-circuit Northwest Carrollton - Carrollton line section | Project Deferral | Northwest Carrollton | Carrollton | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4110-E | 2020-05-15 |  | 138 | 0 | 11.8 | 0 |  | Dallas | Dallas | Tier 4 |  | 2017-01-11 |  | 2362, 2363, 2409, 2535, 2536, 2537, 2540, 2541, 2542, 2545, 2550, 2551, 2552, 12552 | Y | N |  |  | 10433 | 3089
46094 | Add Wolf 345 kV Switch | Wolf 345 kV Switch | New route approved | Wolf | Wolf | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8289 | 2020-05-15 |  | 345 | 0 | 0 | 0 |  | Ward | Ward | Tier 4 |  |  |  | 11007, 11008, 11010, 1018, 1029, 11028, 11084, 1013 | Y |  |  | 0 | 51215 | 46094
5286A | Fayette Area Upgrades | Upgrade existing Fayette - Frelsburg - Mockingbird - Glidden (T176) TL with a minimum rating of 380 MVA and with OPGW. | Planning In-Service Date Change. Updated to a phased project, the original TPIT project number is 5286. | Fayetteville | Glidden | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1019026, 1019024 | 2020-05-15 |  | 138 | 0 | 20 | 0 |  | Fayette | Colorado | Tier 4 | 2017-06-29 | 2017-07-28 |  | 7258, 7263, 7286, 78259 | Y | N |  |  | 14583 | 5286
4817 | TI Dallas - Kirkland Park/Coit Road 138 kV Line | Upgrade existing TI Dallas - Schroeder Road line section | Project Deferral | TI Dallas | Schroeder Road | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4202 | 2020-05-15 01:00 |  | 138 | 0 | 1 | 0 |  | Dallas | Dallas | Tier 4 | 2018-04-05 | 2018-05-08 |  | 2607, 2633, 2636, 2637 | Y | N |  |  | 12423 | 4817
45537 | Lewisville - Lewisville Jones - Lakepointe 138 kV Line | Upgrade the Lewisville - Lewisville Jones - Lakepointe 138 kV Line |  | Lewisville Switch | Lake Point (TNMP) | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R966 | 2020-05-15 12:00 |  | 138 | 0 | 0 | 0 |  | Denton |  | Tier 4 |  |  |  | 645, 1972, 1973, 37010 | Y |  |  | 0 | 45538 | 45537
55609 | Permian Basin Area 138 kV Reconfiguration | Permian Basin Area 138 kV Reconfiguration |  | Aroya - Yucca | Wink - Aroya | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2020-05-15 23:00 |  | 138 | 0 | 0 | 0 |  | Ward | Winkler | Tier 4 |  |  |  | 1001, 1009, 1013, 1074 | Y |  |  | 0 | 55611 | 55609
51236 | Add Wink to Andrews County South 138 kV Second Circuit | Wink to Andrews County South 138 kV Second Circuit |  | Wink | Andrews County South | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8493 | 2020-05-16 |  | 138 | 36.6 | 0 | 0 |  | Winkler | Andrews | Tier 3 | 2019-07-12 | 2019-09-06 |  | 131853, 1009, 1074, 1147, 1149, 1157, 11135 | Y |  |  | 0 | 52912 | 51236
6041 | Ely Tap to Scott REA Tap 69 kV line: Rebuild 69 kV line | Rehab Ely Tap to Scott REA Tap 69 kV line | IN SERVICE | Ely Tap | Scott REA Tap | In-Service | 786 - 0971 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2670 | 2020-05-21 | 2020-05-21 | 69 | 0 | 8.79 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6242, 6246, 60405 | Y | N |  |  | 13760 | 6041
6042 | Scott REA Tap to Eskota 69 kV line: Rebuild 69 kV line | Rehab Scott REA Tap to Eskota 69 kV line |  | Scott REA Tap | Eskota | Planned | 786 - 0971 | AEP | Brent Harris mlforcum@aep.com 918-599-2674 | 2671 | 2020-05-21 |  | 69 | 0 | 11.73 | 0 |  | Taylor | Nolan | Tier 4 |  |  |  | 1340, 6246, 6247 | Y | N |  |  | 13761 | 6042
3754 | Heartland to Yellowjacket: Build 69 kV line | Build new 69 kV line from Heartland to Yellowjacket | IN SERVICE | Heartland | Yellowjacket | In-Service | 637 - 0806 | AEP TNC | Thomas Reynolds mlforcum@aep.com 918-599-2674 | 2592 | 2020-05-28 | 2020-05-28 | 69 | 32 | 0 | 0 |  | Mason | McCulloch | Tier 2 | 2014-01-23 | 2014-11-04 | 2014-11-17 | 6379, 60386, 6363, 6378, 6381, 6406, 6372 | Y | N |  |  | 12085 | 3754
7022 | Forney - Elkton 345 kV line termination at Tri Corner | Forney - Elkton 345 kV line termination at Tri Corner |  | Forney | Tri Corner | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4306 | 2020-05-30 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 13105, 2432, 2437, 3105 | Y | N |  | 0 | 49534 | 7022
44834 | LIMBRG (LIM) 138kV Distribution Substation | Build new 138kV LIMBRG distribution substation. Loop through Ckt.05 Southwyck to Friendswood tap. |  | Southwyck | Friendswood | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 | 2020-04-29 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 43280, 42651, 43260, 47150, 43500, 44361 | Y |  |  | 0 | 50151 | 44834
7005 | Lake Houston (LAK) - 138kV Distribution Substation | Construct service to new 138kV Lake Houston distribution substation. Loop through Ckt.66 Kingwood to Atascocita. |  | Kingwood | Atascocita | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 | 2020-03-09 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40820, 40130, 40390, 40930, 40391, 40830 | Y |  |  | 0 | 50551 | 7005
6696A | Nash 138kV Loop Conversion | Convert Nash Substation to 138kV loop service. Loop from Ckt.02 WA Parish to West Columbia. Reconductor the loop sections to Nash. |  | Nash | WA Parish/West Columbia | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 | 2019-12-11 | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42980, 42981, 43380, 43384, 44010, 44030, 44390, 44721, 44722 | Y | N |  |  | 14478 | 6696
6427 | Refugio-Rincon 69 line MLSE Upgrade | Refugio-Rincon 69 line MLSE Upgrade |  | Refugio | Rincon | In-Service | 962 - 1140 | AEP TCC | Bill Roberts bcogan@aep.com 918-599-2857 | 3720 | 2020-05-31 | 2020-04-06 | 138 | 0 | 1 | 0 |  | San Patricio | Refugio | Tier 3 | 2017-03-28 | 2017-04-21 | 2017-05-08 | 8410, 8802, 8804, 8805, 8416 | Y | N |  |  | 14170 | 6427
6744 | Picacho: Add Distribution | Add a new distribution bank at the existing Picacho station |  | Picacho |  | In-Service | 1100 - 1278 | AEP TCC | James Lutz dnlyons@aep.com 918-599-2698 | 3817 | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Uvalde |  | Tier 4 |  |  |  | 8684 | Y | N |  |  | 14537 | 6744
49554 | Cabaniss: Add Second Distribution Bank | Cabaniss: Add Second Distribution Bank |  | Cabaniss |  | In-Service | 1033 - 1211 | AEP TCC | Thomas Niels bcogan@aep.com 918-599-2857 | 3772 | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8882 | Y | N |  | 0 | 49555 | 49554
52527 | Greens Bayou 345kV Reconfiguration - Ckt. 74F Deepwater to S | Disconnect existing circuits 68B & 74F at Greens Bayou and reconnect circuits to create new Ckt.74F Deepwater to Sheldon (Bypass GBY345). |  | Deepwater | Sheldon | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 | 2020-05-12 | 345 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40450, 40700, 41430 | Y | N |  | 0 | 52528 | 52527
6673B | Freeport - Bridge the Gap | Install 1st 138kV Automatically Switchable Capacitor Bank (Cap Bank #5 - 140 MVAR) at Jones Creek Substation |  | Jones Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 00:01 |  | 138 | 0 | 0 | 0 | 0,140 | Brazoria |  | Tier 1 |  |  | 2017-12-12 | 42535, 42540 | Y | N |  | 0 | 56734 | 6673
6696B | Nash 138kV Loop Conversion | Remove 69kV Nash tap from Ckt.45 Damon to West Columbia |  | Damon | West Columbia | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 00:01 | 2019-12-11 | 69 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42982, 42980, 42340, 43000, 44070, 44290, 43390 | Y | N |  | Cost included in Phase A | 14480 | 6696
6673E | Freeport - Bridge the Gap | Install 2nd 138kV Automatically Switchable Capacitor Bank (Cap Bank #6 - 140 MVAR) at Jones Creek Substation |  | Jones Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 00:02 |  | 138 | 0 | 0 | 0 | 0,140 | Brazoria |  | Tier 1 |  |  | 2017-12-12 | 42536, 42540 | Y | N |  | 0 | 56735 | 6673
6673F | Freeport - Bridge the Gap | Install 3rd 800MVA autotransformer (A3) at Jones Creek substation |  | Jones Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 00:04 |  | 345 | 0 | 0 | 800 |  | Brazoria |  | Tier 1 |  |  | 2017-12-12 | 49038, 42530, 42540 | Y | N |  | 0 | 56737 | 6673
44836 | BURKE (BKE) - Generator 138kV Substation (18INR0062) | New 138kV BURKE generator interconnection for Wagyu Solar. Loop substation to create new Ckt.02 WA Parish to BURKE to NASH. |  | West Columbia | Nash | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 00:05 | 2020-04-02 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42410, 42980, 43384, 44010, 43380 | Y |  |  | 0 | 46324 | 44836
7071 | West Columbia 138kV Load Conversion | Replace 69/12kV West Columbia power transformer with 138/12kV transformer |  | West Columbia |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 00:08 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43384, 43390, 43380, 42410 | Y |  |  |  | 14902 | 7071
5145C | Rafter - New 138 kV Substation | Build a new 138 kV transmission line from Cagnon to Rafter. |  | CAGNON | RAFTER | Planned | S-0837 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0261 | 2020-06-01 |  | 138 | 7.86 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5055, 5355 | Y | N |  |  | 14399 | 5145
51074 | This adds a capacitor to Annetta |  |  | Annetta Substation | Annetta Substation | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2020-06-01 |  | 138 | 0 | 0 | 0 | 0,37.8 | Parker | Parker | Tier 4 |  |  |  | 485 | Y |  |  | 0 | 51075 | 51074
3273B | Southton - New 138kV Substation |  |  | Southton | Braunig-Brooks | Under Construction | S-0750 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0217 | 2020-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5394, 5030, 5045, 5190, 5310, 5395 | Y | N |  | There are no transformers associated with this project | 10624 | 3273
4716 | Tortuga: Build new 3 breaker 138 kV station | Construct new Tortuga 138 kV line and cut it into the Gila - Upriver (Koch) 138 kV line |  | Gila | Upriver (Koch) | In-Service | 717 - 0899 | AEP TCC | John Pulay bcogan@aep.com 918-599-2857 | 3553 | 2020-06-01 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8168, 81680, 8467, 80136, 80141, 80260 | Y |  |  | New or Expand - New Telecom - Yes 345 kV CBs - 0 138 kV CBs - 3 69 kV CBs - 0 SCADA Additions - Yes | 12389 | 4716
3820 | Rebuild Casa Blanca to Sandia to AEP Mathis | Rebuild 69 kV 4-0 ACSR line sections to 795 ACSR on 138 kV capable structures. |  | Casa Blanca | AEP Mathis | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-06-01 | 2020-04-16 | 69 | 0 | 11.45 | 0 |  | Jim Wells | San Patricio | Tier 4 |  |  |  | 5666, 8166, 8407 | Y | N |  |  | 11277 | 3820
44874 | Resaca 69 kV Station | New Resaca 69 kV Station |  | Brownsville | La Palma | In-Service | 974 - 1152 | AEP TCC | Thomas Niels bcogan@aep.com 918-599-2857 | 3732 | 2020-06-02 |  | 69 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8626, 8310, 8332 | Y | N |  | 0 | 44875 | 44874
3967 | Leander - Round Rock Transmission Line Addition | Construct a new 138kV transmission line from Leander to Ridgmar (new substation) to Spanish Oak (new substation) to Round Rock (approximately 13 miles) using bundled 795 ACSR Drake (446 MVA) conductor. | Substation name change from Hero Way to Ridgmar and Parmer to Spanish Oak | Leander | Round Rock | In-Service |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1014352 | 2020-06-24 | 2020-06-04 | 138 | 13 | 0 | 0 |  | Williamson | Williamson | Tier 2 | 2013-12-10 | 2014-05-22 | 2014-06-10 | 7367, 7368, 3668, 7525 | Y | N |  |  | 11463 | 3967
6005 | Airline: Convert 69 kV Station | Upgrade Airline 69 kV station and lines to 138 kV |  | Airline | Naval Base | In-Service | 808 - 0993 | AEP TCC/LCRA | Dave Goetz bcogan@aep.com 918-599-2857 | 3597 | 2020-06-30 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8487, 8494, 8548, 8560, 8561, 78560, 8490, 8495, 8997, 8562, 8856 | Y | Y |  |  | 13771 | 6005
13TPIT0106 | Killeen SS to Ding Dong | Rebuild 477 ACSR line with 955 ACSS |  | Killeen SS | Ding Dong | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 11037 | 2020-06-30 |  | 138 | 0 | 5.8 | 0 |  | Bell | Bell | Tier 4 |  |  |  | 115, 117, 136, 3423 | Y | N |  |  | 9901 | 2608
6742 | Heines Sub: New Distribution Station | Add New Heines Sub Distribution Station |  | Airline | Naval Base | In-Service | 877 - 1055 | AEP TCC | Dave Goetz bcogan@aep.com 918-599-2857 | 3664 | 2020-06-30 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8490, 8997, 78560 | Y | Y |  |  | 14535 | 6742
44860 | Primera 138 kV Station | New Primera 138 kV Station |  | Harlingen SW | South Santa Rosa | In-Service | 975 - 1153 | AEP TCC | Michael Richardson bcogan@aep.com 918-599-2857 | 3733 | 2020-06-30 |  | 138 | 0 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 8638, 8327, 8359 | Y | N |  | 0 | 44861 | 44860
6788 | Tarpley Substation Upgrade | Add two 138 kV Circuit Breakers to Line Terminals to be operated at 69 kV. | Change in schedule | Tarpley |  | Under Construction |  | BANDERA | Tyler Pansing t.pansing@banderaelectric.com 866-226-3372 Ext 6078 | 353985 | 2020-07-01 |  | 69 | 0 | 0 | 0 |  | Bandera |  | Tier 4 |  |  |  | 7439, 7440 | Y | N |  |  | 14582 | 6788
5430L | Conversion to 138kV | Switch the Hickory - Locust line on to the 138kV substations |  | Hickory | Locust | Planned | N/A | DENTON | Chuck Sears Chuck.Sears@cityofdenton.com 940-349-7111 |  | 2020-07-01 | 2019-07-01 | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 914, 910 | Y | N | N/A | 0 | 55206 | 5430
3298 | Skyline - Install a Fourth 345kV Autotransformer. | Install one 600 MVA autotransformer at Skyline switchyard. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0670 | 2020-07-09 |  | 345 | 0 | 0 | 600 |  | Bexar | Bexar | Tier 4 |  |  |  | 5372, 5371, 5368 | Y | N |  | There are no transmission line additions associated with this project | 10649 | 3298
52098 | Rio Pecos: Replace 138/69 kV Auto | Replace 138/69 kV autotransformer #1 at Rio Pecos with a 90 MVA autotransformer | IN SERVICE | Rio Pecos |  | In-Service | 1068 - 1241 | AEP TNC | Thomas Neils mlforcum@aep.com 918-599-2674 | 2829 | 2020-07-12 | 2020-07-12 | 138 | 0 | 0 | 90 |  | Pecos |  | Tier 4 |  |  |  | 6598, 6601 | Y | N |  | 0 | 52099 | 52098
52275 | Bowie Autotransformer replacement | Bowie Autotransformer replacement |  | Bowie | Bowie | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2020-07-13 |  | 138 | 0 | 0 | 0 |  | Montague | Montague | Tier 4 |  |  |  | 621, 620 | Y |  |  | 0 | 52276 | 52275
5965 | Benjamin Tap to Katz (BEC): Build new 138 kV line | Construct new 138 kV ring bus Tardis on the Munday to Paducah 138 kV line, rebuild existing Benjamin Tap to 138 kV, terminate into Tardis, convert Benjamin to 138 kV operation and build new 138 kV line from Benjamin to Katz (BEC) | Update Description | Benjamin Tap | Katz (BEC) | Planned | 769-0954 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2685 | 2020-07-30 |  | 138 | 17.7 | 9 | 0 |  | Knox | Knox | Tier 2 | 2016-02-03 | 2016-05-01 | 2016-05-01 | 6320 | Y | N |  |  | 13680 | 5965
5276 | Flatonia - Hallettsville Transmission Line Upgrade | Upgrade T132 Hallettsville to Flatonia (18.7 mi) 138-kV transmission line to a minimum rating of 380 MVA with OPGW. |  | Flatonia | Hallettsville | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1016188 | 2020-08-01 |  | 138 | 0 | 18.7 | 0 |  | Fayette | Lavaca | Tier 4 |  |  |  | 7246, 7248 | Y | N |  |  | 12952 | 5276
48802 | Gillet: Build New Distribution Station | Gillet: Build New Distribution Station |  | Magnolia Tap | Nixon | Planned | 1032 - 1210 | AEP TCC/LCRA | Brandon Cogan bcogan@aep.com 918-599-2857 | 3771 | 2020-08-01 |  | 138 | 0 | 0 | 0 |  | Karnes |  | Tier 4 |  |  |  | 8583 | Y | Y |  | 0 | 48803 | 48802
48533 | BPUB Rio Grande Susbtation | BPUB has updated effective date for Rio Grande Substation. |  |  |  | Planned |  | BPUB | Javier Martinez jamartinez@brownsville-pub.com 956-083-6530 |  | 2020-08-05 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 59550, 59300, 59480 | Y |  |  | Project has been delayed until 7/1/2020. | 52532 | 52531
51642 | Figaro to Amadeus: Build new 345 kV line | Interconnect Amadeus wind farm on the Clear Crossing to Dermott 345 kV line | Update Schedule | Figaro | Amadeus | Planned | 907 - 1085 | ETT | Jake Tucker mlforcum@aep.com 918-599-2674 | 2825 | 2020-08-21 |  | 345 | 0.742 | 0 | 0 |  | Fisher | Fisher | Tier 4 |  |  |  | 60715, 182405 | Y | N |  | 0 | 51643 | 51642
44872 | Asherton 138 kV Station | Add breaker at Asherton 138 kV Station to Accommodate Shakes Solar |  | Asherton | - | Planned | 966 - 1144 | AEP TCC | Jeremy Brazeal bcogan@aep.com 918-599-2857 | 3724 | 2020-08-30 |  | 138 | 0 | 0 | 0 |  | Dimmit |  | Tier 4 |  |  |  | 88283, 8283 | Y | N |  | 0 | 44873 | 44872
4186C | University Area 138kV Conversions | Convert Blodgett substation from double-tap service to 138kV Ckt.37 loop service. Convert Blodgett TR1 load to 138kV. |  | Blodgett | TECO/Garrott | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1123 | 2020-08-30 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47520, 47521, 47522, 42690, 47430, 47660 | Y | N |  | Cost included in 4186A | 57372 | 4186
6114 | La Pryor - Uvalde 69 kV Line | Rehab La Pryor - Uvalde 69 kV Line |  | La Pryor | Uvalde | In-Service | 810 - 0995 | AEP TCC | James Nivens bcogan@aep.com 918-599-2857 | 3600 | 2020-08-30 | 2020-03-30 | 69 | 0 | 17.603 | 0 |  | Zavala | Uvalde | Tier 4 |  |  |  | 8231, 8672 | Y | N |  |  | 13840 | 6114
6822 | Figaro: Build new 345 kV station | Interconnect Amadeus wind farm on the Clear Crossing to Dermott 345 kV line | Update Schedule | Figaro |  | In-Service | 907 - 1085 | ETT | Jake Tucker mlforcum@aep.com 918-599-2674 | 2731 | 2020-08-30 | 2020-08-21 | 345 | 0 | 0 | 0 |  | Fisher |  | Tier 4 |  |  |  | 60715, 11305, 60704, 60706 | Y | N |  |  | 14623 | 6822
6117 | Pleasanton - Coy City Tap 69 kV Line | Rehab Pleasanton - Coy City Tap 69 kV Line |  | Pleasanton | Coy City Tap | In-Service | 814 - 0998 | AEP TCC | James Nivens bcogan@aep.com 918-599-2857 | 3604 | 2020-08-30 | 2019-12-13 | 69 | 0 | 16.79 | 0 |  | Atascosa |  | Tier 4 |  |  |  | 8200, 8600 | Y | N |  |  | 13843 | 6117
55632 | North Padre Tap to Port Aransas: Replace shield wire | Replace shield wire from North Padre Tap to Port Aransas |  | North Padre Tap | Port Aransas | Under Construction | 1101 1279 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3818 | 2020-08-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | Y |  |  | 0 | 55633 | 55632
49562 | Pig Creek: Build 138 kV terminal | Interconnect Taygete II solar farm at the Pig Creek 138 kV station | Update Schedule | Pig Creek |  | Planned | 1020 - 1198 | AEP | David Baker mlforcum@aep.com 918-599-2674 | 2782 | 2020-08-31 02:00 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60393 | Y | N |  | 0 | 49563 | 49562
07TPIT0060 | Howard Lane to Techridge Reconductor | The project re-conductors Circuit 1004 (Techridge to Howard Lane) using 795 ACSS Drake conductors to increase the capacity to 3000 Amp. |  | Howard Lane | Techridge | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | PLAN_117_P067 PLAN_117_P194 | 2020-09-05 |  | 138 | 0 | 1.72 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9191, 9217 | Y | N |  |  | 8204 | 1028
08TPIT0033 | Gilleland to Techridge 138kV Circuit | Establish a new 138kV circuit from Gilleland to Techridge and maintain a normally close tie between AEN and LCRA's switchyard at Gilleland. |  | Gilleland Substation | Techridge Substation | In-Service |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | PLAN_117_4276 PLAN_117_P207 | 2020-09-05 |  | 138 | 8 | 0 | 0 |  | Travis | Travis | Tier 2 |  | 2009-07-21 | 2009-07-21 | 9054, 9191, 7336, 9190 | Y | N |  |  | 8205 | 1029
51968 | Pinnacle Circuit Breaker Addition | Provide transmission service to a generator. Add circuit breakers in a ring-bus configuration to the existing substation.(ERCOT Generation Interconnection or Change Request No. 20INR0032) |  | Pinnacle Substation | Culberson Substation | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2020-09-25 |  | 138 | 0 | 0 | 0 |  | Culberson | Culberson | Tier 4 |  |  |  |  | Y | N |  | 0 | 51969 | 51968
4575 | BRYN_4575_Steele_Store_138 | Construct Steele Store substation 138kV bus with 138/69kV auto. |  |  |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2020-09-28 |  | 138 | 0 | 0 | 0 |  | Brazos |  | Tier 4 | 2015-10-09 | 2015-11-06 |  | 32852, 32866, 32868 | Y |  |  | 0 | 45782 | 4575
5041 | BRYN_5041_Snook_to_Steele_Store | Construct 138kV line from Snook to Steele Store (Bundled 1033 ACSR - Curlew) as part of the reliability project to loop in Steele Store |  | 32857 | 32852 | Planned |  | BRYN |  |  | 2020-09-28 |  | 138 | 9.2 | 0 | 0 |  | Burleson | Brazos | Tier 4 | 2015-10-09 | 2015-11-06 |  | 32852, 32857 | Y |  |  | 0 | 53866 | 5041
4571 | Atkins Substation Upgrade | Rebuild Atkins 69kV bus |  | 32864 |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2020-09-30 |  | 69 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  |  | Y |  |  | No MOD Changes Necessary | 12153 | 4571
5218A | San Miguel 345/138 kV autotransformer replacements | Replace T1 300 MVA auto with much larger auto and open T2 for construction |  | San Miguel |  | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-09-30 |  | 345 | 0 | 0 | 675 |  | Atascosa |  | Tier 4 |  |  |  | 5908, 5909, 5901, 5902 | Y | N |  | Delayed from 2018 to 2019 in the 2016 RTP. | 45090 | 5218
4883 | McCoy 69 KV substation | Add a new load serving substation between Pleasanton and Tordillo |  | McCoy |  | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-09-30 |  | 69 | 0 | 0 | 0 |  | Atascosa |  | Tier 4 |  |  |  | 5721, 5714, 5715 | Y | N |  |  | 12494 | 4883
3463 | Shady Bus Split | Reconfigure 69kV bus |  |  |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2020-09-30 |  | 69 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  |  | Y |  |  |  | 10843 | 3463
50894 | Bonilla: Add new terminal for West Raymond Wind | Bonilla: Add new terminal for West Raymond Wind |  | Bonilla |  | Planned | 1059 - 1232 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3790 | 2020-09-30 |  | 345 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 88574, 8573 | Y | Y |  | 0 | 50895 | 50894
52636 | Solanum: Build 138 kV temporary tap | Construct new 138 kV temporary hard tap on the Abilene South to Putnam 138 kV line |  | Solanum |  | Planned | 1073 - 1246 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2834 | 2020-09-30 |  | 138 | 0 | 0 | 0 |  | Callahan |  | Tier 4 |  |  |  | 61015, 6309, 60365 | Y | N |  | 0 | 52637 | 52636
6348 | Paint Rock to CRMWD Tap #1 69 kV line: Rebuild 69 kV line | Rehab Paint Rock to CRMWD Tap #1 69 kV line |  | Paint Rock | CRMWD Tap #1 | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2709 | 2020-09-30 |  | 69 | 0 | 6.09 | 0 |  | Concho | Concho | Tier 4 |  |  |  | 6369, 6370, 6376 | Y | N |  |  | 14092 | 6348
5891A | LUBZOL Substation Removal and Substation PATRIK Addition | Remove LUBZOL 138kV substation from CNP service |  | LUBZOL | TIDAL/TRAVIS | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-09-30 00:01 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 40980, 40070, 40470, 41210, 41380, 41580, 41590, 40089, 40530, 41370, 41415, 41450 | Y | N |  | 0 | 52118 | 5891
48748 | Oklaunion: Install 345 kV reactor | Install reactor on the Oklaunion 345 kV bus |  | Oklaunion |  | Planned | 1013 - 1191 | ETT | Dave Goetz mlforcum@aep.com 918-599-2674 | 2774 | 2020-09-30 01:00 |  | 345 | 0 | 0 | 0 | -50,0 | Wilbarger |  | Tier 4 |  |  |  | 6100 | Y | N |  | 0 | 48749 | 48748

## CancelledTPIT100120NoCost
OCTOBER BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 10/1/2020
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar ) (-Reactor, +Capacitor ) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number
44988 | Coral to Toyana: Build 138 kV line | Construct a new 138 kV ring bus at Toyana, build new 138 kV lines to Cryo and Coral from Toyana, and add capacitor banks at Toyana | CANCELLED | Coral | Toyana | Planned | 931 - 1109 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2766 | 2020-11-30 01:00 |  | 138 | 4.28 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 60437, 60721 | N | N |  | 0 | 44989 | 44988
44990 | Toyana: Build 138 kV station and add two capacitor banks | Construct a new 138 kV ring bus at Toyana, build new 138 kV lines to Cryo and Coral from Toyana, and add capacitor banks at Toyana | CANCELLED | Toyana |  | Planned | 931 - 1109 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2765 | 2020-11-30 01:00 |  | 138 | 0 | 0 | 0 | 0,28.8 | Reeves |  | Tier 4 |  |  |  | 60437 | N | N |  | 0 | 44991 | 44990
44056 | Coral to Toyana: Build 138 kV line | Construct a new 138 kV ring bus at Toyana, build new 138 kV lines to Cryo and Coral from Toyana, and add capacitor banks at Toyana | CANCELLED | Coral | Toyana | Planned | 931 - 1109 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2741 | 2020-11-30 01:00 |  | 138 | 0.63 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 60434, 60437 | N | N |  | 0 | 44057 | 44056
44058 | Coral: Build 138 kV station | Construct a new 138 kV ring bus at Toyana, build new 138 kV lines to Cryo and Coral from Toyana, and add capacitor banks at Toyana | CANCELLED | Coral |  | Planned | 931 - 1109 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2742 | 2020-11-30 01:00 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  | 60434 | N | N |  | 0 | 44059 | 44058
13TPIT0064 | Rocky Mound Switching Station series capacitors | Install series capacitors for Willow Creek - Clear Crossing - Dermott Switch (Central B) 345 kV line (Oncor Electric Delivery part) |  | Rocky Mound Switching Station |  | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | C079-E | 2021-05-15 |  | 345 | 0 | 0 | 0 |  | Haskell |  | CREZ |  |  |  | 17012, 17013, 17014, 17015, 1421, 60515 | N | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. | 9943 | 2644
6288 | Watermill - Trinidad 345 kV Line | Install a breaker at Watermill Sw. on the Watermill - Trinidad 345 kV Line to establish double-breaker configuration |  | Watermill | Trinidad | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4249 | 2021-05-15 |  | 345 | 0 | 0 | 0 |  | Dallas | Henderson | Tier 3 |  |  |  | 2996, 2427, 2428, 2432 | N |  |  |  | 14017 | 6288
43367C | LP&L Integration Tie Lines | 345 kV Line from Abernathy to Wadsworth |  | 345 kV Abernathy | 345 kV Wadsworth | Planned |  | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2021-06-01 |  | 345 | 26.2 | 0 | 0 |  | Hale | Lubbock | Tier 1 | 2015-12-29 | 2016-06-09 |  | 59178, 23920 | N |  |  | 0 | 43373 | 43367
43367B | LP&L Integration Tie Lines | 345 kV Line from Abernathy to North |  | 345 kV Abernathy | 345 kV North | Planned |  | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2021-06-01 |  | 345 | 23.32 | 0 | 0 |  | Hale | Lubbock | Tier 1 | 2015-12-29 | 2016-06-09 |  | 59156, 23920 | N |  |  | 0 | 43372 | 43367
43367A | LP&L Integration Tie Lines | 345 kV Line from Ogallala to Abernathy |  | 345 kV Ogallala | 345 kV Abernathy | Planned |  | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2021-06-01 |  | 345 | 50.9 | 0 | 0 |  | Castro | Hale | Tier 1 | 2015-12-29 | 2016-06-09 |  | 23912, 23920 | N |  |  | Cost includes the expansion required at the existing stations to accommodate the new lines | 43371 | 43367
43367 | LP&L Integration Tie Lines | [6 empty] | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2021-06-01 |  |  | 0 | 0 | 0 |  |  |  | Tier 1 | 2015-12-29 | 2016-06-09 |  | 59156, 59178, 79501, 79506 | N |  |  | 0 | 43368 | 43367
6526 | Place second auto at Einstein |  |  | Einstein345 | Einstein138 | Planned |  | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2021-07-01 |  | 345 | 0 | 0 | 708 |  | Glasscock | Glasscock | Tier 4 |  |  |  | 79634, 79632, 79565 | N |  |  |  | 14264 | 6526
50876 | Port Lavaca - Victoria: Line Rebuild | Port Lavaca - Victoria: Line Rebuild |  | Port Lavaca | Victoria | Planned | 1054 - 1227 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3782 | 2021-11-30 |  | 69 | 0 | 29 | 0 |  | Calhoun | Victoria | Tier 3 |  |  |  | 8135, 8136, 8169 | N | N |  | 0 | 50877 | 50876
4875 | Red Gate: Build new 138 kV line | Interconnect STEC Red Gate Power Plant at Permanent with a new 138 kV line into North Edinburg |  | Falfurrias | North Edinburg | Planned | 724 - 0906 | AEP TCC | Teresa Trotman dnlyons@aep.com 918-599-2698 | 3558 | 2021-12-01 12:00 |  | 138 | 7.5 | 7.5 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 88380, 8380, 8896, 83809, 161031 | N | Y |  |  | 12486 | 4875
5490 | Liggett - North Irving138 kV DCKT Line | Upgrade existing Liggett - North Irving138 KV Double Ckt Line |  | Liggett | Hackberry | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4222 | 2021-12-15 |  | 138 | 0 | 11.8 | 0 |  | Dallas | Dallas | Tier 3 |  |  |  | 11923, 11925, 1922, 1924, 2001, 2002, 15002, 15020, 15021, 2010, 15025, 15026, 15045 | N | N |  | 0 | 45577 | 5490
5490 | Liggett - North Irving138 kV DCKT Line | Upgrade existing Liggett - North Irving138 KV Double Ckt Line |  | Liggett | Hackberry | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4222 | 2021-12-15 |  | 138 | 0 | 11.8 | 0 |  | Dallas | Dallas | Tier 3 |  |  |  | 2001, 11923, 11925, 12002, 15022, 15023, 1922, 1924, 2002, 2010, 15002, 15020, 15021, 15025, 15026, 15045 | N | N |  | 0 | 52807 | 5490
5490 | Liggett - North Irving138 kV DCKT Line | Upgrade existing Liggett - North Irving138 KV Double Ckt Line |  | Liggett | Hackberry | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4222 | 2021-12-15 |  | 138 | 0 | 11.8 | 0 |  | Dallas | Dallas | Tier 3 |  |  |  | 11923, 11925, 1922, 1924, 2001, 2002, 15002, 15020, 15021, 2010, 15025, 15026, 15045 | N | N |  | 0 | 52266 | 5490
50989 | Blessing - El Campo: Line Rebuild | Blessing - El Campo: Line Rebuild |  | Blessing | El Campo | Planned | 1060 - 1233 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3791 | 2022-01-31 |  | 69 | 0 | 27.23 | 0 |  | Matagorda | Wharton | Tier 3 |  |  |  | 8100, 8119, 8552, 8556 | N | Y |  | 0 | 50990 | 50989
52293 | Hackberry - North Irving138 kV DCKT Line | Upgrade the Hackberry - North Irving |  |  |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4291 | 2022-05-15 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 3 |  |  |  | 1996, 1997, 2001, 2010, 15020, 15023, 2388, 15022, 15045, 15046 | N |  |  | 0 | 52809 | 52293
52293 | Hackberry - North Irving138 kV DCKT Line | Upgrade the Hackberry - North Irving |  |  |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4291 | 2022-05-15 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 3 |  |  |  | 1996, 1997, 2010, 15023, 2388, 15022, 15045, 15046 | N |  |  | 0 | 52810 | 52293
52293 | Hackberry - North Irving138 kV DCKT Line | Upgrade the Hackberry - North Irving |  |  |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4291 | 2022-05-15 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 3 |  |  |  | 1996, 1997, 2010, 2388, 15045, 15046, 2001, 15020 | N |  |  | 0 | 52294 | 52293
50884 | Ganado - Edna: Line Rebuild | El Campo - Victoria: Line Rebuild |  | Ganado | Edna | Planned | 1062 - 1235 | AEP TCC | Joseph Page bcogan@aep.com 918-599-2857 | 3795 | 2022-11-30 |  | 138 | 0 | 9.72 | 0 |  | Jackson | Jackson | Tier 3 |  |  |  | 8117, 8118 | N | N |  | 0 | 50885 | 50884
50888 | El Campo - Ganado: Line Rebuild | Rebuild El Campo to Victoria 138 kV line |  | El Campo | Ganado | Planned | 1062 - 1235 | AEP TCC | Joseph Page bcogan@aep.com 918-599-2857 | 3794 | 2022-11-30 |  | 138 | 0 | 20.02 | 0 |  | Wharton | Jackson | Tier 3 |  |  |  | 8102, 8117, 88099 | N | N |  | 0 | 50889 | 50888
50886 | Edna - Victoria: Rebuild 138 kV line | Rebuild El Campo to Victoria 138 kV line |  | Edna | Victoria | Planned | 1062 - 1235 | AEP TCC | Joseph Page bcogan@aep.com 918-599-2857 | 3796 | 2022-11-30 |  | 138 | 0 | 21.57 | 0 |  | Jackson | Victoria | Tier 3 |  |  |  | 8118, 8172 | N | N |  | 0 | 50887 | 50886
6282 | Everman - Benbrook 345 kv line | Upgrade the existing 345 kV Line |  | Everman | Benbrook | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5273 | 2023-05-15 |  | 345 |  | 29 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1870, 1886, 1935 | N |  |  |  | 14014 | 6282
6291 | Royse Sw. Sta. - Farmersville Sw. Sta. 345 kV DCKT Line | Rebuild existing 345 kV Line |  | Royse | Farmersville | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4255 | 2023-05-15 |  | 345 | 0 | 30.4 | 0 |  | Rockwall | Collin | Tier 3 |  |  |  | 1685, 2461, 2478 | N |  |  |  | 14020 | 6291
50890 | Port Lavaca: Station Rebuild | Port Lavaca: Station Rebuild |  | Port Lavaca |  | Planned | 1057 - 1230 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3787 | 2023-05-30 |  | 69 | 0 | 37.81 | 0 |  | Calhoun |  | Tier 4 |  |  |  | 8135 | N | N |  | 0 | 50891 | 50890
3901 | Lobo to Freer: Rebuild 69 kV line | Rebuild Lobo to Freer 69 kV line with 795 ACSS | Description Update | Lobo | Freer | Planned | 677 - 0846 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 2596 | 2024-06-30 |  | 69 | 0 | 49.8 | 0 |  | Webb | Duval | Tier 3 |  |  |  | 8505, 80222 | N | N |  |  | 11371 | 3901
44419 | Load serving |  |  | Mayhill | Denton Steam/Brinker | Planned |  | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2024-07-01 | 2024-07-01 | 138 | 5.1 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 927, 929, 982 | N | N |  | 0 | 44420 | 44419
3276 | JT Deely to Martinez MLSE Upgrade | Upgrade terminal at JT Deely to ensure a rating of 2386 A (minimum). |  | JT Deely | Martinez | Planned | S-0759 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2026-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5110, 5294 | N | N |  | There are no transformers associated with this project | 10627 | 3276
50282 | Adds new Jaguar sub near Twin Pines Switch | Adds new Jaguar sub between Twin Pines Switch and Highlands Sub. For AEP load. | AEP is looking at another location to serve the load. | Highlands Sub | Twin Pines Switch | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2027-06-01 |  | 69 | 0 | 0 | 0 |  | Victoria | Victoria | Tier 4 |  |  |  | 5609, 5602, 5604 | N | N |  | 0 | 50283 | 50282
44870 | Charlotte 69 kV Station | Charlotte 69 kV Station: Add Cap Bank |  | Charlotte | - | Planned | 976 - 1154 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3734 | 2027-07-01 |  | 69 | 0 | 0 | 0 | 0,7.2 | Atascosa |  | Tier 3 |  |  |  |  | N | N |  | 0 | 44871 | 44870

## RTPProjects
Project Number | Project Name | Transmission Owner | ERCOT Proposed in-service year | TSP MOD in-service year | Status of Project | Associated TPIT ERCOT Project Number(s) | Notes
2019-C1 | Markham Area 69-kV Upgrades | AEP/STEC | 2021 | 11/1/2020; 12/23/2020; 2/15/2021; 2/28/2021 | Planned; Planned; Planned; Planned | 50342; 50344; 50340; 51996
2019-C2 | Brookhollow to Port Lavaca 69-kV Upgrade | AEP | 2021
2019-C3 | Jones Creek Copper Reconfiguration | CNP | 2024
2016-C8 | Hardy (45840) - North Side (47711) 138-kV Line Uprate | CNP | 2025 | 2022-05-31 | Planned Not in Case | 5244
2018-NC9 | Add a Capacitor Bank of a minimum of 55 MVAR at Anna Southeast (2704) 138-kV substation | Oncor | 2021
2017-NC2 | Liggett Switch (11923, 1922) 138-kV line upgrades | Oncor | 2024 | 2021-12-15 | Cancelled | 5490
2019-NC1 | Irving Valley (2389) - Hackberry (2387) 345-kV switch upgrade | Oncor | 2022
2019-NC7 | Keller Wall Price (2037,2038) - Roanoke (1854,1852) 138-kV line upgrades and new ring bus configuration at Keller Wall Price | Oncor | 2021
2016-N1 | Kiamichi Energy Facility (140077) 345-kV reactor addition | KIOWA POWER PARTNERS LLC (RE) | 2022
2019-NC2 | Southside POI (230) - India (2351) 69-kV line uprate | Brazos Electric | 2024 | 2024-01-01 | Planned | 52260
2019-NC3 | Brand (827)-College(829) 138-kV line upgrade | GP&L | 2022
2019-NC4 | McCree (834)-Shiloh (830) 138-kV line upgrade | GP&L | 2022
2019-NC6 | Add a Capacitor Bank of a minimum of 120 MVAR at Lookout (828) 138-kV substation | GP&L | 2021
2019-NC8 | Prairie Creek Switch (2441) - Mesquite Forney Road (2752) - Thornton East Tap (2747) - Oates (831) 138-kV line upgrades | Oncor | 2021
2019-NC9 2019-N1 | Install two reactors at New Oliver (59196) 345-kV station and Mackenzie (59114) 69-kV Station | LPL | 2022
2019-NC10 2019-N2 | Henrietta West (1543) -Lanham Tap (1452) 69-kV line upgrades | Oncor | 2024
2019-NC11 | Hicks Switch (2081) - Alliance (1855) - Roanoke (1845) 345-kV line upgrades | Oncor | 2024
2019-NC12 | Lake Creek SES (3409) -Tradinghouse SES (13405) 345-kV line upgrades | Oncor | 2024
2019-NC13 | Liggett Switch (1922) - Rochelle (2057) 138-kV line upgrades | Oncor | 2022
2019-NC14 | Trinidad SES (3127) - Nipak Tap (3260) - Oak Grove Tap (2725) 138-kV line upgrades | Oncor | 2024
2019-NC15 | Venus Switch (1907,1906) - Navarro (68091) 345-kV line upgrade | Oncor | 2024
2019-NC16 | Allen Switch (2509) - Plano Custer Road (2525) 138-kV line uprades | Oncor | 2025
2019-NC17 | Carrollton Northwest Auto Upgrade | Oncor | 2025
2019-NC18 | Carrollton East (2577) - Carrollton Tarpley Road (2558) 138-kV line upgrades | Oncor | 2021
2019-NC19 | Cedar Hill (3058) - DeSoto Hampton Road (3059) 138-kV line upgrade | Oncor | 2024
2019-NC20 | Austin Ranch (2378,2377) Cap Bank Addition | Oncor | 2024
2019-NC21 | Royse Switch (2472) - Fate (12703) - Rockwall Aluminum Tap (2733) - Darlrock Road (2735) 138-kV line upgrades | Oncor | 2024
2019-NC22 | Alpha Road (2596) - Inwood Road (2598) - Farmers Branch Gillis (2582) 138-kV line upgrades | Oncor | 2024
2019-NC23 | Industrial (2976) - West Levee Switch (2400) - East Levee Switch (2482) 138-kV line upgrades | Oncor | 2021
2019-NC24 | Cedar Crest (2493,2494,2495) - Dealey Street (2842) - West Levee Switch (2400) 138-kV line upgrades | Oncor | 2021
2019-NC25 | Sargent Road (2947) - Industrial (2976) 138-kV line upgrades | Oncor | 2021
2019-NC26 | Fairdale (805) - College (829) 138-kV line upgrade | GP&L | 2024
2019-NC27 | Miller (824) - Newman (849) - Walnut (823) 138-kV line upgrades | GP&L | 2024
2019-NC28 | Holder (292,293) Auto upgrade | BEPC | 2024
2019-NC29 | Liggett Switch Autos Series Reactors | Oncor | 2021
2019-NC30 | Roanoke Switch Autos Series Reactors | Oncor | 2024
2019-NC31 | Seagoville Switch (2433)-Forney Switch (2437) 345-kV line upgrade | Oncor | 2024
2019-NC32 | Sherry Switch(1920) -General Motors Switch (2140)-Watson (2128) 138-kV line upgrades | Oncor | 2021
2019-NC33 | Temple Elm Creek (13662) - McGregor Phillips Tap (3594) - Waco Atco (3592) 138-kV line upgrade | Oncor | 2021
2019-NC34 | DeSoto Switch (2424) - Glen Heights (217) 138-kV line upgrades | Oncor | 2021
2019-NC35 | Everman Switch (1883) - Forest Hill Switch (1967) - Rolling Hills Tap 1 (2211) 138-kV line upgrades | Oncor | 2021
2019-NC36 | Forney (2437) – Royse (2474) 345-kV line upgrades | Oncor | 2021
2019-FW1 | Quarry Field substation 345-kV addition | ONCOR | 2021
2019-FW2 | McElroy (6607) to Sage (6604) to Crane Tap 2 (6609) 69-kV lines upgrade | AEP | 2021 | 2021-12-15 | Planned | 52728
2019-FW3 | Add a second 138-kV circuit from Horseshoe Springs to Riverton and a capacitor bank at Owl Hills substation | ONCOR | 2021 | 2021-05-15 | Planned | 52309
2019-FW4 | Add a second 345/138/13.8-kV 3-Windings transformer at Quarry Field station | ONCOR | 2021
2019-W1 | 138/69-kV Sandy Creek transformer (7121/7127); and 69-kV lines from Sandy Creek (7121) to Sunrise Beach (7400) to Kingsland (7404) upgrade | LCRA | 2021 | 2020-11-30 | Planned | 53971
2018-S2 | Wormser Road (8295) - Santo Nino (8653) 138-kV line upgrade | AEP | 2025 | 2023-07-01 | Planned | 45513
2019-S1 | Tordillo (5715) - McCoy (5721) - Pleasanton (5714) 69-kV Upgrade | STEC | 2022 | 12/1/2020; 4/1/2021 | Planned; Planned | 50334; 50336
2019-S2 | Pleasanton 69-kV Area Upgrades | AEP | 2021 | 2021-05-31 | Planned | 52068
2019-S4 | Cheniere LNG 345/138-kV Additions | AEP | 2024
2019-S5 | Dupont Switching Station (8422) to Gregory Power (160205) 138-kV Upgrade | AEP | 2022
2019-S6 | Resnik (8580) to Dupont Switching Station (8422) 138-kV Upgrade | AEP | 2024
2019-S7 | Whitepoint (8961) to Hecker (8565) Ckt 1 & 2 138-kV Upgrade | AEP | 2024
2019-SC1 | Hutto 345/138-kV Transformer Addition and Downstream Line Upgrades | Oncor | 2024
2019-SC2 | Hamilton Wolfe (5187) to Medical Center (5300) 138-kV Line Upgrade | CPS | 2024

## TransmissionOwnerProjContac
TRANSMISSION OWNER | TPIT DISTRIBUTION | Primary Contact | Primary Email Address | Primary Phone | Secondary Contacts | Secondary Email Addresses | Secondary PHONE
AEP | Primary & Secondary | Cindy Miller | Camiller2@aep.com | Cindy Miller: 918 599 2891 | Glen Reed; David Kidd; Brad Myers; Mabel See; Mike Forcum; Doug Lee; Daniel Lyons; Bob Lager; Mina Turner; Lisa Kelso; Carole Myser | gareed@aep.com; dekidd@aep.com; blmyers@aep.com; msee@aep.com; mlforcum@aep.com; dnlyons@aep.com; dlee@aep.com; rjlager@aep.com; myturner@aep.com; lokelso@aep.com; camyser@aep.com | David Kidd: 918 599 2637 Glen Reed: 918 599 2664 Brad Myers: 918 599 2690
AUSTIN ENERGY | Primary & Secondary | Reza Ebrahimian | Reza.Ebrahimian@austinenergy.com; | Reza: (512) 322-6740 | Hunt, Dandy; Ron Krautz; Brion Ryan | dandy.hunt@austinenergy.com; ron.krautz@austinenergy.com; Ryan, Brion <Brion.Ryan@austinenergy.com> | Reza:512 322 6740 Dandy:512 322 6748 Ron:512 322 6835 Brion: 512-322-6879
BPUB | Primary | Ramon Sanz | rsanz@brownsville-pub.com; | Ramon: 956 983 6203 | James McCann | jmccann@brownsville-pub.com; | James: 956 983 6204
BEPC (BRAZOS ELECTRIC) | Primary & Secondary | Dwight Beckman | dbeckman@brazoselectric.com | Dwight: 254 750 6373 | David Albers | dalbers@brazoselectric.com | David: 254 750 6358
BTU | Primary & Secondary | Edward Lopez | elopez@btutilities.com | Edward: 979 821 5697 | David Hering | dhering@btutilities.com | David: 979 821 5652
CNP | Primary & Secondary | Wesley Woitt | wesley.woitt@centerpointenergy.com | Wesley Woitt: 713-207-2760 | Yingying Huang; Raja Sekhar Kakarla; Cody Mann | Yingying.Huang@centerpointenergy.com; rajasekhar.kakarla@centerpointenergy.com; cody.mann@centerpointenergy.com | Yingying Huang: 713-207-2831 Raja Sekhar Kakarla: 713-207-3614 Cody Mann: 713-207-3149
COCS | Primary | Wesley Gray | wgray@cstx.gov | Wesley: 979 764 3434 | Timothy Crabb, Stacy Engelmann | tcrabb@cstx.gov; sengelmann@cstx.gov; | Timothy Crabb 979 764 3439 Stacy Engelmann 979 764 3681
CPS | Primary & Secondary | Basileo Rocha, Sunil Dhakal | bdrocha@cpsenergy.com; SDhakal@cpsenergy.com | Basileo: 210 353 4933 Sunil: 210 353 2008 | Kenneth Bowen Trieu Vo | kbowen@cpsenergy.com; tvo@cpsenergy.com; | Kenneth: 210 353 4142 Trieu: 210 353 2127
CTT (Cross Texas Transmission) | Primary & Secondary | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310 | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310
DENTON | Primary & Secondary | Chuck Sears | Chuck.Sears@cityofdenton.com; | Chuck: 940 349 7111 | Brent Heath | brent.heath@cityofdenton.com; | Brent: 940 349 7180
GARLAND | Primary & Secondary | Danh Huynh | Dhuynh@gpltexas.org | Danh: 972 205 3826 | Grubbs, David; Juan Santos | Dgrubbs@gpltexas.org; Jsantos@gpltexas.org | David: 972 205 2664 Juan: 972-205-2603
Golden Spread EC | Primary & Secondary | Chris Koenig | ckoenig@gsec.coop | Chris: 806 349 5201 | Shane McMinn, Mark Reinart | smcminn@gsec.coop; mreinart@gsec.coop | Shane: 806 379 7766 Mark: 806 349 6562
LCRA TSC; BEC (Bandera); BBEC; CTEC; GVEC; NBU; PEC; SBEC; RGEC | Primary & Secondary | Dylan Preas | dylan.preas@lcra.org | Dylan: 512-578-4514 | Naved Khan | naved..khan@lcra.ord | Naved: 512-578-4176
Lone Star | Primary & Secondary | Chenyan Guo | chenyan.guo@fpl.com | Chenyan: 561-304-5692 | Matt Gomes | Matthew.Gomes@LONESTAR-TRANSMISSION.COM | Matt - 512-236-3133
Oncor | Primary & Secondary | Charles Saker | charles.saker@oncor.com | Charles: 214-743-6896 | Paul Bell | paul.bell@oncor.com | Paul: 214-743-6676
Sharyland Utilities | Primary & Secondary | Brad Schwarz | bschwarz@huntpower.com | Brad: 512-289-7425 | Mark Caskey | mcaskey@sharyland.com | Mark: 214 978 8243
STEC | Primary & Secondary | Doug Evans | devans@stec.org | Doug: 361 485 6459 | Paul Person Loretta Gallaga | pperson@stec.org; lgallaga@stec.org; | Paul: 361 485 6151 Loretta: 956 377 7120
TMPA | Primary & Secondary | Ahmad Saboor | asaboor@texasmpa.org | Ahmad: 936 873 1104 | Frank Owens | fowens@texasmpa.org; | Frank: 936 873 1120
TNMP | Primary & Secondary | Robert Lona | Robert.Lona@tnmp.com | Robert: 281-581-4732 | Anthony, Hudson Ballay, Dustin Cloninger, Ross | Anthony.Hudson@tnmp.com; Dustin.Ballay@tnmp.com; Ross.Cloninger@tnmp.com; | Anthony: 281 581 4712 Dustin:281 581 4730 Ross:281 581 4733
Wind Energy Texas Transmission (WETT) | Primary | Julius Horvath | julius.horvath@windenergyoftexas.com | Julius: 512 436 9585; cell: 512 496 9186 | Christina Minchew | christina.Minchew@windenergyoftexas.com | Christina: 512-436-9469