## ImprovementCostSummary06242019
| Project Cost |  |  |  |  | XFMR MVA
| 345 | 138 | 69 | Total |  | 345 | 138 | 69 | Total
2018 | 550380000 | 1276115403 | 418503798 | 2244999201 | 2018 | 5446 | 2300 | 0 | 7746 | For ROS and BOD Reports
2019 | 226046469 | 1005866668 | 726660126.5 | 1958573263.5 | 2019 | 3328 | 820 | 0 | 4148 | ·All Projects (in engineering, routing, licensing and construction): |  |  |  | 3860246822
2020 | 613655800 | 714237980 | 234637214 | 1562530994 | 2020 | 7344 | 220 | 0 | 7564 | ·Transmission Projects Energized in 2019: |  |  |  | 1006930435.5
2021 | 697845000 | 175319000 | 72600000 | 945764000 | 2021 | 1800 | 60 | 0 | 1860
2022 | 39800000 | 45759000 | 6600000 | 92159000 | 2022 | 2086 | 0 | 0 | 2086
2023 | 71200000 | 75600000 | 1950000 | 148750000 | 2023 | 675 | 0 | 0 | 675
2024 | 9000000 | 22700000 | 88500000 | 120200000 | 2024 | 600 | 0 | 0 | 600
2025+ | 0 | 35200000 | 4000000 | 39200000 | 2025+ | 0 | 0 | 0 | 0
2019COM | 151246469 | 553055605 | 302628361.5 | 1006930435.5 | 2019COM | 2428 | 470 | 0 | 2898
2019PLAN | 74800000 | 452811063 | 424031765 | 951642828 | 2019PLAN | 900 | 350 | 0 | 1250
2018-2025+ | 2207927269 | 3350798051 | 1553451138.5 | 7112176458.5 | 2018-2025+ | 21279 | 3400 | 0 | 24679
2018-2019 | 776426469 | 2281982071 | 1145163924.5 | 4203572464.5 | 2018-2019 | 8774 | 3120 | 0 | 11894
2020-2025+ | 1431500800 | 1068815980 | 408287214 | 2908603994 | 2020-2025+ | 12505 | 280 | 0 | 12785
| Circuit Miles New |  |  |  | Circuit Miles Rebuilt, Reconductored or Upgraded |  |  |  |  | Total
| 345 | 138 | 69 | Total |  | 345 | 138 | 69 | Total | 345 | 138 | 69 | Total
2018 | 305 | 291.769 | 2.6 | 599.369 | 2018 | 135.14 | 792.296 | 389.21 | 1316.646 | 440.14 | 1084.065 | 391.81 | 1916.015
2019 | 25.35 | 106.98 | 33.11 | 165.44 | 2019 | 32.8 | 206.6 | 557.098 | 796.498 | 58.15 | 313.58 | 590.208 | 961.938
2020 | 365.6 | 120.41 | 0 | 486.01 | 2020 | 124.45 | 434.15 | 197.523 | 756.123 | 490.05 | 554.56 | 197.523 | 1242.133
2021 | 191.2 | 67.8 | 0 | 259 | 2021 | 76.5 | 53.86 | 42.54 | 172.9 | 267.7 | 121.66 | 42.54 | 431.9
2022 | 0 | 1.7 | 61 | 62.7 | 2022 | 0 | 29.48 | 0 | 29.48 | 0 | 31.18 | 61 | 92.18
2023 | 0 | 0.1 | 0 | 0.1 | 2023 | 141.9 | 61.8 | 0 | 203.7 | 141.9 | 61.9 | 0 | 203.8
2024 | 4 | 8 | 0 | 12 | 2024 | 67.96 | 13.4 | 49.8 | 131.16 | 71.96 | 21.4 | 49.8 | 143.16
2025+ | 0 | 8.4 | 0 | 8.4 | 2025+ | 0 | 26.3 | 2 | 28.3 | 0 | 34.7 | 2 | 36.7
2019COM | 18 | 47.57 | 0 | 65.57 | 2019COM | 32.8 | 133.67 | 260.228 | 426.698 | 50.8 | 181.24 | 260.228 | 492.268
2019PLAN | 7.35 | 59.41 | 33.11 | 99.87 | 2019PLAN | 0 | 72.93 | 296.87 | 369.8 | 7.35 | 132.34 | 329.98 | 469.67
2018-2025+ | 891.15 | 605.159 | 96.71 | 1593.019 | 2018-2025+ | 578.75 | 1617.886 | 1238.171 | 3434.807 | 1469.9 | 2223.045 | 1334.881 | 5027.826
2018-2019 | 330.35 | 398.749 | 35.71 | 764.809 | 2018-2019 | 167.94 | 998.896 | 946.308 | 2113.144
2020-2025+ | 560.8 | 206.41 | 61 | 828.21 | 2020-2025+ | 410.81 | 618.99 | 291.863 | 1321.663

## FutureTPIT060119NoCost
JUNE BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 6/1/2019
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar ) (-Reactor, +Capacitor ) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number
6878 | AEN_New_AshtonW_138KV_SUB |  |  |  |  | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2019-06-03 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 9224, 9226, 9217, 9223 | Y |  |  |  | 14688 | 6878
50160 | Beeville - Goliad: Rebuild 69 kV Line | Beeville - Goliad: Rebuild 69 kV Line |  | Beeville | Goliad | Planned | 961 - 1139 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3719 | 2019-06-14 |  | 69 | 0 | 22.21 | 0 |  | Bee | Goliad | Tier 4 | 2019-04-23 | 2019-05-21 |  |  | Y | N |  | 0 | 50161 | 50160
5221 | Move Oaks load to 138 kV bus | Move the Oaks load from the 69 kV to the 138 kV instead of replacing auto. 2015 RTP |  | Oaks |  | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-06-15 |  | 138 | 0 | 0 | 0 |  | Atascosa |  | Tier 4 |  |  |  | 5713 | Y | N |  |  | 12888 | 5221
5915 | Cypress Creek Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Cypress Creek Substation (This is a two year project). |  | Cypress Creek |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017351 | 2019-06-30 |  | 138 | 0 | 0 | 0 |  | Kendall |  | Tier 4 |  |  |  | 7156 | Y | N |  |  | 13623 | 5915
5920 | Fourmile Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Indian Mesa/Orion/NWP Tap (S564). |  | Indian Mesa/Orion/NWP Tap |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017380 | 2019-06-30 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 76019 | Y | N |  |  | 13628 | 5920
6082 | Basin: Build 138 kV station | Construct new 138 kV box bay on the Solstice to Permian Basin 138 kV line | Schedule Update | Basin |  | Planned | 860 - 1038 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2696 | 2019-06-30 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60415, 60392, 60397 | Y | N |  |  | 13806 | 6082
6107 | Bonniview - Rincon 69 kV Line | Rehab Bonniview - Rincon 69 kV line |  | Bonniview | Rincon | Planned | 834 - 1018 | AEP | Jason Bryant dnlyons@aep.com 918-599-2698 | 3641 | 2019-06-30 |  | 69 | 0 | 11.97 | 0 |  | Refugio | San Patricio | Tier 4 |  |  |  | 8416, 8805 | Y | N |  |  | 13833 | 6107
6746 | Valadez: Add New Distribution Station | Add New Valadez Distribution Station |  | Wooldridge | Barney Davis | Planned | 879 - 1057 | AEP | Brad Duvall dnlyons@aep.com 918-599-2698 | 3666 | 2019-06-30 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8028, 8458, 8492 | Y | N |  |  | 14539 | 6746
44428 | Edith Clarke: Build 345 kV terminal | Interconnect Foard City wind farm at Edith Clarke | Company Contact, Schedule, and Cost Update | Edith Clarke |  | Planned | 934 - 1112 | ETT | Eric Blind mlforcum@aep.com 918-599-2674 | 2747 | 2019-06-30 |  | 345 | 0 | 0 | 0 |  | Foard |  | Tier 4 |  |  |  | 60500 | Y | N |  | 0 | 44429 | 44428
44445 | Riley: Interconnect Electra Wind phase two | Interconnect Electra wind farm phase two, Lockett Station, into the Electra wind farm phase one, Digby substation | Company Contact and Schedule Update | Riley |  | Planned | 935 - 1113 | ETT | Dave Goetz mlforcum@aep.com 918-599-2674 | 2748 | 2019-06-30 |  | 345 | 0 | 0 | 0 |  | Foard |  | Tier 4 |  |  |  | 6101 | Y | N |  | 0 | 44446 | 44445
44495 | Edith Clarke to Foard City: Build 345 kV line | Interconnect Foard City wind farm at Edith Clarke | Company Contact, Schedule, and Cost Update | Edith Clarke | Foard City | Planned | 934 - 1112 | ETT | Eric Blind mlforcum@aep.com 918-599-2674 | 2746 | 2019-06-30 01:00 |  | 345 | 4 | 0 | 0 |  | Foard | Foard | Tier 4 |  |  |  | 60500, 142563 | Y | N |  | 0 | 44496 | 44495
45027 | Brant: Build 69 kV temporary Tap | Build new Brant 69 kV temporary tap on the Rock Springs to Sonora 69 kV line | Schedule Update | Brant |  | Planned | 952 - 1130 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2757 | 2019-06-30 01:00 |  | 69 | 0 | 0 | 0 |  | Sutton |  | Tier 4 |  |  |  | 60438, 6570, 8239 | Y | N |  | 0 | 45028 | 45027
5222 | Rebuild Dilley to Cotulla 69 kV line | Rebuild 4/0 ACSR 69 kV line with 138 kV capable 795 ACSR. 2015 RTP |  | Dilley | Cotulla | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-07-01 |  | 69 | 0 | 15.8 | 0 |  | La Salle | Frio | Tier 4 |  |  |  | 5863, 5876 | Y | N |  |  | 12889 | 5222
6387B | Greenville Arera System Enhancements |  |  |  |  | Planned |  | RYBRN | Charles Gibune 214-678-1192 |  | 2019-07-01 |  | 138 | 0 | 0 | 100 |  | Hunt | Hunt | Tier 3 | 2015-12-15 | 2016-02-15 |  | 837 | Y | N |  | 0 | 47083 | 6387
6387E | Greenville Arera System Enhancements | [6 empty] | RYBRN | Charles Gibune 214-678-1192 |  | 2019-07-01 |  | 138 | 0 | 0 | 0 |  | Hunt |  | Tier 3 | 2015-12-15 | 2016-02-15 |  | 6750, 6879, 6882 | Y | N |  | 0 | 47081 | 6387
6536 | T-283 Bellville South to Quanex Switch | Rebuild transmission line to 138-kV capable 959.6 ACSS-TW conductor due to maintenance on old 69 KV wood pole line and the future conversion to 138 KV. |  | Bellville South | Quanex Switch Structure | Under Construction |  | SBEC | Don Roberts droberts@sbec.org | WO# 17-6071 | 2019-07-01 |  | 69 | 0 | 3.33 | 0 |  | Austin | Austin | Tier 4 |  |  |  | 7269, 7660 | Y | N |  |  | 14276 | 6536
43677 | Add 138kV MASCH Branch Substation | [5 empty] | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2019-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 934, 901, 985 | Y | N | N/A | 0 | 43678 | 43677
47952 | New Coyote Springs Substation | New Coyote Springs Substation (Reeves County 138 kV Conversion) |  | Coyote Springs (Bus #38113) | Reeves County Tap (Bus #38114) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE02819 | 2019-07-01 |  | 138 | 0 | 0.1 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38113, 38114 | Y |  |  | 0 | 48412 | 47952
6920 | Reconfigures Barilla Draw and Interconnects BD-AMI | Reconfigures Barilla Draw and Interconnects BD-AMI (NOMCR # 57681-1) |  | Barilla Draw Tap (Bus #38060) | Barilla Draw-AMI (Bus #38061) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07213 | 2019-07-10 |  | 138 | 0.06 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38060, 38061, 38062, 38065, 38058, 38069 | Y |  |  | 0 | 48422 | 6920
4454 | Henne to Comal Transmission Line Upgrade | Upgrade the 7.6 mile Henne (7174) - Comal (7176) 138-kV transmission line from 159 MVA to 380 MVA using single 959 ACSS Suwannee conductors. |  | Henne | Comal | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1015116 | 2019-07-16 |  | 138 | 0 | 7.6 | 0 |  | Comal | Comal | Tier 4 |  |  |  | 7172, 7174, 7176 | Y | N |  |  | 12014 | 4454
6064 | Anson to Exxon Hawley Tap 69 kV line: Rebuild 69 kV line | Rehab Anson to Exxon Hawley Tap 69 kV line | Schedule Update | Anson | Exxon Hawley Tap | Planned | 786 - 0971 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2674 | 2019-07-31 |  | 69 | 0 | 10.39 | 0 |  | Jones | Jones | Tier 4 |  |  |  | 6175, 6176, 6238 | Y | N |  |  | 13784 | 6064
6834B | IH20 STATCOM RPG | Install +/- 190 MVAR STATCOM at IH20. |  | IH20 138 kV (38045) | IH20 STATCOM 138 kV (38046) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-08-01 |  | 138 | 0 | 0 | 0 | -190190 | Reeves | Reeves | Tier 1 | 2017-10-10 | 2017-12-06 |  | 38046, 38045 | Y |  |  | 0 | 46207 | 6834
46246 | Monument Draw Interconnection | Monument Draw Interconnection (NOMCR # 57718-1). (Cost estimate needs to be verified) |  | All American Tap (Bus #38230) | Lone Star Tap (Bus #38180) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-08-01 |  | 69 | 0.04 | 0 | 0 |  | Winkler | Ward | Tier 4 |  |  |  | 38210, 38211, 38212, 38180, 38230 | Y |  |  | 0 | 48423 | 46246
5552A | North Belt to Greens to Lockwood Ckt.90 Thermal Uprate | Upgrade Ckt.90 North Belt to Greens Road to increase thermal ratings |  | North Belt | Greens Road | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1126 | 2019-08-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45822, 46112 | Y |  |  |  | 14476 | 5552
6387D | Greenville Arera System Enhancements |  |  |  |  | Planned |  | RYBRN | Charles Gibune 214-678-1192 |  | 2019-08-30 |  | 138 | 5 | 0 | 0 |  | Hunt | Hunt | Tier 3 | 2015-12-15 | 2016-02-15 |  | 837, 6750 | Y | N |  | 0 | 47080 | 6387
5533 | Lynx: Build a 138 kV station | Construct a new 138 kV ring bus near Woodward #1 Tap on the Fort Stockton to Rio Pecos Line and terminate Woodward 1 and 2 wind farms into Lynx | Schedule Update | Lynx |  | Planned | 788 - 0973 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2647 | 2019-08-31 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 6632, 60400, 6601, 6671, 130432, 130431 | Y | N |  |  | 13261 | 5533
5552B | North Belt to Greens to Lockwood Ckt.90 Thermal Uprate | Upgrade Ckt.90 Greens Road to Lockwood to increase thermal ratings |  | Greens Road | Lockwood | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1126 | 2019-08-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45822, 46031 | Y |  |  |  | 14477 | 5552
5980 | Bison: Build 69 kV station | Construct new 69 kV ring bus at Powell Field Junction Tap | Schedule Update | Bison |  | Planned | 840 - 1024 | AEP TNC | Brad Duvall mlforcum@aep.com 918-599-2674 | 2680 | 2019-08-31 |  | 69 | 0 | 0 | 0 |  | Crockett |  | Tier 4 |  |  |  | 6548, 60395, 6545, 6547, 6549 | Y | N |  |  | 13695 | 5980
6068 | Onyx to Nugent Tap 69 kV line: Rebuild 69 kV line | Rehab Onyx to Nugent Tap 69 kV line | Schedule Update | Onyx | Nugent Tap | Planned | 786 - 0971 | AEP TNC | Jeremy Brazeal mlforcum@aep.com 918-599-2674 | 2676 | 2019-08-31 |  | 69 | 0 | 6.71 | 0 |  | Jones | Jones | Tier 4 |  |  |  | 6219, 6243, 6388 | Y | N |  |  | 13789 | 6068
5535 | Lynx to Rio Pecos: Rebuild 138 kV line | Rebuild Lynx to Rio Pecos 138 kV line | Schedule and Cost Update | Lynx | Rio Pecos | Planned | 788 - 0973 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2648 | 2019-08-31 |  | 138 | 0 | 2.2 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6601, 60400 | Y | N |  | 0 | 50012 | 50011
47927 | Tesla to Misae: Build new 345 kV line | Interconnect Misae Solar at Tesla | NEW | Tesla | Misae | Planned | 936 - 1114 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2773 | 2019-08-31 01:00 |  | 345 | 0.5 | 0 | 0 |  | Childress | Childress | Tier 4 |  |  |  | 60501, 142815 | Y | N |  | 0 | 47928 | 47927
43214 | Interconnects Calmity Jane to TNMP WTN | New Substation - Calamity Jane (Cost estimate needs to be verified) |  | Worsham (Bus #38021) | Calamity Jane (Bus #38020) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-09-01 |  | 138 | 0.5 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38020, 38021 | Y |  |  | 0 | 48426 | 43214
45114 | TNMP County Road Substation | New Substation - County Road |  | IH20 (Bus #38045) | County Road (Bus #38047) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-09-01 |  | 138 | 0 | 0.2 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38047, 38050, 38040, 38045 | Y |  |  | 0 | 48425 | 45114
49812 |  |  |  | 5945059410 | 79689 |  |  | BPUB |  |  | 2019-09-02 |  | 138 | 0 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 5962, 59410, 59450, 79689 | Y |  |  | 0 | 49813 | 49812
47418 | KingMountainSwitchyardProject | King Mountain Switchyard Project |  | King Mountain Switchyard | Odessa and North McCamey | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2019-09-05 |  | 345 | 5 | 0 | 0 |  | Upton | Ector | Tier 4 |  |  |  | 842, 843, 11028, 76000 | Y | Y |  | 0 | 47419 | 47418
5934 | Warda Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Warda (S407). |  | Warda |  | In-Service |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017411 | 2019-09-09 |  | 138 | 0 | 0 | 0 |  | Fayette |  | Tier 4 |  |  |  | 7312 | Y | N |  |  | 13642 | 5934
6296 | Cowden North - Odessa North 69 kV Line Conversion | Cowden North - Odessa North 69 kV Line Conversion |  | Cowden North | Odessa North | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9028 | 2019-09-15 |  | 138 | 0 | 10.5 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 11259, 1122, 1123, 1141, 1142, 1259 | Y |  |  |  | 14025 | 6296
7110 | Horseshoe Springs - Owl Hills 138 kV Line | Horseshoe Springs - Owl Hills 138 kV Line |  | Horseshoe Springs | Owl Hills | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8383 | 2019-09-15 |  | 138 | 10 | 0 | 0 |  | Culberson |  | Tier 4 |  |  |  | 11090, 11190 | Y |  |  |  | 14944 | 7110
7166 | T535 Plum - Piney Creek MLSE Upgrade | Upgrade terminal equipment at Plum and Piney Creek to achieve a planned static normal and emergency rating of 530 MVA on T535. |  | Plum | Piney Creek | Planned | 1019371 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019371 | 2019-09-27 |  | 138 | 0 | 0 | 0 |  | Fayette | Fayette | Tier 4 |  |  |  | 7274, 7307 | Y | N |  |  | 15007 | 7166
4575 | BRYN_4575_Steele_Store_138 | Construct Steele Store substation 138kV bus with 138/69kV auto. |  |  |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2019-09-30 |  | 138 | 0 | 0 | 0 |  | Burleson |  | Tier 4 | 2015-10-09 | 2015-11-06 |  | 32852, 32866, 32868 | Y |  |  | 0 | 45782 | 4575
5041 | BRYN_5041_Snook_to_Steele_Store | Construct 138kV line from Snook to Steele Store (Bundled 1033 ACSR - Curlew) as part of the reliability project to loop in Steele Store |  | 32857 | 32852 | Planned |  | BRYN | James Tanneberger jtanneberger@btutilities.com 979-821-5763 |  | 2019-09-30 |  | 138 | 9.2 | 0 | 0 |  | Burleson | Brazos | Tier 4 | 2015-10-09 | 2015-11-06 |  | 32852, 32857 | Y |  |  |  | 12690 | 5041
5794 | Mason to Fort Mason: Rebuild 69 kV line | Rebuild Mason to Fort Mason 69 kV line and convert to 138 kV | Schedule and Cost Update | Mason | Ft. Mason | Under Construction | 646 - 0815 | AEP TNC | Michael Richardson mlforcum@aep.com 918-599-2674 | 1810 | 2019-09-30 |  | 69 | 0 | 0.15 | 0 |  | Mason | Mason | Tier 4 |  |  |  | 6393, 60410, 76388, 76390 | Y | N |  |  | 13533 | 5794
5962 | Mason: Add new 138/69 kV autotransformer | Add 138/69 kV autotransformer capacity at Mason | Schedule and Cost Update | Mason |  | Under Construction | 646 - 0815 | AEP TNC | Michael Richardson mlforcum@aep.com 918-599-2674 | 2687 | 2019-09-30 |  | 138 | 0 | 0 | 130 |  | Mason |  | Tier 4 |  |  |  | 60410, 6393 | Y | N |  |  | 13677 | 5962
6004 | Refugio - Melon Creek 69 kV line | Rehab Refugio - Melon Creek 69 kV line |  | Refugio | Melon Creek | Under Construction | 815 - 0999 | AEP | Bill Roberts dnlyons@aep.com 918-599-2698 | 3607 | 2019-09-30 |  | 69 | 0 | 12.6 | 0 |  | Refugio | Calhoun | Tier 4 |  |  |  | 8410, 8800 | Y | N |  |  | 13721 | 6004
6116 | Palacios - Carancahua 69 kV Line | Rehab Palacios - Carancahua 69 kV Line |  | Palacios | Carancahua | Planned | 817 - 1001 | AEP | Jason Bryant dnlyons@aep.com 918-599-2698 | 3612 | 2019-09-30 |  | 69 | 0 | 13.36 | 0 |  | Matagorda | Jackson | Tier 4 |  |  |  | 8131, 8555 | Y | N |  |  | 13842 | 6116
6344 | Harriett to Miles 69 kV line: Rebuild 69 kV line | Rehab Harriett to Miles 69 kV line | Schedule Update | Harriett | Miles | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2713 | 2019-09-30 |  | 69 | 0 | 5.71 | 0 |  | Tom Green | Runnels | Tier 4 |  |  |  | 6410, 6412 | Y | N |  |  | 14088 | 6344
6667 | Stewart and West Galveston 5MVAR Reactors | Remove existing 10MVAR reactor at Stewart 138kV substation and re-install 5MVAR reactor. Install 5MVAR reactor at West Galveston substation |  | Stewart & West Galveston |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-09-30 |  | 138 | 0 | 0 | 0 |  | Galveston |  | Tier 4 |  |  |  | 43290, 43400 | Y | N |  |  | 14451 | 6667
7172 | Refugio: Install 138/69 kV Auto | Install 90 MVA 138/69 kV autotransformer and a 138 kV breaker |  | Refugio |  | Under Construction | 100-0100 | AEP | Wilburt Robert dnlyons@aep.com 918-599-2698 | 2021 | 2019-09-30 |  | 138 | 0 | 0 | 90 |  | Refugio |  | Tier 3 | 2017-03-31 | 2017-04-21 | 2017-06-01 | 8412, 89634, 8410 | Y | N |  |  | 15013 | 7172
44631 | Adds Palmas station and line to E Rio Hondo | Add 138 kV Palmas station to connect a wind farm and the 138 kV line that connects to E Rio Hondo. |  | Palmas | E Rio Hondo | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-09-30 |  | 138 | 6.3 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 5760, 5764 | Y | N |  | 0 | 44632 | 44631
5891A | LUBZOL Substation Removal and Substation PATRIK Addition | Remove LUBZOL 138kV substation from CNP service |  | LUBZOL | TIDAL/TRAVIS | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-09-30 00:01 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 40980, 41580, 41590 | Y | N |  |  | 13608 | 5891
5891B | LUBZOL Substation Removal and Substation PATRIK Addition | Install 138kV customer-owned PATRIK substation (LUBZOL substation replacement) |  | PATRIK | TIDAL/TRAVIS | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-09-30 00:02 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 40981, 41580, 41620 | Y | N |  |  | 13647 | 5891
45579 | Hayter: Build 138 kV temporary tap | Build new Hayter 69 kV temporary tap on the Alamito Creek to Solstice 138 kV line | NEW | Hayter |  | Planned | 1024 - 1202 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2787 | 2019-09-30 01:00 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60444, 6680, 60385 | Y | N |  | 0 | 45580 | 45579
6387C | Greenville Arera System Enhancements |  |  |  |  | Planned |  | RYBRN | Charles Gibune 214-678-1192 |  | 2019-10-01 |  | 138 | 5 | 0 | 0 |  | Hunt | Hunt | Tier 3 | 2015-12-15 | 2016-02-15 |  |  | Y | N |  | 0 | 47079 | 6387
7160 | Jackie Howard: Create Interconnection for Mesteno WF | Create interconnection for Mesteno windfarm by interconnecting the the Mesteno gen-tie line permanently to the last ETT transmission line deadend structure on the existing Del Sol - Jackie Howard line. Windfarm owner will own an interconnecting station named "Charlie Egner". |  | Del Sol | Jackie Howard | Planned | 924 - 1102 | ETT | Kenneth 'Rich' Haley dnlyons@aep.com 918-599-2698 | 3701 | 2019-10-01 |  | 345 | 0 | 0 | 0 |  | Starr | Starr | Tier 4 |  |  |  | 80368, 80355, 162101, 161553, 162104 | Y | N |  |  | 15001 | 7160
44352 | GreenvilleAreaProject (a portion) | The project resolves for local voltage issues in Greenville area |  | Dent Road Switchyard | Dent Road Substation and Wallace-Wieland Rayburn Station | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2019-10-01 |  | 138 | 0.03 | 8.2 |  |  | Hunt | Hunt | Tier 4 |  |  |  | 837, 839, 946, 6750, 6882 | Y | Y |  | 0 | 44353 | 44352
6971 | Magnolia Mercer Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Magnolia Mercer Substation. |  | Magnolia Mercer |  | Planned | 1018915 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018915 | 2019-10-04 |  | 69 | 0 | 0 | 0 |  | Caldwell |  | Tier 4 |  |  |  | 7218, 7215, 7220 | Y | N |  |  | 14788 | 6971
48533 |  | New 138kV Substation with BPUB system. | [5 empty] | BPUB |  |  | 2019-10-04 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 59550, 59300, 59480 | Y |  |  | 0 | 48534 | 48533
5954 | Gillrina: Build new distribution station | Gillrina: Build new distribution station for STEC load |  | Banquette | Stadium | Planned | 805 - 0990 | AEP/STEC | Bill Roberts dnlyons@aep.com 918-599-2698 | 3594 | 2019-10-19 |  | 69 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8031, 88031, 8888, 8889 | Y | Y |  |  | 13667 | 5954
6709 | Heines Substation Addition | Construct a new load-serving substation named Heines off the Airline to Naval Base (T476) transmission line. | [5 empty] | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018754 | 2019-10-30 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 78560, 8487, 8560 | Y |  |  | 0 | 45470 | 6709
6773 | Callicaotte: Add New Distribution Station | Add New Callicaotte Distribution Station |  | Lon Hill | Haisley | Planned | 880 - 1058 | AEP | Tom Reynolds dnlyons@aep.com 918-599-2698 | 3667 | 2019-10-30 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8027, 8452, 8920 | Y | N |  |  | 14567 | 6773
6823 | Goddard: Contruct a new 345 kV station | Interconnect Karankawa I Wind Farm at Goddard. Construct a three breaker ring in breaker and half configuration expandable to four rungs |  | Goddard |  | Under Construction | 960 - 1138 | AEP | Teresa Trotman dnlyons@aep.com 918-599-2698 | 3718 | 2019-10-30 |  | 345 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 8606, 88606, 88607, 5725, 8455 | Y | N |  |  | 14624 | 6823
44850 | Grissom 345 kV Station | New Grissom 345 kV Station |  | Coleto Creek | Lon Hill | Planned | 963 - 1141 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3721 | 2019-10-30 |  | 345 | 0 | 0 | 0 |  | Bee |  | Tier 4 |  |  |  | 8624, 88624, 8164, 8455 | Y | N |  | 0 | 44851 | 44850
48746 | Cedar Canyon Substation Addition | Construct a new substation named Cedar Canyon off the Bakersfield to Schneeman Draw transmission line to support a generation interconnection request (19INR0038). |  | Bakersfield | Schneeman Draw | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019501 | 2019-10-30 |  | 345 | 0 | 0 | 0 |  | Crockett | Pecos | Tier 4 |  |  |  | 76015, 7053, 76002 | Y |  |  | 0 | 48747 | 48746
5206 | Brackettville to Escondido: Construct 138 kV line | Build a double circuit capable 138 kV circuit from Brakettville to Escondido station |  | Brackettville | Escondido | Under Construction | 762-0947 | AEP TCC | Guillermo Taylor dnlyons@aep.com 918-599-2698 | 3570 | 2019-10-31 |  | 138 | 45 | 0 | 0 |  | Kinney | Maverick | Tier 2 | 2016-01-05 | 2017-01-20 | 2017-02-08 | 8252, 8260 | Y | N |  |  | 12865 | 5206
5885 | Tardis to Benjamin Tap: Rebuild 69 kV line | Construct new 138 kV ring bus Tardis on the Munday to Paducah 138 kV line, rebuild existing Benjamin Tap to 138 kV, terminate into Tardis, convert Benjamin to 138 kV operation and build new 138 kV line from Benjamin to Katz (BEC) |  | Benjamin | Tardis | Planned | 769 - 0954 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2656 | 2019-10-31 |  | 138 | 1.67 | 5.99 | 0 |  | Knox | Knox | Tier 2 | 2016-02-03 | 2016-05-01 | 2016-05-01 | 790, 6086, 6087, 6088, 6320, 6085, 6117, 6135, 6107 | Y | N |  |  | 13601 | 5885
5961 | Tardis: Build new 138 kV station | Construct new 138 kV ring bus Tardis on the Munday to Paducah 138 kV line, rebuild existing Benjamin Tap to 138 kV, terminate into Tardis, convert Benjamin to 138 kV operation and build new 138 kV line from Benjamin to Katz (BEC) | Schedule Update | Tardis |  | Planned | 769 - 0954 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2683 | 2019-10-31 |  | 138 | 0 | 0 | 0 |  | Knox |  | Tier 2 | 2016-02-03 | 2016-05-01 | 2016-05-01 | 6320, 6117, 6135 | Y | N |  |  | 13676 | 5961
5969 | Clairmont Tap to Wolfgang 69 kV line: Rebuild 69 kV line | Rehab Clairmont Tap to Wolfgang 69 kV line | Company Contact and Schedule Update | Clairmont Tap | Wolfgang | Under Construction | 786 - 0971 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2658 | 2019-10-31 |  | 69 | 0 | 7.82 | 0 |  | Kent | Kent | Tier 4 |  |  |  | 6162, 6197 | Y | N |  |  | 13684 | 5969
6077 | Bronte Atlantic to Miles 69 kV line: Rebuild 69 kV line | Rehab Bronte Atlantic to Miles 69 kV line |  | Bronte Atlantic | Miles | Under Construction | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2691 | 2019-10-31 |  | 69 | 0 | 17.44 | 0 |  | Coke | Runnels | Tier 4 |  |  |  | 6410, 6418 | Y | N |  |  | 13800 | 6077
6113 | Coy City Tap - Sunniland 69 kV Line | Rehab Coy City Tap - Sunniland 69 kV Line |  | Coy City Tap | Sunniland | Planned | 814 - 0998 | AEP | James Nivens dnlyons@aep.com 918-599-2698 | 3605 | 2019-10-31 |  | 69 | 0 | 16.5 | 0 |  | Atascosa | Live Oak | Tier 4 |  |  |  | 8406, 8600 | Y | N |  |  | 13839 | 6113
6251 | Pecos Valley to TNMP Gomez 69 kV line: Rebuild 69 kV line | Rehab Pecos Valley to TNMP Gomez 69 kV line | Company Contact and Cost Update | Pecos Valley | Gomez | Planned | 786 - 0971 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2699 | 2019-10-31 |  | 69 | 0 | 14.2 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6643, 38470 | Y | N |  |  | 13979 | 6251
6342 | Cross Plains to Santa Anna T 69 kV line: Rebuild 69 kV line | Rehab Cross Plains to Santa Anna Tap 69 kV line | Schedule Update | Cross Plains | Santa Anna Tap | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2719 | 2019-10-31 |  | 69 | 0 | 14.72 | 0 |  | Callahan | Coleman | Tier 4 |  |  |  | 6352, 6356, 6357 | Y | N |  |  | 14086 | 6342
7015 | CNP_18TPIT7015_Refuge_POI_Sub | Loop new 345kV REFUGE substation and install one generator lead for new generator interconnection to PEYTON substation (Peyton Creek Wind). (18INR0018) |  | STP | DOW | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-10-31 |  | 138 | 0 | 0 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 42400, 5915, 42500 | Y |  |  |  | 14837 | 7015
6580 | Clyde Magnolia Tap: Replace 69 kV capacitor bank | Replace 6 Mvar capacitor bank with a 7.2 Mvar capacitor bank at Clyde Magnolia Tap | Company Contact, Schedule, and Cost Update | Clyde Magnolia Tap |  | Planned | 839 - 1023 | AEP TNC | Jim Lutz mlforcum@aep.com 918-599-2674 | 2819 | 2019-10-31 |  | 69 | 0 | 0 | 0 | 0,7.2 | Callahan |  | Tier 4 |  |  |  | 6302 | Y | N |  |  | 15003 | 7162
43536 | RIGBY (RIG) - New 138kV Substation | Construct service to new 138kV customer-owned RIGBY (RIG) substation. Loop through Ckt.86 Crosby to CONNOR |  | RIGBY | Crosby/CONNOR | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-10-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  | 40670, 40155, 40390, 40665 | Y | N |  | 0 | 50152 | 43536
49560 | Jim Treece: Interconnect Blue Summit 3 | Interconnect Blue Summit 3 wind farm at Jim Treece 345 kV station | NEW | Jim Treece |  | Planned | 1019 - 1197 | ETT | Michael Forcum mlforcum@aep.com 918-599-2674 | 2781 | 2019-10-31 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 61001 | Y |  |  | 0 | 49561 | 49560
45021 | Pershing: Build 138 kV temporary tap | Build new Pershing 138 kV temporary tap on the Abilene Northwest to Oak Creek 138 kV line | Schedule Update | Pershing |  | Planned | 978 - 1156 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2763 | 2019-10-31 01:00 |  | 138 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  | 60724, 6229, 6335 | Y | N |  | 0 | 45022 | 45021
5558C | Proposed Substation |  |  |  |  | Planned |  | RYBRN | Charles Gibune 214-678-1192 |  | 2019-11-01 |  | 138 | 0 | 0 | 0 |  | Fannin |  | Tier 4 |  |  |  | 6817, 1807 | Y | N |  |  | 13289 | 5558
5882 | Blackland - Weilande 345/138kV additional source | [6 empty] | RYBRN | Charles Gibune 214-678-1192 |  | 2019-11-01 |  | 138 | 0.42 | 0 | 600 |  | Hunt |  | Tier 4 |  |  |  | 6878, 6879, 2464 | Y | N |  |  | 13598 | 5882
44391 | Rupley Tap: Temporary Hard Tap | Rupley Tap for Victoria Port Generation Interconnection |  | Dupont SW | Victoria | Planned | 959 - 1137 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3717 | 2019-11-01 |  | 138 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  | 88143, 8143, 8172, 111343 | Y | N |  | 0 | 44392 | 44391
5275 | Esperanza Substation Addition | Add a new load serving substation (ring bus) at Esperanza. The station will be built between Boerne an Fair Oaks Ranch off T503. |  | Boerne | Fair Oaks Ranch | Planned |  | LCRATSC/PEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016187 | 2019-11-11 |  | 138 | 0 | 0 | 0 |  | Kendall |  | Tier 4 |  |  |  | 7710, 5470, 7168 | Y | N |  |  | 12951 | 5275
48320 | Add Nelson 138 kV Switch | Add Nelson 138 kV Switch |  | Andrews County South Switch | Fullerton Switch | Planned | R8457 | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2019-11-15 |  | 138 | 0.3 | 0 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 11273, 1134, 1135 | Y |  |  | 0 | 48322 | 48320
45408 | Add Red Lakes Switch | Add Red Lakes Switch |  | Red Lakes Switch | Red Lakes Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8461 | 2019-11-15 23:00 |  | 138 | 0 | 0 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 11293, 1292, 11292, 134093 | Y |  |  | 0 | 45410 | 45408
7164 | T195 Granite Mountain - Marble Falls MLSE Upgrade | Upgrade terminal equipment at Granite Mountain and Marble Falls to achieve a planned static normal and emergency rating of 221 MVA on T195. |  | Granite Mountain | Marble Falls | Planned | 1019369 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019369 | 2019-11-18 |  | 138 | 0 | 0 | 0 |  | Burnet | Burnet | Tier 4 |  |  |  | 7348, 7474 | Y | N |  |  | 15005 | 7164
6784 | Schumansville T1 Replacement | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Schumansville |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2019-11-22 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7609 | Y |  |  |  | 14578 | 6784
4706E | HO Clarke to Webster Ckt.05 | Restore Southwyck to Friendswood Tap after upgrades |  | Southwyck | Friendswood Tap | Conceptual |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-11-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42651, 43260 | Y |  |  | 0 | 50157 | 4706
5195 | Rio Pecos: Build 138 kV terminal | Interconnect Pecos solar farm at Rio Pecos | Schedule and Cost Update | Rio Pecos |  | Planned | 758 - 0942 | AEP TNC | Randy Weaver mlforcum@aep.com 918-599-2674 | 2633 | 2019-11-30 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 6601 | Y | N |  |  | 12854 | 5195
5932 | Jim Briley Substation Addition | Construct a motor operated load serving 138-kV substation off T499 between Geronimo and Seguin. | Substation name change from Strempel to Jim Briley | Seguin | Geronimo | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017707 | 2019-11-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7695, 7228, 7604 | Y | N |  |  | 13640 | 5932
6123 | Turtle Creek - La Pryor 69 kV Line | Rehab Turtle Creek - La Pryor 69 kV Line |  | Turtle Creek | La Pryor | Planned | 810 - 0995 | AEP | James Nivens dnlyons@aep.com 918-599-2698 | 3599 | 2019-11-30 |  | 69 | 0 | 14.603 | 0 |  | Zavala | Zavala | Tier 4 |  |  |  | 8243, 8672 | Y | N |  |  | 13849 | 6123
6166 | Carbide - Greenlake: Rebuild 69 kV Line | Carbide - Greenlake: Rebuild 69 kV Line |  | Carbide | Greenlake | Planned | 868 - 1046 | AEP | Brad Duvall dnlyons@aep.com 918-599-2698 | 3655 | 2019-11-30 |  | 69 | 0 | 2.2 | 0 |  | Calhoun | Calhoun | Tier 4 |  |  |  | 8149, 8159 | Y | N |  |  | 13891 | 6166
6260 | Install 3rd 120MVAR capacitor bank at Jones Creek substation | Install capacitor bank #3 at Jones Creek substation (120MVAR). |  | Jones Creek | Velasco | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-11-30 |  | 138 | 0 | 0 | 0 | 0,120 | Brazoria | Brazoria | Tier 4 |  |  |  | 42543, 42540, 43360 | Y | N |  |  | 13988 | 6260
6354 | Acme Bestwall to Quanah 69 kV line: Rebuild 69 kV line | Rehab Acme Bestwall to Quanah 69 kV line | Company Contact and Schedule Update | Acme Bestwall | Quanah | Planned | 786 - 0971 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2718 | 2019-11-30 |  | 69 | 0 | 5.72 | 0 |  | Hardeman | Hardeman | Tier 4 |  |  |  | 6051, 6052 | Y | N |  |  | 14098 | 6354
6673A | Freeport - Bridge the Gap | Install capacitor bank #4 at Jones Creek substation (120MVAR). |  | Jones Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-11-30 |  | 138 | 0 | 0 | 0 | 0,120 | Brazoria |  | Tier 1 |  |  | 2017-12-12 | 42540 | Y | N |  | 0 | 48847 | 6673
6741 | Closner: Add New Distribution Station | Add New Closner Distribution Station |  | Azteca | South East Edinburg | Planned | 883 - 1061 | AEP | Tom Reynolds dnlyons@aep.com 918-599-2698 | 3670 | 2019-11-30 |  | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  | 8029, 8374, 8708 | Y | N |  |  | 14534 | 6741
7018 | Kleimann Substation Addition | Construct a 138-kV capable breakered substation, in a ring bus arrangement, between Columbus and Stafford Hill on circuit T544. The substation will provide transmission service to AEP load that will be transferred from Columbus Substation. Columbus Substation will be retired. ( Initially modelled at 69-kV until the completion of Glidden area upgrades project) |  | Columbus | Stafford Hill | Planned | 1018910 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018910 | 2019-11-30 |  | 138 | 0 | 0 | 0 |  | Colorado | Colorado | Tier 4 |  |  |  | 78111, 78115, 78107, 78520 | Y | N |  | 0 | 45505 | 7018
44385 | Victoria: Connect 138 kV Generator | Connect 138 kV Victoria City generator tie line into new breakers at Victoria. |  | Victoria | Leupold | Planned | 951 - 1129 | AEP | Glen Reed gareed@aep.com 918-599-2664 | 3715 | 2019-11-30 |  | 138 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  | 8174, 8172, 111363 | Y | N |  | 0 | 44386 | 44385
6261 | Velasco Cap Bank #3 | Install capacitor bank #3 at Velasco substation (120MVAR). |  | Velasco | SURFSI | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-11-30 12:00 |  | 138 | 0 | 0 | 0 | 0,120 | Brazoria | Brazoria | Tier 4 |  |  |  | 43363, 905282, 905283, 43360, 42510, 43315, 43361, 43362 | Y | N |  | 0 | 44948 | 6261
997 | Highway 32-Wimberley | Upgrade and convert the Highway 32 (7546) to Wimberley (7496) transmission line to 138-kV and 795 ACSR (220-MVA). |  | Highway 32 | Wimberley | Planned |  | PEC | Ryan Morlino ryan.morlino@peci.com 830-868-5166 |  | 2019-12-01 |  | 138 | 0 | 4 | 0 |  | Hays | Hays | Tier 4 |  |  |  | 7496, 7545, 7546 | Y | N |  |  | 8173 | 997
4323 | CPSE_Braunig to Brooks_MLSE | Upgrade terminal at Brooks and ensure a rating of 2000 A (minimum) at both Braunig and Brooks terminals |  | Braunig | Brooks | In-Service |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0669 | 2019-12-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5030, 5045 | Y | Y |  |  | 11875 | 4323
5558D | Proposed Substation |  |  |  |  | Planned |  | RYBRN | Charles Gibune 214-678-1192 |  | 2019-12-01 |  | 138 | 0 | 0 | 0 |  | Fannin |  | Tier 4 |  |  |  | 6807, 1835 | Y | N |  |  | 13288 | 5558
6537 | T-283 Quanex Switch Structure - Sunnyside | Rebuild transmission line to 138-kV capable 959.6 ACSS-TW conductor due to maintenance on old 69 KV wood pole line and the future conversion to 138 KV. |  | Quanex Switch Structure | Sunnyside | Under Construction |  | SBEC | Don Roberts droberts@sbec.org | WO# 17-6072 | 2019-12-01 |  | 69 | 0 | 9.75 | 0 |  | Austin | Austin | Tier 4 |  |  |  | 7660, 7664 | Y | N |  |  | 14277 | 6537
6744 | Picacho: Add Distribution | Add a new distribution bank at the existing Picacho station |  | Picacho |  | Planned |  | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 |  | 2019-12-01 |  | 138 | 0 | 0 | 0 |  | Uvalde |  | Tier 4 |  |  |  | 8684 | Y | N |  |  | 14537 | 6744
6755 | Stratton: Add Cap Bank | Add 14.4Mvar Cap Bank at Stratton 138kV Substation |  | Stratton |  | Planned | 903 - 1081 | AEP TCC | Daniel Lyons dnlyons@aep.com 918-599-2698 | 3687 | 2019-12-01 |  | 138 | 0 | 0 | 0 | 0,14.4 | Nueces |  | Tier 4 |  |  |  | 8514 | Y | N |  |  | 14548 | 6755
6789 | Wirtz to Johnson City to Mountain Top Rebuild to 138kV | Rebuild the Wirtz to Johnson City to Mountain Top 69kV Line and convert to 138kV. Convert Johnson City Substation to 138kV. |  | Wirtz | Mountain Top | Under Construction |  | PEC | Ryan Morlino ryan.morlino@peci.com 830-868-5166 |  | 2019-12-01 |  | 138 | 0 | 25 | 0 |  | Burnet | Blanco | Tier 4 | 2017-10-01 | 2017-12-01 |  | 7104, 7107, 7110, 7514, 7516, 7148, 7480 | Y | N |  |  | 14586 | 6789
48415A | TransPecos Capbank in TNMP West Texas System | Install 60 Mvar Capacitor bank at TNMP TransPecos Substation. |  | TransPecos (Bus #38377) | TransPecos (Bus #38377) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07919 | 2019-12-01 |  | 138 | 0 | 0 | 0 | 0,60 | Reeves | Reeves | Tier 4 |  |  |  | 38377 | Y |  |  | 0 | 48416 | 48415
48419 | Keystone Capbank in TNMP West Texas System | Transfer West Texas spare 69kV 10MVar capacitor bank to Kermit #2 Substation |  | Pyote (Bus #38000) | Kermit #2 (Bus #38250) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-12-01 |  | 69 | 0 | 0 | 0 | 0,10 | Ward | Winkler | Tier 4 |  |  |  | 38250 | Y |  |  | 0 | 48420 | 48419
49655 | Interconnects Arroyo to TNMP WTN | Interconnects Arroyo to TNMP WTN |  | TNMP Saddleback (Bus # 38058) | TNMP Arroyo (Bus # 38060) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-12-01 |  | 138 | 0.1 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38060, 38058 | Y |  |  | 0 | 49656 | 49655
43447 | T-283 Quanex Switch yard | LCRA Quanex Switch 69 KV lattice Tower with 3-way GOAB Switch to be replaced with switch yard. Installing three A-Frames with 2000 amp connected bus with 138 KV switches with interupterson each A-Frame plus a midpoint switch with interrupter. This is to be built in 2019 in conjuction with the Project Number 6536 |  | Quanex | Quanex switch | Planned |  | SBEC | James Jouett jjouett@sbec. |  | 2019-12-09 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 7660 | Y |  |  | 0 | 43448 | 43447
17TPIT0023 | Northwest Carrollton - Norwood 138 kV Line | Upgrade existing double-circuit Northwest Carrollton - Carrollton line section | Project Deferral | Northwest Carrollton | Carrollton | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4110-E | 2019-12-15 |  | 138 | 0 | 11.8 | 0 |  | Dallas | Dallas | Tier 4 |  | 2017-01-11 |  | 2362, 2363, 2409, 2535, 2536, 2537, 2540, 2541, 2542, 2545, 2550, 2551, 2552, 12552 | Y | N |  |  | 10433 | 3089
4759 | Riverton - Sand Lake 138 kV Line | Construct new 138 kV line | Construction schedule change | Riverton | Sand Lake | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8341 | 2019-12-15 |  | 138 | 25 | 0 | 0 |  | Reeves | Reeves | Tier 2 | 2016-02-01 | 2016-11-11 |  | 1011, 11097 | Y | N |  | 0 | 46055 | 4759
5500 | Lamar Blossom - Paris East Tap 138 kV Line | Construct new 138 kV line and ring bus | Project Deferral | Lamar Blossom | Paris East Tap | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4103 | 2019-12-15 |  | 138 | 10 | 0 | 0 |  | Lamar | Lamar | Tier 4 |  |  |  | 1769, 1770, 1771 | Y | N |  |  | 13240 | 5500
6276 | Northaven 138 kV Sw Sta | Rebuild the existing 138 kV Switching Station |  | Northaven Switch |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4243 | 2019-12-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 2646, 2649, 2650, 2655, 2656, 2657, 2658, 2659, 2596, 2597, 2651, 2652, 2660, 2661 | Y |  |  | 0 | 49532 | 6276
6833 | Vineyard 138 kV Switching Station | Establish new 138 kV switching station | Project Deferral | Vineyard Switch |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M3211 | 2019-12-15 |  | 138 | 4.2 | 0 | 0 |  | Tarrant | Tarrant | Tier 2 |  |  |  | 2025, 555, 648, 2014, 2015, 2021, 2023, 2031, 12012, 12040 | Y | N |  |  | 14635 | 6833
7111 | Quarry Field 138 kV Sw. Sta. | Quarry Field 138 kV Sw. Sta. |  | Quarry Field |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8412 | 2019-12-15 |  | 138 | 0 | 0 | 0 |  | Loving |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11189, 1093, 11091, 11094, 11100 | Y |  |  |  | 14946 | 7111
45533 | Palestine South - Palestine 138 kV Line | Upgrade the Palestine South - Palestine 138 kV Line to 1033 A |  | Palestine South | Palestine | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6100 | 2019-12-15 |  | 138 | 0 | 1.3 | 0 |  | Anderson | Anderson | Tier 4 |  |  |  | 3271, 3272 | Y | N |  | 0 | 45534 | 45533
48312 | Add Holstein Solar 345 kV POI | Add Holstein Solar 345 kV POI |  | Central Bluff 345 kV Switch | Central Bluff 345 kV Switch | Planned | R8471 | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2019-12-15 |  | 345 | 0.2 | 0 | 0 |  | Nolan | Nolan | Tier 4 |  |  |  | 11405, 11406 | Y |  |  | 0 | 48314 | 48312
48932 | Mabank Tap - Eustace Southeast Switch 138 kV Line Section | R6098 Trinidad Switch - 138 kV Line (Mabank Tap - Eustace Southeast Switch line section) |  | Mabank Tap | Eustace Southeast | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6098 | 2019-12-15 |  | 138 | 0 | 6.7 | 0 |  | Henderson | Henderson | Tier 4 |  |  |  | 3131, 6951, 29266 | Y |  |  | 0 | 48933 | 48932
48820 | Village Creek-Bowen 138 kV Tap | Village Creek-Bowen 138 kV Tap |  | Bowen Tap | Bowen | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5285 | 2019-12-15 12:00 |  | 138 | 1.2 | 1.2 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2219, 2233, 2248, 2232, 2250 | Y | N |  | 0 | 48821 | 48820
4802 | Lake Wichita Sw. Sta. Holliday 69 kV Line conversion | Convert existing 69 kV line to 138 kV operation |  | Lake Wichita Sw. Sta. | Holliday | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4009 | 2019-12-15 23:00 |  | 138 | 0 | 10.1 | 0 |  | Wichita | Archer | Tier 4 |  |  |  | 1447, 11527, 1423, 1424, 1446, 1449, 1527 | Y | N |  |  | 12408 | 4802
6776 | Sherry - Brookhollow Tap 138 kV Line Upgrade | Upgrade existing line |  | SHERRY | BROOKHOLLOW TAP | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5247 | 2019-12-16 |  | 138 | 0 | 16 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1919, 2134, 2138, 2142, 2143 | Y | N |  |  | 14570 | 6776
45493 | Rebuild Garden City Substation to Midkiff Switch 69 kV Line | Rebuild Garden City Substation to Midkiff Switch 69 kV Line |  | Garden City Substation | Midkiff Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8445 | 2019-12-16 |  | 69 |  | 16 | 0 |  | Glasscock | Glasscock | Tier 4 |  |  |  | 1217, 1218, 1225, 1333, 1352, 11218, 11226 | Y |  |  | 0 | 45497 | 45493
7114 | Rondo 138 kV Dynamic Reactive Devices | Rondo 138 kV Dynamic Reactive Devices |  | Quarry Field | Rondo | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8454 | 2019-12-17 |  | 138 | 0 | 0 | 0 | 250250 | Loving |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11173, 11189 | Y |  |  |  | 14949 | 7114
6787 | Utopia Susbtation Upgrade | Add two 138 kV Circuit Breakers to Line Terminals to be operated at 69 kV. | Accelerating Schedule | Utopia |  | Planned |  | BANDERA | Tyler Pansing t.pansing@banderaelectric.com 866-226-33726078 | 353985 | 2019-12-18 |  | 69 | 0 | 0 | 0 |  | Bandera |  | Tier 4 |  |  |  | 7428, 7439, 7440 | Y | N |  |  | 14581 | 6787
7112 | Quarry Field 138 kV Capacitors | Quarry Field 138 kV Capacitors |  | Quarry Field |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8453 | 2019-12-18 |  | 138 | 0 | 0 | 0 | 0,147.2 | Loving |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11189 | Y |  |  |  | 14947 | 7112
3894 | Fowlerton 345 station and 345/138 autotransformer | Add 345 kV bus and autotransformer |  | Fowlerton |  | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-12-20 |  | 345 | 0 | 0 | 600 |  | McMullen |  | Tier 4 |  |  |  | 5706, 5709, 5901, 80219, 5705 | Y | N |  | 2017 RTP moved project up to 2019. Still studying size needed and possible relocation of existing autotransformer. | 44403 | 3894
44381 | Causeway: Add 2nd Distribution Bank | Causeway: Add 2nd Distribution Bank |  | Causeway |  | Planned | 945 - 1123 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3709 | 2019-12-20 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8744 | Y | N |  | 0 | 44382 | 44381
16TPIT0050 | Northaven - Renner 138 kV Line | Upgrade existing line | Project Deferral | Northaven | Renner | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4108-E | 2019-12-30 |  | 138 | 0 | 8.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2356, 2357, 2596, 2597, 2613, 2614, 2615, 2616, 2657, 2658 | Y | N |  |  | 11845 | 3065
3776 | Big Lake to Powell Field Junction Tap: Rebuild 69 kV line | Rebuild Big Lake to Powell Field Junction Tap 69 kV line | Schedule and Cost Update | Big Lake | Powell Field Junction Tap | Planned | 667 - 0836 | AEP TNC | Michael Richardson mlforcum@aep.com 918-599-2674 | 2593 | 2019-12-30 |  | 69 | 0 | 11.7 | 0 |  | Reagan | Crockett | Tier 4 |  |  |  | 6533, 6546, 6547, 60395 | Y | N |  |  | 11196 | 3776
4065 | Add Graham Road Substation |  |  | BTU South | BTU Greens Prairie | Planned |  | COCS | Tony Mickalsky tmichalsky@cstx.gov 979-764-3438 |  | 2019-12-30 |  | 138 | 0 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32007, 32878, 32880 | Y |  |  |  | 11590 | 4065
4871 | Webster Breaker Addition | Install breaker at Webster 138kV substation to connect ring buses | - Delay in project schedule | Webster |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1134 | 2019-12-30 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 43505, 42651, 42970, 43082, 43500, 43507 | Y | N |  |  | 12481 | 4871
6578A | Rebuild Ckt.66 Katy-Freeman-Betka-Hockley | Rebuild Ckt.66 Freeman-Betka-Hockley to address clearance issues (Phase 1 of overall Katy to Hockley upgrades) |  | Freeman | Hockley | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45675, 45880 | Y |  |  |  | 14822 | 6578
6778 | Tri Corner - Watermill 345 kV Line | Upgrade existing line |  | Watermill | Tri Corner | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4226 | 2019-12-30 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 12427, 2427, 2432, 3123 | Y | N |  | 0 | 49535 | 6778
6985 | Gonzales - Harwood Transmission Line Overhaul | Overhaul and upgrade the 69-kV Gonzales - Harwood transmission line supporting circuit T542 with 138-kV capable structures, 795 ASCR Drake, and OPGW static. The planned T542 circuit rating will be (MVA): Rate A=28, Rate B=28, Rate C=28. |  | Luling | Hochheim | Planned | 1018965 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018965 | 2019-12-30 |  | 69 | 0 | 10 | 0 |  | Gonzales | Gonzales | Tier 4 |  |  |  | 7223, 78577 | Y | N |  |  | 14802 | 6985
44379 | Bonilla: New 345 kV Station | New Bonilla 345 kV Station to interconnect Raymond Wind |  | North Edinburg | Rio Hondo | Planned | 944 - 1122 | AEP | Glen Reed gareed@aep.com 918-599-2664 | 3708 | 2019-12-30 |  | 345 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8573, 8318, 8383 | Y | N |  | 0 | 44380 | 44379
17TPIT0019 | Forney - Royse 138 kV Line | Upgrade existing line |  | Forney | Royse | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4111-E | 2019-12-31 |  | 138 | 0 | 18.32 | 0 |  | Kaufman | Rockwall | Tier 4 |  |  |  | 2438, 2471, 2709, 2710, 2711, 2712 | Y | N |  |  | 11839 | 3086
3754 | Heartland to Yellowjacket: Build 69 kV line | Build new 69 kV line from Heartland to Yellowjacket | Company Contact, Schedule, and Cost Update | Heartland | Yellowjacket | Planned | 637 - 0806 | AEP TNC | Tom Reynolds mlforcum@aep.com 918-599-2674 | 2592 | 2019-12-31 |  | 69 | 32 | 0 | 0 |  | Mason | McCulloch | Tier 2 | 2014-01-23 | 2014-11-04 | 2014-11-17 | 6379, 60386, 6363, 6378, 6381, 6406 | Y | N |  |  | 12085 | 3754
3967 | Leander - Round Rock Transmission Line Addition | Construct a new 138kV transmission line from Leander to Ridgmar (new substation) to Spanish Oak (new substation) to Round Rock (approximately 13 miles) using bundled 795 ACSR Drake (446 MVA) conductor. | Substation name change from Hero Way to Ridgmar and Parmer to Spanish Oak | Leander | Round Rock | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1014352 | 2019-12-31 |  | 138 | 13 | 0 | 0 |  | Williamson | Williamson | Tier 2 | 2013-12-10 | 2014-05-22 | 2014-06-10 | 7367, 7368, 3668, 7525 | Y | N |  |  | 11463 | 3967
4426A | Aritek to Chorin to SR Bertron Ckt. 87 Upgrades | Upgrade 138kV Ckt.87 Alexander Island to CHORIN to increase thermal ratings. (Previously known as 'Ckt.87 ARITEK to CHORIN Upgrades') |  | ARITEK | CHORIN | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40120, 40320 | Y | N |  |  | 48257 | 4426
4519 | Heartland: Build 69 kV station | Construct new 69 kV ring bus between MCEC Brady and Katemcy | Company Contact and Schedule Update | Heartland |  | Planned | 637 - 0806 | AEP TNC | Tom Reynolds mlforcum@aep.com 918-599-2674 | 2609 | 2019-12-31 |  | 69 | 0 | 0 | 0 |  | McCulloch |  | Tier 2 | 2014-01-23 | 2014-11-04 | 2014-11-17 | 60386 | Y | N |  |  | 12091 | 4519
4716 | Tortuga: Build new 3 breaker 138 kV station | Construct new Tortuga 138 kV line and cut it into the Gila - Upriver (Koch) 138 kV line |  | Gila | Upriver (Koch) | Planned | 717 - 0899 | AEP | John Pulay dnlyons@aep.com 918-599-2698 | 3553 | 2019-12-31 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8168, 81680, 8467, 80136, 80141, 80260 | Y |  |  | New or Expand - New Telecom - Yes 345 kV CBs - 0 138 kV CBs - 3 69 kV CBs - 0 SCADA Additions - Yes | 12389 | 4716
5312 | Mitchell Bend - Rocky Creek 345 kV line | Upgrade existing line | Project Deferral | Mitchell Bend | Rocky Creek | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1736 | 2019-12-31 |  | 345 | 0 | 32.8 | 0 |  | Hood | Tarrant | Tier 4 |  | 2016-07-22 | 2016-08-22 | 1877, 1880 | Y |  |  |  | 12988 | 5312
5836 | Rebuild Shady Grove to Advance | Rebuild Shady Grove (Bus #515) to Advance (Bus #518) |  |  |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 16017 | 2019-12-31 |  | 69 | 0 | 11.34 | 0 |  | Parker | Parker | Tier 4 |  |  |  | 515, 518 | Y |  |  |  | 13578 | 5836
5838 | New Katz Auto to Benjamin 138 kV | Joint project with AEP to add autotransformer from Katz (bus# 774) to Katz8 (bus #798) and new line to Benjamin (bus # 6088) when AEP converts to 138 kV and builds line from the new Tardis switching station | [5 empty] | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 15016 | 2019-12-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 2 | 2016-02-03 | 2016-05-30 |  | 790, 798, 33798, 745, 774, 6088, 6087 | Y |  |  |  | 14961 | 5838
5965 | Benjamin Tap to Katz (BEC): Build new 138 kV line | Construct new 138 kV ring bus Tardis on the Munday to Paducah 138 kV line, rebuild existing Benjamin Tap to 138 kV, terminate into Tardis, convert Benjamin to 138 kV operation and build new 138 kV line from Benjamin to Katz (BEC) | Schedule Update | Benjamin Tap | Katz (BEC) | Planned | 769-0954 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2685 | 2019-12-31 |  | 138 | 17.7 | 9 | 0 |  | Knox | Knox | Tier 2 | 2016-02-03 | 2016-05-01 | 2016-05-01 | 6320 | Y | N |  |  | 13680 | 5965
5979 | Carver: Build new 138 kV station | Construct a new 138 kV ring bus station to replace the 138 kV portion of the Sonora 138/69 kV station | Schedule Update | Carver |  | Planned | 838 - 1022 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2678 | 2019-12-31 |  | 138 | 0 | 0 | 90 |  | Sutton |  | Tier 4 |  |  |  | 60412, 60433, 6500, 6513, 6515, 6562, 60440 | Y | N |  |  | 13694 | 5979
6002 | Gregory - Rincon 69 kV line | Rehab Gregory - Rincon 69 kV line |  | Gregory | Rincon | Planned | 833 - 1017 | AEP TCC | Jason Bryant dnlyons@aep.com 918-599-2698 | 3634 | 2019-12-31 |  | 69 | 0 | 4.34 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 8416, 8421 | Y | N |  |  | 13719 | 6002
6022 | Stamford to Haskell Tap 1 69 kV line: Rebuild 69 kV line | Rehab Stamford to Haskell Tap 1 69 kV line | Schedule Update | Stamford | Haskell Tap 1 | Planned | 786 - 0971 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2668 | 2019-12-31 |  | 69 | 0 | 12.22 | 0 |  | Jones | Haskell | Tier 4 |  |  |  | 6171, 6172 | Y | N |  |  | 13739 | 6022
6067 | Belknap to Rainey Crk 69 kV line: Rebld 69 kV line | Rehab Belknap to Rainey Creek 69 kV line | Schedule Update | Belknap | Rainey Creek | Planned | 786 - 0971 | AEP TNC | Jeremy Brazeal mlforcum@aep.com 918-599-2674 | 2675 | 2019-12-31 |  | 69 | 0 | 8.33 | 0 |  | Jones | Taylor | Tier 4 |  |  |  | 6215, 6220, 6221, 60409 | Y | N |  |  | 13788 | 6067
6075 | Veribest T to Harriett 69 kV line: Rebuild 69 kV line | Rehab Veribest Tap to Harriett CVEC REA 69 kV line | Schedule Update | Veribest Tap | Harriett CVEC REA | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2690 | 2019-12-31 |  | 69 | 0 | 8.4 | 0 |  | Tom Green | Tom Green | Tier 4 |  |  |  | 6409, 6412 | Y | N |  |  | 13797 | 6075
6111 | Carancahua - Point Comfort 69 kV Line | Rehab Carancahua - Point Comfort 69 kV Line |  | Carancahua | Point Comfort | Planned | 817 - 1001 | AEP TCC | Jason Bryant dnlyons@aep.com 918-599-2698 | 3613 | 2019-12-31 |  | 69 | 0 | 9.18 | 0 |  | Jackson | Calhoun | Tier 4 |  |  |  | 8132, 8555 | Y | N |  |  | 13837 | 6111
6118 | Port Isabel - Causeway 138 kV Line | Rehab Port Isabel - Causeway 138 kV Line |  | Port Isabel | Causeway | Planned | 826 - 1010 | AEP TCC | Rich Haley dnlyons@aep.com 918-599-2698 | 3626 | 2019-12-31 |  | 138 | 0 | 6.74 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8338, 8744 | Y | N |  |  | 13844 | 6118
6121 | Sunchase - South Padre Island 138 kV Line | Rebuild Sunchase - South Padre Island 138 kV Line |  | Sunchase | South Padre Island | Planned | 826 - 1010 | AEP TCC | Rich Haley dnlyons@aep.com 918-599-2698 | 3625 | 2019-12-31 |  | 138 | 0 | 3.33 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8335, 8917 | Y | N |  |  | 13847 | 6121
6202 | North Ella - Premont 69 kV Line | Rehab North Ella - Premont 69 kV Line |  | North Ella | Premont | Planned | 818 - 1002 | AEP TCC | Andrew Garlick dnlyons@aep.com 918-599-2698 | 3615 | 2019-12-31 |  | 69 | 0 | 10.7 | 0 |  | Jim Wells |  | Tier 4 |  |  |  | 8878, 8894 | Y | N |  |  | 13927 | 6202
6254 | Gomez to Fort Stockton Switch 69 kV line: Rebuild 69 kV line | Rehab TNMP Gomez to Fort Stockton Switch 69 kV line | Cost Update | Gomez | Fort Stockton Switch | Planned | 786 - 0971 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2700 | 2019-12-31 |  | 69 | 0 | 4.77 | 0 |  | Pecos | Reeves | Tier 4 |  |  |  | 6645, 38470 | Y | N |  |  | 13982 | 6254
6255A | Rebuild BEVO to Brundage to Big Wells 69 kV lines. | Rebuild 69 kV line with 795 ACSR on 138 kV and double circuit capable structures 2015- NERC assessment |  | Brundage | Big Wells | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-12-31 |  | 69 | 0 | 11.05 | 0 |  | Dimmit | Dimmit | Tier 4 |  |  |  | 5868, 5870 | Y | N |  | 0 | 45066 | 6255
6343 | Dressy Tap to Santa Anna Tap 69 kV line: Rebuild 69 kV line | Rehab Dressy Tap to Santa Anna Tap 69 kV line |  | Dressy Tap | Santa Anna Tap | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2720 | 2019-12-31 |  | 69 | 0 | 13.6 | 0 |  | Callahan | Coleman | Tier 4 |  |  |  | 6352, 6356 | Y | N |  |  | 14087 | 6343
6357 | Spence Pump to Robert Lee 69 kV line: Rebuild 69 kV line | Rehab Spence Pump to Robert Lee 69 kV line |  | Spence Pump | Robert Lee | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2715 | 2019-12-31 |  | 69 | 0 | 8.55 | 0 |  | Coke | Coke | Tier 4 |  |  |  | 6420, 6421 | Y | N |  |  | 14101 | 6357
6683 | Del Sol-Cabezon: Create Permanent Interconnection for Rio Br | Construct 2nd circuit on Cenizo-Del Sol 345 kV line from the Rio Bravo Windfarm Collector Station (Cabezon) to Del Sol. |  | Del Sol | Cabezon | Planned | 896 - 1074 | AEP | Rich Haley dnlyons@aep.com 918-599-2698 | 3680 | 2019-12-31 |  | 345 | 26.5 | 0 | 0 |  | Starr | Starr | Tier 4 |  |  |  | 80380, 80307, 80355, 80225, 161851, 161855 | Y | N |  |  | 14453 | 6683
7004 | CNP_18TPIT7004_New_Garth_Distribution_Sub | Construct service to new 138kV Garth distribution substation. Loop through Ckt.66 Baytown to Highlands tap |  | Baytown | Highlands | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 44630, 40170, 40172, 40790, 40812, 40390 | Y |  |  |  | 14825 | 7004
7007 | CNP_18TPIT7007_WAP_Reactor_Upgrades | Install (2) 5-Ohm Reactors at WA Parish as a fault duty upgrade |  | WAP | WAP | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 |  | 138 | 0 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 4 |  |  |  | 44010, 44015, 44170, 44173, 44651, 44671, 44172, 110013, 110014 | Y |  |  |  | 14829 | 7007
7153 | Fort Stockton Plant to Solstice: Raise Structures on 138 kV | Raise Structures on the Fort Stockton Plant to Solstice 138 kV line | Company Contact Update | Fort Stockton Plant | Solstice | Planned | 923 - 1101 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2820 | 2019-12-31 |  | 138 | 0 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6630, 60385 | Y | N |  |  | 14992 | 7153
43245 | HOPSON - New 138kV Substation | Construct service to new 138kV HOPSON customer-owned substation. Loop through Ckt.84 WARVUE to Cedar Bayou |  | HOPSON | WARVUE/ Cedar Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  | 41690, 40012, 41700 | Y |  |  |  | 43246 | 43245
43458 | Heights Cap Bank #1 | Relocate Harrisburg cap bank #1 to Heights substation and reduce size to 7.2 MVAR |  | Heights |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 |  | 69 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 40800, 47680 | Y | N |  | 0 | 43459 | 43458
43462 | Northside Distribution Substation Expansion | Install third new 138/12 kV, 100 MVA distribution transformer |  | Northside | Northside | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47711, 47712 | Y |  |  | 0 | 43463 | 43462
4426B | Aritek to Chorin to SR Bertron Ckt. 87 Upgrades | Upgrade 138kV Ckt.87 Alexander Island to SR Bertron to increase thermal ratings. |  | Alexander Island | SR Bertron | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | Y | N |  | Cost included in project 4426A | 48256 | 4426
6673B | Freeport - Bridge the Gap | Install 1st 138kV Automatically Switchable Capacitor Bank (Cap Bank #5 - 140 MVAR) at Jones Creek Substation |  | Jones Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 00:01 |  | 138 | 0 | 0 | 0 | 0,140 | Brazoria |  | Tier 1 |  |  | 2017-12-12 | 42535, 42540 | Y | N |  | 0 | 48848 | 6673
6673E | Freeport - Bridge the Gap | Install 2nd 138kV Automatically Switchable Capacitor Bank (Cap Bank #6 - 140 MVAR) at Jones Creek Substation |  | Jones Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-12-31 00:02 |  | 138 | 0 | 0 | 0 | 0,140 | Brazoria |  | Tier 1 |  |  | 2017-12-12 | 42536, 42540 | Y | N |  | 0 | 48849 | 6673
44802 | Tinsley: Build 138 kV temporary tap | Build new Tinsley 138 kV temporary tap on the Carver to Maxwell 138 kV line | Schedule Update | Tinsley |  | Planned | 956 - 1134 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2760 | 2019-12-31 01:00 |  | 138 | 0 | 0 | 0 |  | Sutton |  | Tier 4 |  |  |  | 60440, 6515, 8259, 60412 | Y | N |  | 0 | 44803 | 44802
45421 | McElroy to Sage: Rebuild 69 kV line | Build new Ollin 138 kV station with a 138/69 kV auto; partial build, rebuild, and conversion to 138 kV of Ollin to LCRA Crane; and rebuild McElroy to Sage | Company Contact and Schedule Update | McElroy | Sage | Planned | 939 - 1117 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2768 | 2019-12-31 01:00 |  | 69 | 0 | 1.99 | 0 |  | Crane | Crane | Tier 4 |  |  |  | 6604, 6607 | Y | N |  | 0 | 45422 | 45421
5499 | Everman - Cedar Hill Sw. Sta. 345 kV Line | Upgrade existing Everman - Cedar Hill Sw. Sta. 345 kV Line | Construction schedule change | Everman | Cedar Hill | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5260 | 2019-12-31 11:52 |  | 345 | 0 | 39.14 | 0 |  | Tarrant | Dallas | Tier 4 | 2016-03-10 | 2016-07-22 |  | 1885, 1886, 1931, 1932, 2420 | Y | N |  |  | 13239 | 5499
4504 | BRYN_4504_Rayburn_Rodgers_Upgrade | Reconductor Rayburn to Rodgers with 1033ACSR |  | 32861 | 32849 | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2020-01-01 |  | 69 | 0 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32861, 32849, 32872 | Y |  |  |  | 14761 | 4504
5045 | BRYN_5045_Rodgers_Sub | Construct new Rodgers Substation and remove Nall Lane Substation |  |  |  | Planned |  | BRYN | James Tanneberger jtanneberger@btutilities.com 979-821-5763 |  | 2020-01-01 |  | 69 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32849, 32872, 32874, 32877 | Y |  |  | 0 | 44459 | 5045
6938 | Leonard Road Substation 69 | Construct Leonard Rd Substation with Dual Voltage Transformer. Will be served at 69kV until completion of Smetana to Leonard Rd 138kV line. | [5 empty] | BRYN | James Tanneberger jtanneberger@btutilities.com 979-821-5763 |  | 2020-01-01 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 32851, 32864, 32850 | Y |  |  |  | 14758 | 6938
7036 | Forest Grove Sw. Sta. to Eustace SE 138 kV line section | Rebuild the Forest Grove Sw. Sta. to Eustace SE 138 kV line section |  | Forest Grove Sw. Sta. | Eustace SE | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6014 | 2020-01-01 |  | 138 | 0 | 4.3 | 0 |  | Henderson | Henderson | Tier 4 |  |  |  | 3131, 6951 | Y | N |  |  | 14858 | 7036
47422 | Homestead Substation Addition | Construct a new 138-kV Homestead substation.The Homestead substation will be located approximately ½ mile from the existing Tarbush substation (owned by TNMP) and will include three-PWTs with RGEC distribution (express feeders) to the load. |  | Homestead | Homestead | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2020-01-01 |  | 138 | 0 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 7868, 38295 | Y |  |  | 0 | 47423 | 47422
4489 | Eagle Pass to Escondido: Rebuild 138kV line | Rebuild Eagle Pass to Escondido Circuit #1 |  | Eagle Pass | Escondido | Under Construction | 708 - 0878 | AEP TCC | John Pulay dnlyons@aep.com 918-599-2664 | 2902 | 2020-01-01 21:00 |  | 138 | 0 | 1.5 | 0 |  | Maverick | Maverick | Tier 4 |  |  |  | 8270, 8260 | Y | N |  |  | 12058 | 4489
07TPIT0060 | Howard Lane to Techridge Reconductor | The project re-conductors Circuit 1004 (Techridge to Howard Lane) using 795 ACSS Drake conductors to increase the capacity to 3000 Amp. |  | Howard Lane | Techridge | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | PLAN_117_P067 PLAN_117_P194 | 2020-01-03 |  | 138 | 0 | 1.72 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9191, 9217 | Y | N |  |  | 8204 | 1028
7077 | Horse Crossing - Rio Pecos Transmission Line Addition | Construct a new 138-kV transmission line to a new radially connected generator-serving substation called Horse Crossing from Rio Pecos using double 795 26/7 ACSR Drake OPGW static. The planned transmission circuit rating will be (MVA): Rate A=439, Rate B=448, Rate C=448. |  | Horse Crossing | Rio Pecos | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018600 | 2020-01-20 |  | 138 | 0.9 | 0 | 0 |  | Crane | Crockett | Tier 4 |  |  |  | 76601, 76602, 6601 | Y | N |  |  | 14909 | 7077
5914 | Crosswinds Substation Addition | LCRA TSC will construct a new three breaker ring bus substation to provide transmission service to PEC's planned distribution substation facility. |  | Turnersville | Goforth | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017349 | 2020-01-28 |  | 138 | 0 | 0 | 0 |  | Hays |  | Tier 4 |  |  |  | 7503, 7500, 7501 | Y | N |  |  | 13622 | 5914
5956 | Young: Build new distribution station | Young: Build new distribution station |  | Polk Avenue | Pharr | Planned | 804 - 0989 | AEP | Bill Clarke dnlyons@aep.com 918-599-2698 | 3593 | 2020-01-31 |  | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  | 8030, 8372, 8373 | Y | N |  |  | 13669 | 5956
6352 | Crckett Hghts to Sonora Atlntic 69 kV line: Rbld 69 kV line | Rehab Crockett Heights to Sonora Atlantic 69 kV line |  | Crockett Heights | Sonora Atlantic | Planned | 786 - 0971 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2706 | 2020-01-31 |  | 69 | 0 | 16.8 | 0 |  | Crockett | Sutton | Tier 4 |  |  |  | 6511, 6552 | Y | N |  |  | 14096 | 6352
6851 | Saragosa to Solstice: Rebuild 138 kV line | Build Saragosa to Solstice 138 kV line, retire existing Barrilla Junction to Saragosa 69 kV line, add new auto and capacitor bank at Saragosa. | Company Contact Update | Saragosa | Solstice | Planned | 922 - 1100 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2736 | 2020-01-31 |  | 138 | 0 | 19 | 90 | 0,7.2 | Pecos | Ward | Tier 4 |  |  |  | 60716, 6649, 6650, 6652, 60385, 6653 | Y | N |  |  | 14659 | 6851
43485 | Cryo: Build 138 kV station | Build new Cryo 138 kV station, build Cryo to Saragosa new 138 kV line, add capacitor banks at Cryo | Company Contact Update | Cryo |  | Planned | 926 - 1104 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2740 | 2020-01-31 |  | 138 | 0 | 0 | 0 | 0,28.8 | Reeves |  | Tier 4 |  |  |  | 60721, 60716 | Y | N |  | 0 | 43486 | 43485
43487 | Cryo to Saragosa: Build 138 kV line | Build new Cryo 138 kV station, build Cryo to Saragosa new 138 kV line, add capacitor banks at Cryo | Company Contact Update | Cryo | Saragosa | Planned | 926 - 1104 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2739 | 2020-01-31 |  | 138 | 5 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 60721, 60716 | Y | N |  | 0 | 43488 | 43487
07TPIT0050 | Dunlap to Techridge 138kV Circuit Relocation | This project will reroute the existing Ckt 975 Dunlap-Techridge from near the intersection of Howard Lane and Dessau Road to the Techridge substation. The reroute will use 3000 amp bundled 795 ACSS Drake conductor. |  | Dunlap Substation | Techridge Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | PLAN_117_P071 | 2020-02-01 |  | 138 | 0 | 2.7 | 0 |  | Travis | Travis | Tier 2 | 2009-01-26 | 2009-07-21 |  | 9045, 9190 | Y | N |  |  | 8189 | 1013
44181 | 138kV Cooper Creek - Arco Line Reconstruction |  |  |  |  | Planned |  | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2020-02-01 |  | 138 | 0 | 1.62 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 906, 923 | Y | N |  | Reconstruct 138kV Cooper Creek to Arco | 44182 | 44181
44942 | ApolloToLookoutLineUpgrade | Apollo to Lookout 138kV line upgrade to Cumberland conductor |  | Apollo | Lookout | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2020-02-01 |  | 138 | 0 | 2.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 802, 828 | Y | N |  | 0 | 44943 | 44942
48750 | Gibbs: Construct New 138 kV Station | Gibbs: Construct New 138 kV Station |  | McCampbell | Portland | Planned | 846 - 1030 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3642 | 2020-02-01 |  | 138 | 0 | 0 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  | 8173, 8414, 80470 | Y | N |  | 0 | 48751 | 48750
4505 | BRYN_4505_Smetana_Sub | Construction of a new Smetana Substation at 138kV |  |  |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2020-02-02 |  | 138 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32850, 32853, 32868, 32864 | Y |  |  |  | 12077 | 4505
4576 | BRYN_4576_Smetana_to_Steele_Store | Construct New 138kV line (Bundled 1033 ACSR - Curlew) to new Steele Store substation as part of the reliability project to loop in Steele Store |  | 32853 | 32852 | Planned |  | BRYN | James Tanneberger jtanneberger@btutilities.com 979-821-5763 |  | 2020-02-02 |  | 138 | 4.5 | 0 | 0 |  | Brazos | Burleson | Tier 4 | 2015-10-09 | 2015-11-06 |  | 32852, 32853 | Y |  |  |  | 12158 | 4576
6074 | Concho to Veribest Tap 69 kV line: Rebuild 69 kV line | Rehab Concho to Veribest Tap 69 kV line | Schedule Update | Concho | Veribest Tap | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2689 | 2020-02-28 |  | 69 | 0 | 1.86 | 0 |  | Tom Green | Tom Green | Tier 4 |  |  |  | 6409, 6450 | Y | N |  |  | 13796 | 6074
6083 | Wolfgang: Build 69 kV station | Construct new 69 kV ring bus at Wolfgang | Schedule Update | Wolfgang |  | Planned | 842 - 1026 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2682 | 2020-02-28 |  | 69 | 0 | 0 | 0 |  | Kent |  | Tier 4 |  |  |  | 6162 | Y | N |  |  | 13807 | 6083
6981 | Highway 36 Substation Upgrade | Upgrade the Highway 36 138-kV substation bus to a breaker and a half configuration. |  | Highway 36 |  | Planned | 1019094 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019094 | 2020-02-28 |  | 138 | 0 | 0 | 0 |  | Washington |  | Tier 4 |  |  |  | 7291 | Y | N |  |  | 14798 | 6981
6673C | Freeport - Bridge the Gap | Loop Ckt.27 STP-DOW into Jones Creek to create new Ckt.27 Jones Creek to STP |  | Jones Creek | STP | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-02-28 00:03 |  | 345 | 0.18 | 0 | 0 |  | Brazoria | Matagorda | Tier 1 |  |  | 2017-12-12 | 42400, 42500, 42530 | Y | N |  | 0 | 48850 | 6673
6673F | Freeport - Bridge the Gap | Install 3rd 800MVA autotransformer (A3) at Jones Creek substation |  | Jones Creek |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-02-28 00:04 |  | 345 | 0 | 0 | 800 |  | Brazoria |  | Tier 1 |  |  | 2017-12-12 | 49038, 42530, 42540 | Y | N |  | 0 | 48851 | 6673
6673G | Freeport - Bridge the Gap | Install 7-Ohm in-series reactors at Jones Creek substation on Ckts.18 & 27 Jones Creek to STP |  | Jones Creek | STP | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-02-28 00:05 |  | 345 | 0 | 0 | 0 |  | Brazoria | Matagorda | Tier 1 |  |  | 2017-12-12 | 47531, 47532, 5915, 42400, 42530 | Y | N |  | 0 | 48852 | 6673
6673D | Freeport - Bridge the Gap | Loop Ckt.27 STP-DOW into Jones Creek to create new Ckt.27 Jones Creek to DOW |  | Jones Creek | DOW | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-02-28 00:06 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 1 |  |  | 2017-12-12 | 42500, 42530 | Y | N |  | Cost included in Phase C. | 48853 | 6673
6687 | Rebuild Rio Hondo to East Rio Hondo | Rebuild the 138 kV line from Rio Hondo to East Rio Hondo. |  | Rio Hondo | East Rio Hondo | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-03-01 |  | 138 | 0 | 8.19 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 5764, 8319 | Y | N |  |  | 14458 | 6687
6930 | New Paloma Substation | Adds new station and short line from Midstream |  | Midstream | Paloma | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-03-01 |  | 138 | 0.9 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 5644, 5643 | Y | N |  |  | 14749 | 6930
44395 | Dupont SW: Connect 138 kV Gen Tie Line | Connect 138 kV Victoria Port Generation Tie Line into Dupont SW |  | Dupont SW | Rupley | Planned | 950 - 1128 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3714 | 2020-03-01 |  | 138 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  | 88142, 88143, 8143, 8172, 111343 | Y | N |  | 0 | 44396 | 44395
44848 | Coriolis 138 kV Station | New Coriolis 138 kV Station |  | Big Three | Vistron | Planned | 925 - 1103 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3702 | 2020-03-01 |  | 138 | 0 | 0 | 0 |  | Victoria | Calhoun | Tier 4 |  |  |  | 8658, 8145, 8911 | Y | N |  | 0 | 44849 | 44848
45116 | TNMP Elm First Substation | New Substation - Elm First |  | IH20 (Bus #38045) | Reeves Tap (Bus #38114) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2020-03-01 |  | 138 | 0 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38049, 38090, 38040, 38045, 38114 | Y |  |  | 0 | 48424 | 45116
48407 | Chaparrosa: Construct New 138 kV Box Bay | Chaparrosa: Construct New 138 kV Box Bay |  | La Pryor | Turtle Creek | Planned | 929 - 1107 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3705 | 2020-03-01 |  | 69 | 0 | 0 | 0 |  | Zavala | Zapata | Tier 4 |  |  |  | 8284, 88284, 8243, 8672, 7867 | Y | N |  | 0 | 48408 | 48407
45344 | Pirate: Build 69 kV Station | Pirate: Build 69 kV Station on Beeville - Sinton Line |  | Skidmore | Sinton | Planned | 882 - 1068 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3669 | 2020-03-02 |  | 69 | 0 | 0 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  | 8652, 8405, 8413 | Y | N |  | 0 | 45345 | 45344
6782 | Bandera Substation Upgrade | Remove one 138/69 kV Autotransformer rated for 44.8 MVA and remove one 138 kV Circuit Breaker and convert T281 Leakey to Utopia to 138 kV operation. |  | Bandera |  | Conceptual |  | BANDERA | Tyler Pansing t.pansing@banderaelectric.com 866-226-33726078 | 353985 | 2020-03-17 |  | 138 | 0 | 0 | 0 |  | Bandera |  | Tier 4 |  |  |  | 7426 | N | N |  |  | 14576 | 6782
7159 | Ajo-Stella: Create Permanent Interconnection for Stella WF | Convert Stella Windfarm temporary tap interconnection to a permanent interconnection. ETT will construct an extension of the gen tie-line by adding a second circuit on the Ajo-Zorillo line, therefore creating a dedicated circuit terminating at the Ajo station. |  | Ajo | Stella | Planned | 894 - 1072 | ETT | Teresa Trotman dnlyons@aep.com 918-599-2698 | 3678 | 2020-03-17 |  | 345 | 0 | 7.85 | 0 |  | Kenedy | Kenedy | Tier 4 |  |  |  | 80070, 80071, 80076, 161591, 161953 | Y | N |  |  | 15000 | 7159
6785 | Leakey Substation Upgrade | Replace 69/25 kV and 69/12.5 kV Power Transformers with dual-rated 138-69/25-12.5 kV Power Transformers and add one 138 kV Circuit Breaker to be operated at 69 kV. | Accelerating Schedule | Leakey |  | Planned |  | BANDERA | Tyler Pansing t.pansing@banderaelectric.com 866-226-33726078 | 353985 | 2020-03-18 |  | 69 | 0 | 0 | 0 |  | Bandera |  | Tier 4 |  |  |  | 7426 | Y | N |  |  | 14579 | 6785
44870 | Charlotte 69 kV Station | Charlotte 69 kV Station: Add Cap Bank |  | Charlotte | - | Planned | 976 - 1154 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3734 | 2020-03-30 |  | 69 | 0 | 0 | 0 | 0,7.2 | Atascosa |  | Tier 3 |  |  |  | 8206 | Y | N |  | 0 | 44871 | 44870
45340 | Lemay: Build 138 kV Box Bay | Lemay: Build 138 kV Box Bay on North Laredo SS - Reveille Line |  | Encinal | Reveille | Planned |  | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 |  | 2020-03-30 |  | 138 | 0 | 0 | 0 |  | La Salle | La Salle | Tier 4 |  |  |  | 8627, 88627, 8612, 8619 | Y | N |  | 0 | 45341 | 45340
45032 | Brant: Build 69 kV station | Construct new 69 kV box bay on the Rock Springs to Sonora 69 kV line | Schedule and Cost Update | Brant |  | Planned | 977 - 1155 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2762 | 2020-03-30 01:00 |  | 69 | 0 | 0 | 0 |  | Sutton |  | Tier 4 |  |  |  | 60438, 6570, 8239 | Y | N |  | 0 | 45033 | 45032
4464B | Comal to Loop337 to GPI switchyard Transmission Upgrades | Upgrade/Replace underrated switches to 3000 Amp Switches. Replace and increase fault interrupting rating of breakers 430, 440, 3370, 3380, 5680, 5690, 5700, 2970, 5870 to 63kA. Replace and upgrade CS2965 and CS2975 to 3000 Amp 40kA. Replace and upgrade CS5395 and CS5405 to 40kA. | Switches may be dynamically rated during Winter peak conditions. | Comal | Marion | Planned |  | NBU | Gregory Thomas gthomas@nbutexas.com 830-608-8953 |  | 2020-03-31 |  | 138 | 0 | 0 | 0 |  | Comal | Comal | Tier 4 |  |  |  | 7176, 7456, 7459 | Y | N |  |  | 12381 | 4464
5218A | San Miguel 345/138 kV autotransformer replacements | Replace T1 300 MVA auto with much larger auto and open T2 for construction |  | San Miguel |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-03-31 |  | 345 | 0 | 0 | 672 |  | Atascosa |  | Tier 4 |  |  |  | 5908, 5909, 5901, 5902 | Y | N |  | Delayed from 2018 to 2019 in the 2016 RTP. | 45090 | 5218
5648 | Hamilton Road to Picacho #1, rebuild 138 kV line | Rebuild Hamilton Road to Picacho 138 kV line ckt #1 |  | Hamilton Road | Del Rio | Under Construction | 869-1050 | AEP | Jeremy Brazeal dnlyons@aep.com 918-599-2698 | 3659 | 2020-03-31 |  | 138 | 0 | 8.7 | 0 |  | Val Verde | Val Verde | Tier 4 |  |  |  | 8255, 8584 | Y | N |  |  | 13382 | 5648
5964 | Belknap: Build new 69 kV station | Construct new 69 kV ring bus on the Albany to Rainey Creek 69 kV line, remove existing Spillway SW, reterminate Albany to Rainey Creek and Ft Phantom Pump to Onyx lines into Belknap | Schedule and Cost Update | Belknap |  | Planned | 843 - 1027 | AEP TNC | Jeremy Brazeal mlforcum@aep.com 918-599-2674 | 2684 | 2020-03-31 |  | 69 | 0 | 0 | 0 |  | Jones |  | Tier 4 |  |  |  | 6211, 60409, 6178, 6219, 6220, 6243 | Y | N |  |  | 13679 | 5964
5967 | Burma: Build new 69 kV station | Construct a new 69 kV station near the exsiting Grape Creek tap and reterminate the College Hills to Sterling City and Grape Creek to North San Angelo 69 kV lines into Burma | Company Contact and Schedule Update | Burma |  | Planned | 845 - 1029 | AEP TNC | John Pulay mlforcum@aep.com 918-599-2674 | 2688 | 2020-03-31 |  | 69 | 0 | 0 | 0 |  | Tom Green |  | Tier 4 |  |  |  | 6416, 60411, 6437, 6460, 6468 | Y | N |  |  | 13682 | 5967
6114 | La Pryor - Uvalde 69 kV Line | Rehab La Pryor - Uvalde 69 kV Line |  | La Pryor | Uvalde | Planned | 810 - 0995 | AEP | James Nivens dnlyons@aep.com 918-599-2698 | 3600 | 2020-03-31 |  | 69 | 0 | 17.603 | 0 |  | Zavala | Uvalde | Tier 4 |  |  |  | 8231, 8672 | Y | N |  |  | 13840 | 6114
6117 | Pleasanton - Coy City Tap 69 kV Line | Rehab Pleasanton - Coy City Tap 69 kV Line |  | Pleasanton | Coy City Tap | Planned | 814 - 0998 | AEP | James Nivens dnlyons@aep.com 918-599-2698 | 3604 | 2020-03-31 |  | 69 | 0 | 16.79 | 0 |  | Atascosa |  | Tier 4 |  |  |  | 8200, 8600 | Y | N |  |  | 13843 | 6117
6203 | Premont - Falfurrias 69 kV Line | Rehab Premont - Falfurrias 69 kV Line |  | Premont | Falfurrias | Planned | 818 - 1002 | AEP TCC | Andrew Garlick dnlyons@aep.com 918-599-2698 | 3616 | 2020-03-31 |  | 69 | 0 | 12.25 | 0 |  | Jim Wells | Brooks | Tier 4 |  |  |  | 8508, 8894 | Y | N |  |  | 13928 | 6203
6822 | Figaro: Build new 345 kV station | Interconnect Amadeus wind farm on the Clear Crossing to Dermott 345 kV line | Company Contact, Schedule, and Cost Update | Figaro |  | Planned | 907 - 1085 | ETT | Jake Tucker mlforcum@aep.com 918-599-2674 | 2731 | 2020-03-31 |  | 345 | 0 | 0 | 0 |  | Fisher |  | Tier 4 |  |  |  | 60715, 11305, 60706, 60704 | Y | N |  |  | 14623 | 6822
44940 | Henne and TXI Switch Upgrades/Replacement | Replace and increase fault interrupting rating of breaker 5870 to 63kA, and its continuous rating to 3,000 Amp. Replace CS 5395 and CS 5405 to 40kA units. |  | Henne | TXI | Planned |  | NBU | Gregory Thomas gthomas@nbutexas.com 830-608-8953 |  | 2020-03-31 |  | 138 | 0 | 0 | 0 |  | Comal | Comal | Tier 4 |  |  |  | 7174 | Y | N |  | 0 | 44941 | 44940
45508 | Pig Creek Build 138 kV terminal | Interconnect Taygete solar farm on the Solstice to Yucca Drive 138 kV line | Company Contact and Schedule Update | Pig Creek |  | Planned | 981 - 1159 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2822 | 2020-03-31 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60393 | Y | N |  | 0 | 45509 | 45508
49562 | Pig Creek: Build 138 kV terminal | Interconnect Taygete II solar farm on the Solstice to Yucca Drive 138 kV line | NEW | Pig Creek |  | Planned | 1020 - 1198 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2782 | 2020-03-31 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60393 | Y | N |  | 0 | 49563 | 49562
49574 | Tesla: Build 345 kV terminal | Interconnect Misae II solar farm at Tesla | NEW | Tesla |  | Planned | 1023 - 1201 | ETT | Michael Forcum mlforcum@aep.com 918-599-2674 | 2785 | 2020-03-31 |  | 345 | 0 | 0 | 0 |  | Childress |  | Tier 4 |  |  |  | 60501 | Y | N |  | 0 | 49575 | 49574
44426 | Foxtail: Add 345 kV reactor | Add new 345 kV reactor at Foxtail | Company Contact and Schedule Update | Foxtail |  | Planned | 940 - 1118 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2754 | 2020-03-31 01:00 |  | 345 | 0 | 0 | 0 | -50,0 | Baylor |  | Tier 4 |  |  |  | 6076 | Y | N |  | 0 | 44427 | 44426
10TPIT0025 | Bluff Spring 138kV substation | Establish 138kV Bluff Spring substation with (2) 30MVA transformers and will cut into existing Ckt 987 (Lytton Springs to Slaughter Lane). | Changing name of substation from Rinard Creek to Bluff Springs | Lytton Springs substation | Bluff Springs Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | PLAN_117_P151 PLAN_117_P152 | 2020-04-01 |  | 138 | 0.1 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9262, 9075, 9267 | Y | N |  |  | 8206 | 1030
6716 | Navigation Substation Addition | Construct a new load-serving substation named Navigation off the Citgo N. Oak Park to Valero (T436) transmission line. |  | Citgo N. Oak Park | Valero | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019006 | 2020-04-01 |  | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 78460, 8426, 8466 | Y | N |  |  | 14499 | 6716
44852 | Kelvin 138 kV Station | New Kelvin 138 kV Station |  | La Palma | Rio Hondo | Planned | 965 - 1143 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3723 | 2020-04-01 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8640, 88640, 8314, 8319 | Y | N |  | 0 | 44853 | 44852
6783 | Utopia-Tarpley Re-Termination | Re-Termination of existing T281 Transmission Line, related to reconfiguration of Utopia and Tarpley Substations. | Change in schedule | Utopia | Tarpley | Planned |  | BANDERA | Tyler Pansing t.pansing@banderaelectric.com 866-226-33726078 | 353985 | 2020-04-03 |  | 69 | 0 | 0.25 | 0 |  | Bandera | Bandera | Tier 4 |  |  |  | 7428, 7440 | Y | N |  |  | 14577 | 6783
5276 | Flatonia - Hallettsville Transmission Line Upgrade | Upgrade T132 Hallettsville to Flatonia (18.7 mi) 138-kV transmission line to a minimum rating of 380 MVA with OPGW. |  | Flatonia | Hallettsville | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016188 | 2020-04-24 |  | 138 | 0 | 18.7 | 0 |  | Fayette | Lavaca | Tier 4 |  |  |  | 7246, 7248 | Y | N |  |  | 12952 | 5276
4530 | Heartland to South Brady Tap: Rebuild existing & build new | Construct a new 69 kV line from Heartland to South Brady Tap and rebuild the existing line from Heartland to South Brady Tap | Company Contact and Schedule Update | Heartland |  | Planned | 637 - 0806 | AEP TNC | Tom Reynolds mlforcum@aep.com 918-599-2674 | 2610 | 2020-04-30 |  | 69 | 1.11 | 1.11 | 0 |  | McCulloch | McCulloch | Tier 2 | 2014-01-23 | 2014-11-04 | 2014-11-17 | 6379, 60386, 6378, 6381, 6406 | Y | N |  |  | 12105 | 4530
6065 | Abilene Northwest to Onyx 69 kV line: Rebuild 69 kV line | Rehab Abilene Northwest to Onyx 69 kV line | Schedule Update | Abilene Northwest | Onyx | Under Construction | 786 - 0971 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2673 | 2020-04-30 |  | 69 | 0 | 3.61 | 0 |  | Taylor | Jones | Tier 4 |  |  |  | 6224, 6236 | Y | N |  |  | 13785 | 6065
6345 | Yellowjckt to Menard Phillips T 69 kV line: Rebld 69 kV line | Rehab Yellowjacket to Menard Phillips Tap 69 kV line | Cost Update | Yellowjacket | Menard Phillips Tap | Planned | 786 - 0971 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2711 | 2020-04-30 |  | 69 | 0 | 15.3 | 0 |  | Menard | Kimble | Tier 4 |  |  |  | 6363, 6401 | Y | N |  |  | 14089 | 6345
6347 | Ballinger to Paint Rock 69 kV line: Rebuild 69 kV line | Rehab Ballinger to Paint Rock 69 kV line | Schedule Update | Ballinger | Paint Rock | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2708 | 2020-04-30 |  | 69 | 0 | 14.6 | 0 |  | Runnels | Concho | Tier 4 |  |  |  | 6338, 6369 | Y | N |  |  | 14091 | 6347
6353 | Kirkland to Acme Best Wall 69 kV line: Rebuild 69 kV line | Rehab Kirkland to Acme Best Wall 69 kV line | Company Contact and Schedule Update | Kirkland | Acme Best Wall | Planned | 786 - 0971 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2717 | 2020-04-30 |  | 69 | 0 | 14.6 | 0 |  | Childress | Hardeman | Tier 4 |  |  |  | 6052, 6053 | Y | N |  |  | 14097 | 6353
6569 | Aspermont: Replace the 138/69 kV autotransformer | Replace the 138/69 kV autotransformer at Aspermont with a 130 MVA autotransformer | Company Contact and Schedule Update | Aspermont |  | Planned | 839 - 1023 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2817 | 2020-04-30 |  | 138 | 0 | 0 | 130 |  | Stonwall |  | Tier 4 |  |  |  | 6156, 6158 | Y | N |  |  | 14320 | 6569
44872 | Asherton 138 kV Station | Add breaker at Asherton 138 kV Station to Accommodate Shakes Solar |  | Asherton | - | Planned | 966 - 1144 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3724 | 2020-04-30 |  | 138 | 0 | 0 | 0 |  | Dimmit |  | Tier 4 |  |  |  | 8283 | Y | N |  | 0 | 44873 | 44872
48109 | Dolan Creek: Construct 138 kV Box Bay | Dolan Creek: Construct 138 kV Box Bay |  | Whiting | Cauthorn | Planned | 930 - 1108 | AEP TCC/PEC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3706 | 2020-04-30 |  | 138 | 0 | 0 | 0 |  | Val Verde | Sutton | Tier 4 |  |  |  | 8991, 88991, 8259, 8261, 72194 | Y | Y |  | 0 | 48147 | 48109
44812 | Coulomb: Build new 345 kV station | Interconnect Vera wind farm on the Clear Crossing to Edith Clarke 345 kV line | Company Contact Update | Coulomb |  | Planned | 933 - 1111 | ETT | Eric Blind mlforcum@aep.com 918-599-2674 | 2744 | 2020-04-30 01:00 |  | 345 | 0 | 0 | 0 |  | Knox |  | Tier 4 |  |  |  | 60722, 60500, 60702 | Y | N |  | 0 | 44813 | 44812
45023 | Pershing: Build 138 kV station | Construct new 138 kV box bay on the Abilene Northwest to Oak Creek 138 kV line | Schedule and Cost Update | Pershing |  | Planned | 979 - 1157 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2764 | 2020-04-30 01:00 |  | 138 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  | 60724, 6229, 6335 | Y | N |  | 0 | 45024 | 45023
45415 | Coulomb to Vera: Build new 345 kV line | Interconnect Vera wind farm on the Clear Crossing to Edith Clarke 345 kV line | Contact Update | Coulomb | Vera | Planned | 933 - 1111 | ETT | Eric Blind mlforcum@aep.com 918-599-2674 | 2745 | 2020-04-30 01:00 |  | 345 | 4 | 0 | 0 |  | Knox | Knox | Tier 4 |  |  |  | 60725, 60722 | Y | N |  | 0 | 45416 | 45415
45506 | Coulomb: Build 345 kV terminal | Interconnect TG East wind farm on the Clear Crossing to Edith Clarke 345 kV line | Schedule Update | Coulomb |  | Planned | 980 - 1158 | ETT | Michael Forcum mlforcum@aep.com 918-599-2674 | 2821 | 2020-04-30 01:00 |  | 345 | 0 | 0 | 0 |  | Hardeman |  | Tier 4 |  |  |  | 60722 | Y | N |  | 0 | 45507 | 45506
4971 | Magic Valley II: Build new four breaker 345 kV station | Interconnect Magic Valley II Windfarm at Magic Valley II to connect Magic Valley II to the North Edinburg to Rio Hondo 345 kV line and construct 345 kV line from Bonilla to Ladekidde |  | Cebolla | Ladekidde | Planned | 731 - 0913 | AEP | Terry Weeks dnlyons@aep.com 918-599-2698 | 3562 | 2020-04-30 11:00 |  | 345 | 0 | 0 | 0 |  | Cameron | Willacy | Tier 4 |  |  |  | 8601, 80512, 80076, 8902, 161753 | Y |  |  |  | 12721 | 4971
4501 | Trading Post Circuit Breaker Addition | Install Line Breakers at Trading Post on the Trading Post to Marshall Ford and the Trading Post to Cedar Valley 138kV lines (T315). |  | Trading Post |  | Planned |  | PEC | Ryan Morlino ryan.morlino@peci.com 830-868-5166 |  | 2020-05-01 |  | 138 | 0 | 0 | 0 |  | Travis |  | Tier 4 |  |  |  | 7505 | Y | N |  |  | 12073 | 4501
5277 | Glidden Area Transmission Line Upgrade | Convert existing 69-kV lines (T544) from Glidden to Altair and (T545) from Altair to Nada to 138-kV transmission lines. Relocate existing 45 MVA auto from Glidden to Altair. Add a second new 45 MVA auto at Altair substation. |  | Glidden | Nada | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016219 | 2020-05-01 |  | 138 | 0 | 0.77 | 45 |  | Colorado | Colorado | Tier 4 |  |  |  | 78107, 78111, 78115, 78118, 78170, 78171, 78520, 5536, 7258, 78103, 78106 | Y | N |  | 0 | 46205 | 5277
43623 | McCreeCristBenDavisLinesUpgrade | McCree to Crist to Ben Davis 138kV Lines Upgrade to Cumberland Conductor |  | McCree | Ben Davis | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2020-05-01 |  | 138 | 0 | 6.95 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 834, 850, 968 | Y | N |  | 0 | 43624 | 43623
44860 | Primera 138 kV Station | New Primera 138 kV Station |  | Harlingen SW | South Santa Rosa | Planned | 975 - 1153 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3733 | 2020-05-01 |  | 138 | 0 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 8638, 8327, 8359 | Y | N |  | 0 | 44861 | 44860
45346 | Trade Zone: Build 138 kV Station | Trade Zone: Build 138 kV Station on South McAllen - Stewart Road Line |  | South McAllen | Las Milpas | Planned | 886 - 1064 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3673 | 2020-05-01 |  | 138 | 0 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8644, 8371, 8758 | Y | N |  | 0 | 45347 | 45346
48830 | Pavlov: Construct New 138 kV Station | Pavlov: Construct New 138 kV Station |  | Blessing | Lane City | Planned | 995 - 1173 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3748 | 2020-05-01 |  | 138 | 0 | 0 | 0 |  | Matagorda | Wharton | Tier 4 |  |  |  | 8608, 8121, 8127 | Y | N |  | 0 | 48831 | 48830
4567 | BRYN_4567_Smetana_to_Leonard | Build Smetana to Leonard Rd 138 line in existing 69KV ROW of old Annex to Atkins line |  | 32897 | 32863 | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2020-05-05 |  | 138 | 0.75 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32853, 32851 | Y |  |  |  | 12149 | 4567
5428D | Phase 2 of the conversion to 138kV | Line will be reconfigured to through a 3way tie |  | Woodrow | Spencer Int | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2020-05-05 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 921, 982 | Y | N | N/A |  | 13116 | 5428
5429A | Phase 3 of the conversion to 138kV | Add a new 138kV line from the new Locust station to Woodrow to Spencer Interchange via a three way tie at Woodrow. The section going from the 3way tie to Spencer Int. was added in phase 2. |  | Locust | Spencer Int. | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2020-05-05 |  | 138 | 1.917 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 924, 99999, 921, 982 | Y | N | N/A | 0 | 45742 | 5429
5429C | Phase 3 of the conversion to 138kV | The three way tie will be retired and 138kV locust will tie directly to 138kV Woodrow. The Spencer Int. to the 3way tie will be reconfigured to terminate at the new 138kV Brinker substation. |  | Locust | Spencer Int. | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2020-05-05 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 99999, 921, 924, 982 | Y | N | N/A | 0 | 45744 | 5429
5792 | Leonard Road Substation 138 | Upgrade Leonard Rd from 69kV to 138kV and construct 138 from Leonard to Atkins |  |  |  | Planned |  | BRYN | James Tanneberger jtanneberger@btutilities.com 979-821-5763 |  | 2020-05-05 |  | 138 | 0 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32851, 32862, 32864 | Y |  |  |  | 14760 | 5792
4829 | Hutto Switch second 345/138 kV autotransformer | Install new autotransformer | [5 empty] | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R750 | 2020-05-15 |  | 345 | 0 | 0 |  |  |  |  | Tier 3 |  |  |  | 13660, 3696, 3666 | Y |  |  | 0 | 49638 | 4829
5974 | Saginaw - Denton Ave/Springdale 138 kV DCKT Line | Rebuild existing 69 kV Lines | Construction schedule change | SAGINAW | DENTON AVE | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5245 | 2020-05-15 |  | 138 | 0 | 7.4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1957, 2102, 2146, 2148, 2156, 2157 | Y | N |  |  | 13689 | 5974
6019 | North Main - Denton Ave/Springdale Line | Rebuild existing 69 kV and 138 kV Lines |  | North Main | Richland Junction | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5240 | 2020-05-15 |  | 138 |  | 4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2102, 2148, 2156, 1961, 2099, 2101, 2146, 2157 | Y | N |  |  | 13736 | 6019
6780 | Saginaw 138 kV Switching Station | Rebuild existing Saginaw 138 kV Switching Station |  | SAGINAW |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5277 | 2020-05-15 |  | 138 | 0 | 0 | 0 |  | Tarrant |  | Tier 4 |  |  |  |  | Y | N |  |  | 14574 | 6780
6790 | Sargent Road-East Network 138 kV Line | Construct the new Sargent Road-East Network 138 kV Line | Project Deferral | Sargent Road | Oakland | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4268 | 2020-05-15 |  | 138 | 2.5 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2905, 2949, 2969, 2970, 2971, 12447 | Y | N |  |  | 14588 | 6790
7021 | Collin 345/138 kV Autotransformer 2 Series Reactor | Install 2-ohm series reactor on Collin 345/138 kV Autotransformer 2 |  | Collin Sw. Sta. |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R960 | 2020-05-15 |  | 138 | 0 | 0 | 0 |  | Collin |  | Tier 4 |  |  |  | 2370, 29555 | Y | N |  |  | 14843 | 7021
7104 | Owl Hills - Tunstill POD 138 kV Line | Owl Hills - Tunstill POD 138 kV Line |  | Owl Hills | Tunstill | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8428 | 2020-05-15 |  | 138 | 12 | 0 | 0 |  | Culberson | Reeves | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11090, 11183 | Y |  |  |  | 14938 | 7104
7115 | Quarry Field - Kyle Ranch 138 kV Line | Quarry Field - Kyle Ranch 138 kV Line |  | Quarry Field | Kyle Ranch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8384 | 2020-05-15 |  | 138 | 12 | 0 | 0 |  | Loving |  | Tier 4 |  |  |  | 11089, 11189 | Y |  |  |  | 14951 | 7115
7171 | Andrews County South Switch - No Trees Switch 138 kV Line | Andrews County South Switch - No Trees Switch 138 kV Line |  | Andrews Co South | No Trees | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8407 | 2020-05-15 |  | 138 | 0 | 8.8 | 0 |  | Andrews | Winkler | Tier 4 |  | 2018-09-06 |  | 1149, 1150, 1157, 131853 | Y |  |  |  | 15012 | 7171
44393 | Zapata: Add 138 kV Reactor | Add Reactor at Zapata 138 kV |  | Zapata |  | Planned | 949 - 1127 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3713 | 2020-05-15 |  | 138 | 0 | 0 | 0 | -40,0 | Zapata |  | Tier 4 |  |  |  | 8299 | Y | N |  | 0 | 44394 | 44393
4817 | TI Dallas - Kirkland Park/Coit Road 138 kV Line | Upgrade existing TI Dallas - Schroeder Road line section | Project Deferral | TI Dallas | Schroeder Road | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4202 | 2020-05-15 01:00 |  | 138 | 0 | 1 | 0 |  | Dallas | Dallas | Tier 4 | 2018-04-05 | 2018-05-08 |  | 2607, 2633, 2636, 2637 | Y | N |  |  | 12423 | 4817
45537 | Lewisville - Lewisville Jones - Lakepointe 138 kV Line | Upgrade the Lewisville - Lewisville Jones - Lakepointe 138 kV Line |  | Lewisville Switch | Lake Point (TNMP) | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R966 | 2020-05-15 12:00 |  | 138 | 0 | 0 | 0 |  | Denton |  | Tier 4 |  |  |  | 645, 1972, 1973, 37010 | Y |  |  | 0 | 45538 | 45537
43284D | Baytown Area Upgrades | Upgrade portions of reconfigured Ckt.87 SR Bertron to TEXAS to increase thermal ratings |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-28 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41405, 41540 | Y |  |  | 0 | 48840 | 43284
43284C | Baytown Area Upgrades | Reconfigure SRB to Texas |  |  |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-29 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40089, 40120, 40170, 40430, 40470, 40480, 40540, 41350, 41391, 41405, 41410, 41415, 44051, 44052, 40570, 41355, 41360, 41380, 41400, 41419, 41420, 41540, 44140, 44141, 44780 | Y |  |  | 0 | 48839 | 43284
4186C | University Area 138kV Conversions | Convert Blodgett substation from double-tap service to 138kV Ckt.37 loop service. Convert Blodgett TR1 load to 138kV. |  | Blodgett | TECO/Garrott | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1123 | 2020-05-30 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47520, 47521, 47522, 42690, 47430, 47660 | Y | N |  | Cost included in 4186A | 48944 | 4186
6753 | Quihi: Build 138kV Station | Build new Quihi 138kV In and Out Station on Razorback to Castroville 138kV Line |  | Razorback |  | Planned | 900 -1078 | AEP TCC/STEC | Daniel Lyons dnlyons@aep.com 918-599-2698 | 3684 | 2020-05-30 |  | 138 | 0 | 0 | 0 |  | Medina |  | Tier 4 |  |  |  | 8248, 88248, 5083, 8241 | Y | Y |  |  | 14546 | 6753
43284F | Baytown Area Upgrades | Upgrade Ckt.87 TEXAS to Cedar Bayou tap to increase thermal ratings |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40011, 41540 | Y |  |  | 0 | 48843 | 43284
43454 | Gable Street Reconfigurations | Add 69kV breaker at Gable Street to mitigate P2 contingency load loss |  | Gable Street | Gable Street | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-30 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47640 | Y |  |  | 0 | 43455 | 43454
43284B | Baytown Area Upgrades | Upgrade equipment at EXXON substation to increase thermal ratings on Ckt.66 EXXON to Baytown |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-30 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40170, 40570 | Y |  |  | 0 | 48837 | 43284
4186D | University Area 138kV Conversions | Remove University Auto A1 from service |  | University |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1123 | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 49030, 47755, 47760 | Y | N |  | Cost included in 4186A | 48945 | 4186
4488 | Campwood to Uvalde: Rebuild 69 kV line | Rebuild Campwood to Uvalde 69 kV line, built to 138 kV standard with 795 ACSS conductor, but energized at 69 kV. |  | Campwood | Uvalde | Planned | 707 - 0877 | AEP TCC | Terry Weeks dnlyons@aep.com 918-599-2698 | 2901 | 2020-05-31 |  | 138 | 0 | 37.1 | 0 |  | Real | Uvalde | Tier 3 | 2017-01-17 | 2017-03-20 | 2017-03-20 | 8230, 8633, 8231 | Y | N |  |  | 12057 | 4488
5286A | Fayette Area Upgrades | Upgrade existing Fayette - Frelsburg - Mockingbird - Glidden (T176) TL with a minimum rating of 380 MVA and with OPGW. | Planning In-Service Date Change. Updated to a phased project, the original TPIT project number is 5286. | Fayetteville | Glidden | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019026, 1019024 | 2020-05-31 |  | 138 | 0 | 20 | 0 |  | Fayette | Colorado | Tier 4 | 2017-06-29 | 2017-07-28 |  | 7258, 7263, 7286, 78259 | Y | N |  |  | 14583 | 5286
5970 | Wolfgang to Rotan 69 kV line: Rebuild 69 kV line | Rehab Wolfgang to Rotan 69 kV line | Company Contact and Schedule Update | Wolfgang | Rotan | Planned | 786 - 0971 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2659 | 2020-05-31 |  | 69 | 0 | 12.41 | 0 |  | Kent | Fisher | Tier 4 |  |  |  | 6162, 6196 | Y | N |  |  | 13685 | 5970
6041 | Ely Tap to Scott REA Tap 69 kV line: Rebuild 69 kV line | Rehab Ely Tap to Scott REA Tap 69 kV line | Schedule and Cost Update | Ely Tap | Scott REA Tap | Planned | 786 - 0971 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2670 | 2020-05-31 |  | 69 | 0 | 8.79 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6242, 6246, 60405 | Y | N |  |  | 13760 | 6041
6042 | Scott REA Tap to Eskota 69 kV line: Rebuild 69 kV line | Rehab Scott REA Tap to Eskota 69 kV line | Schedule and Cost Update | Scott REA Tap | Eskota | Planned | 786 - 0971 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2671 | 2020-05-31 |  | 69 | 0 | 11.73 | 0 |  | Taylor | Nolan | Tier 4 |  |  |  | 1340, 6246, 6247 | Y | N |  |  | 13761 | 6042
6573 | Reconductor Dunlavey to Heights Ckt. 31 | Reconductor the Dunlavy to Heights as identified in the 2015 RTP case |  | Dunlavy | Heights | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 47580, 47680 | Y |  |  |  | 14324 | 6573
6578B | Rebuild Ckt.66 Katy-Freeman-Betka-Hockley | Rebuild Ckt.66 Katy to Freeman to address clearance issues (Phase 2 of overall Katy to Hockley upgrades) |  | Katy | Freeman | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Waller | Tier 4 |  |  |  | 44422, 45770, 45675 | Y |  |  |  | 14823 | 6578
6696A | Nash 138kV Loop Conversion | Convert Nash Substation to 138kV loop service. Loop from Ckt.02 WA Parish to West Columbia. Reconductor the loop sections to Nash. |  | Nash | WA Parish/West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42980, 42981, 43380, 44010 | Y | N |  |  | 14478 | 6696
6972 | Dimmit Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Dimmit Substation. |  | Dimmit |  |  |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Dimmit |  | Tier 4 |  |  |  | 78281 | Y | N |  |  | 14789 | 6972
6980 | Weimar Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Weimar Substation. |  | Weimar |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Colorado |  | Tier 4 |  |  |  | 7254 | Y | N |  |  | 14797 | 6980
6983 | Fayetteville - Winchester Transmission Line Upgrade | Upgrade the 138-kV Fayetteville - Winchester transmission line supporting circuit T165 to single 1433 ACSS/TW conductor and OPGW static. The planned T165 circuit rating is (MVA): Rate A=470, Rate B=470, Rate C=470. |  | Fayetteville | Winchester | Planned | 1018933 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018933 | 2020-05-31 |  | 138 | 0 | 18.8 | 0 |  | Fayette | Fayette | Tier 4 |  |  |  | 7286, 7306 | Y | N |  |  | 14800 | 6983
7005 | CNP_18TPIT_New_LakeHouston_Distribution_Sub | Construct service to new 138kV Lake Houston distribution substation. Loop through Ckt.66 Kingwood to Atascocita. |  | Kingwood | Atascocita | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40820, 40130, 40930 | Y |  |  |  | 14826 | 7005
7013 | CNP_18TPIT_NASA_Sub_Upgrades | Upgrade NASA bus equipment to 4000A |  | NASA | NASA | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42970 | Y |  |  |  | 14835 | 7013
43284G | Baytown Area Upgrades | Upgrade Ckt.87 Cedar Bayou to Cedar Bayou tap to increase thermal ratings |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 40011, 40015 | Y |  |  | 0 | 48842 | 43284
44834 | LIMBRG (LIM) 138kV Distribution Substation | Build new 138kV LIMBRG distribution substation. Loop through Ckt.05 Southwyck to Friendswood tap. |  | Southwyck | Friendswood | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 43280, 43260, 42651 | Y |  |  | 0 | 50151 | 44834
48281 | Angleton to West Columbia Ckt 04E Upgrades | Upgrade Ckt 04E Angleton to West Columbia to increase thermal ratings | project on hold for more information from transmission engineering | Angleton | West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42110, 43381, 43380 | N | N |  | 0 | 48283 | 48281
49554 | Cabaniss: Add Second Distribution Bank | Cabaniss: Add Second Distribution Bank |  | Cabaniss |  | Planned | 1033 - 1211 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3772 | 2020-05-31 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8882 | Y | N |  | 0 | 49555 | 49554
6696B | Nash 138kV Loop Conversion | Remove 69kV Nash tap from Ckt.45 Damon to West Columbia |  | Damon | West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 00:01 |  | 69 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42982, 42980, 42340, 43390 | Y | N |  | Cost included in Phase A | 14480 | 6696
43284E | Baytown Area Upgrades | Upgrade Ckt.21 DIABOX to MOMENT to increase thermal ratings |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40480, 41090 | Y |  |  | 0 | 48838 | 43284
43452C | Angleton to MONSAN Ckt.04 Upgrades | Upgrade Ckt.04 Angleton to Liverpool to increase thermal limits |  | Angleton | Liverpool | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 00:02 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42110, 42870 | Y | N |  | 0 | 48829 | 43452
44836 | BURKE (BRK) - Generator Interconnection 138kV Substation (18 | New 138kV BURKE generator interconnection for Wagyu Solar. Loop substation to create new Ckt.02 WA Parish to BURKE to NASH. |  | West Columbia | Nash | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 00:05 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42410, 42980, 43380 | Y |  |  | 0 | 46324 | 44836
7071 | West Columbia 138kV Load Conversion | Replace 69/12kV West Columbia power transformer with 138/12kV transformer |  | West Columbia |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-05-31 00:08 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43384, 43390, 43380, 42410 | Y |  |  |  | 14902 | 7071
17TPIT0002 | Hunt Lane to Pinn Road - 138 kV Transmission Line Rebuild | Rebuild approximately eight circuit miles of 138 kV transmission from Hunt Lane to Pinn Road |  | Hunt Lane | Pinn Rd | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0190 | 2020-06-01 |  | 138 | 0 | 8 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5054, 5305, 5324, 5345, 5427 | Y | N |  | There are no transformers associated with this project | 9558 | 2307
3273B | Southton - New 138kV Substation |  |  | Southton | Braunig-Brooks | Under Construction | S-0750 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0217 | 2020-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5394, 5030, 5045 | Y | N |  | There are no transformers associated with this project | 10624 | 3273
3277 | Shepherd Road - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to Valley line. |  | Shepherd Road | Cagnon-Valley | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2020-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5378, 5053, 5465 | Y | N |  | There are no transformers associated with this project | 10628 | 3277
3298 | Skyline - Install a Fourth 345kV Autotransformer. | Install one 600 MVA autotransformer at Skyline switchyard. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0670 | 2020-06-01 |  | 345 | 0 | 0 | 600 |  | Bexar | Bexar | Tier 4 |  |  |  | 5372, 5371, 5368 | Y | N |  | There are no transmission line additions associated with this project | 10649 | 3298
3820 | Rebuild Casa Blanca to Sandia to AEP Mathis | Rebuild 69 kV 4-0 ACSR line sections to 795 ACSR on 138 kV capable structures. |  | Sandia | AEP Mathis | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-06-01 |  | 69 | 0 | 11.45 | 0 |  | Jim Wells | San Patricio | Tier 4 |  |  |  | 5666, 8166, 8407 | Y | N |  |  | 11277 | 3820
4010 | Rebuild Magnolia - Seminole 138 kV line. | *Project pushed back to 2020. |  | Magnolia Sub | Seminole Sub | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | STE07216 | 2020-06-01 |  | 138 | 0 | 3.3 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 38950, 38990 | Y |  |  |  | 11530 | 4010
4895 | CPSE_Capitol Cement Transmission Reconfiguration | Re-configurate Capitol Cement by loop into the existing Dresden to Skyline 138 kV transmission line and removing the existing Captiol Cement to Tuttle 138 kV transmission line. |  | Capitol Cement | Dresden/Skyline | Planned | S-0767 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0246 | 2020-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5075, 5130, 5370, 5435 | Y | N |  |  | 12507 | 4895
5145C | Rafter - New 138 kV Substation | Build a new 138 kV transmission line from Cagnon to Rafter. |  | CAGNON | RAFTER | Planned | S-0837 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0261 | 2020-06-01 |  | 138 | 7.86 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5055, 5355 | Y | N |  |  | 14399 | 5145
5417 | Buckeye to LA_HTS Rebuild | Rebuild 1.8 mile 138 kV t-line from Buckeye to LA_Hts. Upgrade line terminal at Buckeye Station for Buckeye to LA_HTS t-line. |  | Buckeye | LA_Hts | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0266, S-0899a | 2020-06-01 |  | 138 | 0 | 1.8 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5050, 5285 | Y |  |  |  | 13105 | 5417
6281 | CPSE_Harlandal_Sommers_MLSE | Upgrade terminals at Harlandale and Sommers Substation. | [5 empty] | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0732 | 2020-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5190, 5395 | Y |  |  |  | 14013 | 6281
6685 | Van Vleck substation loop | Replaces single circuit radial line connected to a pole mounted switch with a double circuit transmission loop to the Van Vleck substation. |  | Van Vleck Substation | Van Vleck Switch | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-06-01 |  | 69 | 0 | 2 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 5556, 5554, 5558, 5560 | Y | N |  |  | 14456 | 6685
6834C | IH20 STATCOM RPG | Install fourth 20 MVAR MSC at Collie Capacitor Station (38035). |  | Collie Capacitor Station (38035) | Collie Capacitor Station (38035) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2020-06-01 |  | 138 | 0 | 0 | 0 | 0,20 | Reeves | Reeves | Tier 1 | 2017-10-10 | 2017-12-06 |  | 38035 | Y |  |  | 0 | 46208 | 6834
46456 | LookoutAddsCapbanks | Lookout adds capbanks for voltage reliabilities |  | Lookout | Lookout | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2020-06-01 |  | 138 | 0 | 0 | 0 | 0,120 | Dallas | Dallas | Tier 4 |  |  |  | 828 | Y | N |  | 0 | 46457 | 46456
48325 | New 138kV ROBINSON Ranch Substation. |  |  | 9245 | 9250 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2020-06-01 |  | 138 | 0 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 9250, 9245, 9295 | Y |  |  | 0 | 48326 | 48325
49817A | 4x20 MVAR Elm Street Capacitor Bank | Initial 2x20 MVAR Elm Street Capacitor Bank |  | Elm Street (Bus # 38049) | Elm Street (Bus # 38049) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2020-06-01 |  | 138 | 0 | 0 | 0 | 0,40 | Reeves | Reeves | Tier 4 |  |  |  | 38049 | Y |  |  | 0 | 49818 | 49817
44874 | Resaca 69 kV Station | New Resaca 69 kV Station |  | Brownsville | La Palma | Planned | 974 - 1152 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3732 | 2020-06-02 |  | 69 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8626, 8310, 8332 | Y | N |  | 0 | 44875 | 44874
5230 | Sonne Substation Addition | Provide transmission service for a generator off T554 radial 138-kV line between North McCamey and Tippet Substations. |  | North McCamey | Tippet | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1015964 | 2020-06-15 |  | 138 | 0 | 0 | 0 |  | Upton | Pecos | Tier 4 |  |  |  | 76020, 76021, 76595 | Y | N |  |  | 12903 | 5230
6973 | Welcome Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement,at Welcome Substation. |  | Welcome |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018929 | 2020-06-17 |  | 138 | 0 | 0 | 0 |  | Austin |  | Tier 4 |  |  |  | 7577 | Y | N |  |  | 14790 | 6973
6427 | Refugio - Rincon: Upgrade 69 kV Line | Upgrade line from Rincon - Refugio and terminal equipments at Rincon, Bonneview, Woodsboro, Heard, and Refugio |  | Refugio | Rincon | Under Construction | 962 - 1140 | AEP | Bill Roberts dnlyons@aep.com 918-599-2698 | 3720 | 2020-06-19 |  | 69 | 0 | 1 | 0 |  | San Patricio | Refugio | Tier 3 | 2017-03-28 | 2017-04-21 | 2017-05-08 | 8410, 8802, 8804, 8805, 8416 | Y | N |  |  | 14170 | 6427
13TPIT0106 | Killeen SS to Ding Dong | Rebuild 477 ACSR line with 955 ACSS |  | Killeen SS | Ding Dong | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 11037 | 2020-06-30 |  | 138 | 0 | 5.8 | 0 |  | Bell | Bell | Tier 4 |  |  |  | 115, 117, 136, 3423 | Y | N |  |  | 9901 | 2608
4577 | BRYN_4577_Dansby_Rebuild | Convert Dansby 69kV bus to Double Bus, Double Breaker configuration |  |  |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2020-06-30 |  | 69 | 0 | 0 | 200 |  | Brazos |  | Tier 4 |  |  |  | 32875, 32897 | Y |  |  | 0 | 45636 | 4577
5621 | South McAllen-Bentsen and North Edinburg-West Edinburg | Replace MLSE equipment at North Edinburg and South McAllen |  | North Edinburg | North McAllen | Planned | 795 - 0980 | AEP TCC | Michael Richardson dnlyons@aep.com 918-599-2698 | 3585 | 2020-06-30 |  | 138 | 0 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 5771, 8367, 8371, 8368, 8380, 8758, 8822 | Y | N |  |  | 13351 | 5621
5966 | College Hills to Grape Crk T 69 kV line: Rebuild 69 kV line | Rehab College Hills to Grape Creek Tap 69 kV line | Company Contact and Schedule Update | College Hills | Burma | Planned | 786 - 0971 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2664 | 2020-06-30 |  | 69 | 0 | 10.45 | 0 |  | Tom Green | Tom Green | Tier 4 |  |  |  | 6468, 6416 | Y | N |  |  | 13681 | 5966
6005 | Airline: Convert 69 kV Station | Upgrade Airline 69 kV station and lines to 138 kV |  | Airline | Naval Base | Planned | 808 - 0993 | AEP/LCRA TSC | Dave Goetz dnlyons@aep.com 918-599-2698 | 3597 | 2020-06-30 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8487, 8494, 8548, 8560, 8561, 78560, 8490, 8495, 8997, 8562, 8856 | Y | Y |  |  | 13771 | 6005
47448 | Motorman Substation Addition | Construct a new 138-kV Motorman substation. Motorman Substation is located in west Texas approximately 4.2 miles east of the LCRA TSC Crane East Substation. Construct a 3-breaker ring bus cut in to the existing Crane East to Upton transmission line. |  | Motorman | Motorman | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2020-06-30 |  | 138 | 0 | 0 | 0 |  | Crane | Crane | Tier 4 |  |  |  | 7869, 71212, 71214 | Y | N |  | 0 | 47449 | 47448
45501 | Eldorado Live Oak to Sonora 69 kV line: Rebuild 69 kV line | Rehab Eldorado Live Oak to Sonora 69 kV line | Company Contact and Schedule Update | Eldorado Live Oak | Sonora | Planned | 982 - 1160 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2769 | 2020-06-30 01:00 |  | 69 | 0 | 23.9 | 0 |  | Schleicher | Sutton | Tier 3 | 2018-12-18 | 2019-01-17 |  | 6498, 6505, 6509, 6510, 6513 | Y | N |  | 0 | 45502 | 45501
5218B | San Miguel 345/138 kV autotransformer replacements | Replace T2 300 MVA autos with much larger autos |  | San Miguel |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-07-01 |  | 345 | 0 | 0 | 672 |  | Atascosa |  | Tier 4 |  |  |  | 5909, 5901, 5902 | Y | N |  | Delayed from 2018 to 2019 in the 2016 RTP. | 45091 | 5218
5457 | Load serving | New station to aid in DME's load serving |  | Brinker |  | Planned |  | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2020-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 927, 906, 907, 913, 921 | Y | N |  |  | 13160 | 5457
6788 | Tarpley Substation Upgrade | Add two 138 kV Circuit Breakers to Line Terminals to be operated at 69 kV. | Change in schedule | Tarpley |  | Planned |  | BANDERA | Tyler Pansing t.pansing@banderaelectric.com 866-226-33726078 | 353985 | 2020-07-01 |  | 69 | 0 | 0 | 0 |  | Bandera |  | Tier 4 |  |  |  | 7439, 7440 | Y | N |  |  | 14582 | 6788
48802 | Gillet: Build New Distribution Station | Gillet: Build New Distribution Station |  | Magnolia Tap | Nixon | Planned | 1032 - 1210 | AEP TCC/LCRA | Dan Lyons dnlyons@aep.com 918-599-2698 | 3771 | 2020-07-01 |  | 138 | 0 | 0 | 0 |  | Karnes |  | Tier 4 |  |  |  | 8583 | Y | Y |  | 0 | 48803 | 48802
5946 | Winchester Autotransformer Additions | Add two 672 MVA autotransformers at Winchester Substation. Cut the new 345-kV bus at Winchester into an existing Austin Energy owned 345-kV transmission line from FPP to Lost Pines. |  | FPP #1 | Lost Pines | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017413 | 2020-07-08 |  | 345 | 0 | 0 | 1344 |  | Fayette | Bastrop | Tier 3 | 2017-02-01 | 2017-03-20 |  | 77306, 77308, 77309, 7056, 9041, 7306 | Y | N |  |  | 13657 | 5946
6976 | Riverside Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Riverside Substation. |  | Riverside |  | Planned | 1018919 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018919 | 2020-07-08 |  | 138 | 0 | 0 | 0 |  | Fayette |  | Tier 4 |  |  |  | 7275 | Y | N |  |  | 14793 | 6976
6982 | Boerne Cico - Comfort - Kendall Transmission Line Upgrade | Upgrade the 138-kV Boerne Cico - Comfort transmission line supporting circuit T148 to bundled 795 ACSR conductor. The planned T148 circuit rating is (MVA): Rate A=440, Rate B=440, Rate C=440. Upgrade the 138-kV Comfort - Kendall transmission line supporting circuit T243 to bundled 959 ACSS/TW conductor. The planned T243 circuit rating is (MVA): Rate A=760, Rate B=760, Rate C=760. |  | Boerne Cico | Kendall | Planned | 1019089 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019089 | 2020-08-18 |  | 138 | 0 | 18.1 | 0 |  | Kendall | Kendall | Tier 4 |  |  |  | 7151, 7152, 7155 | Y | N |  |  | 14799 | 6982
3877 | Meadow Lake Substation Addtion | Add a new load serving substation (ring-bus) at Meadow Lake. The station will be built between Cushman and Highway 123 off T572. | Customer Schedule Change | Cushman | Highway 123 | Planned |  | LCRATSC/GVEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016198 | 2020-08-19 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7720, 7221, 7226 | Y | N |  |  | 12940 | 3877
11TPIT0008 | RAINEY_ST 138kV substation | Establish a new 138kV Rainey St. Substation with (2) 50MVA transformers and cut into existing Ckt 1015 (Pedernales to Seaholm). |  | Rainey St Substation | Rainey St Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | PLAN_117_P158 PLAN_117_P166 PLAN_117_P167 | 2020-09-01 |  | 138 | 0.1 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9261, 9118, 9132 | Y | N |  |  | 8208 | 1032
44383 | Las Majadas: Interconnection of Generator at 138 kV | Las Majadas: Interconnection of Generator at 138 kV |  | Rio Hondo | Majadas | Planned | 943 - 1121 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3707 | 2020-09-28 |  | 345 | 9 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 80051, 8318 | Y | N |  | 0 | 44384 | 44383
3463 | Shady Bus Split | Reconfigure 69kV bus |  |  |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2020-09-30 |  | 69 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  |  | Y |  |  |  | 10843 | 3463
4571 | Atkins Substation Upgrade | Rebuild Atkins 69kV bus |  | 32864 |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.co 979-821-5763 |  | 2020-09-30 |  | 69 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  |  | Y |  |  | No MOD Changes Necessary | 12153 | 4571
6348 | Paint Rock to CRMWD Tap #1 69 kV line: Rebuild 69 kV line | Rehab Paint Rock to CRMWD Tap #1 69 kV line |  | Paint Rock | CRMWD Tap #1 | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2709 | 2020-09-30 |  | 69 | 0 | 6.09 | 0 |  | Concho | Concho | Tier 4 |  |  |  | 6369, 6370, 6376 | Y | N |  |  | 14092 | 6348
48748 | Oklaunion: Install 345 kV reactor | Install reactor on the Oklaunion 345 kV bus | NEW | Oklaunion |  | Planned | 1013 - 1191 | ETT | Glen Reed gareed@aep.com 918-599-2664 | 2774 | 2020-09-30 01:00 |  | 345 | 0 | 0 | 0 | -50,0 | Wilbarger |  | Tier 4 |  |  |  | 6100 | Y | N |  | 0 | 48749 | 48748
5604 | Stewart Road: Construct 345 kV cut-in | Construct new 345 kV 4 breaker ring bus station at AEP Stewart Rd, with two 450 MVA 345/138 autotransformers connected to Stewart Rd 138 station. Hairpin the North Edinburg to SU Palmito 345 kV line into new Stewart Rd 345 station. The hairping will be constructed in a double circuit configuration, approximately 5 miles long. Also install 100 Mvar shunt reactor at the new Stewart Rd 345 kV station. |  | Stewart Road |  | Planned | 792 - 0977 | AEP TCC | Teresa Trotman dnlyons@aep.com 918-599-2698 | 3582 | 2020-10-01 |  | 345 | 0 | 0 | 900 | 100,0 | Hidalgo | Hidalgo | Tier 2 | 2015-07-10 | 2016-05-19 | 2016-06-14 | 80137, 8951 | Y | N |  |  | 13334 | 5604
6382 | Stewart Road: Construct 345 kV cut-in | Hairpin the North Edinburg to SU Palmito 345 kV line into new Stewart Rd 345 station. The hairpin will be constructed in a double circuit configuration, approximately 5 miles long. |  | Stewart Road | North Edinburg, SU Palmito | Planned | 874 - 1052 | ETT | Teresea Trotman dnlyons@aep.com 918-599-2698 | 3661 | 2020-10-01 |  | 345 | 5 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 2 | 2015-07-10 | 2016-05-19 | 2016-06-14 | 80137, 5966, 8383 | Y | N |  |  | 14126 | 6382
5887A | RUSSEL 138kV Substation (ARITEK Substation Removal) | Remove ARITEK 138kV substation from CNP service |  | ARITEK | SR Bertron/CHORIN | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-10-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40120, 40320, 41391 | Y | N |  |  | 13612 | 5887
4487 | Nueces Area 69kV Reinforcement | Expand and add new 138/69kV Auto at Valero East 69kV substation. Add 5th breaker to Champlin 138kV substation. Construct Champlin to Valero East 138kV Line. |  | Champlin | Valero East | Planned | 709 - 0879 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2903 | 2020-10-30 01:00 |  | 138 | 1.6 | 0 | 200 |  | Nueces |  | Tier 4 |  |  |  | 8528, 8476, 8859 | Y | N |  |  | 13570 | 4487
49564 | Mantle: Construct New 345 kV Station | Mantle: Construct New 345 kV Station |  | Bonilla | North Edinburg | Planned | 1035 - 1213 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3774 | 2020-10-30 20:00 |  | 345 | 0 | 0 | 0 |  | Cameron | Hidalgo | Tier 4 |  |  |  | 8059, 80598, 8383 | Y | N |  | 0 | 49565 | 49564
49566 | Revilla: Construct New 138 kV Station | Revilla: Construct New 138 kV Station |  | Falcon SS | Lopeno | Planned | 1034 - 1212 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3773 | 2020-10-30 20:00 |  | 138 | 0 | 0 | 0 |  | Starr | Zapata | Tier 4 |  |  |  | 8004, 80084, 8957, 80106 | Y | Y |  | 0 | 49567 | 49566
4495 | AEP_4495_Champlin | Expand existing breaker configuration to a four (4) breaker ring bus expandable to a six (6) breaker ring bus configuration. |  | Champlin |  | Planned | 694 - 0864 | AEP | John Pulay dnlyons@aep.com 918-599-2698 | 3541 | 2020-10-31 |  | 138 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 8476 | Y | N |  |  | 12064 | 4495
44858 | Luna 138 kV Station | New Luna 138 kV Station |  | Mesquite | STEC Rangerville | Planned | 964 - 1142 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3722 | 2020-10-31 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8656, 88656, 8554, 80103 | Y | N |  | 0 | 44859 | 44858
49540 | Avogadro: Build new 345 kV station | Interconnect Griffin Trail wind farm on the Clear Crossing to Edith Clarke 345 kV line | NEW | Avogadro |  | Planned | 1017 - 1195 | ETT | Michael Forcum mlforcum@aep.com 918-599-2674 | 2778 | 2020-10-31 |  | 345 | 0 | 0 | 0 |  | Knox |  | Tier 4 |  |  |  | 60506, 60500, 60700 | Y | N |  | 0 | 49541 | 49540
49548 | Esperanza: Construct New 138 kV Station | Esperanza: Construct New 138 kV Station |  | STP Switch | Celanese Bay City | Planned | 993 - 1171 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3742 | 2020-10-31 |  | 138 | 0 | 0 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 8191, 8116, 8558 | Y | N |  | 0 | 49549 | 49548
48288A | BOGGY (BOG) 138kV Substation (SHELL Substation Replacement) | Remove existing customer-owned SHELL (_SL) 138kV Substation |  | SHELL |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-10-31 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 41450, 40070, 40530, 41320, 41210, 110950, 110951, 110953, 110947, 110948, 110952 | Y | N |  | 0 | 48844 | 48288
48288B | BOGGY (BOG) 138kV Substation (SHELL Substation Replacement) | Install new customer-owned BOGGY 138kV substation. Loop from Ckt.85 to create new Ckt.85 DERICK to BOGGY to AIRPRO |  | BOGGY | DERICK/AIRPRO | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-10-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41460, 40070, 41320, 110950, 110951, 110953, 110947, 110948, 110952 | Y | N |  | 0 | 48845 | 48288
48288C | BOGGY (BOG) 138kV Substation (SHELL Substation Replacement) | Install new customer-owned BOGGY 138kV substation. Loop from Ckt.88 to create new Ckt.88 PAIR to BOGGY to ESBELT |  | BOGGY | PAIR/ESBELT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-10-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40530, 41210, 41460 | Y | N |  | 0 | 48846 | 48288
45155 | Ollin: Build 138 kV station | Construct new Ollin 138 kV station | Project Description, Company Contact, and Schedule Update | Ollin |  | Planned | 939 - 1117 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2752 | 2020-10-31 01:00 |  | 138 | 0 | 0 | 130 |  | Crane |  | Tier 4 |  |  |  | 6600, 6605, 6606, 6669, 60428, 60429, 60432, 60441, 6668, 6610, 6613, 60431, 76615 | Y | N |  | 0 | 45156 | 45155
45174 | Ollin to LCRA Crane: Partial build, partial rebuild, and con | Build new Ollin 138 kV station partial build, rebuild, and conversion to 138 kV of Ollin to LCRA Crane; and rebuild McElroy to Sage | Project Description, Company Contact, and Schedule Update | Ollin | LCRA Crane | Planned | 939 - 1117 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2767 | 2020-10-31 01:00 |  | 138 | 0.57 | 0.47 | 0 |  | Crane | Crane | Tier 4 |  |  |  | 6600, 6605, 6606, 6669, 60428, 60429, 60432, 60441, 6610, 6613, 6668, 60431, 76615 | Y | N |  | 0 | 45175 | 45174
5440 | Riverton 345 kV Switching Station | Construct new 345 kV switching station |  | Riverton |  | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8351 | 2020-11-15 |  | 345 | 0 | 0 | 1200 |  | Reeves |  | Tier 1 | 2016-04-20 | 2017-05-23 | 2017-06-13 | 11075, 11084, 11085, 11083 | Y | N |  |  | 13143 | 5440
7119 | Sand Lake 345 kV Sw. Sta. | Sand Lake 345 kV Sw. Sta. |  | Sand Lake |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8420 | 2020-11-15 |  | 345 | 0 | 0 | 1200 |  | Ward |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11098, 11099, 11109, 11097 | Y |  |  |  | 14955 | 7119
46259 | Big Spring - Buzzard Draw 69 kV Line Conversion | Big Spring - Buzzard Draw 69 kV Line Conversion |  | Big Spring | Buzzard Draw | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9015 | 2020-11-15 23:00 |  | 138 | 0 | 21.3 | 0 |  | Howard | Howard | Tier 4 |  |  |  | 1357, 1358, 1359, 1361, 1365, 1322, 1323, 1355, 1356, 11324 | Y |  |  | 0 | 46262 | 46259
7120 | Riverton Sw. Sta. - Sand Lake Sw. Sta. 345 kV Line | Riverton Sw. Sta. - Sand Lake Sw. Sta. 345 kV Line |  | Riverton | Sand Lake | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8443 | 2020-11-16 |  | 345 | 26 | 0 | 0 |  | Reeves | Ward | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11084, 11098 | Y |  |  |  | 14956 | 7120
6079 | Childress to Kirkland 69 kV line: Rebuild 69 kV line | Rehab Childress to Kirkland 69 kV line | Company Contact and Schedule Update | Childress | Kirkland | Planned | 786 - 0971 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2693 | 2020-11-30 |  | 69 | 0 | 5.61 | 0 |  | Childress | Childress | Tier 4 |  |  |  | 6032, 6053 | Y | N |  |  | 13803 | 6079
7027 | Barrilla Junction to Ft. Stockton SW: Rebuild 69 kV line | Rebuild Barrilla Junction to Ft. Stockton SW to Rio Pecos 69 kV line, convert to 138 kV, reterminate into Solstice, install 138 kV capacitor bank at Solstice, and build new Ft. Stockton Switch 138 kV station | Company Contact and Schedule Update | Solstice | Fort Stockton Switch | Planned | 908 - 1086 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2732 | 2020-11-30 |  | 138 | 0 | 16.3 | 0 |  | Pecos | Pecos | Tier 3 | 2017-12-22 | 2018-02-02 |  | 6645, 60717, 60385, 6653, 38350, 38470 | Y | N |  |  | 14849 | 7027
44361 | Ft. Stockton SW: Build 138 kV station | Rebuild Barrilla Junction to Ft. Stockton SW to Rio Pecos 69 kV line, convert to 138 kV, reterminate into Solstice, install 138 kV capacitor bank at Solstice, and build new Ft. Stockton Switch 138 kV station | Company Contact and Schedule Update | Fort Stockton Switch |  | Planned | 908 - 1086 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2735 | 2020-11-30 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 3 | 2017-12-22 | 2018-02-02 |  | 60717 | Y | N |  | 0 | 44362 | 44361
44485 | Pig Creek: Build 138 kV terminal | Interconnect 138 kV line to Tar Bush |  | Pig Creek |  | Planned | 938 - 1116 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2751 | 2020-11-30 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  | 60393 | Y | N |  | 0 | 44486 | 44485
47440 | Rattler Substation Addition | Construct a new load-serving 138-kV substation. Rattler substation will be located on T262 transmission line between Redwood and McCarty Lane. |  | Rattler | Rattler | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2020-11-30 |  | 138 | 0 | 0 | 0 |  | Hays | Hays | Tier 4 |  |  |  | 7184, 7182, 7188 | Y | N |  | 0 | 47441 | 47440
47541 | Crane Circuit Breaker Addition | Provide transmission service to American Electric Power at Crane Substation. Adding one (1) breaker and associated equipment needed to connect the AEP-owned Crane to Kinnison 138-kV transmission line. |  | Crane Substation | Crane Substation | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2020-11-30 |  | 138 | 0 | 0 | 0 |  | Crane | Crane | Tier 4 |  |  |  | 76615 | Y | N |  | 0 | 47542 | 47541
48335 | RGEC Ft. Stockton US 285 138-kV Substation Addition | Provide transmission service to new 25/30/35 MVA 138/24.9-kV substation to replace (transfer load from) Ft. Stockton 69-kV Substation. This is tied to AEP Project ID # 44361 |  | Fort Stockton | Fort Stockton | Planned |  | RGEC | Larry T. Powell lpowell@rgec.coop 830-563-6178 |  | 2020-11-30 |  | 138 | 0 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 78926, 6645, 60717 | Y |  |  | 0 | 48340 | 48335
44804 | Tinsley: Build 138 kV station | Construct new 138 kV box bay on the Carver to Maxwell 138 kV line | Schedule and Cost Update | Tinsley |  | Planned | 957 - 1135 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2761 | 2020-11-30 01:00 |  | 138 | 0 | 0 | 0 |  | Sutton |  | Tier 4 |  |  |  | 60440, 8259, 60412 | Y | N |  | 0 | 44805 | 44804
44807 | Crossover: Build 138 kV station | Construct new 138 kV box bay on the Santa Rita to North McCamey 138 kV line | Schedule Update | Crossover |  | Planned | 954 - 1133 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2759 | 2020-11-30 01:00 |  | 138 | 0 | 0 | 0 |  | Upton |  | Tier 4 |  |  |  | 60723, 60361, 76032 | Y | N |  | 0 | 44808 | 44807
5491 | Whitestone - Leander 138kV Transmission Line Upgrade | Upgrade the Whitestone - Blockhouse (T469) and the Blockhouse - Leander (T326) 138kV Line to 441MVA. |  | Whitestone | Leander | Planned |  | PEC | Ryan Morlino ryan.morlino@peci.com 830-868-5166 |  | 2020-12-01 |  | 138 | 0 | 5.4 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 7525, 7527, 7529 | Y | N |  |  | 13229 | 5491
6931 | New Cantu Substation | Adds new station and short line from W Edinburg-Alton line |  | West Edinburg | Alton | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-12-01 |  | 138 | 1.8 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 5770, 5771, 5772 | Y | N |  |  | 14750 | 6931
6934A | Elm Creek - New 345 kV Reactor | Install new 345 kV 60 Mvar Reactor at Elm Creek Substation. | [5 empty] | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0873 | 2020-12-01 |  | 345 | 0 | 0 | 0 | 60,0 | Guadalupe |  | Tier 4 |  |  |  | 5133 | Y |  |  |  | 14753 | 6934
48248 | BrandToCollegeLineUpgrade | Brand to College Line Upgrade to Cumberland |  | Brand | College | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2020-12-01 |  | 138 | 0 | 4.16 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 827, 829 | Y |  |  | 0 | 48249 | 48248
6874 | BenDavisAuto1Upgraded | Ben Davis auto1 replacement and at new rating 600 MVA |  | Ben Davis | Ben Davis | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2020-12-01 10:00 |  | 345 | 0 | 0 | 600 |  | Dallas | Dallas | Tier 4 |  |  |  | 970, 968, 993 | Y | N |  |  | 14683 | 6874
4825 | Crockett - Jewett 138kV Line | Upgrade existing line | Project Deferral | Crockett | Jewett | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6061 | 2020-12-15 |  | 138 | 0 | 39.5 | 0 |  | Houston | Leon | Tier 3 | 2017-09-11 | 2017-12-04 | 2017-12-04 | 3354, 3355, 3357, 3358, 13354, 3345, 3394 | Y | N |  |  | 12432 | 4825
5445 | Riverton-Odessa EHV/Moss 345 kV Line | Riverton-Odessa EHV/Moss 345 kV Line |  | Riverton | Odessa EHV | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8356 | 2020-12-15 |  | 345 | 186 | 16 | 0 |  | Reeves | Ector | Tier 1 | 2016-04-20 | 2017-05-23 | 2017-06-13 | 1018, 1029, 11028, 11084 | Y |  |  |  | 14960 | 5445
6255B | Rebuild BEVO to Brundage to Big Wells 69 kV lines. | Rebuild 69 kV line with 795 ACSR on 138 kV and double circuit capable structures 2015- NERC assessment |  | BEVO | Brundage | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2020-12-15 |  | 69 | 0 | 7.3 | 0 |  | Dimmit | Dimmit | Tier 4 |  |  |  | 5870, 5871 | Y | N |  | 0 | 45067 | 6255
6302 | Black Fork-Tyler West 69 kV to 138 kV Line Conversion | Rebuild existing 69 kV line and convert to 138 kV operation |  | Black Fork | Tyler West | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6071 | 2020-12-15 |  | 138 | 0 | 4.9 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3138, 3140, 3142, 3198, 3207, 3139, 3197, 3137, 13235, 3141 | Y | Y |  |  | 14031 | 6302
7020 | Cedar Hill - Camp Wisdom 138 kV Line | Upgrade existing Cedar Hill - Camp Wisdom 138 kV Line |  | Cedar Hill | Camp Wisdom | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4250 | 2020-12-15 |  | 138 | 0 | 9.1 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2421, 2990, 2993, 2994, 2992, 2999 | Y | N |  |  | 14842 | 7020
7121 | Sand Lake Sw. Sta. - Solstice 345 kV Line | Sand Lake Sw. Sta. - Solstice 345 kV Line |  | Sand Lake | Solstice | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8380 | 2020-12-15 |  | 345 | 80 | 0 | 0 |  | Ward |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11098, 60404 | Y |  |  |  | 14957 | 7121
45471 | Lake Creek - Waco East 138 kV Line | Upgrade the Lake Creek Switch - Waco East Switch 138 kV Line to 2071A |  | Lake Creek | Waco East | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R470 | 2020-12-15 |  | 138 | 0 | 9.8 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  | 3410, 3438, 3452 | Y | N |  | 0 | 45472 | 45471
45498 | Construct Shipwreck Substation to Midkiff Switch 138 kV Line | Construct Shipwreck Substation to Midkiff Switch 138 kV Line |  | Shipwreck Substation | Midkiff Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8462 | 2020-12-15 |  | 138 | 0 | 10.3 | 0 |  | Glasscock | Reagan | Tier 4 |  |  |  | 1210, 1211, 1213, 1217, 1219, 11218 | Y |  |  | 0 | 45500 | 45498
45543 | Everman Switch - Marrs Switch 138 kV DCKT Line | Upgrade the Everman Switch - Marrs Switch 138 kV DCKT Line |  | Everman Switch | Marrs Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5279 | 2020-12-15 |  | 138 | 0 | 8 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1883, 1884, 1969, 2211 | Y |  |  | 0 | 45544 | 45543
49834 | Fullerton 138 kV Switch Terminal Addition | Fullerton 138 kV Switch Terminal Addition |  |  |  | Planned | R9037 | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2020-12-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 1274, 11275, 1272, 1284, 11274 | Y |  |  | 0 | 49835 | 49834
7129 | Decordova 345/138 kV Sw. Sta. | Rebuild existing switching station | Project Deferral | Decordova |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5066 | 2020-12-15 02:00 |  | 345 | 0 | 0 | 0 |  | Hood |  | Tier 4 |  |  |  | 1888 | Y | N |  |  | 14967 | 7129
14TPIT0010 | Handley - Sherry 138 kV line | Upgrade existing line |  | Handley | Sherry | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5155-E | 2020-12-15 12:00 |  | 138 | 0 | 8.9 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1919, 1920, 1950, 1951, 2245, 2246, 2247, 2250, 2251, 2252 | Y | N |  |  | 11813 | 2582
45541 | Watermill Switch - Camp Wisdom 138 kV Line | Upgrade the Watermill Switch - Camp Wisdom 138 kV Line |  | Watermill Switch | Camp Wisdom | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4216 | 2020-12-15 12:00 |  | 138 | 0 | 11.5 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2988, 2989, 2990, 3068 | Y |  |  | 0 | 45542 | 45541
45545 | Norwood Switch - Denton Drive 138 kV DCKT Line | Upgrade the Norwood Switch - Denton Drive 138 kV DCKT Line |  | Norwood Switch | Denton Drive Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | m4245 | 2020-12-15 12:00 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2405, 2407, 2488, 2796, 2797, 2800, 2801, 12487 | Y |  |  | 0 | 45546 | 45545
48822 | Carrollton East - Renner_Northaven Double-circuit Line | Upgrade existing line |  | Carollton East | Alpha Road And Knoll Trail | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4232 | 2020-12-15 12:00 |  | 138 | 0 | 13 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2571, 2575, 2582, 2583, 2584, 2596, 2578, 2598, 2613 | Y | N |  | 0 | 49080 | 48822
46094 | Add Wolf 345 kV Switch |  | New route approved | Wolf | Wolf | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8289 | 2020-12-16 |  | 345 | 0 | 0 | 0 |  | Ward | Ward | Tier 3 |  |  |  | 11008, 11010, 1018, 1029, 11028, 11084, 1013 | Y |  |  | 0 | 46095 | 46094
49841 | Fullerton_to_NorthAndrews_138_kV_Conversion_East | Fullerton_to_NorthAndrews_138_kV_Conversion_East |  |  |  | Planned | R9038 | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2020-12-16 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 1285, 1159, 1160, 11274, 11275 | Y |  |  | 0 | 49842 | 49841
49858 | Fullerton_to_NorthAndrews_138_kV_Conversion_West | Fullerton_to_NorthAndrews_138_kV_Conversion_West |  |  |  | Planned | R9039 | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2020-12-17 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 1160, 1267, 1270, 11274, 1159, 1272, 11275 | Y |  |  | 0 | 49859 | 49858
18TPIT0001 | Wiederstein Substation Transformer Replacement | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Wiederstein |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2020-12-18 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7461 | Y | N |  |  | 10675 | 3319
43456 | Greens Bayou 138kV Reconfigurations | Connect Greens Bayou 'East' and 'West' buses with (1) 8-Ohm Reactor. |  | Greens Bayou | Greens Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40710, 40715 | Y |  |  | 0 | 44996 | 43456
44818A | Fort Bend to West Columbia 138kV Conversion | Remove Fort Bend 138/69kV Auto A1 from CNP service |  | Ft Bend | Ft Bend | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 |  | 138 | 0 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 3 | 2018-10-30 | 2018-11-26 |  | 44290, 49014, 44280 | Y |  |  | 0 | 45050 | 44818
44818B | Fort Bend to West Columbia 138kV Conversion | Convert existing 69kV Ckt.45 Fort Bend to Big Creek to 138kV service as Ckt.89 |  | Ft Bend | Big Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:01 |  | 138 | 7.4 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 3 | 2018-10-30 | 2018-11-26 |  | 42391, 44070, 44280, 44290 | Y |  |  | 0 | 45049 | 44818
44818C | Fort Bend to West Columbia 138kV Conversion | Convert existing 69kV Ckt.45 Big Creek to Needville to 138kV service as Ckt.89 |  | Big Creek | Needville | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:02 |  | 138 | 8.2 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 3 | 2018-10-30 | 2018-11-26 |  | 42380, 43000, 44070, 42391 | Y |  |  | 0 | 45047 | 44818
44818D | Fort Bend to West Columbia 138kV Conversion | Convert existing 69kV Ckt.45 Needville to Damon to 138kV service as Ckt.89 |  | Needville | Damon | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:03 |  | 138 | 10.8 | 0 | 0 |  | Fort Bend | Brazoria | Tier 3 | 2018-10-30 | 2018-11-26 |  | 42340, 42370, 43000, 42380 | Y |  |  | 0 | 45043 | 44818
44818E | Fort Bend to West Columbia 138kV Conversion | Convert existing 69kV Ckt.45 Damon to West Columbia to 138kV service as Ckt.89 |  | Damon | West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:04 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2018-10-30 | 2018-11-26 |  | 42370, 43390, 42340, 43380 | Y |  |  | 0 | 45048 | 44818
44818F | Fort Bend to West Columbia 138kV Conversion | Remove West Columbia 138/69kV Auto A2 from CNP service |  | West Columbia | West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:05 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2018-10-30 | 2018-11-26 |  | 43390, 49034, 43380 | Y |  |  | 0 | 45046 | 44818
44818G | Fort Bend to West Columbia 138kV Conversion | Remove TEXWES customer from CNP service |  | West Columbia | TEXWES | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:06 |  | 69 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2018-10-30 | 2018-11-26 |  | 43350, 43390 | Y |  |  | 0 | 45045 | 44818
44818H | Fort Bend to West Columbia 138kV Conversion | Remove 7.2 MVAR cap bank from West Columbia Auto A2 tertiary bus |  | West Columbia | West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-29 00:07 |  | 69 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2018-10-30 | 2018-11-26 |  | 49034 | Y |  |  | 0 | 45044 | 44818
43456B | Greens Bayou 138kV Reconfigurations | Reposition Ckt.94A (GBY to Humble) to connect to GBY 'West' bus |  | Greens Bayou | Humble | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40710, 40715, 41222 | Y |  |  | 0 | 44997 | 43456
14TPIT0056 | Northaven - Morrison 138 kV line | Upgrade existing double-circuit line |  | Northaven | Morrison | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4088-E | 2020-12-31 |  | 138 | 0 | 12 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2657, 2658, 2660, 2661, 2662, 2663, 2782, 2783 | Y | N |  |  | 9773 | 2493
4320 | CPSE_Brooks to Chavaneaux MLSE | Upgrade terminals at Brooks and Chavaneaux to ensure a 1364 A rating (minimum) |  | Brooks | Chavaneaux |  |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0733 | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5045, 5085 | Y | Y |  |  | 11872 | 4320
5530 | Solstice: Build 345 kV station | Construct new 345 kV station with two 345/138 kV autotransformers, reactor, and build new 345 kV line from Solstice to Bakersfield |  | Solstice |  | Planned | 789 - 0974 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2649 | 2020-12-31 |  | 345 | 0 | 0 | 1486 |  | Pecos |  | Tier 1 | 2016-04-01 | 2017-05-23 | 2017-06-21 | 60402, 60404, 60418, 60385 | Y | Y |  |  | 13257 | 5530
5539 | Solstice to Bakersfield: Build 345 kV line | Construct new 345 kV station with two 345/138 kV autotransformers, reactor, and build two new 345 kV lines from Solstice to Bakersfield |  | Solstice | Bakersfield | Planned | 789 - 0974 | AEP TNC/LCRATSC | Brent Harris mlforcum@aep.com 918-599-2674 | 2651 | 2020-12-31 |  | 345 | 136 | 0 | 0 |  | Pecos | Pecos | Tier 1 | 2016-04-01 | 2017-05-23 | 2017-06-21 | 60404, 76002 | Y | Y |  |  | 13267 | 5539
5835 | Rebuild Sardis to Reagor Springs | Rebuild Sardis (Bus #202) to Reagor Springs (Bus #210) |  |  |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 16027 | 2020-12-31 |  | 69 | 0 | 15.46 | 0 |  | Ellis | Ellis | Tier 4 |  |  |  | 202, 210 | Y |  |  |  | 13577 | 5835
6044 | Big Lake to Barnhart 69 kV line: Rebuild 69 kV line | Rehab Big Lake to Barnhart 69 kV line |  | Big Lake | Barnhart | Planned | 786 - 0971 | AEP TNC | Randy Weaver mlforcum@aep.com 918-599-2674 | 2672 | 2020-12-31 |  | 69 | 0 | 17.71 | 0 |  | Reagan | Irion | Tier 4 |  |  |  | 6530, 6534 | Y | N |  |  | 13763 | 6044
6112 | Causeway - Sunchase 138 kV Line | Rehab Causeway - Sunchase 138 kV Line |  | Causeway | Sunchase | Planned | 826 - 1010 | AEP TCC | Rich Haley dnlyons@aep.com 918-599-2698 | 3627 | 2020-12-31 |  | 138 | 0 | 3.56 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8744, 8917 | Y | N |  |  | 13838 | 6112
6346 | Menard Phillips T to Junction 69 kV line: Rbld 69 kV line | Rehab Menard Phillips Tap to Junction 69 kV line | Cost Update | Menard Phillips Tap | Junction | Planned | 786 - 0971 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2712 | 2020-12-31 |  | 69 | 0 | 12.2 | 0 |  | Kimble | Kimble | Tier 4 |  |  |  | 6400, 6401 | Y | N |  |  | 14090 | 6346
6349 | CRMWD Tap #1 to Eden 69 kV line: Rebuild 69 kV line | Rehab CRMWD Tap #1 to Eden 69 kV line |  | CRMWD Tap #1 | Eden | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2710 | 2020-12-31 |  | 69 | 0 | 13.6 | 0 |  | Concho | Concho | Tier 4 |  |  |  | 6372, 6376 | Y | N |  |  | 14093 | 6349
6594 | Solstice: Add 345 kV reactor | Construct new 345 kV station with two 345/138 kV autotransformers, reactor, and build new 345 kV line from Solstice to Bakersfield |  | Solstice |  | Planned | 789 - 0974 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2729 | 2020-12-31 |  | 345 | 0 | 0 | 0 | 50,0 | Pecos |  | Tier 1 | 2016-04-01 | 2017-05-01 | 2017-06-01 | 60404 | Y | N |  |  | 14356 | 6594
6792 | Royse - Anna 138 kV Line | Upgrade existing line |  | Anna Switch | Royse Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4275 | 2020-12-31 |  | 138 | 0 | 31.3 | 0 |  | Rockwall | Collin | Tier 3 |  |  |  | 2340, 2374, 2472, 2520, 2527, 2528, 2707, 2704, 2708, 12527, 12704 | Y | N |  | 0 | 49821 | 6792
6872 | Support 69kV to 138kV Conversion Projects | Removing of Lawler substation from system to support 69kV to 138kV conversion projects |  |  |  | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2020-12-31 |  | 69 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 815, 820, 803, 806 | Y | N |  |  | 14681 | 6872
7022 | Forney - Seagoville/Tri Corner 345 kV Double-circuit Line | Upgrade Forney - Seagoville/Tri Corner 345 kV Double-circuit Line |  | Forney | Tri Corner | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4227 | 2020-12-31 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 3 |  |  |  | 13105, 2432, 2433, 2437, 3105 | Y | N |  | 0 | 49534 | 7022
7025 | Renner Sw. Sta. - Plano Tennyson Sw. Sta. 138 kV Line | Upgrade existing Renner Sw. Sta. - Plano Tennyson Sw. Sta. 138 kV Line |  | Renner Sw. Sta. | Plano Tennysson Sw. Sta. | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M3047 | 2020-12-31 |  | 138 | 0 | 10.6 | 0 |  | Collin | Collin | Tier 4 |  |  |  | 2352, 2353, 2521, 2523, 2524 | Y | N |  |  | 14847 | 7025
43456C | Greens Bayou 138kV Reconfigurations | Reposition Ckt.95C (GBY to Glenwood) to connect to GBY 'West' bus |  | Greens Bayou | Glenwood | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40710, 40715, 41221 | Y |  |  | 0 | 44998 | 43456
45503 | Lynx: Expand 138 kV station | Terminate the TNMP 16th Street to Rio Pecos 138 kV line into Lynx station | Contact and Schedule Update | Lynx |  | Planned | 983 - 1161 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2770 | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 38330, 6601, 38310, 60400, 130533 | Y | N |  | 0 | 49830 | 45503
45575 | Solstice: Add second 345 kV reactor | Add a second 345 kV reactor at Solstice | Schedule and Cost Update | Solstice |  | Planned | 997 - 1175 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2771 | 2020-12-31 |  | 345 | 0 | 0 | 0 | -50,0 | Pecos |  | Tier 4 |  |  |  | 60404 | Y | N |  | 0 | 45576 | 45575
48778 | Dustdevil: Construct New Distribution Station | Dustdevil: Construct New Distribution Station |  | Laredo VFT North | Lobo | Planned | 1029 - 1207 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3768 | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Webb | Webb | Tier 4 |  |  |  | 8038, 80013, 80221 | Y | N |  | 0 | 48779 | 48778
48782 | Progreso: Construct New Distribution Station | Progreso: Construct New Distribution Station |  | Rio Rico | Stewart Road | Planned | 1031 - 1209 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3770 | 2020-12-31 |  | 69 | 0 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8040, 8751, 8949 | Y | N |  | 0 | 48783 | 48782
49528 | NevillRoadSwitchyardProject | Nevill Road Switchyard Project as for POI |  | Neville Road | North McCamey and Bakersfield | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2020-12-31 |  | 345 | 10.3 | 0 | 0 |  | Upton | Upton | Tier 4 |  |  |  | 844, 845, 76000, 76002 | Y | N |  | 0 | 49529 | 49528
44513 | Concho to Live Oak: Rebuild 69 kV line | Rebuild remaining portions of the Concho to Live Oak 69 kV line | Company Contact, Schedule, and Cost Update | Concho | Live Oak | Planned | 941 - 1119 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2755 | 2020-12-31 01:00 |  | 69 | 0 | 3.3 | 0 |  | Tom Green | Schleicher | Tier 4 |  |  |  | 6450, 6494, 6495, 6496, 6497, 6498, 6527 | Y | N |  | 0 | 44514 | 44513
48818 | Ballinger: Replace the 138/69 kV autotransformer | Replace the 138/69 kV autotransformer at Ballinger with a 130 MVA autotransformer | NEW | Ballinger |  | Planned | 1016 - 1194 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2777 | 2020-12-31 01:00 |  | 138 | 0 | 0 | 130 |  | Runnels |  | Tier 4 |  |  |  | 6338, 6340 | Y | N |  | 0 | 48819 | 48818
14TPIT0057 | Cedar Hill Switch - Liggett 138 kV line | Upgrade Cedar Hill Switch - Dalworth existing line section |  | Cedar HIll Switch | Dalworth | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5041-E | 2020-12-31 02:02 |  | 138 | 0 | 8.6 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 1912, 1922, 2265, 2270, 2271, 2274, 2422 | Y | N |  |  | 10276 | 2926
45527 | Plano West - Richardson Collins 138 kV Line | Upgrade the Plano West - Richardson Collins 138 kV Line |  | Plano West Switch | Richardson Collins Switch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M364 | 2020-12-31 12:00 |  | 138 | 0 | 0 | 0 |  | Collin | Dallas | Tier 4 |  |  |  | 2685, 2628, 2673, 2683, 2684, 2686, 12684 | Y |  |  | 0 | 45528 | 45527
44511 | Aransas_Pass-Seawall: Rebuild and re-conductor with 795 ACSS | Rebuild and re-conductor Aransas Pass - Seawall with 795 ACSS (2000 A conductor). This will relieve overload seen in the 2025 SSWG Summer Peak case for loss of Naval Base- North Padre. |  | Aransas Pass | Seawall | Planned | 947 - 1125 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3711 | 2021-01-01 |  | 69 | 0 | 3.2 | 0 |  | Nueces | Nueces | Tier 3 |  |  |  | 8427, 8435 | Y | N |  | 0 | 44512 | 44511
7161 | Naval_Base-North_Padre: Rebuild and re-conductor | For Naval Base-North Padre Tap: Rebuild line to 138 kV standards with 2000A conductor (795 ACSS). For North Padre Tap - North Padre station, double ckt. line is already built to 138 kV standards with 477 ACSR. Re-conductor both circuits with largest possible conductor to achieve maximum rating. The 2nd ckt. is part of the North Padre - Mustang Island branch |  |  |  | Planned | 909 - 1087 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3690 | 2021-01-31 |  | 69 | 0 | 12.7 | 0 |  | Nueces | Nueces | Tier 3 |  |  |  | 8495, 8847, 8856 | Y | N |  |  | 15002 | 7161
43452A | Angleton to MONSAN Ckt.04 Upgrades | Upgrade Ckt.04 PETSON to MONSAN to increase thermal limits |  | PETSON | MONSAN | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-01-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42940, 43070 | Y | N |  | Cost included in 43452C | 48827 | 43452
43452B | Angleton to MONSAN Ckt.04 Upgrades | Upgrade Ckt.04 Liverpool to PETSON to increase thermal limits |  | Liverpool | PETSON | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-01-31 00:01 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42870, 43070 | Y | N |  | Cost included in 43452C | 48828 | 43452
5154 | Holford 138 kV new load substation and connections | Holford 138 kV new substation and its connections to CampbellSW and to Firewheel as well as some load growths at Holford |  | CampbellSW | Firewheel | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2021-02-01 |  | 138 | 0 | 1.5 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 835, 821, 838 | Y |  |  |  | 12810 | 5154
6984 | Rim Rock - Turtle Creek Transmission Line Storm Hardening | Overhaul and upgrade the 138-kV Rim Rock - Turtle Creek transmission line supporting circuit T270 with single 795 ACSR capable structures, single 795 ACSR conductor, and OPGW static. The planned T270 circuit rating is (MVA): Rate A=220, Rate B=220, Rate C=220. |  | Rim Rock | Turtle Creek | Planned | 1018968 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018968 | 2021-02-23 |  | 138 | 0 | 7.6 | 0 |  | Kerr | Kerr | Tier 4 |  |  |  | 7143, 7442 | Y | N |  |  | 14801 | 6984
5889 | MIRAGE - 138kV Substation Removal | Remove 138kV MIRAGE customer-owned substation from CNP service. |  | MIRAGE | MCCABE/BIMONT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-02-28 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42360, 40209, 42351, 40200 | Y | N |  |  | 13606 | 5889
49570 | Goodlett: Build 69 kV station | Build new Goodlett 69 kV station on the Childress to Quanah 69 kV line | NEW | Goodlett |  | Planned | 1021 - 1199 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2783 | 2021-02-28 |  | 69 | 0 | 0 | 0 |  | Hardeman |  | Tier 4 |  |  |  | 60446, 6052, 6053 | Y | N |  | 0 | 49571 | 49570
6979 | Lexington Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Lexington Substation. |  | Lexington |  | Planned | 1018928 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018928 | 2021-03-16 |  | 138 | 0 | 0 | 0 |  | Burleson |  | Tier 4 |  |  |  | 7571 | Y | N |  |  | 14796 | 6979
44854 | Lipton 138 kV Station | New Lipton 138 kV Station, replaces Lipton Hard Tap |  | Asherton | West Batesville | Planned | 973 - 1151 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3731 | 2021-03-30 |  | 138 | 0 | 0 | 0 |  | Zavala |  | Tier 4 |  |  |  | 8285, 88285, 8236, 8283 | Y | N |  | 0 | 44855 | 44854
44862 | Schottky 69 kV Station | New Schottky 69 kV Station, replaces Hard Tap |  | Sunniland | Three Rivers | Planned | 971 - 1149 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3729 | 2021-03-30 |  | 69 | 0 | 0 | 0 |  | Live Oak | Live Oak | Tier 4 |  |  |  | 8507, 88507, 8400, 8406 | Y | N |  | 0 | 45151 | 44862
45334 | Corichi: Build 138 kV Station | Build New Box Bay on El Campo - Victoria Line |  | El Campo | Ganado | Planned |  | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 |  | 2021-03-30 |  | 138 | 0 | 0 | 0 |  | Wharton | Jackson | Tier 4 |  |  |  | 8099, 88099, 8102, 8117 | Y | N |  | 0 | 45335 | 45334
5024 | Crane Loop: Rebuild 69 kV line | Rebuild Crane Loop 69 kV line | Schedule Update | Crane | Crane | Planned | 738 - 0921 | AEP TNC | Jeremy Brazeal mlforcum@aep.com 918-599-2674 | 2619 | 2021-03-31 |  | 69 | 0 | 8.05 | 0 |  | Crane | Crane | Tier 4 |  |  |  | 6600, 6603, 6607, 6609, 6606, 6608, 6613 | Y | N |  |  | 12661 | 5024
5205 | Carrizo Springs-Crystal City: 69 kV Line Rebuild | Rebuild 69 kV line from Carrizo Spring to Crystal City |  | Carrizo Springs | Crystal City | Under Construction | 761-0945 | AEP | Jeremy Brazeal dnlyons@aep.com 918-599-2698 | 3569 | 2021-03-31 |  | 69 | 0 | 13.9 | 0 |  | Dimmit | Zavala | Tier 3 | 2017-07-12 | 2017-08-07 | 2017-08-21 | 8244, 8242 | Y | N |  |  | 12864 | 5205
6167 | Harlingen SS - Raymondville #2: Convert to 138 kV | Harlingen SS - Raymondville #2: Convert to 138 kV |  | Harlingen SS | Raymondville #2 | Planned | 864 - 1042 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3650 | 2021-03-31 |  | 138 | 0 | 0 | 0 |  | Cameron | Willacy | Tier 4 |  |  |  | 8300, 8700, 80436, 8302, 8325, 8327 | Y | N |  |  | 13892 | 6167
5286B | Fayette Area Upgrades | Upgrade existing Plum - Flatonia (T133) TL with a minimum rating of 380 MVA and with OPGW. Upgrade terminal equipment at Plum to achieve a planned static normal and emergency rating of 530 MVA on Piney Creek - Plum (T535). | Planning In-Service Date Change. Updated to a phased project, the original TPIT project number is 5286. | Flatonia | Plum | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019026, 1019024 | 2021-04-30 |  | 138 | 0 | 19.6 | 0 |  | Fayette | Fayette | Tier 4 | 2017-06-29 | 2017-07-28 |  | 7248, 7274, 7307 | Y | N |  |  | 14584 | 5286
48784 | Rowe: Construct New Distribution Station | Rowe: Construct New Distribution Station |  | North McAllen | West McAllen | Planned | 1030 - 1208 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3769 | 2021-04-30 |  | 138 | 0 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8041, 8367, 8368 | Y | N |  | 0 | 48785 | 48784
11TPIT0034 | Sargent Road 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  | Sargent Road |  | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M486-E | 2021-05-15 |  | 345 | 0 | 0 | 600 |  | Dallas |  | Tier 4 |  |  |  | 2946, 2949 | Y | N |  |  | 9001 | 1784
12TPIT0080 | Forney Sw. Sta. Second 600 MVA, 345/138 kV Autotransformer | Add second 345/138 autotransformer | Project Deferral | Forney Sw. Sta. |  | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4037 | 2021-05-15 |  | 345 | 0 | 0 | 600 |  | Kaufman |  | Tier 4 | 2008-06-01 | 2008-07-01 |  | 2437, 2438 | Y | N | 2007-R2 |  | 9769 | 2489
16TPIT0054 | Dialville - Palestine South 138 kV Line | Upgrade existing Dialville - Palestine South line section |  | Dialville | Palestine South | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6019 | 2021-05-15 |  | 138 | 0 | 25 | 0 |  | Cherokee | Andrews | Tier 4 |  |  |  | 3111, 3160, 3271, 3110, 3296 | Y | N |  |  | 10458 | 3114
4304 | Tradinghouse - Sam Switch 345 kV Line | Upgrade existing double-circuit line |  | Tradinighouse | Sam Switch | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1706 | 2021-05-15 |  | 345 | 0 | 45.4 | 0 |  | McLennan | Hill | Tier 4 |  |  |  | 3405, 13405, 68090 | Y | N |  |  | 11860 | 4304
4554 | Ennis Creek - Cogdell 69 kV Line | Convert existing line to 138 kV operation |  | Ennis Creek | Cogdell | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9025 | 2021-05-15 |  | 138 | 0 | 8.6 | 0 |  | Scurry |  | Tier 3 | 2015-12-21 | 2016-10-11 |  | 1400, 1401, 1402, 1411, 1412, 11402, 752, 1410 | Y |  |  | 0 | 49764 | 4554
5310 | Everman - Venus 345 kV Double-circuit line | Upgrade existing line |  | Everman | Venus | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1735 | 2021-05-15 |  | 345 | 0 | 34.6 | 0 |  | Tarrant | Ellis | Tier 4 |  |  |  | 1882, 1886, 1906, 1907 | Y | N |  |  | 12986 | 5310
5408 | Herty N Sw. Sta. 138 kV Rebuild | Rebuild existing 138 kV switching station | Project Deferral | Herty North | Herty North | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6069 | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Angelina | Angelina | Tier 4 |  |  |  | 3317, 3319 | Y | N |  |  | 13094 | 5408
5466 | Herty North Sw. Sta. 345/138 kV Autotransformer | Install new 345/138 kV Autotransformer at Herty North Sw. Sta. |  | Herty North | Herty North | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6076 | 2021-05-15 |  | 345 | 0 | 0 | 600 |  | Angelina | Angelina | Tier 3 |  |  |  | 3321, 3322, 3319 | Y | N |  |  | 13170 | 5466
5467 | Nacogdoches Southeast_HertyN 345kV Line | Establish a new 345kV Line |  | Nacogdoches Southeast | Herty North | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6075 | 2021-05-15 |  | 345 | 13.4 | 0 | 0 |  | Nacogdoches | Angelina | Tier 2 |  |  |  | 3119, 3321 | Y | N |  |  | 13171 | 5467
5475 | Lufkin Sw. Sta. - Herty North Sw. Sta. 345 kV Line | Construct a new 345 kV Line from Lufkin Sw. Sta. to Herty North Sw. Sta. |  | Lufkin Sw. Sta | Herty North Sw. Sta. | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6077 | 2021-05-15 |  | 345 | 8.1 | 0 | 0 |  | Angelina | Angelina | Tier 2 |  |  |  | 3117, 3321 | Y | N |  |  | 13180 | 5475
5490 | Liggett - Hackberry 138 kV DCKT Line | Upgrade existing Liggett - Hackberry 138 KV Double Ckt Line |  | Liggett | Hackberry | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4222 | 2021-05-15 |  | 138 | 0 | 11.8 | 0 |  | Dallas | Dallas | Tier 3 |  |  |  | 11923, 11925, 1922, 1924, 1996, 1997, 2001, 2002, 2010, 15002, 15020, 15021, 2388, 15025, 15026, 15045, 15046 | Y | N |  | 0 | 45577 | 5490
5492 | Venus - Webb/Cedar Hill Sw. Sta. 345 kV DCKT Line | Upgrade existing Venus - Webb/Cedar Hill Sw. Sta. 345 kV Double Ckt Line |  | Ellis | Tarrant | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4230 | 2021-05-15 |  | 345 | 0 | 27 | 0 |  | Ellis | Tarrant | Tier 4 |  |  |  | 1904, 1906, 1907, 1911, 2420, 11901 | Y | N |  |  | 13230 | 5492
5526 | Forney 345 kV Switching Station | Reconstruct existing 345 kV switching station |  | Forney |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4114 | 2021-05-15 |  | 345 | 0 | 0 | 0 |  | Kaufman |  | Tier 3 |  |  |  | 2467, 2433, 2437, 2470, 2478, 150189, 2438, 12438 | Y | N |  | 0 | 49916 | 5526
5624 | Killeen Sw. Sta. 345/138 kV Autotransformer Replacement | Replace existing autotransformer |  | Killeen Sw. Sta. | Killeen Sw. Sta | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R797 | 2021-05-15 |  | 345 | 0 | 0 | 600 | -75,0 | Bell | Bell | Tier 3 |  |  |  | 3422, 3423, 13423 | Y | N |  |  | 13354 | 5624
6269 | Ennis Creek 138 kV Switching Station | Rebuild existing Ennis Creek 138 kV Switching Station | Project Deferral | Ennis Creek |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9026 | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Scurry |  | Tier 4 | 2015-12-21 | 2016-10-11 |  | 1410 | Y | N |  |  | 13999 | 6269
6273 | Saginaw 345/138 kV autotransformer | Install new autotransformer and construct new 345 kV Line at Saginaw |  | SAGINAW | HICKS | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5274 | 2021-05-15 |  | 345 | 15.6 | 0 | 600 |  | Tarrant | Tarrant | Tier 2 |  |  |  | 2065, 2066, 2067, 11957, 11958, 1436, 1860, 1864, 1957, 2068, 2081, 2069, 2070, 11860 | Y | N |  |  | 14003 | 6273
6282 | Everman - Benbrook 345 kv line | Rebuild existing 345 kV Line |  | Everman | Benbrook | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5273 | 2021-05-15 |  | 345 |  | 29 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1870, 1886, 1935 | Y |  |  |  | 14014 | 6282
6287 | Sherry Sw. - Webb/Kennedale 345 kV DCKT Line | Rebuild existing 345 kV Line |  | Sherry | Webb/Kennedale | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4252 | 2021-05-15 |  | 345 | 0 | 11.2 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1911, 1918, 1930, 1929, 1932, 1934 | Y |  |  |  | 14016 | 6287
6288 | Watermill - Trinidad 345 kV Line | Install a breaker at Watermill Sw. on the Watermill - Trinidad 345 kV Line to establish double-breaker configuration |  | Watermill | Trinidad | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4249 | 2021-05-15 |  | 345 | 0 | 0 | 0 |  | Dallas | Henderson | Tier 3 |  |  |  | 2996, 2427, 2428, 2432 | Y |  |  |  | 14017 | 6288
7024 | Norwood Sw. Sta. - Cedar Hill Sw. Sta. 345 kV Line | Upgrade existing Norwood Sw. Sta. - Cedar Hill Sw. Sta. 345 kV Line |  | Norwood | Cedar Hill | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4248 | 2021-05-15 |  | 345 | 0 | 12.4 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2406, 2410, 2420 | Y | N |  |  | 14846 | 7024
7118 | Everman 345 kV Sw. Sta. | Rebuild Everman 345 kV Sw. Sta. |  | Everman |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5278 | 2021-05-15 |  | 345 | 0 | 0 | 0 |  | Tarrant |  | Tier 3 |  |  |  | 1882 | Y |  |  |  | 14954 | 7118
7124 | Barr Ranch Tap - Barr Ranch 138 kV line | Barr Ranch Tap - Barr Ranch 138 kV line |  | Barr Ranch Tap | Barr Ranch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8373 | 2021-05-15 |  | 138 | 12.4 | 0 | 0 |  | Upton | Upton | Tier 4 |  |  |  | 11235, 71214 | Y |  |  |  | 14962 | 7124
7125 | Greenville Ave 138 kV Capacitors | Upgrade existing capacitor banks |  | Greenville Ave | Greenville Ave | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4177 | 2021-05-15 |  | 138 | 0 | 0 | 0 | 0,110.4 | Dallas | Dallas | Tier 4 |  |  |  | 2882, 2883 | Y | N |  |  | 14963 | 7125
44944 | PEC_Burnet_Bertram_Andice_138kV_Conversion | Rebuild Burnet to Bertram to Andice 69 kV line and convert to 138 kV. |  | Burnet | Andice | Planned |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 |  | 2021-05-15 |  | 69 | 0 | 0 | 0 |  | Burnet | Williamson | Tier 3 |  |  |  | 7520, 7521, 7097, 7100, 7522 | Y | N |  | 0 | 44945 | 44944
45517 | Waco West - Waco East 138 kV Line | Upgrade the Waco West Switch - Waco East Switch (Via Baylor Tap) 138 kV Line to 2071 A |  | Waco West | Waco East | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R463 | 2021-05-15 |  | 138 | 0 | 10.6 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  | 3434, 3436, 3438, 3563 | Y | N |  | 0 | 45518 | 45517
47034 | Gabriel- Rivery Transmission Line Storm Hardening | Overhaul and upgrade the 138-kV Gabriel - Rivery transmission line with bundled 795 ACSR capable structures, bundled 795 ACSR conductor (440 MVA), and OPGW static. |  | Gabriel | Rivery | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2021-05-15 |  | 138 | 2.4 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 7346, 7347 | Y | N |  | 0 | 47035 | 47034
47428 | Bellville South - Prairie View Transmission Line Upgrade | The proposed project converts the existing 69-kV transmission line T283 from Bellville South - Quanex Switch - Sunnyside Prairie View Substation to 138-kV. The proposed project improves the reliability of transmission facilities on the 26.1-mile transmission line and increases the line capacity for long term system growth. |  |  |  | Conceptual |  | SBEC | Don Roberts droberts@sbec.org |  | 2021-05-15 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 3 |  |  |  | 7269, 7660, 7664, 7666 | N | N |  | 0 | 47429 | 47428
47432 | LULING - ZORN Transmission Line OverHaul | Increase the reliability of transmission facilities on the T158 Luling - Zorn 28.3-mile 138-kV transmission line. Increase the reliability and capacity of transmission facilities on the T158 Luling - Zorn 28.3-mile 138-kV transmission line. Tear down and rebuild all existing wood structures on the SC section from Seguin split to Luling and replace with 795 ACSR Drake conductor. Add OPGW. |  | Luling | Zorn | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Caldwell | Guadalupe | Tier 4 |  |  |  | 7180, 7222, 7224 | Y | N |  | 0 | 47433 | 47432
47434 | Zorn Auto Replacement | Increase the reliability of substation equipment at Zorn Substation through replacement of the Zorn AT1 autotransformer. |  | Zorn | Zorn | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2021-05-15 |  | 345 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7042 | Y | N |  | 0 | 47435 | 47434
47450 | Naruna Circuit Breaker Addition | LCRA TSC will increase the reliability of transmission facilities along T219 Burnet - Lampasas by adding three 138-kV, 3000A, 40kAIC circuit breakers in a ring bus configuration at Naruna Substation. |  | Naruna | Naruna | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Lampasas | Lampasas | Tier 4 |  |  |  | 7063 | Y | N |  | 0 | 47451 | 47450
47513 | Pooley Road Circuit Breaker Addition | LCRA TSC will convert Pooley Road Substation to ring bus configuration by installing three 138-kV, 3000A, 40kAIC circuit breakers. |  | Pooley Road Substation | Pooley Road Substation | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7222 | Y | N |  | 0 | 47514 | 47513
47539 | Frelsburg Circuit Breaker Addition | Increase the reliability of transmission facilities on the T176 Fayetteville - Glidden 20.0-mile 138-kV transmission line. LCRA TSC will add three 138-kV, 3000A, 40kAIC circuit breakers in ring-bus configuration next to Frelsburg Substation. |  | Frelsburg Substation | Frelsburg Substation | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Colorado | Colorado | Tier 4 |  |  |  | 7263 | Y | N |  | 0 | 47540 | 47539
6777 | Cedar Hill - Liggett 138 kV Line | Loop Cedar Hill - Liggett 138 kV line in to Home Run Substation | Project Deferral | Grand Prairie West | Cedar Hill | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4270 | 2021-05-15 02:01 |  | 138 | 7 | 0 | 0 |  | Dallas | Tarrant | Tier 4 |  |  |  | 1912, 1919, 2138, 2143, 2265 | Y | N |  |  | 14571 | 6777
7116 | Riverton Sw. Sta.- Kyle Ranch 138 kV Line | Riverton Sw. Sta.- Kyle Ranch 138 kV Line |  | Riverton | Kyle Ranch | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8427 | 2021-05-18 |  | 138 | 15 | 0 | 0 |  | Reeves | Loving | Tier 2 | 2018-02-02 | 2018-05-22 |  | 11083, 11089 | Y |  |  |  | 14952 | 7116
6668A | Freeport - Master Plan | Upgrade Ckts. 18 & 27 DOW to Jones Creek to increase thermal limits |  | DOW | Jones Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-30 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 1 |  |  | 2017-12-12 | 42500, 42530 | Y | N |  |  | 14449 | 6668
5356 | Bakersfield: Build 345 kV terminal | Interconnect Maplewood solar farm at Bakersfield | Company Contact and Schedule Update | Bakersfield | Red Barn | Under Construction | 780 - 0965 | ETT | Greg Crane mlforcum@aep.com 918-599-2674 | 2640 | 2021-05-31 |  | 345 | 2.35 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 60420, 76002 | Y | N |  |  | 13042 | 5356
6029 | Anson to Stamford 69 kV line: Rebuild 69 kV line | Rehab Anson to Stamford 69 kV line | Schedule Update | Anson | Stamford | Planned | 786 - 0971 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2667 | 2021-05-31 |  | 69 | 0 | 16.08 | 0 |  | Jones | Jones | Tier 4 |  |  |  | 6172, 6173, 6175, 6180 | Y | N |  |  | 13753 | 6029
6974 | New Bremen Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at New Bremen Substation. |  | New Bremen |  | Planned | 1018919 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018919 | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Austin |  | Tier 4 |  |  |  | 7271, 7270, 7273 | Y | N |  |  | 14791 | 6974
43460 | Moody to Stewart Ckt.63 Upgrades | Upgrade Ckt.63 Moody to Stewart |  | Moody | Stewart | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 42950, 43290 | Y |  |  | 0 | 43461 | 43460
45397 | Lion: 138 kV Station | Lion: 138 kV Station with new line to Stewart Road |  | Lion | Stewart Road | Planned |  | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 |  | 2021-05-31 |  | 138 | 2.71 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8969, 8758, 8951 | Y | N |  | 0 | 50139 | 45397
48774 | Fincas: Construct New Distribution Station | Fincas: Construct New Distribution Station |  | Gateway Tap West | Wormser | Planned | 1026 - 1204 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3765 | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Webb | Webb | Tier 4 |  |  |  | 8039, 8295, 8650 | Y | N |  | 0 | 48775 | 48774
48780 | Pantera: Construct New Distribution Station | Pantera: Construct New Distribution Station |  | Wesmer | Weslaco SW | Planned | 1027 - 1205 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3766 | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8033, 8347, 8348 | Y | N |  | 0 | 48781 | 48780
49576 | Hayter: Build 138 kV station | Construct new 138 kV box bay on the Alamito Creek to Solstcie 138 kV line | NEW | Hayter |  | Planned | 1025 - 1203 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2788 | 2021-05-31 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 6680, 60385, 60444 | Y | N |  | 0 | 49577 | 49576
45015 | Barnhart to Cassava: Rebuild 69 kV line | Rebuild the Barnhart to Cassava 69 kV line | Company Contact Update | Barnhart | Cassava | Planned | 942 - 1120 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2756 | 2021-05-31 01:00 |  | 69 | 0 | 6.021 | 0 |  | Irion | Irion | Tier 4 |  |  |  | 6532, 6530, 6537, 60359 | Y | N |  | 0 | 45016 | 45015
13TPIT0124 | Airport 69 kV Substation | Build new load serving station in the 69 kV line from Lone Tree to Twin Pines Switch. |  | Airport |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-06-01 |  | 69 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  | 5601, 5600, 5602 | Y | N |  |  | 8729 | 1538
15TPIT0031 | Chavaneaux_Chavaneaux Tap Rebuild (Brooks to Chavaneaux ckt) | Rebuild 138 kV transmission from Chavaneaux to Chavaneaux Tap. This rebuild is for Brooks to Chavaneaux ckt. |  | Brooks | Chavaneaux | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0260 | 2021-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5045, 5085 | Y |  |  | There are no transformers associated with this project | 9555 | 2304
17TPIT0001 | 36th St to Merida - 138 kV Transmission Line Rebuild | Rebuild approximately four circuit miles of 138 kV transmission from 36th Street to Merida |  | 36th Street | Merida | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0196 | 2021-06-01 |  | 138 | 0 | 4 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5310, 5427 | Y | N |  | There are no transformers associated with this project | 9559 | 2308
14TPIT0038 | Northland to Mag Plant Circuit 979 Upgrade | Reconductor the existing Northland to Mag Plant circuit from single 795SCAR to bundle 795 ACSR Drake and increase rating to 2000 Amp |  | Northland Substation | Mag Plant Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | NEW | 2021-06-01 |  | 138 | 0 | 4.11 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9128, 9238 | Y | N |  | Will add the project to the base case | 9723 | 2443
3774 | Olinger-Ben Davis Line Upgrade | Olinger to Ben Davis 138 kV line upgrade to Cumberland conductor |  | Olinger | Ben Davis | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2021-06-01 |  | 138 | 0 | 17.25 | 0 |  | Collin | Dallas | Tier 4 |  |  |  | 818, 968 | Y | N |  |  | 11194 | 3774
3818 | Rebuild Calallen to Robstown | Rebuild 4-0 ACSR 69 kV to higher rated and 138 kV capable line, as originally recommended in 2013 RTP. |  | Calallen | Robstown | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-06-01 |  | 69 | 0 | 6.26 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 5626, 5634 | Y | N |  |  | 11275 | 3818
3821 | Pearsall to Palo Duro 138 kV line upgrade | Upgrade Pearsall to Palo Duro 138 kV line as recommended in 2013 RTP. Will investigate using a reconductor on existing structures with ACCC and other high temperature conductors. |  | Pearsall | Paloduro | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-06-01 |  | 138 | 0 | 10.8 | 0 |  | Frio | Frio | Tier 4 |  |  |  | 5866, 5895 | Y | N |  |  | 11278 | 3821
4883 | McCoy 69 KV substation | Add a new load serving substation between Pleasanton and Tordillo |  | McCoy |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2021-06-01 |  | 69 | 0 | 0 | 0 |  | Atascosa |  | Tier 4 |  |  |  | 5721, 5714, 5715 | Y | N |  |  | 12494 | 4883
6834D | IH20 STATCOM RPG | Install fifth and sixth 20 MVAR MSCs at Collie Capacitor Station (38035). |  | Collie Capacitor Station (38035) | Collie Capacitor Station (38035) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2021-06-01 |  | 138 | 0 | 0 | 0 | 0,40 | Reeves | Reeves | Tier 1 | 2017-10-10 | 2017-12-06 |  | 38035 | Y |  |  | 0 | 46209 | 6834
43367C | LP&L Integration Tie Lines | 345 kV Line from Abernathy to Wadsworth |  | 345 kV Abernathy | 345 kV Wadsworth | Planned |  | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2021-06-01 |  | 345 | 26.2 | 0 | 0 |  | Hale | Lubbock | Tier 1 | 2015-12-29 | 2016-06-09 |  | 59178, 79506 | Y |  |  | 0 | 43373 | 43367
43367A | LP&L Integration Tie Lines | 345 kV Line from Ogallala to Abernathy |  | 345 kV Ogallala | 345 kV Abernathy | Planned |  | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2021-06-01 |  | 345 | 50.9 | 0 | 0 |  | Castro | Hale | Tier 1 | 2015-12-29 | 2016-06-09 |  | 79501, 79506 | Y |  |  | Cost includes the expansion required at the existing stations to accommodate the new lines | 43371 | 43367
43367B | LP&L Integration Tie Lines | 345 kV Line from Abernathy to North |  | 345 kV Abernathy | 345 kV North | Planned |  | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2021-06-01 |  | 345 | 23.32 | 0 | 0 |  | Hale | Lubbock | Tier 1 | 2015-12-29 | 2016-06-09 |  | 59156, 79506 | Y |  |  | 0 | 43372 | 43367
44963 | USAA Rebuild 138 kV Station | CPSE_USAA 138 kV Substation Rebuild and Line Reconfiguration. |  |  |  | Planned | S-0896 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0285 | 2021-06-01 |  | 138 | 0.6 | 0 | 0 |  | Bexar | Bexar | Tier 4 | 2019-01-10 |  |  | 5450, 5451, 5452, 5125, 5170, 5208, 5300, 5453 | Y |  |  | 0 | 44964 | 44963
45125 | Quintana Rd to South San Rebuild | Rebuild 1.3 miles of 138 kV transmission line form Quintana Rd substation to South San substation. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0271 | 2021-06-01 |  | 138 | 0 | 1.29 | 0 |  | Bexar | Bexar | Tier 4 | 2019-01-15 |  |  | 5350, 5385 | Y |  |  | 0 | 45126 | 45125
45535 | Valley_to_ValleyTap_Rebuild | Rebuild an approximate four circuits miles of 138 kV Transmission line from Valley Tap to Valley Road substation. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0279 | 2021-06-01 |  | 138 | 0 | 4 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5025, 5053, 5465 | Y |  |  | 0 | 45536 | 45535
46938 | McCreeAdds600MVAAuto2 | McCreeAdds600MVAAuto2 |  | McCree | McCree | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2021-06-01 |  | 345 | 0 | 0 | 600 |  | Dallas | Dallas | Tier 4 |  |  |  | 983, 973, 834 | Y | N |  | 0 | 46939 | 46938
11TPIT0011 | Northeast 138kV Substation | Northeast 138kV Substation |  | Techridge | Northeast SUB |  |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2021-06-15 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9195, 9045, 9190 | Y |  |  |  | 13043 | 5357
44372 | Geronimo T1 Replacement | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Geronimo |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2021-06-25 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 7606 | Y |  |  | 0 | 44373 | 44372
43329 | Geronimo T1 Replacement | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Geronimo |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2021-06-25 02:10 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  |  | Y | N |  | 0 | 43330 | 43329
5430D | Conversion to 138kV | Reconstruct the 69kV Bonnie Brae - North Lakes to 138kV and terminate it at the new 138kV North lakes substation after the 69kV Bonnie Brae substation is converted to 138kV. Reconstruction will be completed by 12/19/2016. Cost already accounted for in the Reconstruct 69kV BonnieBrae-NLakes sub-phase. |  | Bonnie Brae | North Lakes | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2021-07-01 |  | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 905, 915 | Y | N | N/A | 0 | 43909 | 5430
5430G | Conversion to 138kV | Line already insulated for 138kV. Line will be terminated at the new 138kV Hickory substation |  | Bonnie Brae | Hickory | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2021-07-01 |  | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 905, 910 | Y | N | N/A | 0 | 43912 | 5430
5430F | Conversion to 138kV | Retire the existing 69kV North Lakes substation together with the transformer relocated from Denton North |  | North Lakes |  | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2021-07-01 |  | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 915, 928 | Y | N | N/A | 0 | 43911 | 5430
5430H | Conversion to 138kV | Construct new 138kV Hickory substation and terminate the existing Bonnie Brae - Hickory (which is already insulated for 138kV) at the new 138kV Hickory substation. |  | Bonnie Brae | Hickory | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2021-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 922, 931 | Y | N | N/A | 0 | 43913 | 5430
5430E | Conversion to 138kV | Reconstruct the 69kV Bonnie Brae - North Lakes to 138kV and terminate it at the new 138kV North lakes substation after the 69kV Bonnie Brae substation is converted to 138kV. Reconstruction will be completed by 12/19/2016. Cost already accounted for in the Reconstruct 69kV BonnieBrae-NLakes sub-phase. |  | Bonnie Brae | North Lakes | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2021-07-01 |  | 138 | 0 | 1.521 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 928, 931 | Y | N | N/A | 0 | 43910 | 5430
5559 | Add new 138kV Bonnie Brae Substation and retire the 69kV sta |  |  | Bonnie Brae |  | Planned | N/A | DENTON | Charles Sears cxsears@cityofdenton.com 940-349-7111 |  | 2021-07-01 |  | 138 | 0 | 0 | 0 |  | Denton |  | Tier 4 |  |  |  | 905, 931 | Y | N | N/A |  | 13291 | 5559
6988 | Sheriff's Posse to Marion Transmission Line Upgrade | Replace existing T-340 795 ACSR with 959 ACSS. At Sheriff Posse - Upgrade/Replace underrated switches 2967, 2969, 2971 to 3,000 Amp Switches. Replace and increase fault interrupting rating of breaker 2970 to 63kA, and its continuous rating to 3,000 Amp. Replace CS 2965 and CS 2975 to 40kA units. |  | Sheriff's Posse | Marion | Planned |  | NBU | Gregory Thomas gthomas@nbutexas.com 830-608-8953 |  | 2021-07-01 |  | 138 | 0 | 3.35 | 0 |  | Comal | Guadalupe | Tier 4 |  |  |  | 7178, 7460 | Y | N |  |  | 14806 | 6988
6540 | LCRA Gonzales to GVEC Gonzales Transmission Line Upgrade | Replace 0.98 miles of 4/0 ACSR 69 kV T-line, with double circuit 138kV structures, 795 ACSR "Drake", initially operate one circuit at 69 kV; plus terminal improvements |  | LCRA Gonzales | GVEC Gonzales | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2021-08-31 |  | 69 | 0 | 0.98 | 0 |  | Gonzales | Gonzales | Tier 4 |  |  |  | 7592, 7626 | Y | N |  |  | 14280 | 6540
6666 | BRYN_6666_Steele_Store_to_Cooks_Point | Construct 138kV line from BTU Steele Store to LCRA Cooks Point (Bundled 1033 ACSR - Curlew) |  | 32852 | 7569 | Planned |  | BRYN | James Tanneberger jtanneberger@btutilities.com 979-821-5763 |  | 2021-09-30 |  | 138 | 6 | 0 | 0 |  | Brazos | Burleson | Tier 4 | 2016-07-07 | 2017-07-07 |  | 32852, 7569 | Y |  |  |  | 14422 | 6666
48814 | Albany Foundry to Fort Griffin: Rebuild 69 kV line | Rebuild Albany Foundry to Fort Griffin 69 kV line, built to 138 kV standard with 795 ACSS conductor but energized at 69 kV, install Salt Prong box bay, install capacitor banks at Salt Prong, retire Albany Tap #1 to Hubbard Tap #1 | NEW | Albany Foundry | Fort Griffin | Planned | 1014 - 1192 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2775 | 2021-10-31 01:00 |  | 69 | 0 | 4.66 | 0 | 0,14.4 | Shackelford | Shackelford | Tier 4 |  |  |  | 6208, 6213, 60445, 6202, 6212, 60398, 6214 | Y | N |  | 0 | 48815 | 48814
47929 | Rising Star Area Rebuilds | Rising Star Area Rebuilds |  | Downing (281) | Nimrod (289) | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2021-11-01 |  | 69 | 0 | 50.04 | 60 |  | Comanche | Eastland | Tier 3 | 2019-04-04 | 2019-04-30 |  | 281, 285, 289, 293, 277, 1649 | Y |  |  | 0 | 47930 | 47929
6978 | Ranch Road 12 Circuit Breaker Addition | Add circuit breakers, in a ring bus arrangement, at Ranch Road 12 Substation. |  | Ranch Road 12 |  | Planned | 1018923 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018923 | 2021-11-17 |  | 138 | 0 | 0 | 0 |  | Hays |  | Tier 4 |  |  |  | 7186 | Y | N |  |  | 14795 | 6978
3948 | Steamboat to Tuscola: Rebuild 69 kV line | Rebuild Winters to Steamboat and Steamboat to Tuscola | Schedule and Cost Update | Steamboat | Tuscola | Planned | 685 - 0855 | ETT | Michael Forcum mlforcum@aep.com 918-599-2674 | 1851 | 2021-11-30 |  | 69 | 0 | 9.856 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6328, 6331, 60332 | Y | N |  |  | 11441 | 3948
3949 | Steamboat to Winters: Rebuild 69 kV line | Rebuild Winters to Steamboat and Steamboat to Tuscola | Schedule and Cost Update | Steamboat | Winters | Planned | 685 - 0855 | ETT | Michael Forcum mlforcum@aep.com 918-599-2674 | 1850 | 2021-11-30 |  | 69 | 0 | 9.944 | 0 |  | Taylor | Runnels | Tier 4 |  |  |  | 6333, 60332 | Y | N |  |  | 11442 | 3949
46513 | Port Isabel: Rebuild as GIS | Rebuild Port Isabel as a GIS |  | Port Isabel | - | Planned | 958 - 1136 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3716 | 2021-11-30 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8338 | Y | N |  | 0 | 46514 | 46513
49546 | Resnik: Construct New Distribution Station | Resnik: Construct New Distribution Station |  | Dupont SS | McCampbell | Planned | 996 - 1174 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3749 | 2021-11-30 |  | 138 | 0 | 0 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  | 8580, 8422, 8565, 80470 | Y | N |  | 0 | 49547 | 49546
49550 | Port Isabel: Rebuild As GIS Station | Port Isabel: Rebuild As GIS Station |  | Port Isabel |  | Planned | 958 - 1136 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3716 | 2021-11-30 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8338, 8744 | Y | N |  | 0 | 49551 | 49550
49556 | Ozona: Rebuild 69 kV station | Replace existing Ozona 69 kV station with a new 69 kV ring bus | NEW | Ozona |  | Planned | 1018 - 1196 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2780 | 2021-11-30 |  | 69 | 0 | 0 | 0 |  | Crockett |  | Tier 4 |  |  |  | 6550, 6560 | Y | N |  | 0 | 49557 | 49556
48816 | Mulberry Creek: Rebuild 345 kV station | Rebuild Mulberry Creek 345 kV station using multi-bus configuration | NEW | Mulberry Creek |  | Planned | 1015 - 1193 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2776 | 2021-11-30 01:00 |  | 345 | 0 | 0 | 0 |  | Jones |  | Tier 4 |  |  |  | 6230, 1435, 6235, 60040, 6232, 6788 | Y | N |  | 0 | 48817 | 48816
17TPIT0005 | St. Jo Autos | Replace 40 MVA autos with 60 MVA autos |  | St. Jo | St. Jo | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 12005 | 2021-12-01 |  | 138 | 0 | 0 | 60 |  | Cooke |  | Tier 4 |  |  |  | 750, 746 | Y | N |  |  | 9491 | 2243
6934B | Elm Creek - New 345 kV Reactor | Install new 345 kV 60 Mvar Reactor at Elm Creek Substation. | [5 empty] | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0873 | 2021-12-01 |  | 345 | 0 | 0 | 0 | 60,0 | Guadalupe |  | Tier 4 |  |  |  | 5133 | Y |  |  |  | 14754 | 6934
7126 | Renner TPL 138 kV Capacitors | Upgrade existing capacitor banks |  | RENNER SWITCH | RENNER SWITCH | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M3048 | 2021-12-15 |  | 138 | 0 | 0 | 0 | 0,110.4 | Dallas | Dallas | Tier 4 |  |  |  | 2352, 2353 | Y | N |  |  | 14964 | 7126
7127 | East Levee 138 kV Emergency Capacitors | Upgrade East Levee 138 kV Emergency Capacitors |  | EAST LEVEE | EAST LEVEE | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4290 | 2021-12-15 |  | 138 | 0 | 0 | 0 | 0,110.4 | Dallas | Dallas | Tier 4 |  |  |  | 2481, 2482 | Y | N |  |  | 14965 | 7127
6786 | Schumansville T2 Replacement | Replace T2, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Schumansville |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2021-12-17 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7609 | Y |  |  |  | 14580 | 6786
5496 | Forney - Royse 345 kV Line | Upgrade existing Royse - Forney 345 kV Line |  | Royse | Forney | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4235 | 2021-12-31 |  | 345 | 0 | 30 | 0 |  | Rockwall | Kaufman | Tier 3 |  |  |  | 2437, 2467, 2474, 2478 | Y | N |  | 0 | 49917 | 5496
6325 | Install two distribution transfomers at Jones Creek | Install two distribution transformers at Jones Creek. Tap Ckt.59 Jones Creek to Freeport/Surfside and Ckt.59 Jones Creek to CORTEZ |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2021-12-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 42546, 42547, 42541, 42542, 42645, 43440 | Y |  |  |  | 14060 | 6325
6873 | Support 69kV to 138kV East Loop Conversion Projects | Upgraded lines Apollo to Naaman to Walnut to Newman to support 69kV to 138kV East Loop Conversion Projects |  | Apollo | Newman | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2022-02-09 |  | 138 | 0 | 10.1 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 800, 814, 825, 826, 849, 802, 823, 806 | Y | N |  |  | 14682 | 6873
43212B | Caymus Capbanks in TNMP West Texas System | Expands Caymus Capacitor bank by 1 block of 20 Mvar. |  | Caymus (Bus #38410) | Caymus (Bus #38410) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07819 | 2022-03-15 |  | 138 | 0 | 0 | 0 | 0,20 | Reeves | Reeves | Tier 4 |  |  |  | 38410 | Y |  |  | 0 | 48414 | 43212
48415B | TransPecos Capbank in TNMP West Texas System | Expands TransPecos Capacitor bank by 1 block of 20 Mvar. |  | TransPecos (Bus #38377) | TransPecos (Bus #38377) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07919 | 2022-03-15 |  | 138 | 0 | 0 | 0 | 0,20 | Reeves | Reeves | Tier 4 |  |  |  | 38377 | Y |  |  | 0 | 48417 | 48415
6571 | Lake Pauline to Vernon 69 kV line: Rebuild taps | Lake Pauline to Vernon 69 kV line: Rebuild taps | Schedule Update | Lake Pauline | Vernon Main | Planned | 891 - 1069 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2815 | 2022-03-31 |  | 69 | 0 | 2.5 | 0 |  | Hardeman | Wilbarger | Tier 4 |  |  |  | 6048, 6056, 6057, 6058 | Y | N |  |  | 14322 | 6571
6791 | Lake Pauline: Replace 138/69 kV Auto | Replace the 138/69 kV autotransformer at Lake Pauline with a 130 MVA autotransformer | Schedule Update | Lake Pauline |  | Planned | 906 - 1084 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2730 | 2022-03-31 |  | 138 | 0 | 0 | 130 |  | Hardeman |  | Tier 4 |  |  |  | 6048, 6050 | Y | N |  |  | 14589 | 6791
7028 | Ft. Stockton SW to Rio Pecos: Rebuild 69 kV line | Rebuild Barrilla Junction to Ft. Stockton SW to Rio Pecos 69 kV line, convert to 138 kV, reterminate into Solstice, install 138 kV capacitor bank at Solstice, and build new Ft. Stockton Switch 138 kV station | Company Contact and Schedule Update | Fort Stockton Switch | Rio Pecos | Planned | 908 - 1086 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2733 | 2020-11-30 |  | 138 | 0 | 0.42 | 0 |  | Pecos | Pecos | Tier 3 | 2017-12-22 | 2018-02-02 |  | 6641, 6642, 6643, 38470, 38471, 60717, 60718, 60719, 60720, 6598, 6601, 6645 | Y | N |  | This project had its in-service date modified from 3/31/2022 to 11/30/2020 after the official TPIT posting date. See offcycle IDV 'AEP - FortStocktonSwitch-RioPecos' for the change. | 14850 | 7028
44399 | South Padre Island: Rebuild as GIS | Rebuild South Padre Island as a GIS |  | South Padre Island | - | Planned | 948 - 1126 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3712 | 2022-03-31 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8335, 8917 | Y | N |  | 0 | 44400 | 44399
45399 | Bearkat Loop - Bearkat to Longshore | Adds 345 KV line from Bearkat to Longshore. |  | Bearkat | Longshore | Planned |  | WETT/ONCOR | Christina Minchew christina.minchew@windene 512-436-9469 |  | 2022-03-31 |  | 345 | 27 | 0 | 0 |  | Glasscock | Howard | Tier 1 | 2017-08-15 | 2018-09-19 | 2018-10-09 | 1058, 59903 | Y | N |  | 0 | 45473 | 45399
5939 | Cooks Point Substation and Transmission Line Addition | Construct a load serving 138-kV substation in Northern Burleson County called Cooks Point. Construct a 16.7-mile single circuit 138-kV transmission line from Lyle Wolz to Cooks Point 138-kV transmission line with bundled 795 ACSR Drake (440 MVA). Bryan Texas Utilities will construct a 138-kV transmission line from Steele Store Substation to Cooks Point bundled 1033 ACSR Curlew (495 MVA). |  | Cooks Point | Lyle Wolz | Planned | 6666 | LCRATSC/BBEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017348 | 2022-04-08 |  | 138 | 16.7 | 0 | 0 |  | Burleson | Burleson | Tier 4 | 2016-07-07 |  |  | 7569, 7567 | Y | N |  |  | 13650 | 5939
5274 | Camp Wood - Leakey Transmission Line Overhaul | Rebuild T269 Camp Wood to Leakey to be 138-kV capable with a nominal conductor rating of 223 MVA at 138-kV (Single Drake) with OPGW and operated at 69-kV. |  | Camp Wood | Leakey | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016183 | 2022-04-11 |  | 69 | 0 | 17.3 | 0 |  | Real | Real | Tier 4 | 2015-12-16 | 2016-01-27 |  | 7426, 8633 | Y | N |  |  | 12950 | 5274
6668B | Freeport - Master Plan | New 345 kV double-circuit line from Bailey Substation to Jones Creek Substation |  | Bailey | Jones Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-04-30 |  | 345 | 55.2 | 0 | 0 |  | Wharton | Brazoria | Tier 1 |  |  | 2017-12-12 | 42530, 44040 | Y | N |  |  | 14424 | 6668
48776 | Tidehaven: Construct New Distribution Station | Tidehaven: Construct New Distribution Station |  | Blessing | Lolita | Planned | 1028 - 1206 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3767 | 2022-04-30 |  | 138 | 0 | 0 | 0 |  | Matagorda | Jackson | Tier 4 |  |  |  | 8044, 8121, 8125 | Y | N |  | 0 | 48777 | 48776
08TPIT0104 | Elgin Switching Station - Elgin 69 kV line conversion to 138 | Rebuild existing 69 kV line and convert to 138 kV operation | Project Deferral | Elgin Switching Station | Elgin | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R471-E | 2022-05-15 |  | 138 | 0 | 5.9 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 3655, 3650, 3651, 3674, 13674 | Y | N |  |  | 10653 | 1335
4270 | Handley - Hemphill 138 kV Line | Upgrade existing line | Project Deferral | Handley | Hemphill | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5214 | 2022-05-15 |  | 138 | 0 | 7.4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1950, 2164, 2167 | Y | N |  |  | 11818 | 4270
4822 | Bell County (BEC) - Gabriel (LCRA) 138 kV | Upgrade existing line | Construction schedule change | Bell County | Gabriel | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R2008 | 2022-05-15 |  | 138 | 0 | 35.2 | 0 |  | Bell | Williamson | Tier 3 |  |  |  | 121, 132, 3640, 3688, 7346, 13640 | Y | N |  |  | 12428 | 4822
4834 | Cresson - Rocky Creek 138 kV Line | Construct new line |  | Cresson | Rocky Creek | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5228 | 2022-05-15 |  | 138 | 3 | 0 | 0 |  | Tarrant | Parker | Tier 2 |  |  |  | 1881, 2202 | Y | N |  |  | 12436 | 4834
5525 | Forney - Lake Hubbard 345 kV Line | Construct new 345 kV line |  | Forney | Lake Hubbard | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4233 | 2022-05-15 |  | 345 | 0 | 7.5 | 0 |  | Kaufman | Dallas | Tier 2 |  |  |  | 2455, 2467 | Y | N |  |  | 13252 | 5525
46968 | Gabriel Substation Upgrade | LCRA TSC will upgrade the configuration of the 138-kV bus from single bus/single breaker to a breaker and a half bus configuration and replace five existing CBs at Gabriel Substation and provide for future Georgetown PWT addition. |  | Gabriel | Gabriel | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2022-05-15 |  | 138 | 0 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | Y | N |  | 0 | 46969 | 46968
47436 | ROBERT BROWN JR ¿ SAN MARCOS Transmission Line OverHaul | Increase the reliability and capability of circuit T220 on the Robert Brown Jr ¿ San Marcos 4.9-mile 69-kV transmission line. Upgrade all structures to 138-kV class and bundled Suwannee capable. Upgrade conductor to bundled 959 ACSS Suwannee. Add OPGW. |  | Robert Brown JR | San Marcos | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2022-05-15 |  | 138 | 0 | 0 | 0 |  | Hays | Caldwell | Tier 4 |  |  |  | 7191, 7194, 7196 | Y | N |  | 0 | 47437 | 47436
47442 | Graphite Mine Circuit Breaker Addition | LCRA TSC will increase the reliability of transmission facilities along T109 by adding three 138-kV, 3000A, 40kAIC circuit breakers in ring-bus configuration at the Graphite Mine Substation. |  | Graphite Mine | Graphite Mine | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2022-05-15 |  | 138 | 0 | 0 | 0 |  | Burnet | Burnet | Tier 4 |  |  |  | 7084 | Y | N |  | 0 | 47443 | 47442
47537 | Kempner Circuit Breaker Addition | LCRA TSC will add three 138kV, 3000A, 40kAIC circuit breakers in a ring bus configuration at Kempner Substation. |  | Kempner Substation | Kempner Substation | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2022-05-15 |  | 138 | 0 | 0 | 0 |  | Lampasas | Lampasas | Tier 4 |  |  |  | 260 | Y | N |  | 0 | 47538 | 47537
4804 | Wichita Falls South 345/138 kV autotransformer | Install autotransformer |  | Wichita Falls South |  | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4010 | 2022-05-16 |  | 345 | 0 | 0 | 600 |  | Archer |  | Tier 4 |  |  |  | 11464, 11465, 1422, 1425, 1464 | Y | N |  |  | 12410 | 4804
5522 | Lake Hubbard 345/138 kV Switching Station | Construct new 345/138 kV switching station |  | Lake Hubbard |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4139 | 2022-05-17 |  | 345 | 0 | 0 | 600 |  | Dallas |  | Tier 3 |  |  |  | 12455, 12456, 2401, 2402, 2455 | Y | N |  |  | 13249 | 5522
47424 | Clear Fork - Lockhart Transmission Line Overhaul | Increase the reliability and capability of circuit T601 on the Clear Fork - Lockhart 3.0-mile 69-kV transmission line.Upgrade all structures to 138-kV class and bundled Suwannee capable. Upgrade conductor to bundled 959 ACSS Suwannee. Add OPGW. |  | ClearFork | Lockhart | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2022-05-22 |  | 69 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  | 7195, 7215 | Y |  |  | 0 | 47425 | 47424
47426 | Clear Fork - Robert Brown Transmission Line Overhaul | Increase the reliability and capability of circuit T519 on the Clear Fork - Robert Brown Jr 8.8-mile 69-kV transmission line. Upgrade all structures to 138-kV class and bundled Suwannee capable. Upgrade conductor to bundled 959 ACSS Suwannee. Add OPGW. |  | Clear Fork | Robert Brown Jr | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2022-05-22 |  | 69 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  | 7194, 7195 | Y | N |  | 0 | 47427 | 47426
6875 | Support 69kV to 138kV West Loop Conversion Projects | Upgraded line Apollo to Jupiter to support 69kV to 138kV West Loop Conversion Projects |  | Apollo | Jupiter | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2022-05-27 |  | 138 | 0 | 3.1 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 803, 806, 802, 815, 829 | Y | N |  |  | 14684 | 6875
4465 | Wirtz to FlatRock to Paleface Transmission Line Upgrade | Upgrade the 17.34 mile Wirtz (7104) - Flat Rock (7111) - Paleface (7477) 138-kV transmission line to bundled 795 ACSR Drake, 441 MVA. |  | Wirtz | Paleface | Conceptual |  | PEC | Ryan Morlino ryan.morlino@peci.com 830-868-5166 |  | 2022-05-31 |  | 138 | 0 | 17.34 | 0 |  | Burnet | Travis | Tier 3 |  |  |  | 7104, 7111, 7477 | N | N |  |  | 12026 | 4465
5244 | Hardy to Northside Ckt.91 Thermal Uprate | Upgrade Ckt.91 Hardy to Northside to increase thermal ratings | - Overall Date Update | Hardy | Northside | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45840, 47711 | N | N |  |  | 12919 | 5244
5945 | Howard Lane to Wells Branch Transmission Line Upgrade | Rebuild the 0.9-mile 138-kV line from Wells Branch (7288) to Howard Lane Tap (7335) in Travis county such that the new 2-hour emergency rating is at least 710 MVA. |  | Howard Lane | Wells Branch | Conceptual |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2022-05-31 |  | 138 | 0 | 0.9 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 7288, 7335 | N | N |  |  | 13656 | 5945
5949 | Study Butte Substation and Transmission Line Addition | Rebuild Altuda - Persimmon Gap to 138-kV capable structures. Establish a new transmission line 138-kV capable operated at 69-kV from Persimmon Gap to Study Butte Substation. | Scope of project redefined | Persimmon Gap | Study Butte | Conceptual |  | LCRATSC/RGEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017405 | 2022-05-31 |  | 69 | 61 | 0 | 0 |  | Presidio | Brewster | Tier 4 |  |  |  | 76667, 76668, 76669 | N | N |  |  | 13660 | 5949
6572 | Ballinger to Eden 69 kV line: Rebuild taps | Ballinger to Eden 69 kV line: Rebuild taps |  | Ballinger | Eden | Planned | 890 - 1068 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2814 | 2022-05-31 |  | 69 | 0 | 2.8 | 0 |  | Runnels | Concho | Tier 4 |  |  |  | 6338, 6369, 6370, 6372, 6376 | Y | N |  |  | 14323 | 6572
44359 | Solstice: Install 138 kV PST and capacitor bank | Install PST on the Fort Stockton Plant to Solstice 138 kV line at Solstice | Schedule Update | Solstice |  | Planned | 984 - 1162 | AEP TNC | Adam Bittner mlforcum@aep.com 918-599-2674 | 2734 | 2020-05-31 |  | 138 | 0 | 0 | 0 | 0,14.4 | Pecos |  | Tier 4 | 2017-12-22 | 2018-02-02 |  | 60384, 6645, 60717, 6630, 60385 | Y | N |  | This project had its in-service date modified from 5/31/2022 to 5/31/2020 after the official TPIT posting date. See offcycle IDV 'AEP - SolsticePSTandCapacitor' for the change. | 44360 | 44359
16TPIT0007 | McNeil to MagPlant Ckt 977 Upgrade | Reconductor existing McNeil to MagPlant circuit from 2000 to 3000 Amp. Relocate McNeil to Summit Circuit 907 and McNeil to MagPlant Circuit 977 to separate structures |  | McNeil Substation | Mag Plant Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | P396 | 2022-06-01 |  | 138 | 0 | 3.24 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9077, 9238 | Y | N |  | Will add the ptoject to the base case. | 8207 | 1031
15TPIT0044 | Fowlerton Capacitor | Add 19.2 MVAR capacitor |  | Fowlerton |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2022-06-01 |  | 138 | 0 | 0 | 0 | 0,19.2 | La Salle |  | Tier 4 |  |  |  | 5705 | Y | N |  |  | 9835 | 2554
3334 | Fort Sam to Kirby and Fort Sam to Tenth Street MLSE Upgrade | Upgrade entire bus and terminals at Fort Sam and ensure a rating of 2000 A. |  | Fort Sam | Kirby/Tenth Street | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0744 | 2022-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5160, 5250, 5420 | Y | N |  | There are no transformers associated with this project | 10692 | 3334
4425 | New TR-AW Ckt 1032 AW-JV Ckt 961 | Old Description in Planbook Add 2nd Ckt from TR to HL to tie-in to HL-JV Ckt 961 bypassing HL and creating TR-JV Ckt. New description Ckt 1032 from TR-AW and CKT 961 from AW - JV |  | Techridge 9190 AshtonWoods 9224 | AshtonWoods 9226 Jollyville 9223 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2022-06-01 |  | 138 | 1.7 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9190, 9223, 9224, 9226 | Y | N |  |  | 11984 | 4425
45068 | Merida to Harlandale Rebuild | CPSE_Merida to Harlandale Rebuild |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0233 | 2022-06-01 |  | 138 | 0 | 10 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5190, 5310, 5385, 5395 | Y |  |  | 0 | 45069 | 45068
45084B | Braunig to Highland Rebuild | Rebuild approximately sixteen circuit miles of 138kV transmission from Braunig to Highland Hills/Brooks. This rebuild is between 'Schillers Tap to Braunig'. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0194, T-0238 | 2022-06-01 |  | 138 | 0 | 16 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5030, 5095, 5205 | Y |  |  | 0 | 45086 | 45084
45084A | Braunig to Highland Rebuild | Rebuild approximately six circuit miles of 138kV transmission from Braunig to Highland Hills/Brooks. This rebuild is between 'Highland Hills to Schillers Tap'. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0194, T-0238 | 2022-06-01 |  | 138 | 0 | 6 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5030, 5095, 5205 | Y |  |  | 0 | 45085 | 45084
45101 | Chavaneaux_Chavaneaux Tap (Chavaneaux to Palo Alto)- 138 kV | CPSE_Chavaneaux_Chavaneaux 138 kV Tap Rebuild (Chavaneaux to Palo Alto). |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0256 | 2022-06-01 |  | 138 | 0 | 0.9 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5085, 5330 | Y |  |  | 0 | 45102 | 45101
45136 | CPSE_New Midtown Substation | New Mid Town substation looped into Comal St to Olmos transmission line. |  |  |  |  | S-0910 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0283 | 2022-06-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5311, 5096, 5325 | Y |  |  | 0 | 45137 | 45136
4875 | Red Gate: Build new 138 kV line | Interconnect STEC Red Gate Power Plant at Permanent with a new 138 kV line into North Edinburg |  | Falfurrias | North Edinburg | Planned | 724 - 0906 | AEP TCC | Teresa Trotman dnlyons@aep.com 918-599-2698 | 3558 | 2022-06-10 12:00 |  | 138 | 7.5 | 7.5 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 88380, 8380, 8896, 83809, 88309, 161031 | Y | Y |  |  | 12486 | 4875
5165 | Borglum: Construct a new 138/69 kV station | Construct a new 138/69 kV Borglum station near Beeville | Schedule Update | Borglum |  | Planned | 742 - 0925 | AEP | Dave Goetz dnlyons@aep.com 918-599-2698 | 2914 | 2022-06-30 |  | 138 | 0 | 0 | 130 |  | Bee |  | Tier 1 | 2015-03-01 | 2015-09-01 | 2015-10-01 | 8196, 8197, 8205, 8107, 8198, 8199, 8904 | Y | N |  |  | 13315 | 5165
5166 | Borglum to Three Rivers: Rebuild 69 kV line | Reterminate Beeville to Three River 69 kV line into Borglum instead of Beeville and rebuild with 138 kV 795 ACSS conductor | Schedule Update | Borglum | Three Rivers | Planned | 742 - 0925 | AEP | Dave Gotez dnlyons@aep.com 918-599-2698 | 2915 | 2022-06-30 |  | 138 | 6 | 22 | 0 |  | Bee | Live Oak | Tier 1 | 2015-03-01 | 2015-09-01 | 2015-10-01 | 8196, 8198, 8199, 8400, 8403 | Y | N |  |  | 13316 | 5166
5167 | Borglum to Tuleta: Build new double circuit 138/69 kV line | Construct new Borglum station near Beeville, add 138/69 kV autotransformer capacity at Borglum, rebuild Three Rivers to Beeville 69 kV line with 959.6 ACSS/TW and convert to 138 kV and terminate into Borglum, rebuild the Beeville to Kenedy Switch 69 kV line as double circuit 138/69 kV with 959.6 ACSS/TW from Tuleta and terminate into Borglum, cut-in Beeville to Sinton 69 kV line into Borglum, and cut-in Beeville to Mathis 69 kV line into Borglum | Schedule Update | Borglum | Tuleta | Planned | 742 - 0925 | AEP | Dave Goetz dnlyons@aep.com 918-599-2698 | 2916 | 2022-06-30 |  | 138 | 23.5 | 10.5 | 0 |  | Bee | Bee | Tier 1 | 2015-03-01 | 2015-09-01 | 2015-10-01 | 88198, 8196, 8197, 8198, 8592, 8590, 8593 | Y | N |  |  | 13317 | 5167
5430I | Conversion to 138kV | Switch the Hickory - Locust line on to the 138kV substations |  | Hickory | Locust | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2022-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 914, 910 | Y | N | N/A | 0 | 43914 | 5430
5430J | Conversion to 138kV | Construct a new 138kV Eagle substation along the 138kV Hickory - Locust line |  | Eagle |  | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2022-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 926, 924 | Y | N | N/A | 0 | 43915 | 5430
44416 | Add a 2nd circuit at Brinker - Denton Steam |  |  | Brinker | Denton Steam | Planned |  | DENTON | Chuck Sears |  | 2022-07-01 |  | 138 | 0.63068 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 927, 982 | Y | N |  | 0 | 44417 | 44416
3505 | Cibolo Substation, T3 transformer addition | Add T3, 40 MVA 138-26.18 kV power transformer, CSW and low side |  | Cibolo |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2022-10-14 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7608 | Y | N |  |  | 10887 | 3505
44866 | Dilley - Jourdanton 69 kV Line | Rebuild Dilley - Jourdanton 69 kV Line |  | Dilley | Jourdanton | Planned | 967 - 1145 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3725 | 2022-10-30 |  | 69 | 0 | 44.8 | 0 |  | Frio | Atascosa | Tier 4 |  |  |  | 8206, 8208, 8607 | Y | N |  | 0 | 44867 | 44866
49572 | Goodlett to Quanah: Build a new portion of 69 kV line | Build new section of 69 kV line between Goodlett and Quanah | NEW | Goodlett | Quanah | Planned | 1022 - 1200 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2784 | 2022-10-31 |  | 69 | 0 | 0 | 0 |  | Hardeman |  | Tier 4 |  |  |  | 6051, 6052, 60446 | Y | N |  | 0 | 49573 | 49572
5940A | Mountain Home Substation and Transmission Line Addition | Construct new Mountain Home substation and construct a 138-kV transmission line from Hunt substation to Mountain Home substation. | For total project cost please see 5940_C | Hunt | Mountain Home | Planned |  | LCRATSC/CTEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017394 | 2022-12-27 |  | 138 | 7.5 | 0 | 0 |  | Kerr | Kerr | Tier 1 | 2016-11-18 |  |  | 7750, 7144 | Y | N |  | 0 | 46980 | 5940
5940B | Mountain Home Substation and Transmission Line Addition | Construct a 138-kV transmission line from Harper substation to Mountain Home substation. | For total project cost please see 5940_C | Mountain Home | Harper | Planned |  | LCRATSC/CTEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017394 | 2022-12-27 |  | 138 | 11.5 | 0 | 0 |  | Kerr | Gillespie | Tier 1 | 2016-11-18 |  |  | 74100, 7410, 7750 | Y | N |  | 0 | 46981 | 5940
5940C | Mountain Home Substation and Transmission Line Addition | Add one(1) 138/69-kV autotransformer at Harper substation |  | Harper | Live Oak | Planned |  | LCRATSC/CTEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017394 | 2022-12-27 00:10 |  | 138 | 0 | 21.7 | 45 |  | Gillespie | Gillespie | Tier 1 | 2016-11-18 |  |  | 7412, 7130, 7132, 7149, 7410, 7413, 74100 | Y | N |  | 0 | 46982 | 5940
6876 | Support 69kV to 138kV West Loop Conversion Projects | Upgraded line Jupiter to College to support 69kV to 138kV West Loop Conversion Projects |  | Jupiter | College | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2022-12-31 |  | 138 | 0 | 2.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 806, 829 | Y |  |  |  | 14685 | 6876
49948 | McCreeShilohLineUpgrades | McCree to Shiloh Line Upgrades to Cumberland |  | McCree | Shiloh | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2022-12-31 |  | 138 | 0 | 2.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 830, 834 | Y | N |  | 0 | 49949 | 49948
6072 | Eldorado to Ft. McKavitt 69 kV line: Rebuild 69 kV line | Rehab Eldorado to Ft. McKavitt 69 kV line | Schedule Update | Eldorado Tap | Ft. McKavitt | Planned | 786 - 0971 | AEP TNC | Dewey Peters mlforcum@aep.com 918-599-2674 | 2677 | 2023-01-31 |  | 69 | 0 | 19.41 | 0 |  | Schleicher | Schleicher | Tier 4 |  |  |  | 6505, 6506, 6507, 6508 | Y | N |  |  | 13794 | 6072
6373 | Hamilton Road to Picacho ckt #2, rebuild 138 kV line | Rebuild Hamilton Road to Picacho 138 kV line ckt #2 |  | Hamilton Road | Picacho | Planned | 870-1051 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3660 | 2023-03-30 |  | 138 | 0 | 8.4 | 0 |  | Val Verde | Val Verde | Tier 4 |  |  |  | 8186, 8255, 8690, 8688, 8684 | Y | N |  |  | 14117 | 6373
4827 | Lufkin - Nacogdoches Southeast 138 kV Line | Upgrade existing line |  | Lufkin | Nacogdoches | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6062 | 2023-05-15 |  | 138 | 0 | 21.6 | 0 |  | Angelina | Nacogdoches | Tier 4 |  |  |  | 3120, 3314, 3316, 3315, 3318 | Y | N |  |  | 12434 | 4827
5436 | Morgan Creek - McDonald 138 kV Line | Upgrade existing line | Project Deferral | Morgan Creek | McDonald Rd | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8360 | 2023-05-15 |  | 138 | 0 | 31.8 | 0 |  | Howard | Mitchell | Tier 3 |  |  |  | 1032, 1333 | Y | N |  |  | 13139 | 5436
5479 | Trinidad_TriC_Watermill_345kV_DCKT | Upgrade existing DCKT line |  | Trinidad Sw. Sta | TriCorner/Watermill | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4045 | 2023-05-15 |  | 345 | 0 | 92.1 | 0 |  | Henderson | Dallas | Tier 3 |  |  |  | 2427, 2432, 3123, 3124 | Y | N |  |  | 13184 | 5479
5981 | Shamburger North 345/138 kV Sw. Sta. | Establish Shamburger North 345/138 kV Sw. Sta. |  | Shamburger North |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6083 | 2023-05-15 |  | 345 | 0 | 0 | 600 |  | Smith | Smith | Tier 3 |  |  |  | 3217, 3223, 3226, 2470, 2478, 3103, 3201, 3206 | Y | N |  |  | 13696 | 5981
5982 | Relocate existing Shamburger North - Shamburger 138 kV Line | Establish 138 kV Line |  | Shamburger North | Shamburger | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6084 | 2023-05-15 |  | 138 | 10 | 0 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3104, 3206, 3226 | Y | N |  |  | 13697 | 5982
6291 | Royse Sw. Sta. - Farmersville Sw. Sta. 345 kV DCKT Line | Rebuild existing 345 kV Line |  | Royse | Farmersville | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4255 | 2023-05-15 |  | 345 | 0 | 30.4 | 0 |  | Rockwall | Collin | Tier 3 |  |  |  | 1685, 2461, 2478 | Y |  |  |  | 14020 | 6291
7023 | Hicks Sw. Sta. - Roanoke Sw. Sta. 345 kV Double-circuit Line | Upgrade existing Hicks Sw. Sta. - Roanoke Sw. Sta. 345 kV Double-circuit Line |  | Hicks Sw. Sta. | Roanoke Sw. Sta. | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5256 | 2023-05-15 |  | 345 | 0 | 19.4 | 0 |  | Tarrant | Denton | Tier 3 |  |  |  | 1845, 1851, 1847, 1853, 2081 | Y | N |  |  | 14845 | 7023
3297 | Tezel Road - New 138kV Substation | Loop new 138 kV substation into the existing 138 kV Helotes to Bandera line. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2023-06-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 5421, 5020, 5200 | Y |  |  | There are no transformers associated with this project | 10840 | 3297
5942 | Merriltown Substation Addition | Add a new 138-kV breakered substation between Wells Branch and Round Rock South on T526 approximately 0.21 miles from Wells Branch. The substation will serve Oncor load. |  | Wells Branch | Round Rock South | Conceptual |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2023-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Williamson | Tier 4 |  |  |  | 7290, 3672, 7288 | Y | N |  |  | 13653 | 5942
6253 | AEN_New_Kramer_Lane_Substation |  |  | 9238 | 9276 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2023-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9276, 9077, 9238 | Y |  |  |  | 13981 | 6253
45029 | Grandview Highland Hills Rebuild | CPSE_Rebuild of 138 kV double circuit line Line between Grandview to Highland Hills. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0273 | 2023-06-01 |  | 138 | 0 | 11.6 | 0 |  | Bexar | Bexar | Tier 4 | 2019-01-11 |  |  | 5030, 5175, 5095, 5205 | Y |  |  | 0 | 45030 | 45029
48327 | Reconductor 138kV ckt 972 Howard Lane to McNeil to 3000A. |  |  | 9079 | 9217 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinene (512) 322-6740 |  | 2023-06-01 |  | 138 | 0 | 2.81 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9079, 9217 | Y |  |  | 0 | 48328 | 48327
44946 | CPSE_New_Scenic_Loop_138kV_Load_Serving_Station | The new Scenic Loop 138 kV load serving station will be looped into existing Ranchtown to LCRA (Menger Creek) 138 kV transmission line. The substation should be located south west of the existing Fair Oaks Ranch and north east of the existing Ranchtown substation. |  |  |  | Planned | S-0885 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0275 | 2023-06-01 20:00 |  | 138 | 9 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5363, 5358, 7665 | Y |  |  | 0 | 44947 | 44946
20TPIT0000 | Parkway Substation T1 Replacement | Replace T1, 20 MVA with a 40 MVA 138-13.09 kV transformer |  | Parkway |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2023-06-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7611 | Y | N |  |  | 10679 | 3323
5430K | Conversion to 138kV | Construct a new 138kV Eagle substation along the 138kV Hickory - Locust line |  | Eagle |  | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 922, 926 | Y | N | N/A | 0 | 43916 | 5430
5430L | Conversion to 138kV | Reconnect the 69kV Hickory - RD Wells to the 138kV Hickory and RD Wells substations. Line is already insulated for 138kV. |  | Hickory | RD Wells | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 922, 930 | Y | N | N/A | 0 | 43917 | 5430
5430N | Conversion to 138kV | Retire the existing 69kV RD Wells substation together with the autotransformers |  | RD Wells |  | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 932, 930 | Y | N | N/A | 0 | 43919 | 5430
5430M | Conversion to 138kV | Transfer the 69kV Hickory - RD Wells to the 138kV Hickory and RD Wells substations. Line is already insulated for 138kV. |  | Hickory | RD Wells | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 910, 932 | Y | N | N/A | 0 | 43918 | 5430
5461 | Load serving |  |  | Puckrus | Mayhill | Planned |  | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2023-07-01 |  | 138 | 1.9 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 929, 917 | Y | N |  |  | 13164 | 5461
45511 | Laredo - Del Mar: 138 kV Line Rebuild | Rebuild Laredo - Del Mar 138 kV Line with 795 ACSS |  | Laredo | Del Mar | Conceptual | 992 - 1170 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3746 | 2023-07-01 |  | 138 | 0 | 2.73 | 0 |  | Webb | Webb | Tier 4 |  |  |  | 8293, 8645 | Y | N |  | 0 | 45512 | 45511
45513 | Santo Nino - Wormser: 138 kV Line Rebuild | Rebuild Santo Nino - Wormser 138 kV line with 795 ACSS |  | Santo Nino | Wormser | Conceptual | 991 - 1169 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3745 | 2023-07-01 |  | 138 | 0 | 0 | 0 |  | Webb | Webb | Tier 4 |  |  |  | 8295, 8649, 8653 | Y | N |  | 0 | 45514 | 45513
45566 | Holly - Southside: 138 kV Line Rebuild | Rebuild Holly - Southside 138 kV Line |  | Holly | Southside | Conceptual | 994 - 1172 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3747 | 2023-07-01 |  | 138 | 0 | 1.8 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8483, 8486, 8496 | Y | N |  | 0 | 45567 | 45566
48854 | Adds Annova and Port South Bus and lines | Adds Annova and Port South buses, lines to connect Annova to Port South, line from HWY 511 to Port South, and reconnects line from S Carbide to HWY 511 into Port South |  | Annova LNG | Port South | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2023-09-01 |  | 138 | 22.1 | 0 | 0 | 0,120 | Cameron | Cameron | Tier 4 |  |  |  | 5775, 5776, 5767, 8337 | Y | N |  | 0 | 48855 | 48854
4490 | LaPalma: Add 2nd 345/138 kV autotransformer | Add 345/138 kV autotransformer capacity at LaPalma |  | LaPalma |  | Planned | 710 - 0880 | AEP TCC | Teresa Trotman dnlyons@aep.com 918-599-2664 | 2904 | 2023-09-30 |  | 345 | 0 | 0 | 675 |  | Cameron |  | Tier 3 |  |  |  | 8356, 8317, 8314 | N | N |  |  | 12067 | 4490
14TPIT0098 | Cost Substation Addition | Upgrade the existing 69-kV substation |  | Cost |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2023-11-17 |  | 69 | 0 | 0 | 0 |  | Gonzales |  | Tier 4 |  |  |  | 7622 | Y | N |  |  | 10677 | 3321
17TPIT0031 | Elkton 345/138 kV autotransformer | Replace existing autotransformer |  | Elkton | Elkton | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6032-E | 2024-05-15 |  | 345 | 0 | 0 | 600 |  | Smith | Smith | Tier 3 |  |  |  | 3105, 3106, 29150 | Y | N |  |  | 10501 | 3155
4821 | Nacogdoches Southeast - Herty North 138 kV Line | Upgrade existing line |  | Nacogdoches Southeast | Herty North | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6049 | 2024-05-15 |  | 138 | 0 | 13.4 | 0 |  | Nacogdoches | Angelina | Tier 4 |  |  |  | 3120, 3319 | Y | N |  |  | 12427 | 4821
5524 | Royse South 345/138 kV Switching Station | Establish new 345/138 kV switching station |  | Royse | Forney | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4234 | 2024-05-15 12:00 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 3 |  |  |  | 2469, 2470, 12471, 2437, 2471, 2478, 2474, 2710, 3103, 12702 | Y | N |  | 0 | 49918 | 5524
22TPIT0000 | Parkway Substation | Replace T2, 20 MVA with a 40 MVA 138-13.09 kV transformer |  | Parkway |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2024-05-24 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7611 | Y | N |  |  | 10680 | 3324
6304 | Shamburger North - Shamburger 345 kV Line | Upgrade existing 345 kV Line |  | Shamburger North | Shamburger | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6085 | 2024-05-28 |  | 345 | 10 | 10 | 0 |  | Smith | Smith | Tier 3 |  |  |  | 3103, 3223 | Y | N |  |  | 14033 | 6304
4477 | Austrop to Sandow Double 345-kV Transmission Line Upgrade | Upgrade 33.98-mile Austrop (7040) to Sandow (13429) 345-kV double circuit transmission lines to bundled 959 Suwannee conductor (1921 MVA). |  | Austrop | Sandow | Conceptual |  | LCRATSC/Oncor | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2024-05-31 |  | 345 | 0 | 67.96 | 0 |  | Travis | Milam | Tier 1 |  |  |  | 7040, 13429 | N | N |  |  | 12038 | 4477
4479 | Cut T511 Gilleland Creek to Clear Springs into AEN Dunlap | Cut-In the existing Gilleland Creek (7340) to Clear Springs (7050) T511 345kV transmission line into Austin Energy's Dunlap (9044) substation. |  | Gilleland Creek | Clear Springs | Conceptual |  | LCRATSC/AEN | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2024-05-31 |  | 345 | 4 | 0 | 0 |  | Travis | Guadalupe | Tier 1 |  |  |  | 7050, 7340, 9044 | N | N |  |  | 12043 | 4479
5287 | Buda to Turnersville Transmission Line Addition | Construct a second 138-kV transmission line between Buda and Turnersville Substations. |  | Buda | Turnersvile | Conceptual |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2024-05-31 |  | 138 | 0 | 0 | 0 |  | Hays | Hays | Tier 3 |  |  |  | 7498, 7500 | N | N |  |  | 12963 | 5287
19TPIT0000 | Weser Substation | Replace 5.6 MVA with 69-13.09 kV, 20 MVA transformer |  | Weser |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2024-06-28 |  | 69 | 0 | 0 | 0 |  | Goliad |  | Tier 4 |  |  |  | 7239 | Y | N |  |  | 10694 | 3336
3901 | Lobo to Freer: Rebuild 69 kV line | Rebuild Lobo to Freer 69 kV line with 795 ACSS | Description Update | Lobo | Freer | Planned | 677 - 0846 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 2596 | 2024-06-30 |  | 69 | 0 | 49.8 | 0 |  | Webb | Duval | Tier 3 |  |  |  | 8505, 80222 | N | N |  |  | 11371 | 3901
44419 | Load serving |  |  | Mayhill | Denton Steam/Brinker | Planned |  | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2024-07-01 |  | 138 | 5.1 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 927, 929, 982 | Y | N |  | 0 | 44420 | 44419
49926 | Brinker-DentonSteam Ckt1 Upgrade |  |  | Brinker | Denton Steam | Planned |  | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2024-07-01 |  | 138 | 0 | 0.63 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 927, 982 | Y | N |  | 0 | 49929 | 49926
13TPIT0070 | Nash Creek Substation | Replace existing PWT with new 69kVx13.09 kV, new Control House, CSW, structures, containment foundations, bus, panels, etc |  | Nash Creek |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2024-12-16 |  | 69 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7596 | Y | N |  |  | 10678 | 3322
49817B | 4x20 MVAR Elm Street Capacitor Bank | Install additonal 2x20 MVAR blocks (80 MVAR total) to Elm Street Capacitor Bank |  | Elm Street (Bus # 38049) | Elm Street (Bus # 38049) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2025-06-01 |  | 138 | 0 | 0 | 0 | 0,40 | Reeves | Reeves | Tier 4 |  |  |  | 38049 | Y |  |  | 0 | 49819 | 49817
15TPIT0033 | Randolph - 138 kV Substation Equipment Upgrade | Upgrade the Weiderstein and Tuttle terminals and ensure a 2000 A rating (minimum). Reconfigure and-or upgrade the main bus to ensure a 2000 A rating (minimum). |  | Randolph | Tuttle-Weiderstein | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0645b | 2025-06-01 12:00 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5360, 5435 | Y | N |  | There are no transformers associated with this project | 9557 | 2306
6774 | Marina: Add New Distribution Station | Add New Marina Distribution Station |  | Highway 9 | Nueces Bay | Planned | 878 - 1056 | AEP TCC | Teresa Trotman dnlyons@aep.com 918-599-2698 | 3665 | 2026-01-30 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8026, 8441, 8470, 8474 | Y | N |  |  | 14780 | 6774
3276 | JT Deely to Martinez MLSE Upgrade | Upgrade terminal at JT Deely to ensure a rating of 2386 A (minimum). |  | JT Deely | Martinez | Planned | S-0759 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2026-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5110, 5294 | Y | N |  | There are no transformers associated with this project | 10627 | 3276
1549 | Devine Switch breaker addition | Adds breakers to Devine Switch to allow closing of normally open Devine Switch to Devine. Creates 3- terminal switching station |  | Devine Switch |  | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2027-06-01 |  | 69 | 0 | 0 | 0 |  | Medina |  | Tier 4 |  |  |  | 5857, 58570 | N | N |  |  | 8754 | 1549
2161 | Oaks to Loxley | Build new 138 kV 795 ACSR circuit from Oaks to a new AEP switching station Loxley in the Leon Creek to Pleasanton line | Load forecasts have changed since project was RPG approved | Oaks | Loxley | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2027-06-01 |  | 138 | 6 | 0 | 0 |  | Atascosa | Atascosa | Tier 3 | 2011-12-16 | 2012-04-25 |  | 5713, 80491 | N | N |  | This new line was part of Karnes Electric Cooperative Project that was approved in 2012. While much of the projected load is now on the system, not all of the projected load materialized. Studies with newer load projections have not shown the need for this line. STEC recommends evaluating this project as an option when studies show the need for a project in this area of the transmission system. | 9408 | 2161
3595 | Bevo to AEP Carrizo Springs 69 kV line | Add 2 mile line by double circuiting two existing circuits, as recommended in 2013 RTP. |  | Bevo | Carrizo Springs | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2027-06-01 |  | 69 | 0 | 2 | 0 |  | Dimmit | Dimmit | Tier 1 | 2012-04-12 | 2012-08-12 | 2012-09-12 | 5871, 8244 | N | N |  | This new line was part of Karnes and Medina Electric Cooperatives Project that was approved in 2012. This also helped voltage on AEP transmission under contingencies. While much of the projected load is now on the system, not all of the projected load materialized. Studies with newer load projections have not shown the need for this line. STEC recommends evaluating this project as an option when studies show the need for a project in this area of the transmission system. | 10984 | 3595
3822 | San Miguel to Sigmor 138 kV line upgrade | Upgrade San Miguel to Sigmor 138 kV line as recommended in 2013 RTP. Will investigate re-conductoring on existing structures with ACCC and other high temperature conductors. |  | San Miguel | Sigmor | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2027-06-01 |  | 138 | 0 | 26.3 | 0 |  | Atascosa | Live Oak | Tier 3 |  |  |  | 5689, 5902, 8404 | N | N |  | Studies after the 2013 RTP have shown that AEP's approved project to rebuild the 69 kV Beeville to Three Rivers to 138 kV, TPIT 5166, reduces the loading on this line. STEC believes that rebuilding San Miguel to Sigmor is likely to be justified in the future by load growth and or generation additions. STEC recommends evaluating this project as an option when studies show the need for a project in this area of the transmission system. | 11279 | 3822
5220 | Move Orange Grove load to 138 kV bus | Move load from the 69 KV to the 138 KV instead of replacing auto. 2015 RTP |  | Orange Grove |  | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2027-06-01 |  | 138 | 0 | 0 | 0 |  | Jim Wells |  | Tier 4 |  |  |  | 5660 | N | N |  |  | 12887 | 5220
15TPIT0004 | Converse - New 138kV Substation | Loop new 138kV substation into future 138kV Martinez to Skyline transmission line |  | Converse | Martinez-Skyline | Planned | T-0177 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0601 | 2028-06-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5098, 5294, 5368 | Y | N |  | There are no transformers associated with this project | 8143 | 967
12TPIT0009 | Masterson Rd - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to Howard line. |  | Masterson Rd. | Cagnon-Howard | Planned | T-0910 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0538 | 2028-06-01 |  | 138 | 8 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5296, 5054, 5230 | Y | N |  | There are no transformers associated with this project | 9466 | 2218
12TPIT0004 | Sulpher Springs - New 138kV Substation | Loop new 138kV substation into the existing 138kV OW Sommers to Kirby line |  | Sulpher Springs | OW Sommers-Kirby | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0385 | 2028-06-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5416, 5250, 5395 | Y | N |  | There are no transformers associated with this project | 10365 | 3021
5717 | Waller 138kV Substation Reconfiguration | Convert Waller substation from single-circuit radial service to radial & tap service. Install new tap section from Ckt.65 Hockley to Peters. |  | Waller | Hockley/Peters | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2030-12-31 |  | 138 | 2.4 | 0 | 0 |  | Harris | Austin | Tier 4 |  |  |  | 46561, 46560, 45885, 46220 | N | N |  |  | 13459 | 5717
5763C | CHORIN to STRANG Ckt.87 | STRANG to Cedar Bayou Ckt.87 |  | STRANG | Cedar Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2031-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40010, 41500 | Y | N |  | 0 | 45414 | 5763
4997E | Deepwater Area Conversions | Upgrade Harrisburg substation for Ckt.33 loop service. | - Project cancelled...Breakers will remain at Harrisburg substation | Harrisburg | TEXPET/ Reed | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 986 | 2099-10-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40470, 40800, 41040, 41560 | Y |  |  | 0 | 43263 | 4997

## CompletedTPIT060119NoCost
JUNE BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 6/1/2019
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar ) (-Reactor, +Capacitor ) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number
5203 | Bessel 138 kV Station: Install Cap Bank | Install a 14.4 MVAR Cap Bank at Bessel 138 kV station |  | Bessel |  | In-Service | 764-0949 | AEP TCC | James Weaver dnlyons@aep.com 918-599-2698 | 3572 | 2018-01-04 |  | 138 | 0 | 0 | 0 | 0,24.4 | Nueces |  | Tier 4 |  |  |  | 8060 | Y | N |  |  | 12862 | 5203
5713 | Upgrade the Brownwood - Brownwood Sw. | Upgrade the Brownwood - Brownwood Sw. Sta. 138 kV Line |  | Brownwood Sw. Sta. | Brownwood South | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1738 | 2018-01-15 |  | 138 | 0 | 7.4 | 0 |  | Brown | Brown | Tier 4 |  |  |  | 1655, 1656, 1657, 1661 | Y |  |  |  | 13452 | 5713
09TPIT0122 | Shamburger - Tyler NW 138 kV line | Upgrade existing 138 kV line | Construction schedule change | Shamburger | Tyler NW | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6001-E | 2018-01-15 |  | 138 | 0 | 6.3 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3104, 3141 | Y | N | 2009-E6 |  | 8418 | 1240
4263 | Tyler Northwest - Elkton 138 kV Line | Upgrade existing Tyler West - Tyler Northwest 138 kV line Section |  | Tyler West | Tyler Northwest | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6053 | 2018-01-15 |  | 138 | 0 | 3.7 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3139, 3141 | Y | N |  |  | 11811 | 4263
4268 | Breckenridge - Leon Switch 69 kV Line | Upgrade existing line |  | Breckenridge | Leon Switch | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R783 | 2018-01-15 |  | 69 | 0 | 17 | 0 |  | Stephens | Eastland | Tier 3 |  |  |  | 271, 1622, 1615, 1625 | Y | N |  |  | 11816 | 4268
5403 | Lufkin 138 kV Sw. Sta. Rebuild | Rebuild existing 138 kV switching station |  | Lufkin Sw. Sta. | Lufkin Sw. Sta. | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6067 | 2018-01-15 |  | 138 | 0 | 0 | 0 |  | Angelina | Angelina | Tier 4 |  |  |  | 3118, 3349 | Y | N |  |  | 13089 | 5403
4299 | Big Brown - Navarro Switch 345 kV Line | Upgrade existing double-circuit line | Construction Schedule Change | Big Brown | Navarro Switch | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1705 | 2018-01-15 |  | 345 | 0 | 62 | 0 |  | Freestone | Navarro | Tier 4 | 2015-06-15 |  |  | 3380, 68091 | Y | N |  |  | 11855 | 4299
6087 | Flat Top 345 kV Switching Station | Flat Top 345 kV Switching Station |  | Comanche | Brown | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1740 | 2018-01-15 |  | 345 | 0 | 0 | 0 |  | Comanche | Comanche | Tier 4 |  |  |  | 11441, 1440, 1444 | Y | N |  |  | 13811 | 6087
6562B | Crowley - Cresson 69 kV Line Conversion | Rebuild existing 69 kV line section from Crowley - Cresson |  | Crowley | Cresson | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5244 | 2018-01-15 |  | 138 | 0 | 9.1 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2203, 2204, 2205, 12205, 12209, 1883, 1884, 1967, 1968 | Y | N |  |  | 14308 | 6562
4273 | Corsicana - Trinidad 69 kV Line | Upgrade existing line | Construction schedule change | Corsicana | Trinidad | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R794 | 2018-01-15 |  | 69 | 0 | 26.5 | 0 |  | Navarro | Henderson | Tier 3 | 2015-06-15 | 2015-08-15 |  | 3128, 3466, 3467, 3468, 3469 | Y | N |  |  | 11822 | 4273
5405 | Lufkin Corridor Expansion | Rebuild existing Lufkin - Lufkin Sw. Sta. 138 kV lines |  | Lufkin | Lufkin | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6074 | 2018-01-15 |  | 138 | 0 | 4.2 | 0 |  | Angelina | Angelina | Tier 4 |  |  |  | 3118, 3316, 3340, 3268, 3341 | Y | Y |  |  | 13091 | 5405
5398 | Lufkin Pershing 138 kV Emergency Capacitors | Install 18.4 MVar Cap Bank at Lufkin PershingTap |  | Lufkin Pershing Tap | Lufkin Pershing Tap | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6070 | 2018-01-15 |  | 138 | 0 | 0 |  | 0,18.4 | Angelina | Angelina | Tier 4 |  |  |  | 3329 | Y | N |  |  | 13085 | 5398
4082 | CPSE_Howard to Somerset Rebuild | Rebuild approximately seven miles of 138 kV transmission circuit from Howard to Somerset. The Howard to Somerset circuit should be upgraded to 469 MVA, minimum. |  | Howard | Somerset | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0232 | 2018-01-19 |  | 138 | 0 | 7.56 | 0 |  | Bexar | Bexar | Tier 2 | 2014-05-07 | 2014-09-04 |  | 5230, 5390 | Y | N |  |  | 11607 | 4082
5208A | SPLIT INTO PHASES SC ADDITIONS |  |  | Alibates |  |  |  | SHRY | Brad Schwarz 512-289-7425 |  | 2018-01-23 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  | 79520, 79522, 79500 | Y |  |  |  | 14503 | 5208
4253 | Eagle Mountain-Calmont 138 kV Line | Upgrade existing double-circuit line |  | Eagle Mountain | Calmont | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5213 | 2018-01-30 |  | 138 | 0 | 40.8 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1953, 1954, 1975, 1976, 902835, 1865, 1955, 2085, 2086, 2087, 2088, 11860 | Y | N |  |  | 14425 | 4253
6599 | Service to Danforth Substation | GVEC will tie into the AEP Kenedy Switch to Coleto Creek 138 T-line ckt to service the DCP Midstream Danforth Substation, GVEC will only meter the load. |  | Rosata POD | Danforth | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2018-01-30 |  | 138 | 0.029 | 0 | 0 |  | Goliad | Goliad | Tier 4 |  |  |  | 7241, 88153 | Y | N |  |  | 14585 | 6599
5731A | Tri Corner 345 kV Sw Sta | Temporary Configuration for Tri Corner |  | Tri Corner | Tri Corner | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4228 | 2018-02-01 |  | 345 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2432, 2428, 2433, 3102, 3124 | Y |  |  |  | 14310 | 5731
3272 | Potranco - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to AMD line. |  | Cagnon | AMD | Planned | S-845 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0219 | 2018-02-08 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5346, 5002, 5053 | Y | N |  | There are no transformers associated with this project | 10623 | 3272
11TPIT0107 | Steamboat: Reterminate 69 kV Happy Valley tap | Reterminate the Happy Valley tap into Steamboat | IN SERVICE | Happy Valley | Steamboat | In-Service | 341 - 0515 | ETT | Teresa Trotman mlforcum@aep.com 918-599-2674 | 2092 | 2018-02-14 | 2018-02-14 | 69 | 0 | 0.6 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6332, 6328, 6330, 6331, 60332 | Y | N |  |  | 7474 | 302
4752 | Venus Sw Sta - Cedar Hill 138 kV line | Rebuild existing line |  | Venus Sw Sta | Cedar Hill | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4201 | 2018-02-15 |  | 138 | 0 | 20.6 | 0 |  | Ellis | Dallas | Tier 4 |  |  |  | 1908, 2300, 2310, 2311, 2313, 2314, 3053, 3054 | Y | N |  |  | 12347 | 4752
5791 | GEBHRT - 138kV Substation | Build new 138kV GEBHRT customer-owned substation. Loop through Ckt.65 Sealy to Wallis. | New Project | GEBHRT | Sealy/Wallis | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-02-28 |  | 138 | 0 | 0 | 0 |  | Austin | Austin | Tier 4 |  |  |  | 44700, 44190, 44640, 44740, 46220 | Y | N |  |  | 13530 | 5791
4705 | San Felipe to Eureka Ckt.09 | Upgrade Ckt.09 San Felipe to Eureka to increase thermal ratings | Change in project description | San Felipe | Eureka | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1132 | 2018-02-28 |  | 138 | 0 | 3.3 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45750, 47380, 47382 | Y | N |  |  | 12292 | 4705
5179 | Clear Crossing: Add 345 kV reactor | Add reactors to Tesla, Edith Clarke, Clear Crossing, and Riley | IN SERVICE | Clear Crossing |  | Under Construction | 754 - 0937 | ETT | Steve Stein mlforcum@aep.com 918-599-2674 | 2626 | 2018-02-28 |  | 345 | 0 | 0 | 0 | -100,0 | Haskell |  | Tier 4 |  |  |  | 60515 | Y | N |  |  | 12838 | 5179
4711A | CORTEZ 138kV Substation | Construct service to new 138kV CORTEZ customer-owned substation. As part of the project, Quintana substation will be disconnected from direct CNP service, and will be served through CORTEZ substation. CORTEZ will loop through Ckt.48 MARINE to Jones Creek. | Delay in project schedule | CORTEZ | MARINE/Quintana | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 55 | 2018-02-28 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43435, 43440, 42540, 43155, 43362 | Y | N |  |  | 12305 | 4711
5765 | TECO to Blodgett Tap Ckt37 | Upgrade substation equipment at TECO to increase TECO to Blodgett Tap Ckt37 thermal ratings |  | TECO | Blodgett | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-02-28 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47430, 47521, 47660 | Y | N |  |  | 13511 | 5765
5764 | Obrien to WA Parish Ckts.98 & 99 | Increase thermal ratings of Ckst.98 & 99 Obrien to WA Parish by installing shunts on line and upgrading substation equipment |  | Obrien | WA Parish | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-02-28 |  | 345 | 0 | 34 | 0 |  | Fort Bend | Fort Bend | Tier 4 |  |  |  | 44000, 44500 | Y | N |  |  | 13510 | 5764
5554 | Jones Creek Cap Bank #1 | Install capacitor bank #1 at Jones Creek substation (120MVAR). | - Updated project title and description - Updated expected date | Jones Creek |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1113 | 2018-02-28 | 2018-01-25 | 138 | 0 | 0 | 0 | 0,120 | Brazoria |  | Tier 4 |  |  |  | 42541, 42540, 42645 | Y | N |  |  | 13282 | 5554
5768 | Garrott to Blodgett tap Ckt.37 | Upgrade Ckt.37 Garrott to Blodgett tap to increase thermal ratings |  | Garrott | Blodgett | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-02-28 |  | 138 | 0 | 1.3 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47521, 47660 | Y | N |  |  | 13514 | 5768
5270B | Twin Buttes Autotransformer Addition | Replace the existing Twin Buttes AT1 autotransformer with a new 345/138-kV 672 MVA autotransformer. Remove the existing 36 MVAR Twin Buttes AT1 tertiary reactor. | Changed to phased project to show in-service date for major equipment associated with project. | Twin Buttes |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016445 | 2018-03-01 | 2018-01-31 | 345 | 0 | 0 | 672 |  | Tom Green |  | Tier 4 |  |  |  | 77281, 76009, 76011 | Y | N |  |  | 12946 | 5270
6655 | Rosata: Build 138kV Substation | Build new Rosata 138kV POD Switch on Coleto Creek to Kenedy 138kV Line. |  | Coleto Creek | Kenedy | Planned |  | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 |  | 2018-03-02 |  | 138 | 0 | 0 | 0 |  | Goliad |  | Tier 4 |  |  |  | 88153, 8162, 8186 | Y | N |  |  | 14412 | 6655
5174 | Nelson Sharpe: Reconfigure PST | Relocate the PST at Nelson Sharpe from the Barney Davis to Nelson Sharpe 138 kV line to the Nelson Sharpe to Celanese Bishop 138 kV line |  | Nelson Sharpe |  | In-Service | 747 - 0930 | AEP TCC | Dave Goetz dnlyons@aep.com 918-599-2698 | 2921 | 2018-03-02 | 2017-09-28 | 138 | 0 | 0 | 150 |  | Nueces |  | Tier 4 |  |  |  | 85002, 85007, 8515, 8516, 85001 | Y | N |  |  | 12833 | 5174
5169 | Harlingen SS to Raymondville #2: Rebuild 69 kV line | Rehab Harlingen SS to Raymondville #2 |  | Harlingen SS | Raymondville #2 | Under Construction | 749 - 0932 | AEP TCC | John Pulay dnlyons@aep.com 918-599-2698 | 2923 | 2018-03-02 | 2017-12-15 | 138 | 0 | 22.8 | 0 |  | Cameron | Willacy | Tier 4 |  |  |  | 8300, 8325, 8700 | Y | N |  |  | 12827 | 5169
4756 | Wink - Screwbean 138 kV circuit | Add second circuit to existing line |  | Wink | Culberson | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8337 | 2018-03-05 |  | 138 | 54 | 0 | 0 |  | Winkler | Culberson | Tier 4 |  |  |  | 1074, 1081, 1083, 1084, 1093, 1094, 1095 | Y | N |  |  | 12351 | 4756
5985 | Holt - Cowden North 69 kV Line | Holt - Cowden North 69 kV Line |  | Holt | Cowden North | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9024 | 2018-03-15 |  | 69 | 0 | 7.3 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 1142, 1259 | Y | N |  |  | 13700 | 5985
2941A | North Main Switch third transmission source | Construct a third 138 kV line into North Main Switch | Construction schedule change | Randol Mill | North Main Switch | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5161-E | 2018-03-15 |  | 138 | 4.4 | 4.4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1958, 1964, 2093, 2157, 3011, 12093, 902761, 1952, 2106, 2158 | Y | N |  |  | 10285 | 2941
5683E | Line H Rebuild and 138kV conversion. | Convert Pyote facility to 138 kV. Rebuild line from Pyote-Worsham (38001-38021). De-energize 69 kV line Wickett-Pyote (37980-38000). |  | 38001 | 38021 | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2018-03-15 |  | 138 | 0 | 15.43 | 0 |  | Reeves | Reeves | Tier 1 | 2016-03-14 | 2016-08-11 |  | 38000, 38001, 37980, 38021 | Y |  |  |  | 13747 | 5683
4755 | Barstow NW - Culberson 138 kV Line | Construct a new DCKT Line |  | Barstow NW | Culberson | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8342 | 2018-03-15 |  | 138 | 57.12 | 0 | 0 |  | Ward | Culberson | Tier 4 | 2013-02-15 | 2013-02-15 |  | 1080, 1086, 1097 | Y | N |  |  | 12350 | 4755
6748 | Gillrina Build 138kV Tap | Gillrina Temporary Hard Tap on Stadium to Calallen 69kV Line. |  | Stadium |  | In-Service | 901 - 1079 | AEP TCC/STEC | Daniel Lyons dnlyons@aep.com 918-599-2698 | 3594 | 2018-03-16 | 2018-05-30 | 69 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8031, 88031, 8888, 8889 | Y | Y |  |  | 14541 | 6748
5145A | Rafter - New 138 kV Substation | Tap new 138 kV load serving substation into existing Castroville to Texas Research 138 kV transmission line. |  | RAFTER | CASTROVILLE/TX_RSCH | Planned | S-0837 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0261 | 2018-03-29 |  | 138 | 0.5 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5355, 55355, 5083, 5430 | Y | N |  |  | 14398 | 5145
6674 | Oyster Creek 2nd Cap Bank | Install 2nd capacitor bank (40MVAR) at Oyster Creek sub |  | Oyster Creek | Velasco | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-03-30 |  | 138 | 0 | 0 | 0 | 0,40 | Brazoria | Brazoria | Tier 4 |  |  |  | 43337, 43335, 43361 | Y |  |  |  | 14474 | 6674
5808 | Install 160MVAR capacitor bank at Jones Creek substation. | Install 160MVAR capacitor bank at Jones Creek substation. |  | Jones Creek | CORTEZ | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-03-30 |  | 138 | 0 | 0 | 0 | 0,160 | Brazoria | Brazoria | Tier 4 |  |  |  | 42542, 42540, 43440 | Y | N |  |  | 13548 | 5808
6256 | Rebuild Saltdome to a loop | Rebuild single 69 kV 4-0 ACSR lines with 795 ACSR 138 capable double circuit and remove the Clemville Switching Station. |  | Clemville Switch | Saltdome | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2018-03-30 | 2018-03-07 | 69 | 2.6 | 3.4 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 5549, 5559, 5548, 5550, 5551, 5553, 5555 | Y | N |  |  | 13984 | 6256
5553B | Village Creek 138kV Substation | Construct service to new 138kV Village Creek distribution substation. Loop through Ckt.09 Zenith to Franz. | Delay in project schedule | Village Creek | Zenith/Franz | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-03-30 |  | 138 | 0.1 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  |  | Y | N |  |  | 13281 | 5553
3268 | AEP_McCampbell: New Substation Cut In | Customer to construct 138kV substation. Two 138kV circuits Cut-In to McCampbell substation. | Transmission Status, Contact, and schedue update | Dupont SS | Whitepoint SS | Under Construction | 561 - 0729 | AEP TCC | Terry Weeks dnlyons@aep.com 918-599-2698 | 3435 | 2018-03-31 |  | 138 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 | 2000-01-01 | 2000-01-01 | 2000-01-01 | 80469, 8414, 8422, 8961, 80470 | Y | N |  | This project was previously referred to as 4578. Project 4578 was deleted and replaced by this project 3268. | 10619 | 3268
5235 | Bakersfield Reactor Bank Addition(s) | Add two (2) 50 MVAR reactor banks at Bakersfield Substation | Construction Schedule | Bakersfield |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016061 | 2018-03-31 |  | 345 | 0 | 0 | 0 | 0,-100 | Pecos |  | Tier 4 |  |  |  | 76002 | Y | N |  |  | 12908 | 5235
6565 | THW A3 Replacement | Replacement of TH Wharton Auto #3 |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-03-31 |  | 345 | 0 | 0 | 600 |  |  |  | Tier 4 |  |  |  | 49071, 45500, 45515 | Y |  |  |  | 14315 | 6565
4710G | Jones Creek Project | Upgrade CORTEZ loop: Reconductor portions of Ckt.48 Velasco to MARINE to CORTEZ to Jones Creek. |  | Velasco | Jones Creek | Planned | 4950 | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 926 | 2018-03-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 1 | 2014-07-01 | 2014-11-13 | 2015-02-10 | 42540, 42542, 43155, 43360, 43440, 43362 | Y | N |  | 0 | 44757 | 4710
3937 | Brazos Valley Connection | Construct 345kV double circuit from Gibbons Creek to Zenith. Circuit numbers are 18 & 50. | Circuit mileage update | Gibbons Creek | Zenith | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 717 | 2018-03-31 |  | 345 | 126 | 0 | 0 |  | Harris | Grimes | Tier 1 | 2013-07-25 | 2014-02-20 | 2014-04-08 | 967, 3390, 3391, 44645, 44900, 46020 | Y | Y |  |  | 12068 | 3937
5807 | Velasco Cap Bank #2 | Install capacitor bank #2 at Velasco substation (120MVAR). |  | Velasco |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-03-31 00:01 |  | 138 | 0 | 0 | 0 | 0,120 | Brazoria |  | Tier 4 |  |  |  | 43362, 905182, 905183, 43360, 42510, 43155, 43361 | Y | N |  | 0 | 43252 | 5807
5955 | Mesquite: Build new distribution station | Mequite: Build new distribution station |  | Rangerville | Wesmer | In-Service | 803 - 0988 | AEP TCC | Bill Clarke dnlyons@aep.com 918-599-2698 | 3594 | 2018-04-01 | 2018-02-16 | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8554, 8347, 80103 | Y | N |  |  | 13668 | 5955
6527 | Bellville South Autotransformer Refurbishment | Restores Bellville South 138/69-kV autotransformer (failed in January 2017) to service. | Autotransformer delivery date update. | Bellville South |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018388 | 2018-04-01 |  | 69 | 0 | 0 | 0 |  | Austin |  | Tier 4 |  |  |  | 7269, 7270 | Y | N |  |  | 14265 | 6527
6350 | Sonora Atlantic to Sonora 69 kV line: Rebuild 69 kV line | Rehab Sonora Atlantic to Sonora 69 kV line | IN SERVICE | Sonora Atlantic | Sonora | In-Service | 786 - 0971 | AEP TNC | Tram Trinh mlforcum@aep.com 918-599-2674 | 2707 | 2018-04-01 | 2018-04-01 | 69 | 0 | 11.9 | 0 |  | Sutton | Sutton | Tier 4 |  |  |  | 6511, 6513 | Y | N |  |  | 14094 | 6350
6164 | Unitec: Build new distribution station | Unitec: Build new distribution station |  | North Laredo SS | Gateway Tap | In-Service | 866 - 1044 | AEP TCC | Rich Haley dnlyons@aep.com 918-599-2698 | 3653 | 2018-04-03 | 2018-04-03 | 138 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  | 8134, 8650, 8909 | Y | N |  |  | 13889 | 6164
5171 | Bates to Wormser: Raise structures increase MOT | Increase the MOT rating of the Bates to Wormser 138kV line by raising four structures and remedying MLSE Equipment |  | Bates | Wormser | Under Construction | 750 - 0933 | AEP TCC | Eric Johnson dnlyons@aep.com 918-599-2698 | 2924 | 2018-04-15 |  | 138 | 0 | 126.48 | 0 |  | Hidalgo | Webb | Tier 4 |  |  |  | 8299, 8392, 8394, 8399, 8795, 8957, 8985, 80106, 80230, 8295 | Y | N |  |  | 12829 | 5171
3669 | Albany Foundry to Moran: Rebuild 69 kV line | Rebuild Albany to Putnam 69 kV line | IN SERVICE | Albany Foundry | Moran | In-Service | 645 - 0814 | AEP TNC | Jason Bryant mlforcum@aep.com 918-599-2674 | 1808 | 2018-04-30 |  | 69 | 0 | 10 | 0 |  | Shackelford | Shackelford | Tier 4 |  |  |  | 6202, 60426 | Y | N |  |  | 11081 | 3669
5278 | Arco Tap Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Arco Tap. |  | Arco |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016390 | 2018-04-30 |  | 138 | 0 | 0 | 0 |  | Crane |  | Tier 4 |  |  |  | 1199, 71199, 1201, 71230, 76615 | Y | N |  |  | 12954 | 5278
5886 | Bellaire Auto A1 - Upgrade Limiting Equipment | Upgrade limiting equipment for Bellaire auto A1 |  | Bellaire |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-04-30 |  | 345 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47000, 47010, 49001 | Y |  |  |  | 13602 | 5886
6351 | Friend Ranch to Crockett Heights 69 kV line: Rbld 69 kV line | Rehab Friend Ranch to Crockett Heights 69 kV line | IN SERVICE | Friend Ranch | Crockett Heights | In-Service | 786 - 0971 | AEP TNC | Tram Trinh mlforcum@aep.com 918-599-2674 | 2705 | 2018-05-01 | 2018-05-01 | 69 | 0 | 1.23 | 0 |  | Crockett | Crockett | Tier 4 |  |  |  | 6550, 6552 | Y | N |  |  | 14095 | 6351
5208B | SPLIT INTO PHASES SC ADDITIONS |  |  | Tule Canyon |  |  |  | SHRY | Brad Schwarz 512-289-7425 |  | 2018-05-01 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  | 79521, 79523, 79503 | Y |  |  |  | 14504 | 5208
5933 | Tippett Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Tippet Substation and move the existing generation interconnection at Desert Sky #2 to Tippet Substation. |  | Desert Sky Tap #2 | Tippet | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017409 | 2018-05-01 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 76016, 76021, 6586, 76001, 76013, 76595, 131033 | Y | N |  |  | 13641 | 5933
6396 | Treadwell: Build temporary tap | Interconnect Cactus Flats wind farm on the SAPS to Yellowjacket 138 kV line | IN SERVICE | Treadwell |  | In-Service | 875 - 1053 | AEP TNC | Tom Reynolds mlforcum@aep.com 918-599-2674 | 2726 | 2018-05-11 | 2018-05-11 | 138 | 0 | 0 | 0 |  | Concho |  | Tier 4 |  |  |  | 60423, 6365, 6480 | Y | Y |  |  | 14155 | 6396
4937 | Wolf 138 kV Switching Station | Construct new 138 kV switching station |  | Wolf Switching Station |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8262 | 2018-05-14 |  | 138 | 0 | 0 | 0 |  | Ward |  | Tier 4 |  |  |  | 1013, 1001, 1009, 1010, 1019, 1074, 1087, 1103, 1107, 1146, 1292, 1015 | Y | N |  |  | 12570 | 4937
4574 | Briarcrest to Nall Cable Upgrade | Upgrade Briarcrest to Nall Cable to match OH section |  | 32877 | 32872 | Planned |  | BRYN |  |  | 2018-05-14 |  | 69 | 0 | 0.5 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32872, 32877 | Y |  |  |  | 12156 | 4574
6026 | Mountain Creek - Cockrell Hill 138 kV Line | Upgrade terminal equipment on Mountain Creek - Cockrell Hill 138 kV Line |  | Mountain Creek | Cockrell Hill | Under Construction |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4162 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Dallas |  | Tier 4 |  |  |  | 2411, 3015 | Y | N |  |  | 13750 | 6026
6028 | Rice Sw. - Markley 138 kV Line | Upgrade terminal equipment on Rice Sw. - Markley 138 kV Line |  | Rice Sw. | Markley | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4016 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Young |  | Tier 4 |  |  |  | 1476, 1477 | Y | N |  |  | 13752 | 6028
6037 | Irving Grant - Norwood 138 kV Line Section | Upgrade terminal equipment on Irving Grant - Norwood 138 kV Line |  | Irving Grant | Norwood | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4165 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Dallas |  | Tier 4 |  |  |  | 2055, 2408 | Y | N |  |  | 13756 | 6037
6027 | Cockrell Hill - Hampton Rd 138 kV Line Double-circuit Line | Upgrade terminal equipment on Cockrell Hill - Hampton Rd 138 kV Double-circuit Line |  | Cockrell Hill | Hampton Rd | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4163 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Dallas |  | Tier 4 |  |  |  | 3014, 3016 | Y | N |  |  | 13751 | 6027
6036 | Roanoke Sw. - Park Vista POI 138 kV Line | Upgrade terminal equipment on Roanoke Sw. - Park Vista POI 138 kV Line |  | Roanoke Sw. | Park Vista POI | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4168 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Denton | Tarrant | Tier 4 |  |  |  | 1852, 1854, 15100, 15101 | Y |  |  |  | 13755 | 6036
15TPIT0083B | Collin - Arco (TMPA) 138 kV Line (Oncor's section) | Add second circuit to existing line from Krugerville to Arco (TMPA) |  | Krugerville | Arco (TMPA) | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R929 | 2018-05-15 |  | 138 | 5.7 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 923, 33662 | Y | N |  |  | 12101 | 3216
4757 | Riverton 138 kV Switching Station | Construct new switching station |  | Mason |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8338 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  | 11083, 1083, 1094, 11080, 11091 | Y | N |  |  | 12352 | 4757
4932 | Wink - Yukon 138 kV Line | Wink - Yukon 138 kV Line | Construction schedule change | Wink | Yukon | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8346 | 2018-05-15 |  | 138 | 36 | 9 | 0 |  | Ector | Winkler | Tier 3 | 2015-06-19 | 2015-07-29 |  | 1252, 1074, 1075, 1250, 1251, 1254, 1253, 1258 | Y | N |  |  | 12565 | 4932
4367 | Screwbean Tap - Culberson 138 kV Line | Rebuild existing 138 kV line | Construction schedule change | Screwbean Tap | Culberson | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8274 | 2018-05-15 |  | 138 | 0 | 19.6 | 0 |  | Culberson | Culberson | Tier 4 |  |  |  | 1083, 1095, 1096, 1097, 11079 | Y | N |  |  | 11916 | 4367
4843 | Hicks Sw. Sta. 345/138 kV autotransformer #2 | Install second 345/138 kV autotransformer |  | Hicks Sw. Sta. |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5229 | 2018-05-15 |  | 345 | 0 | 0 | 600 |  | Tarrant |  | Tier 4 |  |  |  | 2082, 2081 | Y | N |  |  | 12445 | 4843
09TPIT0044 | E. Richardson - Apollo 138kV line (Oncor' section) | Upgrade existing 138 kV line |  | E. Richardson | Apollo | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M3033-WA | 2018-05-15 |  | 138 | 0 | 2.3 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 802, 2690 | Y | N |  |  | 10414 | 3070
6301 | Tyler Northwest 138 kV Sw. Sta. | Establish Black Fork Sw. Sta. |  | Black Fork |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6072 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Smith |  | Tier 4 |  |  |  | 3137, 3139, 3141, 3202 | Y | Y |  |  | 14030 | 6301
5983 | Pyote 138 kV Capacitors | Pyote 138 kV Capacitors |  | Whiting Oil |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9023 | 2018-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Ward |  | Tier 4 |  |  |  | 1080 | Y | N |  |  | 13698 | 5983
6385 | BRECKENRIDGE TAP-GRAHAM SW. STA. | Upgrade Terminal Equipment at BRECKENRIDGE TAP-GRAHAM SW. STA. |  | Breckenridge | Graham | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R2022 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Stephens | Young | Tier 4 |  |  |  | 1431, 1613, 1618 | Y | N |  |  | 14139 | 6385
4280 | Allen Switching Station 138 kV series reactor | Install series reactor on 345/138 kV autotransformer #2 |  | Allen Switching Station |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R961 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Collin |  | Tier 4 |  |  |  | 12514, 2512, 2514, 12512 | Y | N |  |  | 11830 | 4280
4524 | Culberson 138 kV Switching Station | Rebuild 138 kV bus | Construction schedule change | Culberson Switching station |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8366 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Culberson |  | Tier 4 | 2013-02-15 | 2013-02-15 |  | 1097, 1080, 1086, 11078 | Y | N |  |  | 12096 | 4524
15TPIT0058 | Permian Basin - Ward Gulf Tap - Wink 138 kV line | Upgrade existing 138 kV line |  | Permian Basin | Wink | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8189-E | 2018-05-15 |  | 138 | 0 | 16.5 | 0 |  | Ward | Winkler | Tier 4 |  |  |  | 1010, 1074, 1087 | Y | N |  |  | 10182 | 2834
6039 | Carrollton NW 345/138 kV Auto #1 | Upgrade terminal equipment on Carrollton NW 345/138 kV Auto #1 |  | Carrollton NW |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4167 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Dallas |  | Tier 4 |  |  |  | 2360, 2362, 2363 | Y | N |  |  | 13758 | 6039
4257 | Stryker Creek - Gresham Road 138 kV line | Upgrade existing line |  | Stryker Creek | Gresham Road | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6054 | 2018-05-15 |  | 138 | 0 | 9.1 | 0 |  | Cherokee | Rusk | Tier 4 |  |  |  | 3110, 3301 | Y | N |  |  | 11803 | 4257
5197 | Abilene Northwest to Elm Creek: Rebuild 69 kV line | Rebuild Abilene Northwest to Elm Creek 69 kV line |  | Abilene Northwest | Elm Creek | In-Service | 759 - 0943 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2634 | 2018-05-16 | 2018-05-16 | 69 | 0 | 3.07 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6253, 6225 | Y | N |  |  | 12856 | 5197
5020 | Red Creek: Replace the other 345/138 kV autotransformer | Replace both 345/138 kV autotransformers at Red Creek with 480 MVA autotransformers | IN SERVICE | Red Creek |  | In-Service | 566 - 0740 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2615 | 2018-05-24 | 2018-05-24 | 345 | 0 | 0 | 480 |  | Tom Green |  | Tier 4 |  |  |  | 6769, 6444, 6442, 6295 | Y | N |  |  | 12653 | 5020
3819 | Rebuild San Miguel Tap to North Calliham | Rebuild 4-0 ACSR 69 kV to higher rated and 138 kV capable line, as originally recommended in 2013 RTP. Not Rebuild 336 ACSR portion from San Miguel to San Miguel Tap. |  | Sam Miguel Tap | North Calliham | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2018-05-29 | 2018-06-01 | 69 | 0 | 17.5 | 0 |  | Atascosa | McMullen | Tier 4 |  |  |  | 5693, 5698 | Y | N |  | Not Rebuild 336 ACSR portion from San Miguel to San Miguel Tap. | 11276 | 3819
4997B | Deepwater Area Conversions | Convert CHANEL sub to 138kV service. Loop from Ckt.70 BRANUM to LYDELL. |  | CHANEL | BRANUM/LYDELL | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 986 | 2018-05-29 00:02 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 40275, 40270, 41009, 40640 | Y | N |  | 0 | 43260 | 4997
6356 | Cedar Hill to Edith 69 kV line: Rebuild 69 kV line | Rehab Cedar Hill to Edith 69 kV line | IN SERVICE | Cedar Hill | Edith | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2714 | 2018-05-30 | 2018-05-30 | 69 | 0 | 12.6 | 0 |  | Coke | Coke | Tier 4 |  |  |  | 6422, 6423 | Y | N |  |  | 14100 | 6356
4706B | HO Clarke to Webster Ckt.05 | Upgrade Southwyck to Webster Ckt.05 to increase thermal ratings |  | Southwyck | Friendswood | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2018-05-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42651, 43260, 44361 | Y | N |  | 0 | 50154 | 4706
6312A | PH Robinson Autotransformer A3 800MVA Addition | Install PH Robinson 800MVA 345/138kV Auto A3 |  | PH Robinson |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-05-30 00:01 |  | 345 | 0 | 0 | 800 |  | Harris |  | Tier 4 |  |  |  | 49049, 42000, 42015 | Y | N |  | 0 | 43464 | 6312
4997D | Deepwater Area Conversions | Remove CHANEL 69kV Service |  | CHANEL | Harris/Deepwater | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 986 | 2018-05-30 00:04 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 40270, 40470, 40800 | Y | N |  | 0 | 43262 | 4997
4703B | Bellaire to San Felipe Ckt.09 & Bellaire tap Ckt.24 | Upgrade Ckt.24 Bellaire to Bellaire tap |  | Bellaire | Bellaire | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1132 | 2018-05-31 | 2018-04-27 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47010, 47014 | Y |  |  | 0 | 48254 | 4703
3951 | TH Wharton to Fairbanks Ckt.81 | Reconductor 138kV Ckt.81 TH Wharton to Fairbanks and upgrade substation equipment at TH Wharton and Fairbanks to increase thermal ratings. | - Overall Date Update | TH Wharton | Fairbanks | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 995 | 2018-05-31 |  | 138 | 0 | 3.8 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45510, 45511, 45515, 45730, 45781, 45760, 45921, 45922, 46610 | Y | N |  | 0 | 47571 | 3951
5600 | New 138 kV Retrieve Breakered Substation | Expand existing 138kV Retrieve substation to switching substation with breaker-and-half configuration. Loop Ckt.02 West Columbia to Lake Jackson. Also loop two TNMP circuits into new substation. |  | Retrieve | West Columbia/Lake Jackson | Planned |  | CNP/CNP/TNMP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-05-31 |  | 138 | 0.2 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 43145, 43170, 43171, 43172, 39560, 39600, 42150, 42215, 42810, 42880, 43380, 48006 | Y | N |  |  | 13330 | 5600
5272 | Smithville - Winchester Line Overhaul | Rebuild T175 Smithville to Winchester with 795 ACSR (Drake) and OPGW. |  | Smithville | Winchester | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016207 | 2018-05-31 |  | 138 | 0 | 14.6 | 0 |  | Bastrop | Fayette | Tier 4 |  |  |  | 7306, 7314 | Y | N |  |  | 12948 | 5272
5925 | Gilleland Creek - Hutto Transmission Line Upgrade | Upgrade terminal equipment on T21452 at Gilleland Creek to minimum 3000 Amp rating. Needed to support an ONCOR project to upgrade the Hutto Sw. Station to Round Rock Southeast to Gilleland Creek 138-kV line. |  | Gilleland Creek | Hutto | Planned | 16TPIT0062 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017384 | 2018-05-31 |  | 138 | 0 | 0 | 0 |  | Travis | Williamson | Tier 4 |  |  |  | 7336 | Y | N |  |  | 13633 | 5925
5919 | Fort Mason Substation Upgrade | Convert Fort Mason to entirely 138-kV. Upgrade terminal equipment on T21444 to 2000 Amps. Remove autotransformer. |  | Fort Mason | Mason | Planned | 5962 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017379 | 2018-05-31 | 2018-05-01 | 138 | 0 | 0 | 0 |  | Mason |  | Tier 4 |  |  |  | 76388, 76390, 6393 | Y | N |  |  | 13627 | 5919
5921 | Cuero - Guadalupe Transmission Line Overhaul | Tear down and rebuild 28 structures from Cuero to Structure 238. The replacement conductor on this section of T542 will be 795 ACSR Drake, the line rating will not change. Add OPGW to the line section. |  | Cuero | Guadalupe | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016350 | 2018-05-31 |  | 69 | 0 | 3 | 0 |  | DeWitt | Guadalupe | Tier 4 |  |  |  | 78190, 78577 | Y | N |  |  | 13629 | 5921
13TPIT0160 | Whitepoint: Add 138 kV breaker terminal for WF interconnect | Interconnect Midway Wind Farm at Whitepoint and construct a 138 kV breaker terminal |  | Whitepoint |  | In-Service | 573-0750 | AEP TCC | Terry Weeks DNLYONS@AEP.COM 918-599-2698 | 3454 | 2018-05-31 | 2018-10-19 | 138 |  |  |  |  | San Patricio |  | Tier 4 |  |  |  | 8961 | Y | N |  |  | 11151 | 3731
4445 | Kerrville Stadium to Harper Road Transmission Line Upgrade | Upgrade the 1.6 mile Kerrville Stadium (7138) - Harper Road (7140) 138-kV transmission line to bundled 795 ACSR Drake, 440 MVA. |  | Kerrville Stadium | Harper Road | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1015115 | 2018-05-31 |  | 138 | 0 | 1.6 | 0 |  | Kerr | Kerr | Tier 4 |  |  |  | 7138, 7140 | Y | N |  |  | 12008 | 4445
5271 | FPP Bus Tie Upgrades | Add a second bus tie between LCRA TSC FPP 345-kV Yard #1 and Yard #2 with a minimum 1793 MVA rating. Upgrade T405 to a minimum rating of 1793 MVA. |  | FPP #1 | FPP #2 | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016189 | 2018-05-31 |  | 345 | 0 | 0 | 0 |  | Fayette | Fayette | Tier 4 |  |  |  | 7055, 7056 | Y | N |  |  | 12947 | 5271
5923 | Fayetteville - FPP 138-kV Transmission Line Overhaul | Overhaul FPP to Fayetteville 138-kV and reconductor with 959 ACSS/TW Suwannee. New circuit rating (MVA): Rate A=287, Rate B=287, Rate C=380. |  | Fayetteville | FPP | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016108 | 2018-05-31 |  | 138 | 0 | 6.9 | 0 |  | Fayette |  | Tier 4 |  |  |  | 7278, 7286 | Y | N |  |  | 13631 | 5923
5204 | Jourdanton to Pleasanton: 69 kV Transmission Line Rebuild | Rebuild 69 kV line from Jourdanton to Pleasanton. Install 2 x 7.2 MVAR Cap Bank at Jourdanton station |  | Jourdanton | Pleasanton | In-Service | 765-0950 | AEP TCC | Terry Weeks dnlyons@aep.com 918-599-2698 | 3573 | 2018-05-31 |  | 69 | 0 | 6 | 0 | 0,14.4 | Atascosa | Atascosa | Tier 4 |  |  |  | 8607, 8200 | Y | N |  |  | 12863 | 5204
5924 | Harwood - Waelder Transmission Line Overhaul | Upgrade T145 from Harwood to Waelder to 795 ACSR Drake conductor with minimum rating of 111 MVA at 69-kV and 221 MVA at 138-kV and add OPGW. Rate A=44, Rate B=44, Rate C=111. | Project Schedule Expedited | Harwood | Waelder | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017388 | 2018-05-31 |  | 138 | 0 | 12.5 | 0 |  | Gonzales |  | Tier 4 |  |  |  | 7223, 7230, 7231, 7232 | Y | N |  |  | 13632 | 5924
6669 | CNP_TPIT6669_Satsuma_Tap_Reconductor | Reconductor Satsuma Tap |  | Satsuma Tap | Satsuma | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  | 2017-12-12 | 42011, 42562, 42842, 44120, 44910, 45515, 45610, 45611, 45711, 45801, 45802, 46300, 46302, 43502, 43610, 45811, 45812, 45952, 46301, 46311, 46312 | Y |  |  |  | 14454 | 6669
5922 | Flatonia - Waelder Transmission Line Overhaul | Overhaul the Flatonia to Waelder and reconductor with 795 ACSR Drake conductor. New rating (MVA): Rate A=42, Rate B=42, Rate C=111. | Project Schedule Expedited | Flatonia | Waelder | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017377 | 2018-05-31 |  | 69 | 0 | 11.8 | 0 |  | Gonzales | Fayette | Tier 4 |  |  |  | 7232, 7247 | Y | N |  |  | 13630 | 5922
43284A | Baytown Area Upgrades | Reconfigure Baytown to Miller |  |  |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-05-31 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40170, 41405, 41420 | Y |  |  | 0 | 48841 | 43284
4706C | HO Clarke to Webster Ckt.05 | Reconfigure Southwyck TR1 to tap from Ckt.26 between Telview and Karsten. Upgrade Ckt.26 with partial reconductor. Southwyck TR2 & TR3 will continue to have loop service from Ckt.05. |  | Southwyck | Southwyck | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2018-05-31 00:03 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 43261, 43260, 42015, 42041, 42651, 42652, 44361, 44390, 42061, 42960, 43500, 44552, 47150 | Y |  |  | 0 | 50155 | 4706
4962 | Adding second 345/138 kV auto at Vealmoor station |  |  | Vealmoor 345 | Vealmoor 138 | Planned |  | SHRY | Brad Schwarz 512-289-7425 |  | 2018-06-01 |  | 345 | 0 | 0 | 708 |  | Borden | Borden | Tier 4 |  |  |  | 79602, 79640, 79600 | Y | N |  |  | 12595 | 4962
5683F | Line H Rebuild and 138kV conversion. | Construct Wickett 138 kV substation. Rebuild line from Wickett-Pyote (37981-38001). Build 138 kV line Oncor Wolf-TNMP Wickett (1013-37981). |  | 38001 | 1013 | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2018-06-01 |  | 138 | 6.1 | 12.89 | 0 |  | Reeves | Reeves | Tier 1 | 2016-03-14 | 2016-08-11 |  | 37981, 1013, 38001 | Y |  |  |  | 13748 | 5683
6161 | Las Cruces: Build new distribution station | Las Cruces: Build new distribution station |  | Laredo VFT North | Milo | In-Service | 865 - 1043 | AEP TCC | Bill Clarke dnlyons@aep.com 918-599-2698 | 3652 | 2018-06-01 | 2018-05-31 | 138 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  | 8112, 8918, 80013 | Y | N |  |  | 13886 | 6161
5131 | CPSE_Brooks to Chavaneaux Transmission Rebuild | Rebuild approximately 11 circuit miles of 138 kV transmission along the 410 corridor between Brooks and Chavaneaux. Included in the rebuild are segments of Harlandale to Sommers and Merida to Sommers 138 kV transmission lines. |  | Brooks/Sommers | Chavaneaux/Merida/Harlandale | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0230 | 2018-06-01 |  | 138 | 0 | 11 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5045, 5190, 5310, 5085, 5395 | Y | N |  |  | 12784 | 5131
5603 | Holbrook_to_Kirby_Rebuild | Rebuild 2.3 miles of 138 kV transmission line from Holbrook to Kirby. |  | Holbrook | Kirby | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0264 | 2018-06-01 |  | 138 | 0 | 2.3 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5005, 5160, 5218, 5250, 5420 | Y |  |  |  | 13333 | 5603
5188 | Quaint Station: Build 69 kV station | Construct new 69 kV ring bus on the Abilene Northwest to Anson 69 kV Line | IN SERVICE | Quaint |  | In-Service | 753 - 0936 | AEP TNC | Jason Bryant mlforcum@aep.com 918-599-2674 | 2623 | 2018-06-05 | 2018-06-05 | 69 | 0 | 0 | 0 |  | Jones |  | Tier 4 |  |  |  | 6237, 6388, 6236, 6238, 6243, 6249 | Y | N |  |  | 12847 | 5188
5971 | Truscott Hmble T to Benjamin T 69 kV line: Rbld 69 kV line | Rehab Truscott Humble Tap to Benjamin Tap 69 kV line | IN SERVICE | Truscott Humble Tap | Benjamin Tap | In-Service | 786 - 0971 | AEP TNC | Guillermo Taylor mlforcum@aep.com 918-599-2674 | 2660 | 2018-06-25 | 2018-06-25 | 69 | 0 | 11.08 | 0 |  | Knox | Knox | Tier 4 |  |  |  | 790, 6084, 6085, 6086, 6087 | Y | N |  |  | 13686 | 5971
7146 | Howard Lane Tie Upgrade | Upgrade the 138-kV Howard Lane tie line to bundle 2250 AAC. The planned tie line rating will be (MVA): Rate A=640, Rate B=710, Rate C=710. |  | Howard Lane | Howard Lane | In-Service |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2018-06-27 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 7335, 9217 | Y | N |  |  | 14985 | 7146
5928 | McElmurray Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at McElmurray Substation. |  | McElmurray |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017393 | 2018-06-30 |  | 138 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  | 76319 | Y | N |  |  | 13636 | 5928
5912 | Bellville North Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Bellville North Substation. |  | Bellville North |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017342 | 2018-06-30 |  | 138 | 0 | 0 | 0 |  | Austin |  | Tier 4 |  |  |  | 7287 | Y | N |  |  | 13620 | 5912
5273 | Bergheim Substation Upgrade | Add a 345-kV bus and a 345/138-kV 336 MVA autotransformer at Bergheim Substation. | Construction schedule update | Bergheim |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016178 | 2018-06-30 |  | 345 | 0 | 0 | 336 |  | Comal |  | Tier 4 |  |  |  | 7770, 7771, 7043, 7046, 7170 | Y | N |  |  | 12949 | 5273
6097 | Amoco to Mustang Bayou Ckt.04 | Upgrade 138kV Ckt.04 Amoco to Mustang Bayou to increase thermal ratings. |  | Amoco | Mustang Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-06-30 |  | 138 | 0 | 7.5 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42090, 42960 | Y | N |  |  | 13822 | 6097
5918 | Evant Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Evant Substation. |  | Evant |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017373 | 2018-06-30 |  | 138 | 0 | 0 | 0 |  | Lampasas |  | Tier 4 |  |  |  | 7065 | Y | N |  |  | 13626 | 5918
5935 | Webberville Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Webberville (S470). |  | Webberville |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017412 | 2018-06-30 |  | 138 | 0 | 0 | 0 |  | Travis |  | Tier 4 |  |  |  | 7329 | Y | N |  |  | 13643 | 5935
5494 | Bus Differential Redundancy | Upgrade the 138-kV bus differential protection at Gillespie, North McCamey and Zorn Substations. |  | Zorn |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016182 | 2018-06-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7180 | Y | N |  |  | 13232 | 5494
5910 | Butler Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Butler Substation. |  | Butler |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017345 | 2018-06-30 |  | 138 | 0 | 0 | 0 |  | Bastrop |  | Tier 4 |  |  |  | 7324 | Y | N |  |  | 13617 | 5910
5187 | Add 2nd Palmito Transfomer |  |  | Palmito | Loma Alta | Planned |  | SHRY | Brad Schwarz 512-289-7425 |  | 2018-07-01 |  | 345 | 0 | 0 | 450 |  | Cameron | Cameron | Tier 4 |  |  |  | 5962, 79652, 79690, 5966 | Y | N |  |  | 12846 | 5187
5180 | Add second circuit to SLU panhandle loop |  |  | Alibates | Tule Canyon | Planned |  | SHRY | Brad Schwarz 512-289-7425 |  | 2018-07-01 |  | 345 | 166 | 0 | 0 |  | Carson | Briscoe | Tier 1 |  |  |  | 79500, 79501, 79502, 79503, 79504 | Y | N |  |  | 12839 | 5180
5189 | Exxon Hawley Tap to Onyx Switch Station: Rebuild 69 kV line | Rebuild Hawley Tap to Onyx Switch Station | IN SERVICE | Hawley Tap | Onyx Switch Station | In-Service | 753 - 0939 | AEP TNC | Jason Bryant mlforcum@aep.com 918-599-2674 | 2630 | 2018-07-18 | 2018-07-18 | 69 | 0 | 6.57 | 0 |  | Jones | Jones | Tier 4 |  |  |  | 6236, 6238, 6388 | Y | N |  |  | 12848 | 5189
5683G | Line H Rebuild and 138kV conversion. | Install 69-138 kV Autotransformer at Wickett. |  | 37980 | 37981 | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2018-07-23 |  | 138 | 0 | 0 | 150 |  | Reeves | Reeves | Tier 1 | 2016-03-14 | 2016-08-11 |  | 37980, 37981 | Y |  |  |  | 13749 | 5683
6368 | Jacintoport Substation Upgrades | Upgrade equipment and transmission conductor at Jacintoport substation to increase thermal ratings |  | Jacintoport | BORDEN/EPOTH | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-07-30 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 40860, 40210, 40290, 40520, 40410 | Y | N |  |  | 14112 | 6368
14TPIT0079 | Glen Rose to Meridian Rebuild NOMCR 54300 energized 8/1/2018 | Rebuild Glen Rose to Meridian with 795 ACSR, 138 kV construction (operate at 69 kV) |  | Glen Rose | Meridian | Planned |  | BEPC | Dwight Beckman kdye@brazoselectric.com 254-750-6373 | 15024 | 2018-08-01 |  | 69 | 0 | 18.18 | 0 |  | Somervell | Bosque | Tier 4 |  |  |  | 315, 319 | Y | N |  |  | 9485 | 2237
4761 | Trinidad - Jewett 138 kV Line | Upgrade Trinidad - Big Brown Tap line section |  | Trinidad | Big Brown Tap | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R2004 | 2018-08-02 |  | 138 | 0 | 26.4 | 0 |  | Henderson | Leon | Tier 4 |  |  |  | 212, 3127, 3505 | Y | N |  |  | 12359 | 4761
5542 | Gila-Hwy9_ckt2: replace underground cable | Gila-Hwy9 circuit 2: Install new underground conduits and dielectric cable with 1300A normal/2150A emergency rating, below Corpus ship channel, from Gila 138 kV station yard to cable terminal. Also, remove Gila-Morris St. 138 kV line from service and return Gila-Nueces Bay 138 kV line to service. |  | Gila | Cable Terminal | In-Service | 791 - 0975 | AEP TCC | Terry Weeks dnlyons@aep.com 918-599-2698 | 3581 | 2018-08-02 | 2017-07-28 | 138 | 0 | 0.41 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8441, 8470, 8474, 80260 | Y | N |  |  | 13270 | 5542
5173 | Airline to Westside: Reconductor 138 kV line | Reconductor Airline to Westside |  | Airline | Westside | In-Service | 746 - 0929 | AEP TCC | Dave Goetz dnlyons@aep.com 918-599-2698 | 2920 | 2018-08-02 | 2018-08-29 | 138 | 0 | 6.1 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8485, 8490, 8882 | Y | N |  |  | 12832 | 5173
4548 | Yucca Drive Switching Station | Construct new switching station |  | Yucca Drive Switching Station |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8261 | 2018-08-02 |  | 138 | 0 | 0 | 300 |  | Ward |  | Tier 4 |  |  |  | 1001, 1015, 18110, 1009, 1010 | Y | N |  |  | 12125 | 4548
4241 | Texaco Mabee Tap - Texaco Mabee 138 kV Line | Rebuild existing line as a double-circuit line |  | Texaco Mabee Tap | Texaco Mabee | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8221 | 2018-08-02 |  | 138 | 11.4 | 11.4 | 0 |  | Midland | Andrews | Tier 4 |  |  |  | 1171, 1175, 1177, 1179, 11175, 1184, 11169, 11177, 11179 | Y | N |  |  | 11789 | 4241
4267 | Andrews County South - North Andrews 138 kV Line | Upgrade existing line |  | Andrews County South | North Andrews | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8235 | 2018-08-02 |  | 138 | 0 | 19 | 0 |  | Andrews | Andrews | Tier 3 | 2016-02-01 | 2016-05-01 |  | 1155, 1153, 1157, 1159 | Y | N |  |  | 11815 | 4267
4751 | Lufkin Sw Sta - Crockett 138 kV Line | Rebuild existing line |  | Lufkin | Crockett | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6004 | 2018-08-02 |  | 138 | 0 | 42.9 | 0 |  | Angelina | Houston | Tier 3 | 2015-06-15 | 2015-08-15 |  | 3118, 3349, 3351, 3354 | Y | N |  |  | 12346 | 4751
6092 | Port Aransas - Seawall 69 kV line rebuild | Rebuild ~8.1 miles of 69 kV line from Port Aransas to Seawall |  | Port Aransas | Seawall | In-Service | 861-1039 | AEP TCC | Mark Strabala dnlyons@aep.com 918-599-2698 | 2698 | 2018-08-02 | 2018-10-17 | 69 | 0 | 8.1 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 8435, 8442 | Y | N |  |  | 13817 | 6092
5537 | Gila-Hwy9_ckt1: replace underground cable | Install new underground conduits and dielectric cable with 1300A normal/2150A emergency rating, below Corpus Ship channel, from Gila 138 kV station yard to cable terminal. |  | Gila | Cable Terminal | In-Service | 790 - 0975 | AEP TCC | Terry Weeks dnlyons@aep.com 918-599-2698 | 3580 | 2018-08-02 | 2017-05-13 | 138 | 0 | 0.41 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8470, 80260 | Y | N |  |  | 13265 | 5537
1332 | Elm Mott - Waco West/Waco East 138 kV Line | Upgrade existing Elm Mott - Waco Northeast Tap line section |  | Elm Mott | Waco Northeast Tap | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1719 | 2018-08-02 12:00 |  | 138 | 0 | 6.7 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  | 3407, 3550, 3551, 3575 | Y | N |  |  | 8511 | 1332
7046 | Pig Creek to County Road 101: Rebuild 138 kV line | Rebuild Solstice to Yucca Drive 138 kV line and add dynamic reactive devices at Lotebush | IN SERVICE | Pig Creek | County Road 101 | In-Service | 713 - 0946 | AEP TNC | John Pulay mlforcum@aep.com 918-599-2674 | 2737 | 2018-08-04 | 2018-08-04 | 138 | 0 | 13.411 | 0 |  | Reeves | Reeves | Tier 1 | 2015-12-15 | 2016-09-21 | 2016-10-26 | 6657, 6673, 60393 | Y | N |  |  | 14868 | 7046
5176 | Riley: Add 345 kV reactors | Add reactors to Tesla, Edith Clarke, Clear Crossing, and Riley | IN SERVICE | Riley |  | In-Service | 754 - 0937 | ETT | Steve Stein mlforcum@aep.com 918-599-2674 | 2627 | 2018-08-08 | 2018-08-08 | 345 | 0 | 0 | 0 | -200,0 | Wilbarger |  | Tier 4 |  |  |  | 6101 | Y | N |  |  | 12835 | 5176
3938A | Angleton Area Ckt.26 & 82 Upgrades |  |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2018-08-14 00:04 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42110, 43300 | Y | N |  |  | 11424 | 3938
5168 | Airline to Holly: Build new 138 kV line | Build new Airline to Holly 138 kV line by installing a second circuit on the existing Barney Davis to Holly 138 kV line |  | Airline | Holly | In-Service | 745 - 0928 | AEP TCC | Dave Goetz dnlyons@aep.com 918-599-2698 | 2919 | 2018-08-17 | 2018-06-07 | 138 | 1.7 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8486, 8490, 8517 | Y | N |  |  | 12910 | 5168
5257 | Solstice to Pig Creek: Rebuild 138 kV line | Rebuild Solstice to Yucca Drive 138 kV line and add dynamic reactive devices at Lotebush | IN SERVICE | Solstice | Pig Creek | Planned | 713 - 0946 | AEP TNC | John Pulay mlforcum@aep.com 918-599-2674 | 2636 | 2018-08-20 |  | 138 | 0 | 13.285 | 0 |  | Pecos | Reeves | Tier 1 | 2015-12-15 | 2016-09-21 | 2016-10-26 | 60385, 60393 | Y | Y |  |  | 12932 | 5257
5145B | Rafter - New 138 kV Substation | Loop existing Rafter 138 kV substation into existing Castroville to Texas Research 138 kV transmission line. |  | RAFTER | CASTROVILLE/TX_RSCH | Planned | S-0837 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0261 | 2018-08-26 |  | 138 | 0.5 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 55355, 5083, 5355, 5430 | Y | N |  |  | 12799 | 5145
5913 | Colton Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Colton Substation. | Construction Schedule | Colton |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017347 | 2018-08-30 |  | 138 | 0 | 0 | 0 |  | Travis |  | Tier 4 |  |  |  | 7208 | Y | N |  |  | 13621 | 5913
13TPIT0045 | Blumenthal Substation | Construct a new 11.5 mile 138 kV transmission line from a new station tap point on the Kendall CTEC - Mountain Top 138 kV transmission line named Maenius Road to the new Blumenthal substation using 336 ACSR Linnet. | CCN approved November 19, 2015 | Blumenthal | Kendall CTEC - Mountain Top | Planned |  | LCRATSC/CTEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1010656 | 2018-08-31 |  | 138 | 12.8 | 0 | 0 |  | Kendall | Gillespie | Tier 4 |  |  |  | 7418, 7419 | Y | N |  |  | 13618 | 990
5941 | T-283 Quanex Switch to Quanex Substation | Replacement of wood poles from Quanex Switch to Quanex Substation. |  | Quanex Switch | Quanex | Under Construction |  | SBEC | Don Roberts droberts@sbec.org | WO# 17-6070 | 2018-09-01 | 2018-08-23 | 69 | 0 | 1.73 | 0 |  | Austin | Austin | Tier 4 |  |  |  | 7660, 7662 | Y | N |  |  | 13652 | 5941
6925 | Additional capacitors at Driver and Canal |  |  | 138 kV Driver | 138 kV Canal Rd | Planned |  | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2018-09-01 |  | 138 | 0 | 0 | 0 | 0,48 | Midland | Upton | Tier 4 |  |  |  | 79612, 79624 | Y |  |  |  | 14743 | 6925
4950B | Oyster Creek 138kV Substation - GINR - 16INR0003 | Build two 138 kV leads to LEVEE substation. |  | Oyster CReek | LEVEE | Planned | 4710 | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 932 | 2018-09-02 00:01 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 43335, 111302 | Y | N |  | Cost is Included in 4950A Project. | 14160 | 4950
5585 | West Edinburg loop in line | Loops the North Edinburg to Palmhurst line into West Edinburg |  | West Edinburg |  | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2018-09-07 | 2018-10-30 | 138 | 0.1 | 0 | 0 |  | Hidalgo |  | Tier 1 | 2015-07-01 | 2016-05-19 | 2016-06-01 | 5771, 5774, 8380 | Y | N |  | Part of AEPSC Hidalgo Starr transmission project | 13312 | 5585
7045 | County Road 101 to Yucca Drive: Rebuild 138 kV line | Rebuild Solstice to Yucca Drive 138 kV line and add dynamic reactive devices at Lotebush | IN SERVICE | County Road 101 | Yucca Drive | In-Service | 713 - 0946 | AEP TNC | John Pulay mlforcum@aep.com 918-599-2674 | 2738 | 2018-09-20 | 2018-10-03 | 138 | 0 | 8.889 | 0 |  | Reeves | Ward | Tier 1 | 2015-12-15 | 2016-09-21 | 2016-10-26 | 6656, 60392, 60397, 6657, 60415 | Y | N |  |  | 14867 | 7045
6582 | Ajo-Zorillo: Create Temporary Tap | Create temporary tap on the Ajo-Zorillo 345 kV line for Stella Windfarm. |  | Ajo | Zorillo | In-Service | 893 - 1071 | ETT | Teresa Trotman dnlyons@aep.com 918-599-2698 | 3677 | 2018-09-21 | 2018-11-14 | 345 | 0 | 0 | 0 |  | Kenedy |  | Tier 4 |  |  |  | 80070, 80071, 80076 | Y | N |  |  | 14336 | 6582
6394 | Bakersfield to Waymark: Build 345 kV line | Interconnect Waymark solar farm at Bakersfield | IN SERVICE | Bakersfield | Waymark | In-Service | 802 - 0987 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2655 | 2018-09-22 | 2018-09-22 | 345 | 5 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 60419, 76002 | Y | N |  |  | 14153 | 6394
3418 | Nelson Sharpe: Add 345 kV Terminal for WF Interconnect | Add a new 345 kV line terminal at Nelson Sharpe for the Patriot WF Interconnect |  | Nelson Sharpe | - | In-Service | 515 - 0756 | AEP TCC | Dave Goetz dnlyons@aep.com 918-599-2698 | 3474 | 2018-09-28 | 2018-07-25 | 345 | 0 | 0 | 0 |  | Kleberg |  | Tier 4 |  |  |  | 85008, 85000, 161653 | Y | Y |  | 0 | 44681 | 3418
6670 | Katy to Flewellen Ckt.09 | Upgrade Ckt.09 Katy to Flewellen to increase thermal ratings |  | Katy Tap | Flewellen | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-09-30 |  | 138 | 0 | 0 | 0 |  | Waller | Fort Bend | Tier 4 |  |  |  | 44230, 44420 | Y |  |  |  | 14473 | 6670
6311 | Obrien Auto A2 | Replace the failed 600MVA autotransformer 2A and existing 600MVA autotransformer 2B with a new 800MVA autotransformer A2 | - Delayed project schedule | Obrien |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-09-30 00:01 |  | 345 | 0 | 0 | 800 |  | Harris |  | Tier 4 |  |  |  | 44500, 44505, 44510, 44515, 49064, 49065, 44513 | Y | N |  |  | 14040 | 6311
6222 | DERICK - 138kV Customer-Owned Substation | Install 138kV DERICK customer-owned substation. Loop through Ckt.85 South Channel to Shell. |  | DERICK | South Channel/Shell | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-09-30 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41320, 40070, 40089, 40470, 40530, 41370, 41210, 41380, 41410, 41415, 41450, 41590 | Y | N |  |  | 13947 | 6222
6244 | Rio Pecos to Sun Valley 69 kV line: Rebuild 69 kV line | Rehab Rio Pecos to Sun Valley 69 kV line | IN SERVICE | Rio Pecos | Sun Valley | In-Service | 786 - 0971 | AEP TNC | Tram Trinh mlforcum@aep.com 918-599-2674 | 2703 | 2018-10-01 | 2018-10-01 | 69 | 0 | 9.4 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6598, 6641 | Y | N |  |  | 13969 | 6244
3887 | Relocate Hallettsville Auto to Nixon | Relocate 138/69 kV Auto at Hallettsville to LCRA Nixon, associated GCBs, Bus |  | LCRA Nixon |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2018-10-01 |  | 138 | 0 | 0 | 40 |  | Gonzales |  | Tier 1 | 2012-09-01 | 2012-10-31 | 2013-03-10 | 7585, 7617, 7246, 7621 | Y | N |  |  | 11352 | 3887
3683 | Abilene South to Sawgrass: Rebuild 69 kV line | Rebuild Abilene South to Sawgrass 69 kV line | IN SERVICE | Abilene South | Sawgrass | In-Service | 651 - 0820 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 1815 | 2018-10-01 | 2018-10-01 | 69 |  | 2.15 |  |  | Taylor | Taylor | Tier 4 |  |  |  | 6284, 60394, 6283, 6285, 6636 | Y | N |  |  | 12804 | 3683
4706D | HO Clarke to Webster Ckt.05 | Outage Southwyck to Friendswood Tap for upgrades |  | Southwyck | Friendswood Tap | Conceptual |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2018-10-01 00:02 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42651, 43260 | Y |  |  | 0 | 50156 | 4706
5963 | Big Hill: Build 345 kV terminal | Interconnect Live Oak wind farm at Big Hill | IN SERVICE | Big Hill |  | In-Service | 844 - 1028 | ETT | Greg Crane mlforcum@aep.com 918-599-2674 | 2685 | 2018-10-05 | 2018-10-05 | 345 | 0 | 0 | 0 |  | Schleicher |  | Tier 4 |  |  |  | 76003 | Y | N |  |  | 13678 | 5963
6315A | Distribution Cap Banks at Knight | Add 7.2 MVAr Distribution Capacitor Bank at Knight. |  | Knight |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-10-05 00:01 |  | 138 | 0 | 0 | 0 | 0,7.2 | Harris |  | Tier 4 |  |  |  | 47332 | Y | N |  | 0 | 44953 | 6315
6315C | Distribution Cap Banks at Knight | Add two 7.2 MVAr Distribution Capacitor Banks at Gulf Gate. |  | Gulf Gate |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-10-05 00:03 |  | 138 | 0 | 0 | 0 | 0,14.4 | Harris |  | Tier 4 |  |  |  | 42742 | Y | N |  | 0 | 44955 | 6315
6315B | Distribution Cap Banks at Knight | Add 7.2 MVAr Distribution Capacitor Bank at Pearland |  |  | Pearland | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-10-10 00:02 |  | 138 | 0 | 0 | 0 | 0,7.2 | Harris |  | Tier 4 |  |  |  | 43051 | Y | N |  | 0 | 44954 | 6315
44370 | Wingarten Substation Addition | Construct a 69-kV unbreakered substation between La Pryor and Turtle Creek on an AEP owned line. The substation will provide transmission service for a DSP load interconnection request. |  | La Pryor | Turtle Creek | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2018-10-12 |  | 69 | 0 | 0 | 0 |  | Zavala | Zavala | Tier 4 |  |  |  | 7867, 8243, 8672 | Y | N |  | 0 | 44371 | 44370
6104 | Refugio - Heard Tap 69 kV Line | Rehab Refugio - Heard Tap 69 kV Line |  | Refugio | Heard Tap | In-Service | 834 - 1018 | AEP TCC | Jason Bryant dnlyons@aep.com 918-599-2698 | 3635 | 2018-10-14 | 2018-12-20 | 69 | 0 | 2.36 | 0 |  | Refugio |  | Tier 4 |  |  |  | 8410, 8802 | Y | N |  |  | 13830 | 6104
6095 | South Channel to Jefferson Ckt.06 | Upgrades substation equipment at South Channel and/or Jefferson substation to increase thermal ratings. |  | South Channel | Jefferson | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-10-18 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41370, 41371 | Y | N |  |  | 13820 | 6095
5716 | GLOBAL - 138kV Substation | Build new 138kV ME Global customer-owned substation. Loop through Ckt.82 Oyster Creek to Velasco. |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-10-29 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 43345, 42190, 43335, 43337, 43336, 43361 | Y | N |  |  | 13457 | 5716
5172 | Laredo: Add two 138 kV breakers | Add two 138 kV breakers to the STATCOM yard and rebuild the Laredo to Laredo STATCOM 138 kV tie with 1026 ACCC/TW |  | Laredo | Laredo | In-Service | 744 - 0927 | AEP TCC | Rich Haley dnlyons@aep.com 918-599-2698 | 2918 | 2018-10-31 | 2018-12-20 | 138 | 0 | 0.111 | 0 |  | Webb | Webb | Tier 4 |  |  |  | 8293, 80021 | Y | N |  |  | 12831 | 5172
5767 | TECO to Grant Ckt.37 | Upgrade Ckt.37 TECO to Grant to increase thermal ratings |  | TECO | Grant | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-10-31 | 2018-10-31 | 138 | 0 | 0.1 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47110, 47350, 47430 | Y | N |  |  | 13513 | 5767
6581 | HUDSON (Brazoria Energy) - Generator Interconnection 138kV S | New 138kV HUDSON (Brazoria Energy) generator interconnection. Loop substation to create new Ckt.04 MONSAN to HUDSON to Mustang Bayou | - Accelerated project schedule | HUDSON | MONSAN/ Mustang Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-10-31 |  | 138 | 0.1 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42100, 905111, 905118, 42090, 42652, 42940, 42960, 111321, 43500 | Y | N |  |  | 14334 | 6581
5894 | Install Third Zenith 345/138kV 800MVA Transformer | Install a third 800MVA autotransformer at Zenith Substation. |  | Zenith |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-10-31 00:01 |  | 345 | 0 | 0 | 800 |  | Harris |  | Tier 4 |  |  |  | 49091, 44900, 44910 | Y | N |  |  | 13615 | 5894
5223A | 2015 RTP rebuild 4 sections from George West through Mathis | Rebuild 4/0 ACSR from George West Substation to Mathis with 795 ACSR that is 138 capable. 2015 RTP |  | GW Substation | Mathis | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2018-11-09 | 2018-12-13 | 69 | 0 | 18.44 | 0 |  | Live Oak | Live Oak | Tier 4 |  |  |  | 5668, 5684 | Y | N |  | 0 | 43339 | 43336
5993 | Owls: Build 138 kV station | Construct new 138 kV ring bus with a 138/69 kV autotransformer | IN SERVICE | Owls |  | Planned | 841 - 1025 | AEP TNC | Brad Duvall mlforcum@aep.com 918-599-2674 | 2681 | 2018-11-13 |  | 138 | 0 | 0 | 90 |  | Reagan |  | Tier 4 |  |  |  | 60413, 60414, 6536, 6544, 60361, 60396 | Y | N |  |  | 13709 | 5993
6579 | DALTON 138kV Substation | Construct service to new 138kV DALTON customer-owned substation. Loop through Ckt.86 CITIES to WINFRE. |  | DALTON | DALTON | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-11-14 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  | 40740, 40220, 40340, 40855, 40857, 40764, 904985 | Y |  |  | 0 | 43366 | 6579
5977 | Mertzon (CVEC T) to Tankersley 69 kV line: Rbld 69 kV line | Rehab Mertzon (CVEC Tap) to Tankersley 69 kV line | IN SERVICE | Mertzon (CVEC Tap) | Tankersley | In-Service | 786 - 0971 | AEP TNC | Bill Roberts mlforcum@aep.com 918-599-2674 | 2662 | 2018-11-16 | 2018-11-16 | 69 | 0 | 13.2 | 0 |  | Irion | Irion | Tier 4 |  |  |  | 6526, 6528, 6529 | Y | N |  |  | 13692 | 5977
44404 | Jim Treece: Interconnect Blue Summit II | Interconnect Blue Summit II wind farm into Blue Summit station | IN SERVICE | Jim Treece |  | In-Service | 932 - 1110 | AEP TNC | Dave Goetz mlforcum@aep.com 918-599-2674 | 2743 | 2018-11-16 | 2018-11-16 | 345 | 0 | 0 | 0 |  | Wilbarger |  | Tier 4 |  |  |  | 61001 | Y | N |  | 0 | 44405 | 44404
3897 | Add New Weltner Rd. Sub | Construct a new 138-kV Weltner Rd. (7758) substation, which will cut into the LCRA TSC Clear Springs (7680) to Freiheit (7462) 138-kV transmission line | Substation name change from FM758 to Weltner | Weltner Road | Freiheit Road / Clear Springs | Planned |  | LCRATSC/NBU | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1015105 | 2018-11-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7758, 7462, 7680 | Y | N |  |  | 12022 | 3897
5493 | Hays Energy Substation Upgrade | Upgrade the Hays Energy 345-kV substation bus to a double bus double breaker configuration. |  | Hays Energy |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1016230 | 2018-11-30 |  | 345 | 0 | 0 | 0 |  | Hays |  | Tier 4 |  |  |  | 7043 | Y | N |  |  | 13231 | 5493
6241 | WINMIL 138kV Substation | Construct service to new 138kV WINMIL customer-owned substation. Loop through Ckt.26 Rosharon to Angleton | - Delay in project schedule | WINMIL | Rosharon/ Angleton | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-11-30 |  | 138 | 0.6 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 44531, 42110, 44410, 42870, 44600 | Y | N |  |  | 13966 | 6241
6001 | Goliad - Fannin 69 kV line | Rehab Goliad - Fannin 69 kV line |  | Goliad | Fannin | In-Service | 809 - 0994 | AEP TCC | James Nivens dnlyons@aep.com 918-599-2698 | 3598 | 2018-11-30 | 2018-12-20 | 69 | 0 | 5 | 0 |  | Goliad | Victoria | Tier 4 |  |  |  | 5736, 8587 | Y | N |  |  | 13718 | 6001
18TPIT0002 | Martinez - New 138kV Substation | Loop new 138kV substation into the existing 138kV Deely to Skyline line |  | Deely | Skyline | Planned | S-0751 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0218 | 2018-12-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5294, 5110, 5368 | Y | N |  | There are no transformers associated with this project | 9511 | 2263
6245 | Sun Valley to Masterson Field 69 kV line: Rebuild 69 kV line | Rehab Sun Valley to Masterson Field 69 kV line | IN SERVICE | Sun Valley | Masterson Field | In-Service | 786 - 0971 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2702 | 2018-12-01 | 2018-12-01 | 69 | 0 | 7.17 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6641, 6642 | Y | N |  |  | 13973 | 6245
44864 | Schottky 69 kV Hard Tap | New Schottky 69 kV Hard Tap |  | Pleasanton | Three Rivers | Planned | 970 - 1148 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3728 | 2018-12-01 |  | 69 | 0 | 0 | 0 |  | Live Oak |  | Tier 4 |  |  |  | 88507, 8400, 8406 | Y | N |  | 0 | 44865 | 44864
6105 | Heard Tap - Woodsboro 69 kV Line | Rehab Heard Tap - Woodsboro 69 kV line |  | Heard Tap | Woodsboro | In-Service | 834 - 1018 | AEP TCC | Jason Bryant dnlyons@aep.com 918-599-2698 | 3636 | 2018-12-01 | 2018-12-20 | 69 | 0 | 2.41 | 0 |  | Refugio |  | Tier 4 |  |  |  | 8802, 8804 | Y | N |  |  | 13831 | 6105
5943 | T-283 Prairie View to Sunnyside | Rebuild transmission line to 138-kV capable 959.6 ACSS-TW conductor due to maintenance on old 69 KV wood pole line and the future conversion to 138 KV. |  | Prairie View | Sunnyside | Under Construction |  | SBEC | Don Roberts droberts@sbec.org | WO# 17-6069 | 2018-12-01 |  | 69 | 0 | 13 | 0 |  | Waller | Waller | Tier 4 |  |  |  | 7664, 7666 | Y | N |  |  | 13654 | 5943
4711B | CORTEZ 138kV Substation | Add 138kV CORTEZ Load |  | CORTEZ |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 55 | 2018-12-01 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43440 | Y |  |  |  | 13648 | 4711
5926 | Kendall CTEC Circuit Breaker Addition | Add circuit breakers in a SB/SB arrangement at Kendall CTEC Tap (S343). |  | Kendall CTEC |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017390 | 2018-12-03 |  | 138 | 0 | 0 | 0 |  | Kendall |  | Tier 4 |  |  |  | 7147 | Y | N |  |  | 13634 | 5926
5017 | Lotebush: Build 138 kV station and add 2 capacitor banks | Construct new 138 kV station on the Barrilla Junction to Permian Basin Line and add two 28.8 Mvar capacitor banks | IN SERVICE | Lotebush |  | Under Construction | 736 - 0919 | AEP TNC | David Baker mlforcum@aep.com 918-599-2674 | 2616 | 2018-12-05 | 2018-12-05 | 138 | 0 | 0 | 0 | 0,57.6 | Reeves |  | Tier 4 |  |  |  | 6656, 1009, 6657, 6673, 38370, 60392, 60397, 60393, 60415 | Y | N |  |  | 14994 | 5017
5968 | Alpine to Alpine REA 69 kV line: Rebuild 69 kV line | Rehab Alpine to Alpine REA 69 kV line | IN SERVICE | Alpine | Alpine REA | In-Service | 786 - 0971 | AEP TNC | Guillermo Taylor mlforcum@aep.com 918-599-2674 | 2657 | 2018-12-11 | 2018-12-11 | 69 | 0 | 8.82 | 0 |  | Brewster | Brewster | Tier 4 |  |  |  | 6665, 6666 | Y | N |  |  | 13683 | 5968
6122 | Sunniland - Three Rivers 69 kV Line | Rehab Sunniland - Three Rivers 69 kV Line |  | Sunniland | Three Rivers | In-Service | 814 - 0998 | AEP TCC | James Nivens dnlyons@aep.com 918-599-2698 | 3606 | 2018-12-12 | 2018-12-20 | 69 | 0 | 7.18 | 0 |  | Live Oak |  | Tier 4 |  |  |  | 8400, 8406 | Y | N |  |  | 13848 | 6122
6080 | Concho to Christoval 69 kV line: Rebuild 69 kV line | Rehab Concho to Christoval 69 kV line | IN SERVICE | Concho | Christoval | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2694 | 2018-12-13 | 2018-12-13 | 69 | 0 | 16.8 | 0 |  | Tom Green | Tom Green | Tier 4 |  |  |  | 6450, 6495, 6477, 6527 | Y | N |  |  | 13804 | 6080
6003 | Knippa - Uvalde 69 kV line | Rehab Knippa - Uvalde 69 kV line |  | Knippa | Uvalde | In-Service | 811 - 0996 | AEP TCC | James Nivens dnlyons@aep.com 918-599-2698 | 3601 | 2018-12-13 | 2018-12-15 | 69 | 0 | 4.62 | 0 |  | Uvalde |  | Tier 4 |  |  |  | 8231, 8628 | Y | N |  |  | 13720 | 6003
6568 | SAPS: Replace the 138/69 kV autotransformer | Replace the 138/69 kV autotransformer at SAPS with a 130 MVA autotransformer | IN SERVICE | SAPS |  | In-Service | 839 - 1023 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2818 | 2018-12-14 | 2018-12-14 | 138 | 0 | 0 | 130 |  | Tom Green |  | Tier 4 |  |  |  | 6480, 76320, 6478 | Y | N |  |  | 14319 | 6568
5150 | Southwest Vernon: Replace 138/69 kV autotransformer | Add 138/69 kV autotransformer capacity at Southwest Vernon | IN SERVICE | Southwest Vernon |  | In-Service | 741 - 0924 | AEP TNC | Aaron Schwerman mlforcum@aep.com 918-599-2674 | 2913 | 2018-12-14 | 2018-12-14 | 138 | 0 | 0 | 130 |  | Wilbarger |  | Tier 4 |  |  |  | 6064, 6066 | Y | N |  |  | 12805 | 5150
7128 | Paris 138 kV Sw. Sta. | Rebuild existing switching station |  | PARIS |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4104 | 2018-12-15 |  | 138 | 0 | 0 | 0 |  | Lamar |  | Tier 4 |  |  |  | 1693 | Y | N |  |  | 14966 | 7128
6274 | Payne 138 kV Sw Sta | Rebuild the existing 138 kV Switching Station |  | Payne Sw. Sta |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R981 | 2018-12-15 |  | 138 | 0 | 0 | 0 |  | Grayson |  | Tier 4 |  |  |  | 1758, 1839, 11760, 1699, 1704, 1713, 1732, 1746, 1753, 1763, 12468, 140002, 1759, 11759 | Y |  |  | 0 | 44079 | 6274
6038 | Irving - Norwood 138 kV Line Section | Upgrade terminal equipment on Pleasant Valley - Ceramic 138 kV Line |  | Irving | Norwood | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4166 | 2018-12-15 |  | 138 | 0 | 0 | 0 |  | Dallas |  | Tier 4 |  |  |  | 2053, 2054, 2408 | Y | N |  |  | 13757 | 6038
5996 | Corsicana 69 kV Switching Station | Corsicana 69 kV Switching Station |  | Corsicana | Corsicana | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R2020 | 2018-12-15 |  | 138 | 0 | 0 | 100 |  | Navarro | Navarro | Tier 4 |  |  |  | 3466, 3467, 3469, 3480, 3127, 3128, 3455, 3468, 3478, 3479 | Y | N |  |  | 13713 | 5996
6779 | Wagley Robertson - Saginaw 138 kV Double-circuit Line | Upgrade existing line | Construction schedule changed | WAGLEY ROBERTSON | SAGINAW | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5250 | 2018-12-15 |  | 138 | 0 | 23 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 564, 1957, 2071, 2075, 2076, 2077 | Y | N |  |  | 14573 | 6779
5997 | Temple - Belton 138 kV Line | Temple - Belton 138 kV Line |  | Temple | Belton | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R784 | 2018-12-15 |  | 138 | 0 | 10.9 | 0 |  | Bell | Bell | Tier 4 |  |  |  | 3415, 3602, 3610, 3611, 3612 | Y | N |  |  | 13714 | 5997
5973 | Forest Hill 138 kV Switching Station | Rebuild existing Forest Hill 138 kV Switching Station |  | Forest Hill Sw. Sta. |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5268 | 2018-12-15 |  | 138 | 0 | 0 | 0 |  | Tarrant |  | Tier 4 |  |  |  | 1883, 1967, 2194 | Y | N |  |  | 13688 | 5973
5532 | NW Paris 138 kV Sw. Sta. | Construct new 138/69 kV switching station | Construction schedule change | NW Paris | Paris | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4100 | 2018-12-15 |  | 138 | 0 | 3.5 | 100 |  | Lamar |  | Tier 4 |  |  |  | 1700, 1703, 1778, 1803, 1805, 1806, 6846, 11701, 11778, 1693, 1694, 1777, 1788, 1820, 1821 | Y | N |  |  | 13260 | 5532
4549 | Yucca Drive - Barilla Junction (AEP) 138 kV Line | Rebuild Oncor's section of the existing line |  | Yucca Drive | Barilla Junction (AEP) | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8272 | 2018-12-15 |  | 138 | 0 | 15 | 0 |  | Ward | Pecos | Tier 3 | 2015-12-15 | 2016-09-21 | 2016-10-11 | 1009, 60397 | Y | N |  |  | 12126 | 4549
06TPIT0042 | Lake Wichita Switch - Wichita Falls Switch 69 kV line | Upgrade existing 69 kV line |  | Lake Wichita Switch | Wichitia Falls Switch | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R933-E | 2018-12-15 |  | 138 | 0 | 6.3 | 0 |  | Archer | Wichita | Tier 4 |  |  |  | 1446, 1447, 1448, 1449 | Y | N |  |  | 10565 | 3217
6035 | Liggett Sw. Sta. - Irving/Irving Grant 138 kV Double-circuit | Upgrade terminal equipment on Liggett Sw. Sta. - Irving/Irving Grant 138 kV Double-circuit Line section |  | Liggett | Irving Grant | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4164 | 2018-12-15 |  | 138 | 0 | 0 | 0 |  | Dallas |  | Tier 4 |  |  |  | 1922, 1924, 2053, 2055 | Y | N |  |  | 13754 | 6035
5434 | Littman - Fullerton 138 kV Line | Construct new 138 kV line |  | Littman | Fullerton | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8344 | 2018-12-15 |  | 138 | 10 | 5.5 | 0 |  | Andrews | Andrews | Tier 3 | 2016-08-24 | 2016-10-10 |  | 1273, 1134, 1275, 1274 | Y | N |  |  | 13137 | 5434
6271 | Wichita Falls 138 kV Sw Sta Rebuild | Rebuild the existing 138 kV switching station and install a second 138/69 kV autotransformer |  | Wichita Falls Sw. Sta. |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R970 | 2018-12-15 |  | 138 | 0 | 0 | 150 |  | Wichita |  | Tier 4 |  |  |  | 11448, 1448, 1446, 1449 | Y |  |  |  | 14001 | 6271
4840 | Crockett 138 kV Sw. Sta | Upgrade existing station |  | Crockett |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6060 | 2018-12-15 |  | 138 | 0 | 0 | 0 |  | Houston |  | Tier 4 |  |  |  | 3351, 3354 | Y | N |  |  | 12442 | 4840
4837 | Everman - Cleburne Sw. Sta. 138 kV Line | Upgrade existing Everman - Burleson line section | Construction schedule change | Everman | Burleson | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5204 | 2018-12-15 |  | 138 | 0 | 16.6 | 0 |  | Tarrant | Johnson | Tier 4 |  |  |  | 1883, 2208, 2209 | Y | N |  |  | 12439 | 4837
17TPIT0022 | Nacogdoches - Nacogdoches Southeast 138 kV Line | Upgrade existing Camino - Nacogdoches Southeast 138 kV line section |  | Camino | Nacogdoches Southeast | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6037-E | 2018-12-15 |  | 138 | 0 | 10.8 | 0 |  | Nacogdoches | Nacogdoches | Tier 4 |  |  |  | 3120, 3310, 3311, 13303 | Y | N |  |  | 14738 | 3152
5731B | Tri Corner 345 kV Sw Sta | Ultimate Configuration for Tri Corner |  | Tri Corner | Tri Corner | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4228 | 2018-12-15 |  | 345 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2432, 2428, 2433, 3102, 3124 | Y |  |  |  | 14311 | 5731
7042 | White Settlement - Hilltop 69 kV Line | Convert 4.3-mile section of 69 kV Line out of White Settlement to 138 kV. Install 100 MVA 138/69 kV autotransformer at White Settlement. |  | White Settlement | White Settlement West | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5230 | 2018-12-15 |  | 138 | 3 | 4.3 | 100 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 506, 1953, 1954, 1975, 2085, 2086, 2087, 2088, 2089 | Y | N |  |  | 14864 | 7042
5800 | Hutto-Taylor 138 kV Line | Upgrade existing 138 kV Line |  | Hutto | Taylor | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R775 | 2018-12-15 |  | 138 | 0 | 15.6 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 3658, 3666, 3673 | Y | N |  |  | 13540 | 5800
5485 | Nacogdoches Southeast Switching Station | Upgrade existing 138 kV switching station |  | Nacogdoches Southeast Sw. Sta. | Nacogdoches Southeast Sw. Sta. | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6068 | 2018-12-15 |  | 138 | 0 | 0 | 0 |  | Nacogdoches | Nacogdoches | Tier 4 |  |  |  | 3120, 3319 | Y | N |  |  | 13223 | 5485
5427 | Holt-Andrews North-Andrews County South 138 kV DCKT Line | Upgrade existing line |  | Holt | Andrews North | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8352 | 2018-12-15 |  | 138 | 0 | 30 | 0 |  | Andrews | Ector | Tier 3 | 2016-02-01 | 2016-05-01 |  | 1262, 1263, 1141, 1142, 1159, 1157, 1267 | Y | N |  |  | 13112 | 5427
4527 | Fullerton Switching Station | Construct new switching station |  | Fullerton |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8277 | 2018-12-15 |  | 138 | 0 | 0 | 0 |  | Andrews |  | Tier 4 |  |  |  | 1272, 1275, 1271, 1274, 1284, 11274 | Y | N |  |  | 12102 | 4527
6275 | Everman 345/138 kV autotransformer | Replace the existing autotransformer #1 and remove autotransformer #2 |  |  |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5263 | 2018-12-15 12:00 |  | 138 | 0 | 0 | 600 |  | Tarrant |  | Tier 4 |  |  |  | 24997, 1882, 1886, 1883, 11882, 11884, 11886 | Y |  |  | 0 | 45492 | 6275
44189 | Upgrade Wolf Holllow - Comanche Peak 345 kV Line |  |  | WOLF HOLLOW | COMANCHE PEAK | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2018-12-15 12:00 |  | 345 | 0 | 7.8 | 0 |  | Hood | Somervell | Tier 4 |  |  |  | 1900, 1981 | Y | N |  | 0 | 44190 | 44189
5431 | Holt 138 kV Switching Station | Expand existing 138 kV switching station |  | Holt |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8353 | 2018-12-15 12:00 |  | 138 | 0 | 0 | 0 |  | Ector |  | Tier 4 |  |  |  | 1142, 1259, 1123, 1141, 1257 | Y | N |  |  | 13134 | 5431
4251 | Everman - Wedgwood 138 kV Line | Upgrade existing double-circuit line | Construction schedule change | Everman | Wedgwood | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5210 | 2018-12-16 |  | 138 | 0 | 18 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1883, 1967, 2184, 2185, 2190, 2191, 2192, 2193, 2194, 2195 | Y | N |  |  | 11797 | 4251
6562A | Crowley - Cresson 69 kV Line Conversion | Rebuild existing 69 kV line section from Crowley - Cresson |  | Crowley | Cresson | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5244 | 2018-12-18 |  | 138 | 0 | 0 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2202, 2203, 1884, 1967, 2205 | Y | N |  |  | 14307 | 6562
5199 | Vernon Main Street: Add 138 kV capacitor banks | Add two 14.4 Mvar capacitor banks at Vernon Main Street | IN SERVICE | Vernon Main Street |  | In-Service | 760 - 0944 | AEP TNC | Dave Goetz mlforcum@aep.com 918-599-2674 | 2635 | 2018-12-21 | 2018-12-21 | 138 | 0 | 0 | 0 | 0,28.8 | Wilbarger |  | Tier 4 |  |  |  | 6060 | Y | N |  |  | 12858 | 5199
6081 | Chillicothe to Vernon Main 69 kV line: Rebuild 69 kV line | Rehab Chillicothe to Vernon Main 69 kV line | IN SERVICE | Chillicothe | Vernon Main | In-Service | 786 - 0971 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2695 | 2018-12-22 | 2018-12-22 | 69 | 0 | 14.17 | 0 |  | Hardeman | Wilbarger | Tier 4 |  |  |  | 6056, 6057, 6058 | Y | N |  |  | 13805 | 6081
5994 | Owls to Pwll Fld Jnctn T (Bison) 69 kV line: Rbld 69 kV line | Rehab Owls to Powell Field Junction Tap (Bison) 69 kV line | IN SERVICE | Owls | Bison | In-Service | 786 - 0971 | AEP TNC | Michael Richardson mlforcum@aep.com 918-599-2674 | 2665 | 2018-12-27 | 2018-12-27 | 69 | 0 | 11.53 | 0 |  | Reagan | Crockett | Tier 4 |  |  |  | 6545, 60396, 60395, 60413 | Y | N |  |  | 13710 | 5994
16TPIT0034 | Coleto Creek to Tuleta: New 138 kV Line | Build a double circuit capable 138 kV circuit from Coleto Creek station to new Tuleta station. |  | COLETO CREEK | TULETA | Under Construction | 606-0771 | AEP TCC | Dave Goetz dnlyons@aep.com 918-599-2698 | 3481 | 2018-12-30 |  | 138 | 56 | 0 | 0 |  | Goliad | Bee | Tier 1 | 2012-08-31 | 2012-12-27 | 2013-04-05 | 8595, 8162, 8590 | Y | N |  |  | 10877 | 3495
6078 | Bronte to Bronte Atlantic 69 kV line: Rebuild 69 kV line | Rehab Bronte to Bronte Atlantic 69 kV line | IN SERVICE | Bronte | Bronte Atlantic | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2692 | 2018-12-30 | 2018-12-30 | 69 | 0 | 3.73 | 0 |  | Runnels | Coke | Tier 4 |  |  |  | 6414, 6418 | Y | N |  |  | 13802 | 6078
5527 | Euler 138 kV Station: Construct a new station | Build a double circuit capable 138 kV circuit from Coleto Creek station to new Tuleta station. |  | Euler | - | Under Construction | 606-0771 | AEP TCC | Dave Goetz dnlyons@aep.com 918-599-2698 | 3481 | 2018-12-30 |  | 138 | 0 | 0 | 0 |  | Goliad |  | Tier 1 | 2012-08-31 | 2012-12-27 | 2013-04-05 | 8595, 5675 | Y | N |  |  | 13254 | 5527
5588 | La Palma Dynamic Reactive | Add +300/-300 MVAR Dynamic Reactive to La Palma 138 kV station |  | La Palma | - | In-Service | 793 - 0978 | AEP TCC | Teresa Trotman dnlyons@aep.com 918-599-2698 | 3583 | 2018-12-30 | 2018-11-20 | 138 | 0 | 0 | 0 | -300300 | Cameron |  | Tier 1 | 2015-04-16 | 2016-05-19 | 2016-06-16 | 80319, 80320, 80322, 80323, 8314 | Y | N |  |  | 13318 | 5588
6312B | PH Robinson Autotransformer A3 800MVA Addition | Move PH Robinson 800MVA 345/138kV Auto A1 to North bus. | - Delayed project schedule | PH Robinson |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-12-30 00:01 |  | 345 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 42000, 42010, 42015, 49026 | Y | N |  | 0 | 43465 | 6312
43531 | PH Robinson - Replace Failed Auto A4 | Replace failed PH Robinson auto A4 (800MVA) |  | PH Robinson |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-12-31 |  | 345 | 0 | 0 | 0 |  | Galveston |  | Tier 4 |  |  |  | 49047, 42000, 42010 | Y | N |  | 0 | 43532 | 43531
5998 | Ganso: Build new 138 kV station | Build new three breaker ring in place of Eagle Pass Hydro Tap |  | Ganso | - | In-Service | 835 - 1019 | AEP TCC | Terry Weeks dnlyons@aep.com 918-599-2698 | 3637 | 2018-12-31 | 2018-11-08 | 138 | 0 | 0.3 | 0 |  | Maverick |  | Tier 4 |  |  |  | 8264, 8267, 8260, 8263, 8692 | Y | N |  |  | 13715 | 5998
5951 | Bishop-Stratton: Rebuild 69 kV line | Rebuild Bishop - Stratton 69 kV line |  | Bishop | Stratton | In-Service | 825 - 1009 | AEP TCC | Teresa Trotman dnlyons@aep.com 918-599-2698 | 3624 | 2018-12-31 | 2018-05-25 | 69 |  | 5 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8498, 8512 | Y | N |  |  | 13662 | 5951
5596 | Pharr Dynamic Reactive | Add +300/-300 MVAR Dynamic Reactive to Pharr 138 kV station |  | Pharr | - | In-Service | 794 - 0979 | AEP TCC | Rich Haley dnlyons@aep.com 918-599-2698 | 3584 | 2018-12-31 | 2018-12-23 | 138 | 0 | 0 | 0 | -300300 | Hidalgo |  | Tier 1 | 2015-04-16 | 2016-05-19 | 2016-06-16 | 80372, 80373, 80375, 80376, 8372 | Y | N |  |  | 14072 | 5596
5715A | Red Bluff - 138kV Substation | Install temporary service for Red Bluff 138kV substation. Tap from Ckt.79 SEPTON to BAYWAY. |  | Red Bluff | Terminal/Bayway | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2018-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42931, 42170, 42955 | Y | N |  |  | 13454 | 5715
5429B | Phase 3 of the conversion to 138kV | Retire the existing 69kV line from the existing 69kV locust substation to Spencer Switch |  | Locust | Spencer Switch | Planned | N/A | DENTON | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2019-01-01 | 2017-07-01 | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 | 2015-11-10 |  | 2016-01-20 | 904, 914 | Y | N | N/A | 0 | 45743 | 5429
4186E | University Area 138kV Conversions |  |  | University |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1123 | 2019-01-14 00:03 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47760, 47752, 49030 | Y |  |  | 0 | 48946 | 4186
5223B | 2015 RTP rebuild 4 sections from George West through Mathis | Rebuild 4/0 ACSR from George West Switching Station to Kittie West Substation with 795 ACSR that is 138 capable. Removes the GOAB at West George West Switch. 2015 RTP |  | George West Switching Station | Kittie West | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-01-18 | 2019-06-15 | 69 | 0 | 4.25 | 0 |  | Live Oak | Live Oak | Tier 4 |  |  |  | 5685, 5683, 5684, 5686 | Y | N |  | 0 | 43337 | 43336
6583 | Del Sol-Cenizo: Create Temporary Tap | Install temporary tap on the Del Sol - Cenizo 345 kV line for the Rio Bravo windfarm temporary itnerconnection. The windfarm will build and own the gen-tie line from their collector station up to the tap point. The collector station name is CABEZON. |  | Del Sol | Cenizo | Planned | 895 - 1073 | ETT | Rich Haley dnlyons@aep.com 918-599-2698 | 3679 | 2019-01-22 |  | 345 | 0 | 0 | 0 |  | Starr |  | Tier 4 |  |  |  | 80380, 80225, 80307 | Y | N |  |  | 14337 | 6583
5763A | CHORIN to STRANG Ckt.87 | Upgrade 138kV Ckt.87 CHORIN to STRANG to increase thermal ratings. | - Transmission upgrade portion now on hold...Substation upgrades still expected | CHORIN | STRANG | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-01-23 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40320, 41500 | Y | N |  | 0 | 45412 | 5763
5763B | CHORIN to STRANG Ckt.87 | STRANG to Cedar Bayou Ckt.87 |  | STRANG | Cedar Bayou | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-01-23 00:01 | 2019-04-30 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40010, 41500 | Y | N |  | 0 | 45413 | 5763
6242 | Pinto Creek Substation Addition | Install a new motor operated 138-kV load serving substation on T464 between Brackettville and Hamilton Road. |  | Pinto Creek |  | Planned |  | LCRATSC/RGEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017994 | 2019-01-25 |  | 138 | 0 | 0 | 0 |  | Kinney |  | Tier 4 |  |  |  | 78255, 8252, 8255 | Y | N |  |  | 13967 | 6242
5535 | Lynx to Rio Pecos: Rebuild 138 kV line | Rebuild Lynx to Rio Pecos 138 kV line |  | Lynx | Rio Pecos | Planned | 788 - 0973 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2648 | 2019-01-31 |  | 138 | 0 | 2.23 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6601, 60400 | Y | N |  |  | 13263 | 5535
5217 | Rebuild Cotulla to Big Wells 69 kV line | Rebuild 69 kV line with 795 ACSR on 138 kV and double circuit capable structures 2015- NERC assessment |  | Cotulla | Big Wells | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-02-15 12:00 | 2019-02-18 | 69 | 0 | 22.2 | 0 |  | La Salle | Dimmit | Tier 4 |  |  |  | 5868, 5876 | Y | N |  |  | 12882 | 5217
6358 | Christoval to Arrott 69 kV line: Rebuild 69 kV line | Rehab Christoval to Arrott 69 kV line | IN SERVICE | Christoval | Arrott | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2721 | 2019-02-20 | 2019-02-20 | 69 | 0 | 8.17 | 0 |  | Tom Green | Schleicher | Tier 4 |  |  |  | 6495, 6496 | Y | N |  |  | 14102 | 6358
5972 | Benjamin Tap to Munday 69 kV line: Rebuild 69 kV line | Rehab Benjamin Tap to Munday 69 kV line | IN SERVICE | Benjamin Tap | Munday | In-Service | 786 - 0971 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2661 | 2019-02-28 | 2019-02-28 | 69 | 0 | 13.12 | 0 |  | Knox | Knox | Tier 4 |  |  |  | 790, 6086, 6087, 6107 | Y | N |  |  | 13687 | 5972
6636 | CELNES 138kV Substation | Install 138kV customer-owned CELWST substation. Loop from Ckt.94 BAYWAY to HIMONT |  | Himont | Bayway | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-02-28 | 2019-02-14 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42250, 42170, 42790 | Y |  |  | 0 | 43475 | 6636
5766A | Knight to BUNKER to HOC Ckt.08 Upgrades | Upgrade Ckt.08 Knight to BUNKER to increase thermal ratings |  | Knight | BUNKER | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-02-28 |  | 138 | 0 | 1.6 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47331, 47340 | Y | N |  |  | 13512 | 5766
5766B | Knight to BUNKER to HOC Ckt.08 Upgrades | Upgrade Ckt.08 HOC to BUNKER to increase thermal ratings |  | HO Clarke | BUNKER | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-02-28 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47150, 47340 | Y | N |  | Cost is Reflected in Phase A of TPIT Project 5766 | 13536 | 5766
47973 | Interconnects Saddleback and Roy Bean to TNMP WTN | Interconnects Saddleback and Roy Bean to TNMP WTN system (NOMCR # 55847-1). |  | Salt Draw Tap (Bus #38055) | Barilla Draw Tap (Bus #38065) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE04018 | 2019-03-01 |  | 138 | 0.1 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 38058, 38059, 38055, 38060 | Y |  |  | 0 | 48421 | 47973
5223C | 2015 RTP rebuild 4 sections from George West through Mathis | Rebuild 4/0 ACSR from Kittie West Substation to George West Substation to Mathis with 795 ACSR that is 138 capable. 2015 RTP |  | Kittie West | George West Substation | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-03-01 | 2019-04-15 | 69 | 0 | 6.44 | 0 |  | Live Oak | Live Oak | Tier 4 |  |  |  | 5684, 5683 | Y | N |  | 0 | 43338 | 43336
5634 | Rebuild Danevang to Clemville Sw 69 kV line | Rebuild the Danevang Sub to Clemville Switch 4/0 ACSR 69 kV line with 795 ACSR 138 capable. 2016 RTP |  | Danevang | Clemville | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2019-03-01 12:00 | 2019-03-08 | 69 | 0 | 5.1 | 0 |  | Wharton | Matagorda | Tier 4 |  |  |  | 5548, 5550 | Y | N |  |  | 13368 | 5634
44389 | Torrecillas POI | [6 empty] | ETT | Terry Weeks dnlyons@aep.com 918-599-2698 |  | 2019-03-02 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 80210, 80219, 161257 | Y |  |  | 0 | 44390 | 44389
6000 | Banquete - Calallen 69 kV line | Rehab Banquete - Calallen 69 kV line |  | Calallen | Banquete | Planned | 816 - 1000 | AEP/STEC | Andrew Garlick dnlyons@aep.com 918-599-2698 | 3609 | 2019-03-02 |  | 69 | 0 | 12.7 | 0 |  | Nueces |  | Tier 4 |  |  |  | 5626, 8888 | Y | Y |  |  | 13717 | 6000
4531 | Solstice to Clovis: Build 138 kV line | Interconnect Roserock solar farm with a new 138 kV line from Solstice to Clovis |  | Solstice | Clovis | Planned | 705 - 0875 | AEP TNC | Brent Harris mlforcum@aep.com 918-599-2674 | 2811 | 2019-03-02 |  | 138 | 4.5 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6630, 60383, 60385 | Y | N |  |  | 12106 | 4531
45053 | Schottky 69 kV Hard Tap | Schottky 69 kV Hard Tap |  | Sunniland | Three Rivers | Under Construction | 970 - 1148 | AEP | Glen Reed gareed@aep.com 918-599-2664 | 3728 | 2019-03-02 |  | 69 | 0 | 0 | 0 |  | Live Oak | Live Oak | Tier 4 |  |  |  | 88507, 8400, 8406 | Y | N |  | 0 | 45054 | 45053
6110 | Blessing - Palacios 69 kV Line | Rehab Blessing - Palacios 69 kV Line |  | Blessing | Palacios | Planned | 817 - 1001 | AEP | Jason Bryant dnlyons@aep.com 918-599-2698 | 3611 | 2019-03-02 |  | 69 | 0 | 9.27 | 0 |  | Matagorda |  | Tier 4 |  |  |  | 8119, 8131 | Y | N |  |  | 13836 | 6110
6119 | Rockport - Fulton 69 kV Line | Rehab Rockport - Fulton 69 kV Line |  | Rockport | Fulton | Planned | 827 - 1011 | AEP | Dave Goetz dnlyons@aep.com 918-599-2698 | 3628 | 2019-03-02 |  | 69 | 0 | 7.66 | 0 |  | San Patricio | Aransas | Tier 4 |  |  |  | 8431, 8432, 8841 | Y | N |  |  | 13845 | 6119
6201 | Alice - North Ella 69 kV Line | Rehab Alice - North Ella 69 kV Line |  | Alice | North Ella | Planned | 818 - 1002 | AEP | Andrew Garlick dnlyons@aep.com 918-599-2698 | 3614 | 2019-03-02 |  | 69 | 0 | 11.56 | 0 |  | Jim Wells |  | Tier 4 |  |  |  | 8500, 8878 | Y | N |  |  | 13926 | 6201
6011 | Laredo Plant: Replace 138/69 kV autotransformer | Upgrade 138/69 kV autotransformer capacity at Laredo Plant |  | Laredo Plant | - | In-Service | 806 - 0991 | AEP | Randy Weaver dnlyons@aep.com 918-599-2698 | 3595 | 2019-03-02 | 2018-12-20 | 138 | 0 | 0 | 180 |  | Webb |  | Tier 4 |  |  |  | 8530, 8290, 8642, 8293, 8298, 8303 | Y | N |  |  | 13728 | 6011
2979 | Melon Creek: Build new 138 kV station | Construct new Melon Creek station near Refugio, cut-in Airco to Rincon 138 kV line into Melon Creek, and cut-in Refugio to Tatton 69 kV line into Melon Creek. | Company Contact Update | Melon Creek | - | In-Service | 100 - 0100 | AEP | Bill Roberts dnlyons@aep.com 918-599-2698 | 2021 | 2019-03-02 | 2018-11-15 | 138 | 3 | 0 |  |  | Refugio |  | Tier 3 | 2017-03-31 | 2017-04-21 | 2017-06-01 | 8144, 8437, 8800, 8811, 80065, 8410, 8412, 80066 | Y | N |  |  | 10323 | 2979
44868 | McKenzie - Westside 138 kV Line | Rebuild McKenzie - Westside 138 kV Line |  | McKenzie Road | Westside | Planned | 968 - 1146 | ETT | Glen Reed gareed@aep.com 918-599-2664 | 3726 | 2019-03-02 |  | 138 | 0 | 11.48 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8485, 8858 | Y | N |  | 0 | 44869 | 44868
7006A | CNP_18TPIT7006_HOC_Reactor_Upgrades | Remove cap bank C1 from HOC Ckt.05 to WAP (position between HOC breakers H850 & H810) |  | HOC | HOC | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-03-07 | 2019-03-07 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47171, 44081, 47170 | Y |  |  |  | 14828 | 7006
45342 | Lemay: Build 138 kV Hard Tap | Lemay: Build 138 kV Hard Tap on North Laredo SS - Reveille Line |  | Encinal | Reveille | Planned |  | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 |  | 2019-03-11 |  | 138 | 0 | 0 | 0 |  | La Salle | La Salle | Tier 4 |  |  |  | 88088, 88627, 8619, 8612 | Y | N |  | 0 | 47935 | 45342
6355 | Robert Lee to Bronte 69 kV line: Rebuild 69 kV line | Rehab Robert Lee to Bronte 69 kV line | IN SERVICE | Robert Lee | Bronte | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2716 | 2019-03-11 |  | 69 | 0 | 8.72 | 0 |  | Coke | Coke | Tier 4 |  |  |  | 6414, 6419, 6420 | Y | N |  |  | 14099 | 6355
44814 | Ollin: Build 69 kV temporary tap | Build new Ollin 69 kV temporary tap on the Crane 69 kV loop | IN SERVICE | Ollin |  | In-Service | 955 - 1131 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2753 | 2019-03-14 01:00 | 2019-03-14 | 69 | 0 | 0 | 0 |  | Crane |  | Tier 4 |  |  |  | 6668, 6606, 6610, 6611 | Y | N |  | 0 | 44815 | 44814
44816 | Ollinphi: Build 69 kV temporary tap | Build new Ollinphi 69 kV temporary tap on the Crane 69 kV loop | IN SERVICE | Ollinphi |  | In-Service | 953 - 1132 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2758 | 2019-03-14 02:00 | 2019-03-14 | 69 | 0 | 0 | 0 |  | Crane |  | Tier 4 |  |  |  | 6669, 6606, 6610, 6668, 6611 | Y | N |  | 0 | 44817 | 44816
5931 | Shiner Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Shiner (S183). |  | Shiner |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017402 | 2019-03-21 |  | 138 | 0 | 0 | 0 |  | Lavaca |  | Tier 4 |  |  |  | 7238 | Y | N |  |  | 13639 | 5931
6246 | Masterson Fld to Pecos Valley 69 kV line: Rebuild 69 kV line | Rehab Masterson Field to Pecos Valley 69 kV line | IN SERVICE | Masterson Field | Pecos Valley | In-Service | 786 - 0971 | AEP TNC | Amanda Martin mlforcum@aep.com 918-599-2674 | 2701 | 2019-03-26 | 2019-03-26 | 69 | 0 | 8.84 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 6642, 6643 | Y | N |  |  | 13974 | 6246
4185 | HO Clarke Partial Load Conversion (TR1) | Convert HO Clarke TR1 load to 138kV. Tap off of Ckt.90 HO Clarke to Garrott | - Delayed project schedule | HO Clarke |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1112 | 2019-03-27 | 2019-03-27 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47155, 47160, 47150, 47322 | Y | N |  |  | 11715 | 4185
6750 | Quihi: Build 138kV Tap | Quihi Temprary 138kV Hard Tap on Razorback to Castroville 138kV Line |  | Quihi Tap | - | Planned | 899 - 1077 | AEP TCC/STEC | Daniel Lyons dnlyons@aep.com 918-599-2698 | 3683 | 2019-03-28 08:00 |  | 138 | 0 | 0 | 0 |  | Medina |  | Tier 4 |  |  |  | 88248, 5083, 8241 | Y | Y |  |  | 14543 | 6750
4996 | HO Clarke Load Conversion | Convert HO Clarke TR2 & TR3 to 138kV service. Tap off of Ckt.25 HO Clarke to Fondren. | - Delayed project schedule | HO Clarke | Fondren | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-03-30 | 2019-03-30 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 47151, 47152, 47160, 47100, 47150, 47412 | Y |  |  |  | 12629 | 4996
4186A | University Area 138kV Conversions | Convert University TR2 load to 138kV. |  | University | COUGAR | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1123 | 2019-03-30 | 2019-03-30 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47750, 47751, 47752, 47755, 47760, 47762, 47764, 42690, 47560, 47600, 47670, 47700, 47763, 49030 | Y | N |  | 0 | 48942 | 4186
6165 | Whitepoint: Install 100 MVAR Reactor | Whitepoint: Install 100 MVAR Reactor |  | Whitepoint | - | Planned | 867 - 1045 | AEP TCC | Dave Goetz dnlyons@aep.com 918-599-2698 | 3654 | 2019-03-31 |  | 345 | 0 | 0 | 0 | -100,0 | San Patricio |  | Tier 4 |  |  |  | 8956 | Y | N |  |  | 13890 | 6165
6106 | Woodsboro - Bonniview 69 kV Line | Rehab Woodsboro - Bonniview 69 kV line |  | Woodsboro | Bonniview | Planned | 834 - 1018 | AEP | Jason Bryant dnlyons@aep.com 918-599-2698 | 3640 | 2019-03-31 | 2019-02-10 | 69 | 0 | 5.37 | 0 |  | Refugio |  | Tier 4 |  |  |  | 8804, 8805 | Y | N |  |  | 13832 | 6106
4186B | University Area 138kV Conversions | Convert University TR3 load to 138kV. |  | University | Eastside | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1123 | 2019-03-31 | 2019-03-30 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47763, 47755, 47600, 47760 | Y | N |  | Cost included in 4186A | 48943 | 4186
6328A | REED - Substation Removal | Outage REED load |  | REED |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-03-31 00:01 |  | 69 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 41340 | Y |  |  | 0 | 45475 | 6328
6009 | Kenedy Switch: Replace 138/69 kV autotransformer | Upgrade 138/69 kV autotransformer capacity at Kenedy Switch |  | Kenedy Switch | - | Planned | 837 - 1021 | AEP | James Nivens dnlyons@aep.com 918-599-2698 | 3639 | 2019-04-03 | 2019-04-16 | 138 | 0 | 0 | 130 |  | Karnes |  | Tier 4 |  |  |  | 8184, 8186 | Y | N |  |  | 13726 | 6009
6889 | GSEC_6889_69kV_Add_Enterprise_Lake_Ivey_Sub | [6 empty] | GOLDENSPREAD | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2019-04-03 16:00 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 9431, 6377 | Y |  |  |  | 14704 | 6889
6781 | Leakey - Utopia Transmission Line Overhaul | Rebuild T281 Leakey to Utopia to be 138 kV capable with a nominal conductor rating of 223 MVA at 138 kV (Single Drake) with ADSS and operated at 69 kV. | Accelerating Schedule | Leakey | Utopia | Under Construction |  | BANDERA | Tyler Pansing t.pansing@banderaelectric.com 866-226-3372 Ext 6078 | 353985 | 2019-04-05 |  | 69 | 0 | 17.95 | 0 |  | Real | Bandera | Tier 4 |  |  |  | 7426, 7428 | Y | N |  |  | 14575 | 6781
6341 | Lake Pauline to Chillicothe 69 kV line: Rebuild 69 kV line | Rehab Lake Pauline to Chillicothe 69 kV line | IN SERVICE | Lake Pauline | Chillicothe | In-Service | 786 - 0971 | AEP TNC | Joseph Page mlforcum@aep.com 918-599-2674 | 2704 | 2019-04-09 | 2019-04-09 | 69 | 0 | 9.4 | 0 |  | Hardeman | Hardeman | Tier 4 |  |  |  | 6048, 6057 | Y | N |  |  | 14085 | 6341
4538 | Add new 138kV line from Tall City to Glass Ranch |  |  | Tall City | Glass Ranch | Planned |  | SHRY | Brad Schwarz 512-289-7425 |  | 2019-04-10 |  | 138 | 10 | 0 | 0 |  | Midland | Martin | Tier 2 |  |  |  | 79507, 79558 | Y | N |  |  | 12115 | 4538
6359 | Arrott to Pave Paws 69 kV line: Rebuild 69 kV line | Rehab Arrott to Pave Paws 69 kV line | IN SERVICE | Arrott | Pave Paws | In-Service | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2722 | 2019-04-11 | 2019-04-11 | 69 | 0 | 6.47 | 0 |  | Schleicher | Schleicher | Tier 4 |  |  |  | 6494, 6496, 6497 | Y | N |  |  | 14103 | 6359
5259 | Lotebush: Add dynamic reactive device | Rebuild Solstice to Yucca Drive 138 kV line and add dynamic reactive devices at Lotebush | IN SERVICE | Lotebush |  | In-Service | 713 - 0946 | AEP TNC | John Pulay mlforcum@aep.com 918-599-2674 | 2638 | 2019-04-12 | 2019-04-12 | 138 | 0 | 0 | 0 | -100100 | Reeves |  | Tier 1 | 2015-12-15 | 2016-09-21 | 2016-10-26 | 60392, 60439 | Y | N |  |  | 14312 | 5259
5887B | RUSSEL 138kV Substation (ARITEK Substation Removal) | Install 138kV customer-owned RUSSEL substation (ARITEK substation replacement). Loop from Ckt.84 DOWLAP to Morgans Point. |  | RUSSEL | DOWLAP/Morgans Point | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-04-13 | 2019-04-13 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40125, 40070, 40490, 41310, 41391, 41415, 41631, 41100, 41400, 41419, 41450, 42610 | Y | N |  |  | 13613 | 5887
5831 | Rebuild Gustine to Energy SW | Rebuild Gustine (Bus #273) to Energy SW (Bus #265) per RTP study results |  |  |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 16013 | 2019-04-18 |  | 69 | 0 | 5.05 | 0 |  | Comanche | Comanche | Tier 4 |  |  |  | 265, 273 | Y |  |  |  | 13573 | 5831
5930 | Robbins Switch Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Robbins Switch (S547). |  | Robbins Switch |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017400 | 2019-04-22 |  | 138 | 0 | 0 | 0 |  | Upton |  | Tier 4 |  |  |  | 76597 | Y | N |  |  | 13638 | 5930
4960 | Adding Nat Dam to Sales 17 miles 138 kV line |  |  | Sales Ranch | Natural Dam | Planned |  | SHRY | Brad Schwarz 512-289-7425 |  | 2019-04-25 |  | 138 | 17 | 0 | 0 |  | Martin | Howard | Tier 4 | 2015-06-29 | 2015-07-29 |  | 79508, 79509 | Y | N |  |  | 12593 | 4960
5715B | Red Bluff - 138kV Substation | Construct service to new 138kV Red Bluff distribution substation. Loop through Ckt.79 Terminal to Bayway |  | Red Bluff | Terminal/Bayway | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-04-29 | 2019-04-29 | 138 | 1.1 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42930, 42931, 905210, 42170, 42955, 43225 | Y | N |  |  | 13455 | 5715
7163 | T180 Lakeway - Marshall Ford MLSE Upgrade | Upgrade terminal equipment at Lakeway and Marshall Ford to achieve a planned static normal and emergency rating of 217 MVA on T180. |  | Lakeway | Marshall Ford | Planned | 1019367 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019367 | 2019-04-30 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 7356, 7538 | Y | N |  |  | 15004 | 7163
6021 | Haskell Tap 1 to Paint Creek 69 kV line: Rebuild 69 kV line | Rehab Haskell Tap 1 to Paint Creek 69 kV line | IN SERVICE | Haskell Tap 1 | Paint Creek | In-Service | 786 - 0971 | AEP TNC | Greg Crane mlforcum@aep.com 918-599-2674 | 2669 | 2019-04-30 | 2019-04-30 | 69 | 0 | 14 | 0 |  | Haskell | Haskell | Tier 4 |  |  |  | 6005, 6159, 6171, 6174 | Y | N |  |  | 13738 | 6021
10TPIT0062 | Marion Power Transformer Addition (Formerly Weil Road) | Expand the Marion substation 138-kV bus. Install a 138-26.18 kV 40 MVA power transformer at Marion 138 kV bus. | Delayed due to ERCOT outage restrictions | Marion |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org | 1015120 | 2019-04-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7178 | Y | N |  |  | 9648 | 2384
6101 | Lon Hill: Replace 345/138 kV autotransformers | Replace 345/138 kV autotransformers at Lon Hill | Formerly TPIT project 6040 | Lon Hill | - | Planned | 829 - 1013 | AEP | Bill Roberts dnlyons@aep.com 918-599-2698 | 3630 | 2019-04-30 | 2019-04-24 | 345 | 0 | 0 | 1350 |  | Nueces |  | Tier 4 |  |  |  | 8455, 8452, 8499, 8502 | Y | N |  | Formerly TPIT project 6040 | 13826 | 6101
6120 | Sabinal - Knippa 69 kV line | Rehab Sabinal - Knippa 69 kV line |  | Sabinal | Knippa | Planned | 811 - 0996 | AEP | James Nivens dnlyons@aep.com 918-599-2698 | 3602 | 2019-04-30 | 2019-04-23 | 69 | 0 | 2.655 | 0 |  | Uvalde |  | Tier 4 |  |  |  | 8628, 8630 | Y | N |  |  | 13846 | 6120
6715 | Noelke Substation Addition | Construct a new substation named Noelke off the Bakersfield to Schneeman Draw transmission line to support a generation interconnection request (20INR0011). |  | Bakersfield | Schneeman Draw | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1018746 | 2019-04-30 |  | 345 | 0 | 0 | 0 |  | Pecos | Crockett | Tier 4 |  |  |  | 7053, 76004, 76002, 76005 | Y | N |  |  | 14498 | 6715
6109 | Stadium - Banquete 69 kV Line | Rehab Stadium - Banquete 69 kV Line |  | Stadium | Banquete | Planned | 816 - 1000 | AEP TCC | Andrew Garlick dnlyons@aep.com 918-599-2698 | 3610 | 2019-04-30 |  | 69 | 0 | 16.43 | 0 |  | Jim Wells | Nueces | Tier 4 |  |  |  | 8031, 8888, 8889 | Y | Y |  |  | 13835 | 6109
6377 | Pave Paws to Eldorado Live Oak 69 kV line: Rbld 69 kV line | Rehab Pave Paws to Eldorado Live Oak 69 kV line |  | Pave Paws | Eldorado Live Oak | Planned | 786 - 0971 | AEP TNC | Andrew Garlick mlforcum@aep.com 918-599-2674 | 2723 | 2019-04-30 |  | 69 | 0 | 7.71 | 0 |  | Schleicher | Schleicher | Tier 4 |  |  |  | 6494, 6498 | Y | N |  |  | 14121 | 6377
7165 | T505 Geronimo - Clear Springs MLSE Upgrade | Upgrade terminal equipment at Geronimo and Clear Springs to achieve a planned static normal and emergency rating of 492 MVA on T505. |  | Geronimo | Clear Springs | Planned | 1019370 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019370 | 2019-04-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7604, 7680 | Y | N |  |  | 15006 | 7165
48685 | This adds capacitance to Hamilton | This adds capacitance to Hamilton NOMCR 56568 |  |  |  | Under Construction |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2019-05-01 |  | 69 | 0 | 0 | 0 | 0,7.6 | Comanche | Comanche | Tier 4 |  |  |  | 258 | Y |  |  | 0 | 48686 | 48685
45338 | Dobbin Tap: Build 138 kV Hard Tap | Dobbin Tap: Build 138 kV Hard Tap on Bunsen - Lon Hill Line |  | Bunsen | Lon Hill | Planned |  | AEP | Glen Reed gareed@aep.com 918-599-2664 |  | 2019-05-01 |  | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 88463, 8452, 8459 | Y | N |  | 0 | 45339 | 45338
47971 | Rebuild Friendswood-Seminole 138kV line with 795 ACSS | NOMCR # 58045-1 |  | TNMP Friendswood (Bus #38980) | TNMP Seminole (Bus #38990) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | STE07219 | 2019-05-01 |  | 138 | 0 | 2.9 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 38980, 38990 | Y |  |  | 0 | 48411 | 47971
6834A | IH20 STATCOM RPG | Re-conductor Collie Field Tap-Collie Field with 795 ACSR. Construct Collie Yard Tap and Collie Capacitor Station. Install three initial 20 MVAR MSCs at Collie Capacitor Station (38035). |  | Collie Field Tap (38037) | Collie Capacitor Station (38035) & Collie Field (38038) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-05-01 |  | 138 | 0.085227 | 0.056818 | 0 | 0,60 | Reeves | Reeves | Tier 1 | 2017-10-10 | 2017-12-06 |  | 38035, 38036, 38037, 38038 | Y |  |  | 0 | 46206 | 6834
48800 | [5 empty] | Planned |  | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 |  | 2019-05-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 8580, 8422, 8565, 80470 | Y |  |  | 0 | 48801 | 48800
5048 | Falfurius: Upgrade | Replace DSTATCOM with SVC Plus at Falfurius station +50 & -40 MVAR capability |  | Falfurrias | Falfurrias | Under Construction | 873-1049 | ETT | Kenneth 'Rich' Haley 918-599-2664 dnlyons@aep.com | 3658 | 2019-05-01 |  | 69 | 0 | 0 | 0 | -40,50 | Brooks | Brooks | Tier 4 |  |  |  | 8625, 88508, 8508 | Y | N |  |  | 12699 | 5048
6387A | Greenville Arera System Enhancements | [6 empty] | RYBRN | Charles Gibune 214-678-1192 |  | 2019-05-01 | 2019-05-01 | 138 | 0 | 0 | 0 |  | Hunt |  | Tier 3 | 2015-12-15 | 2016-02-15 |  | 6883 | Y | N |  | 0 | 47082 | 6387
43212A | Caymus Capbanks in TNMP West Texas System | Install 60 Mvar Capacitor bank at TNMP Caymus Substation (NOMCR # 57482-1). |  | Caymus (Bus #38410) | Caymus (Bus #38410) | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07819 | 2019-05-01 |  | 138 | 0 | 0 | 0 | 0,60 | Reeves | Reeves | Tier 4 |  |  |  | 38410 | Y |  |  | 0 | 48413 | 43212
6754 | Bunsen: Add Breakers | Add Breakers at Bunsen 138kV Substation for customer Interconnect. Build 0.75 mile of 138kV Line between Bunsen and Customer. |  | Bunsen |  | Planned | 902 - 1080 | AEP TCC | Daniel Lyons dnlyons@aep.com 918-599-2698 | 3686 | 2019-05-02 |  | 138 | 0.8 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 88464, 88465, 8459 | Y | N |  |  | 14547 | 6754
6749 | Rosata: Build 138kV Substation | Build new Rosata 138kV POD Switch on Coleto Creek to Kenedy 138kV Line |  | Coleto Creek | Kenedy | Planned | 898 - 1076 | AEP TCC/GVEC | Daniel Lyons dnlyons@aep.com 918-599-2698 | 3682 | 2019-05-02 | 2018-01-10 | 138 | 0 | 0 | 0 |  | Goliad |  | Tier 4 |  |  |  | 8153, 88153, 7241, 8162, 8186 | Y | Y |  |  | 14542 | 6749
6328B | REED - Substation Removal | Remove 69kV REED substation from CNP transmission service |  | REED |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-02 00:01 | 2019-05-02 | 69 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 41340, 40352, 40800, 41040 | Y |  |  | 0 | 45474 | 6328
6640 | PARKES 138kV Substation | Install 138kV customer-owned PARKES substation. Loop from Ckt.84 Channelview to HADEN |  | PARKES | Channelview/ HADEN | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-03 | 2019-05-03 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40881, 40280, 40780 | Y |  |  |  | 14397 | 6640
5917 | Desert Mesa Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Desert Sky Tap #1 (S566). |  | Desert Sky Tap #1 |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017353 | 2019-05-09 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 76022 | Y | N |  |  | 13625 | 5917
4758 | Sand Lake 138 kV Switching Station | Construct new switching station |  | Sand Lake |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8340 | 2019-05-14 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  | 11097, 1086, 11086, 11104, 11197 | Y | N |  |  | 12353 | 4758
17TPIT0024 | Payne - Anna Switch 138 kV Line | Upgrade existing line | Project Deferral | Payne | Anna Switch | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R938-E | 2019-05-15 |  | 138 | 0 | 20.8 | 0 |  | Grayson | Collin | Tier 4 |  |  |  | 1713, 1748, 1754, 1839, 2374 | Y | N |  |  | 10561 | 3213
6764 | Round Rock Capacitors | Upgrade existing capacitor banks at Round Rock Switching Station |  | Round Rock | Round Rock | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R764 | 2019-05-15 |  | 138 | 0 | 0 | 0 | 0,110.4 | Williamson | Williamson | Tier 4 |  |  |  | 3668 | Y | N |  |  | 14558 | 6764
2941B | North Main Switch third transmission source |  |  | North Main Tap | North Main Sw | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5161-E | 2019-05-15 |  | 138 | 0 | 0.1 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2093, 2106 | Y | N |  |  | 14910 | 2941
5805 | Holland 69 kV Capacitors | Install 69 kV Capacitors |  | Holland | Holland | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R772 | 2019-05-15 |  | 69 | 0 | 0 | 0 | 0,9.2 | Bell | Bell | Tier 4 |  |  |  | 3646 | Y | N |  |  | 13545 | 5805
7101 | Wink Sw. Sta. - No Trees Sw. Sta. 138 kV Line | Rebuild Wink Sw. Sta. - No Trees Sw. Sta. 138 kV Line |  | Wink | No Trees | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8406 | 2019-05-15 |  | 138 | 0 | 27.8 | 0 |  | Winkler | Winkler | Tier 3 |  | 2018-09-06 |  | 1074, 1147, 131853 | Y |  |  |  | 14935 | 7101
45573 | Hayter Ranch Substation Addition | Construct a new 138-kV Hayter Ranch substation. The Hayter Ranch Substation will be located on the Alamito Creek to Solstice 138-kV transmission line. The total length of the line is 68.12 miles and the Hayter Ranch substation will be approximately 8.5 miles from Solstice. |  | Alamito Creek | Solstice | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2019-05-15 |  | 138 | 0 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 78925, 60444 | Y | N |  | 0 | 45574 | 45573
45809 | Add Yucca Drive 138 kV Capacitors | Add Yucca Drive 138 kV Capacitors |  | Yucca | Yucca | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8466 | 2019-05-15 |  | 138 | 0 | 0 | 0 |  | Ward | Ward | Tier 4 |  |  |  | 1009, 1010 | Y |  |  | 0 | 45811 | 45809
5834 | Salt Creek to Cogdell | RPG Project for Salt Creek (Bus# 743) to Clairmont (Bus# 752) to ONCOR's Cogdell (Bus# 1402) |  |  |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 14032 | 2019-05-15 |  | 138 | 20 | 0 | 0 |  | Kent | Scurry | Tier 2 | 2015-12-21 | 2016-06-27 |  | 752, 743, 6198 | Y |  |  |  | 13576 | 5834
7100 | Wolf - General Tire 138 kV Series Reactor | Wolf - General Tire 138 kV Series Reactor |  | Wolf | General Tire | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8448 | 2019-05-15 |  | 138 | 0 | 0 | 0 |  | Ward | Ector | Tier 4 |  |  |  | 11018, 1013, 1103 | Y |  |  |  | 14934 | 7100
7102 | Wink - Yukon 138 kV Second Circuit | Wink - Yukon 138 kV Second Circuit |  | Wink | Yukon | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8449 | 2019-05-15 |  | 138 | 26.6 | 0 | 0 |  | Winkler | Ector | Tier 4 |  |  |  | 1251, 1253, 1258, 11237, 1074, 1250, 1252, 1254, 11253, 11260, 11252 | Y |  |  | 0 | 49707 | 7102
13TPIT0059 | Cedar Crest - Industrial 138 kV line | Upgrade existing line | Construction schedule change | Cedar Crest | Industrial | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4072-E | 2019-05-15 |  | 138 | 0 | 3.2 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2494, 2976, 2981 | Y | N | 2009-R23 |  | 9775 | 2495
5484 | Royse-Terrell 138 kV Line | Upgrade existing Royse - Terrell 138 kV line |  | Royse | Terrell Sw | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4224 | 2019-05-15 |  | 138 | 0 | 28 | 0 |  | Rockwall | Kaufman | Tier 4 |  |  |  | 2715, 2472, 2713, 2717, 2718, 2719, 2721, 2723 | Y | N |  |  | 13222 | 5484
6763 | Round Rock switching station | Reconfigure existing 138 kV Round Rock switching station |  | Round Rock | Round Rock | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R767 | 2019-05-15 |  | 138 | 0 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | Y | N |  |  | 14557 | 6763
5801 | Hutto - Rnd Rck SE - Gil | Upgrade138 kV line | Project Deferral | Hutto | Gilleland | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R2005 | 2019-05-15 |  | 138 | 0 | 7.5 | 0 |  | Williamson | Travis | Tier 4 |  |  |  | 3654, 3666, 7336 | Y | N |  |  | 13541 | 5801
6759 | Ranger Gulf 69 kV Emergency Capacitors | Install 18.4 MVar Cap Bank at Ranger Gulf |  | Ranger Gulf | Ranger Gulf | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R1746 | 2019-05-15 |  | 69 | 0 | 0 | 0 | 0,18.4 | Eastland | Eastland | Tier 4 |  |  |  | 1627 | Y | N |  |  | 14553 | 6759
7092 | Moss Sw. Sta. 345/138 kV Autotransformer #2 | Moss Sw. Sta. 345/138 kV Autotransformer #2 |  | Moss |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8275 | 2019-05-15 |  | 345 | 0 | 0 | 600 |  | Ector |  | Tier 4 |  |  |  | 18526, 1018, 1019 | Y |  |  |  | 14926 | 7092
4274 | Navarro - Corsicana 69 kV Line | Upgrade existing line |  | Navarro | Corsicana | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R793 | 2019-05-15 |  | 69 | 0 | 12.5 | 0 |  | Navarro | Navarro | Tier 4 |  |  |  | 3468, 3475, 3479, 3480, 13468 | Y | N |  |  | 11823 | 4274
5488 | Northwest Carrollton - LakePointe TNP 138 kV Line | Upgrade existing NW Carrollton - LakePointe 138 kV Line | Construction schedule change | Northwest Carrollton | LakePointe | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5156 | 2019-05-15 |  | 138 | 0 | 2.1 | 0 |  | Dallas | Denton | Tier 4 |  |  |  | 2362, 37010 | Y | N |  |  | 13226 | 5488
5927 | King Mountain Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at King Mountain West Tap (S563). |  | King Mountain |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017391 | 2019-05-15 |  | 138 | 0 | 0 | 0 |  | Crane |  | Tier 4 |  |  |  | 76635 | Y | N |  |  | 13635 | 5927
7099 | Yucca - Moss 138 kV Series Reactor | Yucca - Moss 138 kV Series Reactor |  | Yucca | Moss | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8447 | 2019-05-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 11015, 1009, 1019, 37980 | Y |  |  | 0 | 49925 | 7099
16TPIT0061 | Norwood - Record Crossing - East Levee 138 kV Line | Upgrade existing line | Construction schedule change | Norwood | East Levee | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4107-E | 2019-05-15 12:00 |  | 138 | 0 | 7.6 | 0 |  | Dallas | Dallas | Tier 4 |  | 2016-08-22 |  | 2405, 2407, 2482, 2811, 2812, 2813, 2815, 2816, 2814, 2819, 2823, 2824 | Y | N |  |  | 11846 | 3067
46280 | Screwbean Tap - Screwbean 138 kV Line | Rebuild Screwbean Tap - Screwbean 138 kV Line |  | Screwbean Tap | Screwbean | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8465 | 2019-05-15 23:00 |  | 138 | 0 | 0.8 | 0 |  | Culberson | Culberson | Tier 4 |  |  |  | 1079, 1090, 1095 | Y |  |  | 0 | 46282 | 46280
45118 | Add Dune Switch | Add Dune Switch |  | Dune Switch | Dune Switch | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R9050 | 2019-05-16 |  | 138 | 2 | 0 | 0 |  | Winkler | Winkler | Tier 4 |  |  |  | 11260, 1251, 11253, 182301 | Y |  |  | 0 | 45407 | 45118
6945 | Horseshoe Spring 138 kV Sw. Sta. | Horseshoe Spring 138 kV Sw. Sta. |  | Horseshoe Springs Switch |  | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8408 | 2019-05-16 |  | 138 | 0 | 0 | 0 |  | Culberson | Culberson | Tier 4 |  |  |  | 11190, 1096, 1097, 11079, 11097, 11103, 11191 | Y |  |  | 0 | 45510 | 6945
17TPIT0008 | Marion to Cibolo T-Line (T-302) Circuit Addition | Add another 138 kV circuit, to existing Marion to Cibolo T-Line (T-302), 1192 ACSR, 4.81 miles; Replace 3-138 breakers to 63 kA rating at Marion; Add 138 terminal w 138 breaker and associated relaying at Cibolo sub | Construction Schedule | Marion | Cibolo | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2019-05-17 |  | 138 | 4.81 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7178, 7608 | Y | N |  |  | 10137 | 2792
6946 | Add Horseshoe Draw 138 kV Dynamic Reactive Devices | Construct Horseshoe Draw 138 kV -250/+250 MVAR STATCOM |  | Horseshoe Spring | Horsehsoe Draw | Planned |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8418 | 2019-05-17 |  | 138 | 0 | 0 | 0 | 250250 | Culberson |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11172, 11190 | Y |  |  |  | 14768 | 6946
5234 | Cibolo to Schertz T-Line (T303), Breaker upgrades | Add 138kV Breaker at Schertz, replace 138 breaker at Cibolo; upgrad associated 138 switches relaying to achieve 277 MVA rating on the Cibolo to Schertz Cirtcuit #2. | Construction Schedule | Cibolo | Schertz | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2019-05-17 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7608, 7610 | Y | N |  |  | 12907 | 5234
7097 | Add Horseshoe Springs 138 kV Capacitors | Add 4 blocks of 36.8 MVAR capacitors at Horseshoe Springs Sw. Sta. |  | Horseshoe Springs |  | In-Service |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8410 | 2019-05-18 |  | 138 | 0 | 0 | 0 | 0,147.2 | Culberson |  | Tier 1 | 2018-02-02 | 2018-05-22 |  | 11079, 11103, 11190 | Y |  |  |  | 14931 | 7097
44902 | Marion Switch Upgrades and Replacement | Upgrade/Replace underrated switches 5679, 5681, 5689, 5691, 5699, 5701 to 3000 Amp Switches. Replace and increase fault interrupting rating of breakers 5680, 5690, 5700 to 63kA, and continuous rating to 3,000Amp. |  | Marion | Marion | Under Construction |  | NBU | Gregory Thomas gthomas@nbutexas.com 830-608-8953 |  | 2019-05-19 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7178 | Y | N |  | 0 | 44903 | 44902
6397 | Treadwell: Build new 138 kV station | Interconnect Cactus Flats wind farm on the SAPS to Yellowjacket 138 kV line | IN SERVICE | Treadwell |  | In-Service | 875 - 1053 | AEP TNC | Tom Reynolds mlforcum@aep.com 918-599-2674 | 2727 | 2019-05-22 | 2019-05-22 | 138 | 0 | 0 | 0 |  | Concho |  | Tier 4 |  |  |  | 60423, 6365, 6480 | Y | Y |  |  | 14156 | 6397
5978 | Tankersley to Mathis Field 69 kV line: Rebuild 69 kV line | Rehab Tankersley to Mathis Field 69 kV line | IN SERVICE | Tankersley | Mathis Field | In-Service | 786 - 0971 | AEP TNC | Bill Roberts mlforcum@aep.com 918-599-2674 | 2663 | 2019-05-23 | 2019-05-23 | 69 | 0 | 9.99 | 0 |  | Irion | Tom Green | Tier 4 |  |  |  | 6477, 6528 | Y | N |  |  | 13693 | 5978
44856 | Lipton 138 kV Hard Tap | New Lipton 138 kV Hard Tap |  | Asherton | West Batesville | Planned | 972 - 1150 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3730 | 2019-05-30 |  | 138 | 0 | 0 | 0 |  | Zavala |  | Tier 4 |  |  |  | 88285, 8236, 8283 | Y | N |  | 0 | 44857 | 44856
44460 | Tesla: Build 345 kV terminal | Interconnect Misae Solar at Tesla | Company Contact Update | Tesla |  | Planned | 936 - 1114 | ETT | Eric Blind mlforcum@aep.com 918-599-2674 | 2749 | 2019-05-30 |  | 345 | 0 | 0 | 0 |  | Childress |  | Tier 4 |  |  |  | 60501 | Y | N |  | 0 | 44461 | 44460
43511 | Keystone Capbank in TNMP West Texas System | Transfer West Texas spare 69kV 10MVar capacitor bank to Keystone Substation |  | East Toyah (Bus #38129) | Keystone (Bus #38290) | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2019-05-30 |  | 69 | 0 | 0 | 0 | 0,10 | Reeves | Winkler | Tier 4 |  |  |  | 38290 | Y |  |  | 0 | 48418 | 43511
5916 | Darst Creek Circuit Breaker Addition | Add circuit breakers in a ring bus arrangement at Darst Creek Substation (138-kV capable). |  | Darst Creek |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1017352 | 2019-05-30 |  | 69 | 0 | 0 | 0 |  |  | Guadalupe | Tier 4 |  |  |  | 78195 | Y | N |  |  | 13624 | 5916
6314A | BASF-HOFMAN-LakeJackson_Ckt.02_Upgrades | Upgrade 138kV Ckt.02 BASF to HOFMAN to increase thermal ratings. |  | BASF | HOFMAN | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-30 | 2019-04-22 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42150, 42810 | Y | N |  | 0 | 44960 | 6314
45336 | Corichi Tap: Build 138 kV Hard Tap | Corichi Tap: Build 138 kV Hard Tap on El Campo - Victoria Line |  | El Campo | Ganado | Planned |  | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 |  | 2019-05-30 |  | 138 | 0 | 0 | 0 |  | Wharton | Jackson | Tier 4 |  |  |  | 88099, 8102, 8117 | Y | N |  | 0 | 45337 | 45336
44397 | Continental: Rebuild 69 kV Station | Rebuild Continental 69 kV Station |  | Continental |  | Planned | 946 - 1128 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3710 | 2019-05-30 |  | 69 | 0 | 0 | 0 |  | Starr |  | Tier 4 |  |  |  | 8799 | Y | N |  | 0 | 44398 | 44397
6743 | Magellan Tank Farm: LCRA Interconnect | Add 138kV Tie Line between Navigation 138kV substation and Magellan's 138kV substation. Add Metering at Magellan's Substation. |  | Navigation | Magellan | Planned | 905 - 1083 | AEP TCC/LCRA | Dan Lyons dnlyons@aep.com 918-599-2698 | 3689 | 2019-05-30 |  | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 78460 | Y | Y |  |  | 14536 | 6743
7006B | CNP_18TPIT7006_HOC_Reactor_Upgrades | Install (1) 5-Ohm Reactor at HO Clarke as a fault duty upgrade |  | HOC | HOC | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47175, 42041, 47150, 47155, 47170, 47165, 49009 | Y |  |  |  | 14827 | 7006
6745 | Reading: New Distribution Station | Add New Reading Distribution Station |  | Uvalde | STEC Downie | Planned | 876 - 1054 | AEP TCC | Guillermo Taylor dnlyons@aep.com 918-599-2698 | 3663 | 2019-05-30 |  | 138 | 0 | 0 | 0 |  | Uvalde |  | Tier 4 |  |  |  | 8024, 5885, 8234 | Y | N |  |  | 14538 | 6745
6742 | Heines Sub: New Distribution Station | Add New Heines Sub Distribution Station |  | Airline | Naval Base | Planned | 877 - 1055 | AEP TCC | Dan Lyons dnlyons@aep.com 918-599-2698 | 3664 | 2019-05-30 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8490, 8997, 78560 | Y | Y |  |  | 14535 | 6742
6115 | Melon Creek - Tatton 69 kV Line | Rehab Melon Creek - Tatton 69 kV Line |  | Melon Creek | Tatton | Under Construction | 815 - 0999 | AEP | Bill Roberts dnlyons@aep.com 918-599-2698 | 3608 | 2019-05-30 | 2019-01-18 | 69 | 0 | 7.75 | 0 |  | Refugio | Aransas | Tier 4 |  |  |  | 80065, 8811 | Y | N |  |  | 13841 | 6115
3938C | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.82 Angleton to Richwood to increase thermal ratings. | - Overall change in schedule | Angleton | Richwood | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-05-30 00:03 |  | 138 | 0 | 14.2 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42110, 43150 | Y | N |  | Cost Included in TPIT Project 3938E | 45096 | 3938
3938B | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.26 STRATT to SINTEK to increase thermal ratings. |  | STRATT | SINTEK | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-05-30 00:04 |  | 138 | 0 | 6.4 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43240, 43300 | Y | N |  | Cost Included in TPIT Project 3938E | 45095 | 3938
3938D | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.82 Richwood to Cavern to increase thermal ratings. | - Overall change in schedule | Richwood | Cavern | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-05-30 00:04 |  | 138 | 0 | 5.4 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43150, 43330 | Y | N |  | Cost Included in TPIT Project 3938E | 45097 | 3938
3938E | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.26 Angleton to STRATT to increase thermal ratings. | - Overall change in schedule | Angleton | STRATT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-05-30 00:04 |  | 138 | 0 | 13.8 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42110, 43300 | Y | N |  |  | 45094 | 3938
43165 | Campbell138kVSwitchyardProjectAdded | Campbell138kVSwitchyardProjectAdded |  | Firewheel | Lookout | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2019-05-31 |  | 138 | 0 | 2 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 838, 821, 828 | Y | N |  | 0 | 43166 | 43165
4473 | Zorn to Marion 2nd 345-kV Transmission Line Addition | Add 345-kV Zorn (7042) to Marion (7044) 2nd circuit using bundled Suwannee. Portion of the CPS-Tie Project. |  | Zorn | Marion | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1015208 | 2019-05-31 |  | 345 | 18 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 1 | 2014-06-29 | 2015-03-26 | 2015-04-14 | 7042, 7044 | Y | N |  |  | 12034 | 4473
5555A | Clodine-Obrien Ckt25 & Ck73 Thermal Uprate | Upgrade Ckt.25 Clodine to Obrien to increase thermal ratings | Delay in project schedule | Clodine | Obrien | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1118 | 2019-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Fort Bend | Tier 4 |  |  |  | 44145, 44510, 44511 | Y | N |  |  | 13283 | 5555
6986 | Upton County Capacitor Bank Additions | Install two (2) 31.2 MVAR capacitor banks at Benedum Substation. |  | Benedum |  | Planned | 6717 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019103, 1019103 | 2019-05-31 |  | 138 | 0 | 0 | 0 | 0,31.2 | Upton |  | Tier 4 |  |  |  | 71213 | Y | N |  |  | 14803 | 6986
4844 | 2nd Marion Autotransformer | Add a Second 345/138-kV Autotransformer at Marion. Part of the CPS Tie Project |  | Marion | Marion | Planned | 4473 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1015208 | 2019-05-31 |  | 345 | 0 | 0 | 478 |  | Guadalupe | Guadalupe | Tier 1 | 2014-06-29 | 2015-03-26 | 2015-04-14 | 77044, 7044, 7178 | Y | N |  |  | 12446 | 4844
6314B | BASF-HOFMAN-LakeJackson_Ckt.02_Upgrades | Upgrade 138kV Ckt.02 HOFMAN to Lake Jackson to increase thermal ratings. | - Delayed project schedule | HOFMAN | Lake Jackson | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-31 | 2019-04-22 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42215, 42810, 42880, 48006 | Y | N |  | Cost included in 18TPIT6314A | 44961 | 6314
5242 | Clodine to Barker Ckt.73 Thermal Uprate | Upgrade Ckt.73 Clodine to Barker to increase thermal ratings | Delay in project schedule | Clodine | Barker | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1055 | 2019-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 44052, 44140 | Y | N |  |  | 12917 | 5242
3775 | Firewheel-WylieSW Line Upgrade | Firewheel to Wylie Switch 138 kV line upgrade to Cumberland conductor |  | Firewheel | WylieSW | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2019-05-31 |  | 138 | 0 | 17.77 | 0 |  | Dallas | Collin | Tier 4 |  |  |  | 821, 833 | Y | N |  |  | 11195 | 3775
6314C | BASF-HOFMAN-LakeJackson_Ckt.02_Upgrades | Upgrade 138kV Ckt.02 Lake Jackson to Retrieve to increase thermal ratings. |  | Lake Jackson | Retrieve | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2019-05-31 | 2019-04-22 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 42880, 43172 | Y | N |  | Cost included in 18TPIT6314A | 44962 | 6314
5555B | Clodine-Obrien Ckt25 & Ck73 Thermal Uprate | Upgrade Ckt.73 Clodine to Obrien to increase thermal ratings | Delay in project schedule | Clodine | Obrien | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1118 | 2019-05-31 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Fort Bend | Tier 4 |  |  |  | 44140, 44512 | Y | N |  |  | 13284 | 5555
4703A | Bellaire to San Felipe Ckt.09 & Bellaire tap Ckt.24 | Reconductor Ckt.09 Bellaire to San Felipe and upgrade substation equipment to increase thermal ratings. |  | Bellaire | San Felipe | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 | 1132 | 2019-05-31 00:01 |  | 138 | 0 | 2 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 46600, 47010, 47013, 47165, 47300, 47380, 47381, 47680 | Y | N |  | 0 | 48255 | 4703
3273A | Southton - New 138kV Substation | Rebuild Brooks to Brooks Tap |  |  |  | Under Construction | S-0750 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0217 | 2019-06-01 |  | 138 | 0 | 1.6 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5045, 5030, 5085 | Y |  |  | 0 | 45521 | 3273
44687 | New 345kV substation |  |  |  |  | Planned |  | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2019-06-01 |  | 345 | 0 | 0 | 0 |  | Deaf Smith | Deaf Smith | Tier 4 |  |  |  | 79513, 79502, 79504 | Y |  |  | 0 | 44688 | 44687
4083 | CPSE_Merida to Westside Rebuild | Rebuild approximately four miles of 138 kV transmission circuit from Merida to Westside. |  | Merida | Westside | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0235 | 2019-06-01 |  | 138 | 0 | 4 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5310, 5490 | Y | N |  |  | 11608 | 4083
4084 | Barton-Vega: Upgrade Ckt 928 | Reconductor to 2000 amps |  | Barton | Vega | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2019-06-01 |  | 138 | 0 | 4.05 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9158, 9285 | Y |  |  |  | 11609 | 4084
5144 | CPSE_Pleasanton Rd Transmission Rebuild | Rebuild approximately seven circuit miles of 138 kV transmission on Pleasanton Road from Loop 410 to Harlandale Tap. This project includes partial rebuild of the Sommers to Harlandale and Sommers to Merida 138 kV transmission circuits. |  | Sommers | Harlandale/Merida | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0192 | 2019-06-01 |  | 138 | 0 | 7 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5190, 5310, 5395 | Y | N |  |  | 12797 | 5144
11TPIT0084 | Hidden Lakes - New Substation | Build a new 138-12.47 kV substation to accommodate new subdivision growth along the FM 517 and FM 646 corridors in Dickinson, Texas. Project delayed until 2019 RMC. |  | Leave blank | Leave blank | Planned |  | TNMP | Anthony Hudson Anthony.Hudson@tnmp.com. 281-581-4712 | STE02416 | 2019-06-01 |  | 138 | 0 | 0 | 0 |  | Galveston |  | Tier 4 |  |  |  | 38900, 38890, 42015 | Y | N |  |  | 8439 | 1261
08TPIT0033 | Gilleland to Techridge 138kV Circuit | Establish a new 138kV circuit from Gilleland to Techridge and maintain a normally close tie between AEN and LCRA's switchyard at Gilleland. |  | Gilleland Substation | Techridge Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | PLAN_117_4276 PLAN_117_P207 | 2019-06-01 |  | 345 | 8 | 0 | 0 |  | Travis | Travis | Tier 2 |  | 2009-07-21 | 2009-07-21 | 9054, 9191, 7336, 9190 | Y | N |  |  | 8205 | 1029

## CancelledTPIT060119NoCost
JUNE BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 6/1/2019
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar ) (-Reactor, +Capacitor ) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number
6717 | Roadrunner Substation Addition | Construct a new load-serving substation named Roadrunner off the Benedum to Midkiff (T611) transmission line. |  | Benedum | Midkiff (Oncor) | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1019008 | 2019-06-30 |  | 138 | 0 | 0 | 0 |  | Upton | Upton | Tier 4 |  |  |  | 71220, 1210, 71213 | N | N |  |  | 14500 | 6717
6570 | Big Lake to Bison 69 kV line: Rebuild taps | Big Lake to Bison 69 kV line: Rebuild taps | CANCELLED | Big Lake | Bison | Planned | 892 - 1070 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2816 | 2019-12-31 |  | 69 | 0 | 1 | 0 |  | Reagan | Crockett | Tier 4 |  |  |  | 6533, 6546, 6547, 60395 | N | N |  |  | 14321 | 6570
5299 | Red Creek to Coke Street: Rebuild 138 kV line | Rebuild Red Creek to Coke Street 138 kV line | CANCELLED | Red Creek | Coke Street | Planned | 768 - 0953 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2639 | 2020-06-30 |  | 138 | 0 | 8.01 | 0 |  | Tom Green | Tom Green | Tier 4 |  |  |  | 6442, 6449 | N | N |  |  | 12975 | 5299
44056 | Coral to Toyana: Build 138 kV line | Construct a new 138 kV ring bus at Toyana, build new 138 kV lines to Cryo and Coral from Toyana, and add capacitor banks at Toyana | CANCELLED | Coral | Toyana | Planned | 931 - 1109 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2741 | 2020-11-30 01:00 |  | 138 | 0.63 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 60434, 60437 | N | N |  | 0 | 44057 | 44056
44058 | Coral: Build 138 kV station | Construct a new 138 kV ring bus at Toyana, build new 138 kV lines to Cryo and Coral from Toyana, and add capacitor banks at Toyana | CANCELLED | Coral |  | Planned | 931 - 1109 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2742 | 2020-11-30 01:00 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  | 60434 | N | N |  | 0 | 44059 | 44058
44988 | Coral to Toyana: Build 138 kV line | Construct a new 138 kV ring bus at Toyana, build new 138 kV lines to Cryo and Coral from Toyana, and add capacitor banks at Toyana | CANCELLED | Coral | Toyana | Planned | 931 - 1109 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2766 | 2020-11-30 01:00 |  | 138 | 4.28 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  | 60437, 60721 | N | N |  | 0 | 44989 | 44988
44990 | Toyana: Build 138 kV station and add two capacitor banks | Construct a new 138 kV ring bus at Toyana, build new 138 kV lines to Cryo and Coral from Toyana, and add capacitor banks at Toyana | CANCELLED | Toyana |  | Planned | 931 - 1109 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2765 | 2020-11-30 01:00 |  | 138 | 0 | 0 | 0 | 0,28.8 | Reeves |  | Tier 4 |  |  |  | 60437 | N | N |  | 0 | 44991 | 44990
3777 | Ozona to Midway Lane: Rebuild 69 kV line | Rebuild Ozona to Midway Lane 69 kV line | CANCELLED | Ozona | Midway Lane | Planned | 667 - 0836 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2594 | 2020-12-31 |  | 69 | 0 | 16.96 | 0 |  | Crockett | Crockett | Tier 4 |  |  |  | 6549, 6560 | N | N |  |  | 11197 | 3777
13TPIT0064 | Rocky Mound Switching Station series capacitors | Install series capacitors for Willow Creek - Clear Crossing - Dermott Switch (Central B) 345 kV line (Oncor Electric Delivery part) |  | Rocky Mound Switching Station |  | Conceptual |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | C079-E | 2021-05-15 |  | 345 | 0 | 0 | 0 |  | Haskell |  | CREZ |  |  |  | 17012, 17013, 17014, 17015, 1421, 60515 | N | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. | 9943 | 2644
6526 | Place second auto at Einstein |  |  | Einstein345 | Einstein138 | Planned |  | SHRY | Bradley Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2021-07-01 |  | 345 | 0 | 0 | 708 |  | Glasscock | Glasscock | Tier 4 |  |  |  | 79634, 79632, 79565 | N |  |  |  | 14264 | 6526
5752 | City of Brady to Heartland: Build 69 kV line | Construct new 69 kV line from City of Brady to Heartland | CANCELLED | City of Brady | Heartland | Planned | 796 - 0981 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 3587 | 2022-05-31 |  | 69 | 2 | 0 | 0 |  | McCulloch | McCulloch | Tier 2 |  |  |  | 6383, 60386 | N | N |  |  | 13492 | 5752

## RTPProjects
Project Number | Project Name | Transmission Owner | ERCOT Proposed in-service year | TSP MOD in-service year | Status of Project | Associated TPIT ERCOT Project Number(s) | Notes
2017-N1 | Kiamichi Energy Facility (140077) 345-kV reactors addition | KIOWA POWER PARTNERS LLC (RE) | 2020 |  |  |  | A mitigation plan has been identified to address this issue. The plan is currently implemented in Ercot Operations.
2017-N2 | Wichita Falls (1449) - Henrietta West (1543) - Lanham Tap 69kV line upgrades | Oncor | 2022
2017-N3 | Payne Switch (1758) - Anna Switch (2374) 138-kV line upgrades | Oncor | 2019 | 2019-05-15 | Planned | 17TPIT0024
2017-NC1 | Ranger Gulf (1627) -Thurber TNP (37850) 69-kV terminal equipment upgrade | TNMP/Oncor | 2019
2017-NC2 | Liggett Switch - Hackberry (2388) 138-kV double circuit line upgrade | Oncor | 2022 | 2021-05-15 | Planned | 5490
2017-NC3 | College (803)-Lawlert (815)-Jupiter (806) 69kV to 138kV line conversion and new 345 KV station additions. | Garland/Oncor | 2019
2017-NC4 | Olsen (37470) - Clifton (37600) - Walnut Spring 69-kV terminal equipment upgrade | TNMP | 2019
2017-NC5 | Allen Switch (2509) - Plano Custer Road (2525) 138-kV line upgrade | Oncor | 2019
2017-NC6 | Roanoke Switch (1854,1852) - Park Vista (15101,15100) 138-kV line upgrades | Oncor | 2019
2017-NC7 | Watermill Switch (2430) - Witt Road (3068) 138-kV line upgrade | Oncor | 2019
2017-NC8 | Plano West (2673,2680) - Richardson Alcatel (2685) - Richardson Spring (2689) 138-kV line upgrades | Oncor | 2019
2017-NC9 | Add a Capacitor Bank of minimum 112.5 MVAr at Heritage(559) | BREC | 2019
2017-NC10 | Wagley Robertson (2076) - Blue Mound (2071) 138-kV line upgrade | Oncor | 2019 | 2018-12-15 | Planned | 6779
2017-NC11 | Weatherford West Switch (1585) - Weatherford East (1586,1587) - Hilltop (506) 69-kV line upgrade | Oncor/BEPC | 2020
2017-NC12 | Wichita Falls (1449) - Wichita Falls Basin Tap (1508) 69-kV line upgrade | Oncor | 2023
2017-NC13 | Collins Switch (2372-2370) 345/138-kV transformer #2 reactor addition | Oncor | 2022
2017-NC14 | Richardson Spring Creek (2689) to Richardson East (2690) 138-kV line upgrade | Oncor | 2022
2017-NC15 | Add a Capacitor Bank of minimum 120 MVAr at LookOut (828) | Garland | 2020
2017-NC16 | Cedar Hill (2422) - Eagle Ford (3049) - Sorcey Road (3050) - Duncanville South (3052) 138-kV line upgrades | Oncor | 2019
2017-NC 17 | Highlands TNP (1974) - Argyle (1984) 138-kV line upgrade | Oncor | 2022
2017-NC 18 | Industrial (2976) - West Network (2875) - East Levee (2482) 138-kV line upgrades | Oncor | 2020
2017-NC19 | Liggett 345/138-kV transformers #1 and #2 series reactors | Oncor | 2020
2017-NC20 | Sargent Road (2941,2947,2940) - St Augustine (2951) - Southerland (2973) 138-kV line upgrades | Oncor | 2020
2017-NC21 | Rebuild existing Plano Tennyson 345/138 kV switching station (2522). | Oncor | 2022
2017-NC22 | Hicks Switch (2082) - Alliance (1855) - Roanoke (1854) 138-kV lines extension | Oncor | 2023
2017-NC23 | Bosque Switch (252) - Olsen TNP (37460) 138-kV line terminal equipment upgrade | TNMP | 2019
2017-NC 24 | Cedar Crist Switch(2493) - Dealey Street Switch(2842) 138-kV line upgrade | Oncor | 2019
2017-NC 25 | Everman Switch(1883) - Forest Hill Switch(1967) - Alcon Tap (2194) 138-kV line upgrade | Oncor | 2019
2017-NC 26 | Cooper Creek(906) - Arco(1993)138-kV line upgrade | TTMPA,TDME | 2019
2017-NC 27 | McCree(834) - Crist(850) - Ben Davis(968) 138-kV line upgrade | TTMPA | 2019 | 2020-05-01 | Planned | 43623
2017-NC 28 | Ben Davis 345/138-kV auto #2 upgrade | TTMPA | 2019 | 2020-12-01 10:00 | Planned | 6874
2017-NC 29 | Norwood Switch (2404) to Norwood Switch(2405) 138 -kV bus tie upgrade | Oncor | 2019
2017-NC 30 | Desoto Switch(2424) - Glenn Heights (2426) 138-kV line upgrade | Oncor | 2019
2017-NC 31 | Mesquite Forney Road (2752)-Thorne(12747)-Thornton East Tap(2747) 138-kV line upgrade | Oncor | 2020
2017-NC32 | Randol Mill Tap East (2104) to Randol Mill(2106) 138-kV line upgrade | Oncor | 2020
2017-NC34 | South Royse (2478) 345/138-kV transformer addition and line extensions | Oncor | 2022 | 2024-05-15 12:00 | Planned | 5524
2017-C1 | Grant Avenue TNP (39400) - Arco Pipeline TNP (39410) 69-kV line upgrade | TNMP | 2019
2017-C2 | Add a Capacitor Bank of minimum 50 MVAr at Plaza 138-kV substation | CNP | 2019 | 2018-10-05 00:01 | Planned | 6315
2017-C3 | Dunlavy (47580) - Heights (47680) 69-kV line upgrade | CNP | 2022 | 2020-05-31 | Planned | 6573
2017-C4 | New line from Villick (44270) - Tanner (46311) 138-kV line | CNP | 2022 | 2018-09-30 | Planned | 6670
2017-C5 | Jones Creek (42530) area bridge the gap upgrades | CNP | 2020 | 2019-11-30 | BOD Approved | 6673
2017-C7 | New Copper (42215) - Jones Creek (42541) 138-kV line | CNP | 2019 | 2019-05-30 | Operational | 6314
2017-C8 | SR Bertron (41400) - Alexander Island (41392) - Dowlap (40490) - Russel (40125) 138-kV line upgrade | CNP | 2019 | 2019-12-31 | Planned | 4426
2017-C9 | Add 4th 345/138-kV transformer at PH Robinson (42000) | CNP | 2023 | 2018-05-30 00:01 | Planned | 6312
2017-C10 | Add 6th 345/138-kV transformer at Dow Chemical (42500) | DOW | 2019
2017-FW1 | Big Lake - Bison -Midway 69kV line upgrade | AEP | 2019
2017-W1 | Hamilton Road (8255) - Del Rio City (8690) 138-kV line rebuild | AEP | 2022
2017-W2 | Picacho (8684) - Buena Vista (8688) 138-kV line rebuild | AEP | 2022
2017-W3 | San Angelo Power Station (6480) – Schkade (76320) 138-kV line terminal equipment upgrade | LCRA/AEP | 2019 | 2018-12-14 | Operational | 6568
2017-S1 | Holly (8486) - Holly (8517) 138-kV bus tie upgrade | AEP/STEC | 2019 | 2018-08-17 | Operational | 5168
2017-S2 | Azteca Sub (8708) - SE Edinburg (8374) - Pharr (5762) and North Edinburg (8380) - McColl Road (8908) 138-kV terminal equipment upgrade | AEP | 2019
2017-S3 | Melon Creek substation and transformer addition and 69-kV line rebuild | AEP | 2019
2017-S4 | Escondido (8260) - Eagle Pass (8270) 138-kV line upgrade | AEP | 2019
2017-S6 | North McAllen (8368) - North Edinburg (8380) 138-kV line upgrade | AEP | 2023
2017-S7 | Charlotte (8206) - Dilley2 (8208) 69-kV line upgrade | AEP | 2023 | 2022-10-30 | Planned | 44866
2017-S8 | Add 345/138-kV transformer at Fowlerton (5709) | STEC | 2019 | 2019-12-20 | Planned | 3894
2017-S9 | North McAllen (8368) - West McAllen (8367) - South McAllen (8371) 138-kV line upgrades | AEP | 2019 | 2020-06-30 | Planned | 5621
2017-SC1 | Gay Hill (7572) - Lyons (7573) 138-kV line rebuild | LCRA/BBEC | 2023 | 2022-04-08 | Planned | 5939
2017-SC2 | -Fayette Plant 138 (7278) - Weimar (7254) 138-kV line addition. -Fayette Plant 138 (7278) - Fayette River Pump (7280) 138-kV line terminal upgrade -Fayette Plant 138 (7278) - Fayetteville (7286) 138-kV line rebuild | LCRA | 2022 | 2020-05-31 | Planned | 5286
2017-SC3 | Wirtz (7104) - Johnson City (7516) - Blanco Tap (7514) - Mountain Top (7480) 138-kV line rebuilds | LCRA/PDECO | 2023 | 2019-12-01 | Planned | 6789

## TransmissionOwnerProjContac
TRANSMISSION OWNER | TPIT DISTRIBUTION | Primary Contact | Primary Email Address | Primary Phone | Secondary Contacts | Secondary Email Addresses | Secondary PHONE
AEP | Primary & Secondary | Cindy Miller | Camiller2@aep.com | Cindy Miller: 918 599 2891 | Glen Reed; David Kidd; Brad Myers; Mabel See; Mike Forcum; Doug Lee; Daniel Lyons; Bob Lager; Mina Turner; Lisa Kelso; Carole Myser | gareed@aep.com; dekidd@aep.com; blmyers@aep.com; msee@aep.com; mlforcum@aep.com; dnlyons@aep.com; dlee@aep.com; rjlager@aep.com; myturner@aep.com; lokelso@aep.com; camyser@aep.com | David Kidd: 918 599 2637 Glen Reed: 918 599 2664 Brad Myers: 918 599 2690
AUSTIN ENERGY | Primary & Secondary | Reza Ebrahimian | Reza.Ebrahimian@austinenergy.com; | Reza: (512) 322-6740 | Hunt, Dandy; Ron Krautz; Brion Ryan | dandy.hunt@austinenergy.com; ron.krautz@austinenergy.com; Ryan, Brion <Brion.Ryan@austinenergy.com> | Reza:512 322 6740 Dandy:512 322 6748 Ron:512 322 6835 Brion: 512-322-6879
BPUB | Primary | Ramon Sanz | rsanz@brownsville-pub.com; | Ramon: 956 983 6203 | James McCann | jmccann@brownsville-pub.com; | James: 956 983 6204
BEPC (BRAZOS ELECTRIC) | Primary & Secondary | Dwight Beckman | dbeckman@brazoselectric.com | Dwight: 254 750 6373 | David Albers | dalbers@brazoselectric.com | David: 254 750 6358
BTU | Primary & Secondary | Edward Lopez | elopez@btutilities.com | Edward: 979 821 5697 | David Hering | dhering@btutilities.com | David: 979 821 5652
CNP | Primary & Secondary | Wesley Woitt | wesley.woitt@centerpointenergy.com | Wesley Woitt: 713-207-2760 | Yingying Huang; Raja Sekhar Kakarla; Cody Mann | Yingying.Huang@centerpointenergy.com; rajasekhar.kakarla@centerpointenergy.com; cody.mann@centerpointenergy.com | Yingying Huang: 713-207-2831 Raja Sekhar Kakarla: 713-207-3614 Cody Mann: 713-207-3149
COCS | Primary | Wesley Gray | wgray@cstx.gov | Wesley: 979 764 3434 | Timothy Crabb, Stacy Engelmann | tcrabb@cstx.gov; sengelmann@cstx.gov; | Timothy Crabb 979 764 3439 Stacy Engelmann 979 764 3681
CPS | Primary & Secondary | Basileo Rocha, Sunil Dhakal | bdrocha@cpsenergy.com; SDhakal@cpsenergy.com | Basileo: 210 353 4933 Sunil: 210 353 2008 | Kenneth Bowen Trieu Vo | kbowen@cpsenergy.com; tvo@cpsenergy.com; | Kenneth: 210 353 4142 Trieu: 210 353 2127
CTT (Cross Texas Transmission) | Primary & Secondary | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310 | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310
DENTON | Primary & Secondary | Chuck Sears | Chuck.Sears@cityofdenton.com; | Chuck: 940 349 7111 | Brent Heath | brent.heath@cityofdenton.com; | Brent: 940 349 7180
GARLAND | Primary & Secondary | Danh Huynh | Dhuynh@gpltexas.org | Danh: 972 205 3826 | Grubbs, David; Juan Santos | Dgrubbs@gpltexas.org; Jsantos@gpltexas.org | David: 972 205 2664 Juan: 972-205-2603
Golden Spread EC | Primary & Secondary | Chris Koenig | ckoenig@gsec.coop | Chris: 806 349 5201 | Shane McMinn, Mark Reinart | smcminn@gsec.coop; mreinart@gsec.coop | Shane: 806 379 7766 Mark: 806 349 6562
LCRA TSC; BEC (Bandera); BBEC; CTEC; GVEC; NBU; PEC; SBEC; RGEC | Primary & Secondary | Charles DeWitt | Charles.dewitt@lcra.org | Charlie: 512-578-4199 | Cris Urena, Ken Chui | cris.urena@lcra.org; ken.chui@lcra.org | Cris: 512 578 4525, Ken: 512 578 4510
Lone Star | Primary & Secondary | Chenyan Guo | chenyan.guo@fpl.com | Chenyan: 561-304-5692 | Matt Gomes | Matthew.Gomes@LONESTAR-TRANSMISSION.COM | Matt - 512-236-3133
Oncor | Primary & Secondary | Charles Saker | charles.saker@oncor.com | Charles: 214-743-6896 | Paul Bell | paul.bell@oncor.com | Paul: 214-743-6676
Sharyland Utilities | Primary & Secondary | Brad Schwarz | bschwarz@huntpower.com | Brad: 512-289-7425 | Mark Caskey | mcaskey@sharyland.com | Mark: 214 978 8243
STEC | Primary & Secondary | Doug Evans | devans@stec.org | Doug: 361 485 6459 | Paul Person Loretta Gallaga | pperson@stec.org; lgallaga@stec.org; | Paul: 361 485 6151 Loretta: 956 377 7120
TMPA | Primary & Secondary | Ahmad Saboor | asaboor@texasmpa.org | Ahmad: 936 873 1104 | Frank Owens | fowens@texasmpa.org; | Frank: 936 873 1120
TNMP | Primary & Secondary | Robert Lona | Robert.Lona@tnmp.com | Robert: 281-581-4732 | Anthony, Hudson Ballay, Dustin Cloninger, Ross | Anthony.Hudson@tnmp.com; Dustin.Ballay@tnmp.com; Ross.Cloninger@tnmp.com; | Anthony: 281 581 4712 Dustin:281 581 4730 Ross:281 581 4733
Wind Energy Texas Transmission (WETT) | Primary | Julius Horvath | julius.horvath@windenergyoftexas.com | Julius: 512 436 9585; cell: 512 496 9186 | Christina Minchew | christina.Minchew@windenergyoftexas.com | Christina: 512-436-9469