## ImprovementCostSummary12012010
PRIVILEGED AND CONFIDENTIAL, DO NOT release outside of ERCOT Staff or Transmission Providers organization. Contains critical cost information that can affect bids for projects.
| Project Cost | [5 empty] | Circuit Miles |  |  |  |  | XFMR MVA
| Project Cost | [5 empty] | XFMR MVA
| 345 | 138 | 69 | total |  |  | 345 | 138 | 69 | total
2008 | 108438234 | 315361481 | 121906069 | 545705784 |  | 2008 | 1500 | 529 | 60 | 2089
2009 | 185095941 | 452787047 | 98206585 | 736089573 |  | 2009 | 2467 | 1462 | 0 | 3929 |  | For ROS and BOD reports
2010 | 552303440 | 363014745 | 95670910 | 1010989095 | 2292784452 | 2010 | 5957 | 758 | 0 | 6715 | 12733
2011 | 683604120 | 436924764 | 253175506 | 1373704390 |  | 2011 | 5522 | 617 | 0 | 6139 |  | ·All Projects (in engineering, routing, licensing and construction) (sum of F13, E16) |  |  |  | 9272866650
2012 | 824478536 | 348215914 | 132917025 | 1305611475 |  | 2012 | 3178 | 404 | 75 | 3657
2013 | 4562866973 | 274861894 | 29562496 | 4867291363 |  | 2013 | 8344 | 595 | 0 | 8939 |  | ·Transmission Projects Energized in 2009 (E15) |  |  |  | 857094959
2014 | 195698998 | 188378926 | 74463755 | 458541679 |  | 2014 | 1800 | 80 | 60 | 1940
2015 | 247477980 | 50022135 | 33452500 | 330952615 |  | 2015 | 600 | 0 | 0 | 600
2016+ | 568101044 | 204575246 | 10194702 | 782870992 | 9118972514 | 2016+ | 5604 | 667 | 0 | 6271 | 27546
2010COM | 467603661 | 309783138 | 79708160 | 857094959 |  | 2010COM | 5357 | 758 | 0 | 6115
2010PLAN | 84699779 | 53231607 | 15962750 | 153894136 |  | 2010PLAN | 600 | 0 | 0 | 600
2008-2016+ | 7928065266 | 2634142152 | 849549548 | 11411756966 |  | 2008-2016+ | 34972 | 5112 | 195 | 40279
2008-2010 | 845837615 | 1131163273 | 315783564 | 2292784452 |  | 2008-2010 | 9924 | 2749 | 60 | 12733
2011-2016+ | 7082227651 | 1502978879 | 533765984 | 9118972514 |  | 2011-2016+ | 25048 | 2363 | 135 | 27546
| Circuit Miles New | [5 empty] | Circuit Miles Rebuilt, Reconductored or Upgraded |  |  |  |  | TOTAL
| 345 | 138 | 69 | total |  |  | 345 | 138 | 69 | total |  | 345 | 138 | 69 | total
2008 | 21.6 | 52.2 | 0 | 73.8 |  | 2008 | 13.4 | 295.2 | 146.5 | 455.1 |  | 35 | 347.4 | 146.5 | 528.9
2009 | 107.1 | 52.8 | 1 | 160.9 |  | 2009 | 0.5 | 350.2 | 119.3 | 470 |  | 107.6 | 403 | 120.3 | 630.9
2010 | 417.7 | 76.3 | 27.5 | 521.5 | 756.2 | 2010 | 119.5 | 275.7 | 81.2 | 476.4 | 1401.5 | 537.2 | 352 | 108.7 | 997.9
2011 | 583.8 | 102.2 | 3.9 | 689.9 |  | 2011 | 24.2 | 320.1 | 374 | 718.3 |  | 608 | 422.3 | 377.9 | 1408.2
2012 | 559.8 | 100.9 | 0 | 660.7 |  | 2012 | 65 | 302.7 | 109.5 | 477.2 |  | 624.8 | 403.6 | 109.5 | 1137.9
2013 | 3681.6 | 84.1 | 0 | 3765.7 |  | 2013 | 0 | 182.8 | 35.8 | 218.6 |  | 3681.6 | 266.9 | 35.8 | 3984.3
2014 | 28.2 | 67.9 | 18.7 | 114.8 |  | 2014 | 20.7 | 107.9 | 53.6 | 182.2 |  | 48.9 | 175.8 | 72.3 | 297
2015 | 160 | 15.4 | 0 | 175.4 |  | 2015 | 16.4 | 20.4 | 56.4 | 93.2 |  | 176.4 | 35.8 | 56.4 | 268.6
2016+ | 313.3 | 33.1 | 0 | 346.4 | 5752.9 | 2016+ | 46.3 | 158.2 | 25.8 | 230.3 | 1919.8 | 359.6 | 191.3 | 25.8 | 576.7
2010COM | 348.4 | 67.7 | 27.5 | 443.6 |  | 2010COM | 93.3 | 251.5 | 52.6 | 397.4 |  | 441.7 | 319.2 | 80.1 | 841
2010PLAN | 69.3 | 8.6 | 0 | 77.9 |  | 2010PLAN | 26.2 | 24.2 | 28.6 | 79 |  | 95.5 | 32.8 | 28.6 | 156.9
2008-2016+ | 5873.1 | 584.9 | 51.1 | 6509.1 |  | 2008-2016+ | 306 | 2013.2 | 1002.1 | 3321.3 |  | 6179.1 | 2598.1 | 1053.2 | 9830.4
2008-2010 | 546.4 | 181.3 | 28.5 | 756.2 |  | 2008-2010 | 133.4 | 921.1 | 347 | 1401.5 |  | 679.8 | 1102.4 | 375.5 | 2157.7
2011-2016+ | 5326.7 | 403.6 | 22.6 | 5752.9 |  | 2011-2016+ | 172.6 | 1092.1 | 655.1 | 1919.8 |  | 5499.3 | 1495.7 | 677.7 | 7672.7

## TPITFutureNoCost12012010
DECEMBER BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS As Of 09/01/2010
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) (only in completed tab) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Requested Additional Information (Optional) | Other (Optional)
09TPIT0098 | Dilley, add 138 kV terminal | Construct 9 miles 795 ACSR 138 kV line from Palo Duro to Dilley | Schedule update | AEP GROUP 382 | AEP/TCC | Brian Johnson 918-599-2653 | 3098 | 2010-12-01 |  | 138 | 0 | 0 | 0 | 0 | FRIO | FRIO | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
09TPIT0173 | Waco West - Waco Woodway - Waco Atco 138 kV line | Rebuild existing line | Construction schedule changed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R409-WA | 2010-12-01 |  | 138 | 0 | 5.84 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 | 2008-07-07 |  |  | 3436, 3591, 3592 | Y |  | Project submitted to RPG by Luminant.
08TPIT0009 | Hutto Switch - Round Rock NE - Round Rock 138 kV line | Rebuild existing 138 kV single-circuit line from Hutto Switch to Round Rock with larger conductor and double-circuit structures and add a second circuit to structures to create a Hutto Switch - Round Rock circuit and a Hutto Switch - Gabriel (LCRA) circuit. |  | R456 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R406-WA | 2010-12-01 |  | 138 | 8.4 | 8.9 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | 3666, 3670, 3667, 3669, 3668 | Y |  | Hutto Switch - Round Rock NE section will be completed in June 2010.
11TPIT0095 | Renner SVC Phase II | Install one static var compensator (+300 Mvar/-265 Mvar) | Construction schedule changed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4058B-WA | 2010-12-01 |  | 138 | 0 | 0 | 0 | 300 | DALLAS |  | Tier 1 | 2008-10-16 |  | 2009-02-01 | 12356, 12357 | Y |  | The first phase of the project was approved on 8/19/2008, and the second phase was approved on 2/2/2009. Phase I will go into service in May 2010, and Phase II will go into service in May 2011.
10TPIT0021 | Krum West Switch - NW Carrollton 345 kV circuit (Oncor Electric Delivery section) | Add second 345 kV circuit on existing structures . |  | C017 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C037-WA | 2010-12-01 |  | 345 | 37.2 | 0 | 0 | 0 | DENTON | DALLAS | CREZ |  |  |  | 988, 1730, 2361 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0101 | Willow Creek - Parker 345 kV line | Rebuild 345 kV line for double-circuit operation. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C040-WA | 2010-12-01 |  | 345 | 22.25 | 22.25 | 0 | 0 | WISE | PARKER | CREZ |  |  |  | 1421, 1436 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. Cost covers entire Jacksboro Switch - Willow Creek - Parker 345 kV line.
12TPIT0077 | Liggett 345/138 kV Autotransformer #1 | Replace 480 MVA Autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5107-WA | 2010-12-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 | 2008-06-01 | 2008-07-01 |  | 1923, 1926 | Y | 2007-R5
10TPIT0142 | Waples Capacitor | Install 36 MVA capacitor bank at Wapels 138 kV bus |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2010-12-05 |  | 138 | 0 | 0 | 0 | 36 | HOOD |  | Tier 4 |  |  |  | 467 | Y
10TPIT0157 | Relocation of Line 138-S for Road work on FM 524 | Relocate impacted 138kV transmission line segment for Farm to Market Road 524 work |  |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE07310 | 2010-12-10 |  | 138 | 0 | 0.75 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 4 |  |  |  |  | N
10TPIT0154 | Penascal Wind Phases 2 Generation Interconnect | Penascal Wind Phases 2 and 3 Install ERCOT EPS Metering |  | AEP GROUP 489 | AEP/ETT/TCC | John Pulay 918-599-2653 | 3381 | 2010-12-13 |  | 345 | 0 | 0 | 0 | 0 | KENNEDY |  | Tier 4 |  |  |  |  | Y
10TPIT0079 | Morris Sheppard to Oran Rebuild | Rebuild Morris Sheppard to Oran with 959ACSS |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2010-12-16 |  | 69 | 0 | 18.4 | 0 | 0 | PALO PINTO | PALO PINTO | Tier 4 |  |  |  | 343785 | Y
08TPIT0042 | Seaton to Barclay Rebuild | Rebuild existing Seaton to Barclay with 1033 ACSR |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2010-12-23 |  | 69 | 0 | 10.2 | 0 | 0 | BELL | FALLS | Tier 4 |  |  |  | 69131 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0167 | MVEC Merett-MVEC Pharr | Rebuild 138kV line from Merett to MVEC Pharr Substations | Clearance approved until 12-30-10 | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org | 984505 | 2010-12-30 |  | 138 | 0 | 2.2 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8752-8762 | Y
09TPIT0077 | McCree-Shiloh 138 kV line | Line reconductor | FUNDED |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2010-12-31 |  | 138 | 0 | 2.2 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 830, 834 | Y |  | This project is a line reconductor for solving overload
10TPIT0132 | Britmore - Addicks Ckt.09 Reconductor | Upgrade 138 kV Ckt.09 Britmore - Addicks to increase thermal ratings. |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-12-31 |  | 138 | 0 | 2.03 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 44120, 45610 | Y |  | No transformer capacity to be added.
11TPIT0073 | Kirby - Garrott Ckt. 37 | Upgrade 138kV Ckt. 37 Kirby - Garrott to increase thermal ratings. |  | 11TPIT0072 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-12-31 |  | 138 | 0 | 2.32 | 0 | 0 | HARRIS | HARRIS | Tier 3 | 2009-07-01 | 2009-07-01 | N/A | 47320, 47660 | Y |  | Part of Garrott - Midtown - Polk Ckt. 90 Upgrade
10TPIT0122 | Formosa: Interconnect New Generation at Formosa Substation | Upgrade generator disturbance monitoring, metering, and communications at the Formosa 138 kV substation. Add generator monitoring, protection, and communications at the Formosa CFB Plant. |  | AEP GROUP 437 | AEP/TCC | Paul Hassink 918-599-2653 | 3333 | 2010-12-31 |  | 138 | 0 | 0 | 0 | 0 | CALHOUN | CALHOUN | Tier 4 |  |  |  |  | Y |  | Schedule based on customer requested date
11TPIT0105 | La Palma to San Benito: Rebuild 0.2 miles | Construct a new 138/69 kV Switching Station near East Harrison substation and reconductor the 69 kV line from La Palma to San Benito | Schedule Update | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 |  | 2010-12-31 |  | 138 | 0.2 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  |  | Y
10TPIT0114 | Roanoke Tap to West Denton 345kV CREZ Circuit | Add 345kV circuit to vacant position of TMPA-owned double circuit line from Roanoke Tap over West Denton | Delayed due to coordination with Oncor construction schedule for remainder of line |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T09003 | 2010-12-31 |  | 345 | 9.8 | 0 | 0 | 0 | DALLAS |  | CREZ |  |  |  | 988, 1730, 2361 | Y
11TPIT0113 | Oasis - Meadow Ckt.99 | Upgrade 345kV Ckt. 99 Oasis to Meadow to increase thermal ratings. |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-12-31 |  | 345 | 0 | 3.91 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 4 |  |  |  | 43035, 43030 | Y |  | 1) Identified by ERCOT as an Economic Project in 2009 5-Year Plan. Needed by summer peak 2011. 2) No transformer capacity to be added.
09TPIT0189 | Pearsall to Dilley 69 kV Line | Upgrade 21.8 miles of 69 kV to 795 ACSR conductor from Pearsall to Derby to Dilley. | Upgrade 69 kV line for new generation at Pearsall |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-01-01 |  | 69 | 0 | 21.8 | 0 | 0 | FRIO | FRIO | Tier 4 | 2006-02-01 | 2006-06-29 | 2006-08-01 | 5893-5842--5860 | Y
09TPIT0119 | Whitesboro SE - Gordonville 138 kV tap line | Construct 138 kV line and convert existing 69 kV line and substations to 138 kV operation. | Construction schedule changed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R546-WA | 2011-01-01 |  | 138 | 0.9 | 7.9 | 0 | 0 | GRAYSON | GRAYSON | Tier 4 |  |  |  | 1744, 1725 | Y
10TPIT0108 | Dowling Rd Substation Additions | Build new distibution substation in BTU transmission line from BTU South Switch to TAMU Substation |  |  | COCS/BTU | Tony Michalsky 979- 764-3438 tmichalsky@cstx.gov |  | 2011-01-01 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
08TPIT0085 | Palo Duro Switching Station | Construct a new Palo Duro switching substation in the 138 kV transmission line, from Pearsall to Batesville, at the point where the line changes from a north/south direction to an east/west direction, ties-in new 138 kV transmission line to AEP Dilley. | Negotiation of site is in progress. Acquiring Right-Of-Way Easements. |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-01-01 |  | 138 | 0 | 0 | 0 | 0 | FRIO |  | Tier 4 | 2006-02-01 | 2006-06-29 | 2006-08-01 | 5866 | Y
08TPIT0094 | Palo Duro to AEP Dilley SS 138 kV Line | Construct 9 miles 795 ACSR 138 kV line from Palo Duro to AEP Dilley. | Changed responsibility to STEC |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-01-01 |  | 138 | 9 | 0 | 0 | 0 | FRIO | FRIO | Tier 4 | 2006-02-01 | 2006-06-29 | 2006-08-01 | 5866-8212 | Y
09TPIT0022 | Killeen Switch - S. Harker Heights 138 kV line | Upgrade existing 138 kV line | Construction schedule changed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R410-WA | 2011-01-01 |  | 138 | 0 | 5.3 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3423, 3633 | Y
08TPIT0032 | Gilleland 345/138kV autotransformer | Install a 672 MVA 345/138kV autotransformer at the new Gilleland switching substation |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-01-01 |  | 345 | 0 | 0 | 672 | 0 | TRAVIS |  | Tier 4 |  |  |  | The 345kV bus is 7340 and the 138kV bus is 7336 | Y
10TPIT0076 | Stephenville to Granbury 138KV Conversion | Convert exisitng Stephenville to Granbury 69KV line to 138KV operation |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-01-04 |  | 138 | 0 | 0 | 0 | 0 | HOOD | ERATH | Tier 4 |  |  |  | 306, 307, 309, 306, 305, 304, 303, 299 | Y
12TPIT0055 | Hill Country to Stonegate - 138 kV 2nd Circuit | Build second 138kV transmission line from Hill Country to Stonegate on existing transmission structures |  | S-0580 | CPS | PM: Hector Torres | T-0163 | 2011-01-31 |  | 138 | 10.01 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5209 5415 | Y |  | There are no transformers associated with this project
08TPIT0020 | Zorn/Clear Springs-Gilleland Creek-Hutto Switch 345-kV line | Construct a 345 kV double circuit (bundled 959 ACSS) line between Zorn/Clear Springs and Hutto Switch and other ONCOR and AE projects. Upgrade the 7.5-mile McNeil (7334)-Gilleland(7336) 795 ACSR 138-kV transmission line to 1433 ACSS/TW. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org | Not yet assigned | 2011-02-01 |  | 345 | 165 | 7.5 | 0 | 0 | WILLIAMSON | GUADALUPE | Tier 1 | 2001-12-01 | 2001-12-01 | 2002-02-01 | 7042, 7050, 7340, 3696 | Y |  | Harris Branch substation replaced with Gilleland Creek substation as an in-line termination point for one of the
07TPIT0055 | Frisco to Kruegerville Rebuild | Rebuild existing Frisco to Kruegerville with1590 or Acss conductor |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-02-17 |  | 138 | 0 | 11.7 | 0 | 0 | COLLIN | DENTON | Tier 3 | 2009-10-13 | 2009-11-01 | N/A | 662, 1994, 681 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
10TPIT0050 | Rayburn Substation | Install (3) Breaker ring to include (2) 69 lines and (1) 69/12.5 transformer |  |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2011-02-28 |  | 69 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
09TPIT0130 | Newman 138 kV, install 24.0 MVAR Cap Bank | Install 24 MVAR capacitor bank to support local low voltage problems | FUNDED |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2011-03-01 |  | 138 | 0 | 0 | 0 | 24 | DALLAS |  | Tier 4 |  |  |  | 849 | Y |  | This project is a capacitor bank installing for supporting local load voltage problems
10TPIT0123 | Sioux 138 kV substation | Build New 138kV Sioux Substation in the Line from Doedyns-Gandy. | Acquiring Right-Of-Way Easements on Sioux-Gandy T/L | 06TPIT9999 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-03-01 |  | 138 | 0 | 0 | 0 | 0 | HIDALGO |  | Tier 4 |  |  |  | 8792 | Y
06TPIT9999 | Sioux-Gandy 138kV Line | Build New 138kV Line from Sioux-Gandy Substations | Acquiring Right-Of-Way Easements | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org | 789640 | 2011-03-01 |  | 138 | 4.5 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 2 | 2005-02-01 | 2005-04-20 |  | 8792-8755 | Y
11TPIT0135 | Navo Capacitor Bank | Install additional 75 MVAR at Navo sub |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-03-04 |  | 138 | 0 | 0 | 0 | 75 | DENTON |  | Tier 4 |  |  |  | 662 | Y
11TPIT0111 | Thompson Creek to Snook Transmission Line | Build 3.43 miles of 1033ACSR transmission line insulated for 138kV but operated at 69kV; intersect the existing Atkins-Snook transmission line and remove from that point to Atkins Sub |  |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2011-03-30 |  | 69 | 3.4 | 0 | 0 | 0 | BRAZOS | BURLESON | Tier 4 |  |  |  |  | Y
05TPIT0172 | Thompson Creek to Dansby 138, New line construction | Build a 1033 ACSR 138 kV line |  | 10TPIT0065 11TPIT0030 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com | 802 | 2011-03-30 |  | 138 | 10.2 | 0 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  | 32897, 32863 | Y
10TPIT0065 | Dansby Substation | Install (1) Breaker in existing ring bus for a 138 lines to Thompson Creek Substation |  | 05TPIT0172 11TIPIT0030 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2011-03-30 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32897 | Y
11TPIT0030 | Thompson Creek Substation | Install (3) Breaker ring to include (1) 138 lines, (1) 14MVA 138/69 auto transformer, and (1) 138/12.5 transformer |  | 05TPIT0172 10TIPIT0065 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2011-03-30 |  | 138 | 0 | 0 | 14 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
11TPIT0126 | Cactus tap located on the Ft. Lancaster to West Yates 69 kV line | SouthWest Texas Electric Co-Op distribution station |  | AEP Group 491 | AEP/TNC | Joe Gilbert 918-599-2653 | 2429 | 2011-03-31 |  | 69 | 0 | 0 | 0 | 0 | CROCKETT | CROCKETT | Tier 4 |  |  |  |  | Y
11TPIT0141 | Ft. Lancaster to Illinois #4, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | NEW | AEP GROUP 474 | AEP/TNC/ETT | Larry Roberson 918-599-2653 | 2437 | 2011-03-31 |  | 69 | 0 | 17.21 | 0 | 0 | PECOS | CROCKETT | CREZ Modified |  |  |  |  | Y
08TPIT0162 | Convert Alta Loma 69/138kV dual voltage substation to a 138kV substation. | Convert Alta Loma 69/138kV dual voltage double tap configuration substation to a 138kVsectionalizing substation looped into Ckt.93 PH Robinson to Hitchcock. | Change in project schedule |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-03-31 |  | 138 | 0 | 0.1 | 0 | 0 | GALVESTON |  | Tier 4 |  |  |  | 42061, 42062 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0103 | Alamito Creek, add 2nd 138/69 kV auto | Add 2nd 138/69 kV autotransformer at Alamito Creek, and install a NaS Battery at Gonzales |  | AEP GROUP 358 | AEP/TNC | Jim Eriksen 918-599-2653 | 1178 | 2011-03-31 |  | 138 | 0 | 0 | 50 | 0 | PRESIDIO |  | Tier 1 | 2008-03-21 | 2008-06-10 | 2008-07-15 |  | Y
11TPIT0117 | Leakey | Remove a 15.6 MVAR Capacitor bank from the Bandera substation (7439) and add a 15.6 MVAR capacitor bank at the Leakey substation (7426) |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-04-01 |  | 69 | 0 | 0 | 0 | 0 | BANDERA | REAL | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
10TPIT0012 | Barclay to Silver City Rebuild | Rebuild existing Barclay to Silver City 69kv line |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-04-01 |  | 69 | 0 | 17 | 0 | 0 | FALLS | MILAM | Tier 4 |  |  |  | 69,65 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT7777 | MVEC Pharr-Alberta Switch | Rebuild 138kV line from Pharr to Alberta Switch Substations | Delay of Start of Construction | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-04-01 |  | 138 | 0 | 1.2 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8759-8762 | Y
05TPIT0040 | Fairview to Aledo | Construct 138kv 795 line from Fairview to Aledo, rebuild Waples to Fairview radial |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-04-26 |  | 138 | 32 | 5.8 | 0 | 0 | HOOD | PARKER | Tier 2 |  | 2002-09-01 | 2003-01-01 | 467, 470, 527, 526 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
11TPIT0118 | Cheapside - New Substation | Construct a new 138-13.09KV, 20 MVA x two, redundant backup substation |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2011-04-30 |  | 138 | 0 | 0 | 0 | 0 | GONZALES |  | Tier 4 |  |  |  | See Project Title | Y
11TPIT0119 | Texas Substation Conversion | Convert Texas substation from 69kV to 138kV service. | Change in project schedule |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-04-30 |  | 138 | 0.76 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 41550, 41540 | Y |  | No transformer capacity to be added.
09TPIT0101 | Oleander, Construct 138/69 kV Substation | Construct a new 138/69 kV Switching Station near East Harrison substation and reconductor the 69 kV line from La Palma to San Benito | Schedule Update | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 3101 | 2011-04-30 |  | 138 | 0 | 0 | 93 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  |  | Y
09TPIT0176 | Bertram-Andice | Close the normally open Bertram (7520)-Andice(7521) 69 kV transmission line. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-05-01 |  | 69 | 0 | 0 | 0 | 0 | BURNET | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
09TPIT0116 | Gatesville Tap - Gatesville TDC 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R497-WA | 2011-05-01 |  | 69 | 0 | 4.4 | 0 | 0 | MCLENNAN | CORYELL | Tier 4 |  |  |  | 3587, 3583 | Y
11TPIT0089 | Cottonwood Road 69 kV Switch | Construct new switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R588-E | 2011-05-01 |  | 69 | 0 | 0 | 0 | 0 | ARCHER |  | Tier 4 |  |  |  | 1605 | Y
11TPIT0153 | Colorado City 69 kV terminal equipment | Upgrade terminal equipment on line to Morgan Creek |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8026-E, R8026B-E, R8026C-E & R8026D-E | 2011-05-01 |  | 69 | 0 | 0 | 0 | 0 | MITCHELL | MITCHELL | Tier 4 |  |  |  | 1378, 1033 | Y
06TPIT0112 | Lakeway second circuit from LCRA tap to the substation. | Construct 0.88 mile long 138kV circuit from Lakeway substation to the LCRA tap between Marshall Ford and Bee Creek substation. |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3230_117_4255 | 2011-05-01 |  | 138 | 0.88 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 7349, 9235 | Y
10TPIT0148 | Willacy Tap Switch- 138kV | Install 138kV Single Switch in AEP Raymondville #2 to AEP North Rio Hondo Line which will be normally open. | Project on Hold due to AEP Raymondville #2 Breaker/Bus additions |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-05-01 |  | 138 | 0 | 0 | 0 | 0 | WILLACY | WILLACY | Tier 4 |  |  |  |  | N
11TPIT0148 | Ayers 138 kV terminal equipment | Upgrade terminal equipment on line from Handley to Hemphill |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5169-E | 2011-05-01 |  | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1950, 2167, 2164 | Y
11TPIT0149 | Hemphill 138 kV terminal equipment | Upgrade terminal equipment on line to Randol Mill |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5167-E, M5167B-E & M5167C-E | 2011-05-01 |  | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2164, 2105 | Y
11TPIT0150 | Hemphill 138 kV terminal equipment | Upgrade terminal equipment on line to Ayers |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5167D-E & M5167E-E | 2011-05-01 |  | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2164, 2167 | Y
11TPIT0151 | Mesquite 138 kV terminal equipment | Upgrade terminal equipment on the E Mesquite - Mesquite - Seagoville Switch line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4046-E | 2011-05-01 |  | 138 | 0 | 0 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2771, 2775, 2776 | Y
11TPIT0152 | Randol Mill 138 kV terminal equipment | Upgrade terminal equipment on Hemphill - Randol Mill - Handley/Saginaw line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5168-E, M5168B-E, M5168C-E & M5168D-E | 2011-05-01 |  | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2164, 2105, 2103, 2104, 2106 | Y
11TPIT0053 | Gresham Road 138 kV Switching Station | Construction switching station to connect a new power plant |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6000-WA | 2011-05-01 |  | 138 | 0 | 0 | 0 | 0 | NACOGDOCHES |  | Tier 4 |  |  |  | 3301 | Y
11TPIT0080 | Killeen Switch - Killeen South - Killeen Fort Hood West Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R741-E | 2011-05-01 |  | 138 | 0 | 7 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3423, 3428 | Y | 2009-R32
11TPIT0090 | Benbrook Switch capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5158-WA | 2011-05-01 |  | 138 | 0 | 0 | 0 | 220.8 | TARRANT |  | Tier 4 |  |  |  | 1874, 1875 | Y
11TPIT0091 | Elkton Switch capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6003-WA | 2011-05-01 |  | 138 | 0 | 0 | 0 | 110.4 | SMITH |  | Tier 4 |  |  |  | 3106 | Y
11TPIT0092 | Handley SES capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5159-WA | 2011-05-01 |  | 138 | 0 | 0 | 0 | 110.4 | TARRANT |  | Tier 4 |  |  |  | 1951 | Y
11TPIT0093 | Saginaw Switch capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5160-E | 2011-05-01 |  | 138 | 0 | 0 | 0 | 55.2 | TARRANT |  | Tier 4 |  |  |  | 1957 | Y
11TPIT0094 | Venus Switch capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3096-E | 2011-05-01 |  | 138 | 0 | 0 | 0 | 110.4 | ELLIS |  | Tier 4 |  |  |  | 1908 | Y
12TPIT0066 | Laguna Vista 138 kV tap lines | Construct 138 kV tap lines to convert Laguna Vista Substation to 138 kV service. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R587-E | 2011-05-01 |  | 138 | 10.4 | 10.4 | 0 | 0 | PARKER | PARKER | Tier 4 |  |  |  | 528, 1590, 529 | Y
08TPIT0068 | Collin - Frisco (Brazos) 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M596-WA | 2011-05-01 |  | 138 | 0 | 1.7 | 0 | 0 | COLLIN | DENTON | Tier 4 |  |  | 2010-06-15 | 2370, 681 | Y | 2009-R14
07TPIT0018 | Lewisville Switch (Brazos) - Highland (TNMP) 138 kV line (Oncor portion) | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5067-E | 2011-05-01 |  | 138 | 0 | 1.6 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | 2010-06-15 | 645, 1970 | Y
11TPIT0120 | Pegasus 138 kV Tap and Point of Interconnection | Convert the tap line to Pegasus and South Pegasus substations to 138 kV and connect to the Odesaa - Crane 138 kV line (Oncor portion) |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8010-WA | 2011-05-01 |  | 138 | 0 | 11.4 | 0 | 0 | ECTOR | MIDLAND | Tier 4 |  |  |  | 1235, 1234 | Y | 2009-R2
11TPIT0122 | Cedar Hill Switch 138 kV terminal equipment | Upgrade 138 kV terminal equipment used to connect the 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4083B-E | 2011-05-01 |  | 138 | 0 | 0 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 2421, 2422 | Y
10TPIT0115 | Gibbons Creek Substation Upgrade Project | Install new control houses for both 138kV and 345kV systems. Upgrade all relays and SCADA devices and install new cabling for yard equipment. Install high-side load-break switches for autotransformers 1 and 2. | Revised due to coordination with generation plant outage schedule |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T09002 | 2011-05-01 |  | 345 | 0 | 0 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  |  | N
11TPIT0146 | Big Brown 345 kV terminal equipment | Upgrade terminal equipment on line to Venus |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R752-E | 2011-05-01 |  | 345 | 0 | 0 | 0 | 0 | FREESTONE | FREESTONE | Tier 4 |  |  |  | 3380, 1906 | Y
11TPIT0147 | Venus 345 kV terminal equipment | Upgrade terminal equipment on line to Big Brown |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3103-E & M3103B-E | 2011-05-01 |  | 345 | 0 | 0 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 3380, 1906 | Y
11TPIT0121 | Parker - Comanche Peak - Everman 345 kV line | Connect Parker - Everman 345 kV line into Comanche Peak |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2011-05-01 |  | 345 | 0 | 0 | 0 | 0 | SOMERVELL |  | Tier 2 | 2009-07-01 | 2010-03-31 |  | 1900 | Y
11TPIT0127 | Graham 345/138 kV autotransformer | Replace existing autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R904A-WA | 2011-05-01 |  | 345 | 0 | 0 | 450 | 0 | YOUNG |  | Tier 4 |  |  |  | 1596, 1430 | Y
11TPIT0021 | Nassau Bay to Nassau Bay Sw. Rebuild | Rebuild existing 138 kV 4/0 line from Nassau Bay to Nassau Bay Sw. with 1033 double-circuit construction |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-05-03 |  | 69 | 0 | 1.21 | 0 | 0 | HOOD | HOOD | Tier 4 |  |  |  | 364373451455 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
11TPIT0102 | Waples to Hoold Conversion | Convert existing Waples to Hood line to 138 kV operation |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-05-03 |  | 138 | 0 | 7.25 | 0 | 0 | HOOD | HOOD | Tier 4 |  |  |  | 466, 373, 455, 451, 364 | Y
07TPIT0026 | Booneville to Hearne Southwest Rebuild | Rebuild existing Booneville - Hearne Southwest with 795 | row issues |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-05-05 |  | 69 | 0 | 22.2 | 0 | 0 | ROBERTSON | BRAZOS | Tier 4 |  |  |  | 38, 32870 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
11TPIT0132 | Olney 2nd Auto | Add 60 MVA, 138/69 kV auto |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-05-09 |  | 138 | 0 | 0 | 60 | 0 | YOUNG |  | Tier 4 |  |  |  | 787, 788 | Y
10TPIT0039 | East Bell County - TNP One 345 kV Line Project | Expansion of 345 kV Switchyard at TNP One associated with East Bell County TNP One 345 kV Line Project |  | 10TPIT0037 | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2011-05-11 |  | 345 | 0 | 0 | 0 | 0 | ROBERTSON | ROBERTSON | Tier 4 | 2006-11-30 | 2007-01-02 |  | 39950 | Y | See Oncor Electric Delivery Entry for this project, 10TPIT0037
11TPIT0116 | FM 237 Yorktown - New Substation | Construct a new 69-13.09x26.18-KV, 7.0 MVA substation |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2011-05-15 |  | 69 | 0 | 0 | 0 | 0 | DEWITT |  | Tier 4 |  |  |  | See Project Title | Y
11TPIT0131 | Hearne Auto | Replace 60 MVA, 138/69 kV auto with 100 MVA auto |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-05-23 |  | 138 | 0 | 0 | 100 | 0 | ROBERTSON |  | Tier 4 |  |  |  | 35, 36 | Y
10TPIT0073 | Buda-Rutherford | Replace under-rated limiting line terminal equipment at Buda to increase Buda (7498)-Rutherford (7509) to the conductor's rating. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-05-30 |  | 138 | 0 | 0 | 0 | 0 | HAYS |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
09TPIT0060 | Buda-Turnersville | Replace under-rated limiting line terminal equipment at Buda to increase Buda (7498)-Turnersville (7500) to the conductor's rating. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-05-30 |  | 138 | 0 | 0 | 0 | 0 | HAYS | HAYS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
10TPIT0126 | Galveston Area 138kV Circuit Upgrades Phase One | Reconductor a portion of 138 kV Ckt. 93 PH Robinson - Alta Loma to increase thermal ratings. | Change in project schedule |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 |  | 138 | 0 | 5.34 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 42015, 42061 | Y |  | No transformer capacity to be added. Project is part of the 2009 ERCOT 5-Year Plan.
11TPIT0074 | Galveston Area 138kV Circuit Upgrades Phase Two | Upgrade 138 kV Ckt. 63 Webster to Stewart to increase thermal ratings. Upgrade 138kV Ckt. 93 Alta Loma to Hitchcock to West Galveston to increase thermal ratings. Upgrade 138 kV Ckt. 01 Webster to Tiki Island to Galveston to increase thermal ratings. |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 |  | 138 | 0 | 62.05 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 43500, 43507, 42861, 42061, 42800, 42862, 43355 | Y |  | No transformer capacity to be added. Project is part of the 2009 ERCOT 5-Year Plan. Construction included in cancelled project 11TPIT0071 is now included in 11TPIT0074.
11TPIT0112 | Hockley - Peters Ckt.58 | Convert Hockley to Peters Ckt. 58 from 69kV to 138kV |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 |  | 138 | 0 | 28.5 | 0 | 0 | HARRIS | AUSTIN | Tier 4 |  |  |  | 45890, 46250, 46230 | Y |  | No transformer capacity to be added. After completion of conversion to 138kV, Ckt. 58 will become Ckt. 65.
11TPIT0124 | Construct Service to Crystal Bay 138kV Substation | Serve substation by looping into Ckt.84 Borden to Dowlap. |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 |  | 138 | 0.2 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 40290 | Y |  | No transformer capacity to be added.
10TPIT0069 | Thomaston: Install 138 kV PST, Add 3-28.8 MVAR Cap Banks, Reterminate 138 kV Line | Upgrade Thomaston substation to 3 breaker ring bus, install 180/200 MVA PST on Thomaston to LCRA Cuero 138 kV line. |  | AEP GROUP 402 | AEP/ETT/TCC | Dave Goetz 918-599-2653 | 2294 | 2011-05-31 |  | 138 | 0 | 0 | 150 | 86.4 | DEWITT |  | Tier 4 |  |  |  |  | Y
11TPIT0087 | Putnam, Recofigure Station | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line |  | AEP GROUP 466 | AEP/TNC | Dave Goetz 918-599-2653 | 2400 | 2011-05-31 |  | 138 | 0 | 0 | 0 | 0 | CALLAHAN | CALLAHAN | CREZ Modified |  |  |  |  | Y
10TPIT0047 | Zenith 345kV Switching Station | Build a new 345 kV Zenith substation. Loop Ckt.99 Singleton - Obrien, Ckt.98 Singleton - T.H. Wharton, Ckt 98 T.H. Wharton - Obrien into the new substation. |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 |  | 345 | 1 | 0 | 0 | 0 | HARRIS |  | Tier 3 | 2007-04-28 | 2007-07-16 | 2007-08-21 | 44900 | Y |  | Added to Houston Area Constraint Mitigation Project, Phase II per discussion with ERCOT.
11TPIT0051 | Riley, Build 345 kV switch station, cutting in the existing Oklaunion to Bowman 345 kV line | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 |  | AEP GROUP 467 | AEP/ETT | Tommy Vannoy 918-599-2653 | 2350 | 2011-05-31 |  | 345 | 0 | 0 | 0 | 0 | WILBARGER | WILBARGER | CREZ Modified |  |  |  |  | Y
11TPIT0035 | McCree 69 kV, install 18.0 MVAR Cap Bank | Install 18 MVAR capacitor bank to support local low voltage problems | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2011-06-01 |  | 69 | 0 | 0 | 0 | 18 | DALLAS |  | Tier 4 |  |  |  | 832 | Y |  | This project is a capacitor bank installing for supporting local load voltage problems
10TPIT0080 | Olney to South Bend Switch Rebuild | Rebuild Olney to South Bend Switch with 959ACSS |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-06-01 |  | 69 | 0 | 24 | 0 | 0 | YOUNG | YOUNG | Tier 4 |  |  |  | 788, 795 | Y
10TPIT0095 | VH Braunig - Grandview 138kV Line Reroute | Reroute VH Braunig - Grandview to become VH Braunig - Coliseum Rd | Delayed due to Rail Road permit | S-0554 | CPS | PM: Ulrich Skerhut | T-0130 | 2011-06-01 |  | 138 | 2.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5030 5095 5175 | Y |  | There are no transformers associated with this project
11TPIT0075 | Kirby to Tuttle - 138 kV Circuit | Construct a 138 kV circuit between Kirby and Tuttle using existing ROW and install new substation terminal equipment | Delayed due to Rail Road permit |  | CPS | PM: Bruce Raney | T-0206 | 2011-06-01 |  | 138 | 6.475 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5250 5435 | Y |  | There are no transformers associated with this project
10TPIT0044 | Marbach substation removal - Reconfigure 138kV lines at Marbach and Cagnon | Reroute the 138kV lines at Marbach and Cagnon. Due to removal of the Marbach substation. |  | S-0401 | CPS | T: Aaron Finley PM:Hector Torres | T-0129 | 2011-06-01 |  | 138 | 0.3 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5295 | Y |  | There are no transformers associated with this project
11TPIT0039 | Dresden to LA Heights - 138kV line upgrade | Upgrade the existing Dresden to LA Heights 138kV transmission line |  | S-0308 | CPS | PM: Bruce Raney | T-0156 | 2011-06-01 |  | 138 | 0 | 3.29 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5130 5285 5286 | Y |  | There are no transformers associated with this project
09TPIT0054 | LA Heights - 138kV Breaker Installations | Install line breakers between LA Heights bus A & B. | Delayed due to Budget Constraints | T-0156 | CPS | PM: Bruce Raney | S-0308 | 2011-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5285 5286 | Y |  | This is a line terminal addition, there are no additional tranformer capacity or transmission circuit miles associated with this project
05TPIT0068 | Marshall Ford-Buttercup | Upgrade the 9.8-mile Marshall Ford(7356)-Buttercup(7531) 795 ACSR (220-MVA) 138-kV transmission line to bundled 795 ACSR (440MVA). |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-06-01 |  | 138 | 0 | 9.8 | 0 | 0 | TRAVIS | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
09TPIT0214 | Alberta Switch 138kV Substation | Build new 138kV Switching Station |  | 07TPIT7777 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-06-01 |  | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8759 | Y
11TPIT0088 | La Quinta: Configure station to 3 breaker ring bus | Construct new 138kV La Quinta Substation to directly interconnect 150MW Cedro Hill Wind Farm | Schedule update | AEP GROUP 398 | AEP/ETT | Tommy Vannoy 918-599-2653 | 3351 | 2011-06-01 |  | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB | Tier 4 |  |  |  |  | Y
11TPIT0145 | Goldsmith 138 kV Tap Line | Rebuild existing 69 kV line as a double-circuit line with a 138 kV circuit and a 69 kV circuit and convert Goldsmith Substation to 138 kV. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8021-E | 2011-06-01 |  | 138 | 3.3 | 3.3 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 11256, 11250, 1141, 1145 | Y
11TPIT0054 | Abilene South - Leon 138 kV line (Oncor Electric Delivery's section) | Rebuild existing 69 kV line for 138 kV operation. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C042-E | 2011-06-01 |  | 138 | 0 | 8.4 | 0 | 0 | EASTLAND | EASTLAND | CREZ |  |  |  | 1624 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0128 | Leon Switch | Install 138 kV breaker. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C042-E | 2011-06-01 |  | 138 | 0 | 0 | 0 | 0 | EASTLAND |  | CREZ |  |  |  | 1624 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0067 | Tonkawa Switch | Expand existing switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C859-E | 2011-06-01 |  | 345 | 0 | 0 | 0 | -100 | MITCHELL |  | CREZ |  |  |  | 11048 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0068 | Tonkawa - Sweetwater East 345 kV line | Construct double-circuit 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1007-E | 2011-06-01 |  | 345 | 63.4 | 0 | 0 | 0 | MITCHELL | NOLAN | CREZ |  |  |  | 11048, 11420 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0069 | Sweetwater East Switch | Construct 345 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C858-E | 2011-06-01 |  | 345 | 0 | 0 | 0 | -100 | NOLAN |  | CREZ |  |  |  | 11420 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0040 | Scurry County South Switch (Central A) | Construct 345 kV switching station with 345/138 kV autotransformers and shunt reactor |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1004-E | 2011-06-01 |  | 345 | 0 | 0 | 1200 | -100 | SCURRY |  | CREZ |  |  |  | 11318 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0041 | Dermott Switch (Central B) | Construct 345 kV switching station with 345/138 kV autotransformers and shunt reactor |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1003-E | 2011-06-01 |  | 345 | 0 | 0 | 1200 | -150 | SCURRY |  | CREZ |  |  |  | 11305 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0137 | Hilltop Lakes Auto | Replace 40 MVA, 138/69 kV auto with 60 MVA auto |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-06-03 |  | 138 | 0 | 0 | 60 | 0 | MADISON |  | Tier 4 |  |  |  | 47, 48 | Y
11TPIT0125 | Teasley Substation - Add 28 MVA Transformer | Install an additional 138kV circuit breaker and a new 28 MVA tranformer in the existing Teasley Substation to accommodate additional load growth | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602766 | 2011-06-11 |  | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 918 | Y
10TPIT0078 | Granbury to Glen Rose Rebuild | Rebuild Granbury to Geln Rose with 959ACSS |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-06-27 |  | 69 | 0 | 14.2 | 0 | 0 | HOOD | SOMERVELL | Tier 4 |  |  |  | 315307 | Y
08TPIT0080 | Abilene South to Steamboat, Rebuild portions of 69 kV line | Re-Build Portions of the Ballinger to Abilene South 69 kV line | Schedule Update, Circuit Miles Update | AEP GROUP 354 | AEP/ETT | Teresa Trotman 918-599-2653 | 2455 | 2011-06-30 |  | 69 | 0 | 11.4 | 0 | 0 | TAYLOR | TAYLOR | Tier 1 | 2008-06-20 | 2009-03-19 | 2009-08-06 |  | Y
11TPIT0044 | Highway 9 to Valero East 69 kV transmission line upgrades | Upgrade the Upriver to Highway 9 69 kV Loop and add transformation to remove contingency overloads during off-peak maintenance | Schedule Update | AEP GROUP 399 | AEP/ETT/TCC | Michael Glueck 918-599-2653 |  | 2011-06-30 |  | 69 | 0 | 3.96 | 0 | 0 | NUECES | NUECES | Tier 1 | 2009-03-18 | 2009-10-09 | 2009-12-01 |  | Y
11TPIT0005 | Talley Rd - New 138kV Substation | Loop new 138kV substation into future 138kV Medina Lake to CPS line (06TPIT0080) |  | T-0160 | CPS | PM: Ulrich Skerhut | S-0383 | 2011-06-30 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5422 | Y |  | There are no transformers associated with this project
11TPIT0139 | Construct Service to DUNCAN 138kV Substation | Serve DUNCAN substation by looping into Ckt.86 BENDER - BARHIL. |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-06-30 |  | 138 | 0.3 | 0 | 0 | 0 | CHAMBERS | CHAMBERS | Tier 4 |  |  |  | 40360 | Y |  | No autotransformer capacity to be added.
10TPIT0087 | Putnam to Leon, Convert 69 kV line to 138 kV | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line |  | AEP GROUP 466 | AEP/ETT/ONCOR | Larry Roberson 918-599-2653 | 2347 | 2011-06-30 |  | 138 | 0 | 17.38 | 0 | 0 | NUECES | EASTLAND | CREZ Modified | 2008-06-20 | 2009-03-19 | 2009-08-06 |  | Y
11TPIT0056 | Cisco, Convert station to 138 kV | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line |  | AEP GROUP 466 | AEP/TNC | Dave Goetz 918-599-2653 | 2341 | 2011-06-30 |  | 138 | 0 | 0 | 0 | 0 | EASTLAND | EASTLAND | CREZ Modified |  |  |  |  | Y
10TPIT0141 | Olney to Rice | Rebuild existin Olney to Rice 138 kV line |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-07-05 |  | 138 | 0 | 17.1 | 0 | 0 | YOUNG | YOUNG | Tier 4 |  |  |  | 787, 1477 | Y | 2009-R10
10TPIT0011 | Olney to Lake Kemp Switch Rebuild | Rebuild exisitng Olney to Lake Kemp Switch 69kv line |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-07-08 |  | 69 | 0 | 29 | 0 | 0 | YOUNG | BAYLOR | Tier 3 |  |  |  | 788781784782 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
11TPIT0133 | Bowie to Montague Rebuild | Rebuild Bowie to Montague 69kV line with 959 ACSS |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-08-12 |  | 69 | 0 | 11 | 0 | 0 | MONTAGUE | MONTAGUE | Tier 4 |  |  |  | 621, 632, 633 | Y
11TPIT0142 | Illinois #4 to Comstock, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | NEW | AEP GROUP 474 | AEP/TNC/TCC/ETT | Larry Roberson 918-599-2653 | 2438 | 2011-08-31 |  | 69 | 0 | 63.6 | 0 | 0 | CROCKETT | VALVERDE | CREZ Modified |  |  |  |  | Y
11TPIT0072 | Garrott - Midtown - Polk Ckt. 90 | Upgrade 138 kV underground Ckt. 90 Garrott to Midtown to Polk by building additional underground cable parallel to existing cable. |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-08-31 |  | 138 | 0 | 2.36 | 0 | 0 | HARRIS | HARRIS | Tier 3 | 2009-07-01 | 2009-07-01 | N/A | 47660, 47705, 47730 | Y |  | No transformer capacity to be added.
09TPIT0105 | Rattlesnake Road Switch - Lake Creek 345 kV line | Upgrade existing 345 kV line |  | R499 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R499A-E | 2011-09-01 |  | 345 | 0 | 1.5 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3399, 3409 | Y
11TPIT0143 | Comstock to Rough Canyon, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | NEW | AEP GROUP 474 | AEP/TCC/ETT | Larry Roberson 918-599-2653 | 2439 | 2011-09-30 |  | 69 | 0 | 21.6 | 0 | 0 | VALVERDE | VALVERDE | CREZ Modified |  |  |  |  | Y
12TPIT0035 | Riley, Expand 345 kV switch station for the additon of the new Bowman to Riley 345 kV double circuit | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 |  | AEP GROUP 467 | AEP/ETT | Tommy Vannoy 918-599-2653 | 2434 | 2011-09-30 |  | 345 | 0 | 0 | 0 | 0 | WILBARGER | WILBARGER | CREZ Modified |  |  |  |  | Y
11TPIT0154 | Montell: Construct 69 kV Substation Including Motor Operated Switches with Interrupters | Add new 69 kV Montell Substation for STEC distribution interconnection |  | AEP GROUP 498 | AEP/TCC | Rue Galyean 918-599-2653 | 3419 | 2011-10-01 |  | 69 | 0 | 0 | 0 | 0.0 | UVALDE |  | Tier 4 |  |  |  | 8230 | N
10TPIT0026 | Mueller 138kV substation | Establish a new 138kV Mueller substation with one 30MVA transformer and two underground feeders. The substation will cut into existing Ckt 938 (Kingsbery to Wheless Lane). |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3230_117_2793 3240_117_4793 3230_117_4229 | 2011-10-01 |  | 138 | 1 | 0 | 60 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9342 | Y
10TPIT0082 | Carlton Switch to Mountary Rebuild | Rebuild Carlton Switch to Mountary with 959ACSS |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-10-04 |  | 69 | 0 | 9.6 | 0 | 0 | ERATH | COMANCHE | Tier 4 |  |  |  | 297, 294 | Y
08TPIT0097 | Rhome to Roanoke Rebuild | Rebuild existing Rhome to Roanoke |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-10-14 |  | 138 | 0 | 16.6 | 0 | 0 | WISE | DENTON | Tier 4 |  |  |  | 602-640, 1866-8152 | Y |  | 602-640 completed 5/3/2011 1852-1866 completed 10/14/2011
11TPIT0134 | Dye Mound Capacitor Bank | Install 25 MVAR at Dye Mound sub |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-10-21 |  | 138 | 0 | 0 | 0 | 25 | MONTAGUE |  | Tier 4 |  |  |  | 741 | Y
11TPIT0106 | Pelican 138 kV: Build 4 Breaker GIS ring Bus | Pelican 138 kV Switching Station for ultimate interconnect of Papalote Creek and Cotton Windfarms |  | AEP GROUP 397 | AEP/ETT/TCC | Tommy Vannoy 918-599-2653 |  | 2011-10-31 |  | 138 | 0 | 0 | 0 | 0 | SAN PATRICIO |  | Tier 4 |  |  |  |  | Y
12TPIT0032 | Fort Mason to Pitsburg | Rebuild and convert the capacity of the existing transmission line (approximately 31 miles) between the LCRA TSC Fort Mason (76390) and Pitsburg (7120) stations. The new transmission line will consist of 1x795 ACSR Drake conductor to provide a thermal rating of 220 MVA. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-11-01 |  | 138 | 0 | 31 | 0 | 0 | MASON | LLANO | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y
11TPIT0130 | Webberville Solar Project | A new 30MW solar plant operated at 138kV level and tapped into an existing Austrop to Decker Ckt 921. | New Project |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P311 | 2011-11-01 |  | 138 | 0.91 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9030, 9185, 9289 | N |  | Will add idev files in this TPIT updates to reflect the new project.
11TPIT0085 | Doedyns-Sioux 138kV Line | Build New 138kV Line from Doedyns-Sioux Substations | Delays due to property condemnations | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org | 789640 | 2011-11-01 |  | 138 | 5.5 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 2 | 2005-02-01 | 2005-04-20 |  | 8753-8792 | Y
11TPIT0115 | Reagor Springs to Purdon Rebuild | Rebuild existing Reagor Springs to Purdon 69 kV line to serve new load at Emmett. |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-11-04 |  | 69 | 0 | 28.55 | 0 | 0 | ELLIS | NAVARRO | Tier 4 |  |  |  | 204, 210, 193, 194, 198 | Y |  | Load-serving project, necessitated by a large load addition at Emmett.
11TPIT0101 | Reno to Rhome Rebuild | Rebuld existing Reno to Rhome 138 kV Line |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-11-28 |  | 138 | 0 | 13.85 | 0 | 0 | PARKER | WISE | Tier 4 |  |  |  | 541, 572, 576 | Y
11TPIT0129 | Pilot Grove - New Substation | Construct a new 138-13.09KV, 60 MVA x two, redundant backup substation, 31 MVAR Cap Bank |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2011-11-30 |  | 138 | 0 | 0 | 0 | 0 | LAVACA |  | Tier 4 |  |  |  | See Project Title | Y
11TPIT0138 | Deer Park Area Reconfigurations | Reconfigure Ckt. 84 SOUTH - WABURN and Ckt. 96 CONIAL - Morgan's Point to create new Ckt. 84 SOUTH - Morgan's Point and Ckt. 84 WABURN - CONIAL. |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-11-30 |  | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 43250, 41670, 40370, 41100, 40442, 40443, 42241 | Y |  | No autotransformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
11TPIT0086 | Bruni 138kV Station: Install breaker | Construct new 138kV La Quinta Substation to directly interconnect 150MW Cedro Hill Wind Farm |  | AEP GROUP 398 | AEP/TCC | Tommy Vannoy 918-599-2653 | 3354 | 2011-11-30 |  | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB | Tier 4 |  |  |  |  | Y
11TPIT0060 | Lamesa - Ackerly Vealmoor 69 kV line | Rebuild existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8005-E | 2011-12-01 |  | 69 | 0 | 21.5 | 0 | 0 | DAWSON | HOWARD | Tier 4 |  |  | 2009-07-21 | 1164, 1364, 1362, 1363, 1356 | Y | 2009-R3 | ERCOT BOD approved this project as part of the RMR exit strategy for Permian Basin generation. Ackerly Vealmoor - Sparenburg section will be completed in 6/2011, and Sparenburg - Lamesa section will be completed in 12/2011.
10TPIT0024 | Stoney Ridge 138kV substation (original title is Linda Vista substation) | Establish new 138kV Stoney Ridge substation and install (2) 30MVA transformers. The substation will cut into Ckt 962 (Garfield to Onion Creek). |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3230_117_2894 3230_117_4894 | 2011-12-01 |  | 138 | 0.1 | 0 | 30 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9237 | Y
10TPIT0090 | Copperas Cove - Killeen Clark Road Tap - Killeen Fort Hood West 138 kV line upgrade | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R717-E | 2011-12-01 |  | 138 | 0 | 7.6 | 0 | 0 | CORYELL | BELL | Tier 4 |  |  |  | 3630, 3620, 3629 | Y
11TPIT0100 | Moss Switch | Install 138 kV circuit breakers |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C005-E | 2011-12-01 |  | 138 | 0 | 0 | 0 | 0 | ECTOR |  | CREZ |  |  |  | 1019 | Y |  | Proposed in-service date is an estimate since the in-service date will not be set until after the Certificate of Convenience and Necessity ("CCN") has been granted by the PUCT. Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0070 | Dermott Switch (Central B) - Scurry County South Switch (Central A) 345 kV line | Construct double-circuit 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1009-E | 2011-12-01 |  | 345 | 65.4 | 0 | 0 | 0 | SCURRY | SCURRY | CREZ |  |  |  | 11305, 11318 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0042 | Scurry County South Switch (Central A) - Tonkawa 345 kV line | Construct double-circuit 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1008-E | 2011-12-01 |  | 345 | 30.4 | 0 | 0 | 0 | SCURRY | MITCHELL | CREZ |  |  |  | 11318, 11048 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0037 | Bell County East - TNP One 345 kV line and Bell County East Switching Station (Oncor Electric Delivery part of project) | Install 345 kV switching station and construct a double-circuit 345 kV line |  | R704A, R705 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R494-E | 2011-12-01 |  | 345 | 82.6 | 0 | 0 | 0 | ROBERTSON | BELL | Tier 1 | 2006-11-30 |  | 2007-07-01 | 39950, 3687 | Y |  | Bell County East Switching Station will be completed in 6/2011.
10TPIT0103 | Bowman Switch terminal equipment | Replace terminal equipment on line to Fisher Road. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C032-WA | 2011-12-01 |  | 345 | 0 | 0 | 0 | 0 | ARCHER |  | CREZ |  |  |  | 1422, 1425 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0104 | Bowman Switch terminal equipment | Replace terminal equipment on line to Graham. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C070-WA | 2011-12-01 |  | 345 | 0 | 0 | 0 | 0 | ARCHER |  | CREZ |  |  |  | 1422, 1430 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0047 | Twin Buttes - Brown 345 kV line (Oncor Electric Delivery section) | Add second 345 kV circuit |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C038-E | 2011-12-01 |  | 345 | 0.2 | 0 | 0 | 0 | BROWN | BROWN | CREZ |  |  |  | 76009 | Y | 2007-E7f | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0061 | Bowman - Riley (Oklaunion) 345 kV line (Oncor Electric Delivery portion) | Construct double-circuit 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C073-E | 2011-12-01 |  | 345 | 85.2 | 0 | 0 | 0 | WILBARGER | ARCHER | CREZ |  |  |  | 1422, 6101 | Y | 2007- E7e | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0062 | Sweetwater East - Central Bluff 345 kV line | Construct double-circuit 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C058-E | 2011-12-01 |  | 345 | 71.6 | 0 | 0 | 0 | NOLAN | NOLAN | CREZ |  |  |  | 11420, 11406 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0063 | Central Bluff Switch | Construct 345 kV switching station with 345/138 kV autotransformers |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C074-E | 2011-12-01 |  | 345 | 0 | 0 | 1200 | -150 | NOLAN |  | CREZ |  |  |  | 11406 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0064 | Central Bluff - Bluff Creek 345 kV line | Construct double-circuit 345 kV line with one circuit |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C075-E | 2011-12-01 |  | 345 | 19 | 0 | 0 | 0 | NOLAN | TAYLOR | CREZ |  |  |  | 11406, 60040 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0098 | Bowman Switch | Rebuild switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C009-E | 2011-12-01 |  | 345 | 0 | 0 | 0 | 0 | ARCHER |  | CREZ |  |  |  | 1422 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0099 | Temple Switch circuit breaker | Install 345 kV circuit breaker on line to Salado Switch. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R739-E | 2011-12-01 |  | 345 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 3414 | Y
11TPIT0059 | Odessa EHV Switch #2 | Build new switching station adjacent to existing switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1010-E | 2011-12-01 |  | 345 | 0 | 0 | 0 | 0 | ECTOR |  | CREZ |  |  |  | 11028 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0041 | Temple Switch - Salado Switch 345 kV line | Upgrade existing 345 kV line | Construction schedule changed | R494 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R705-E | 2011-12-01 |  | 345 | 0 | 15.2 | 0 | 0 | BELL | BELL | Tier 1 | 2006-11-01 |  | 2007-07-01 | 3414, 3699 | Y
09TPIT0132 | Bonnie Brae Substation Constrcution | Construct new 50MVA, 69kV to 13.2kV substation adjacent to DME's 69kV Hickory to North Lakes transmission line 1/4 mile south of US 380 | On schedule | 07TPIT0097 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602099 | 2011-12-11 |  | 69 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 905 | Y
10TPIT0064 | Parkway(7611) - Schertz(7610) Transmission Line | Add new 138-kV 795 "Drake" transmission line circuit or replace existing 795 "Drake" circuit with 680T19 ACCR composite conductor |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2011-12-15 |  | 138 | 2.8 | 0 | 0 | 0 | GUADALUPE | GUADALUPE | Tier 4 |  |  |  | See Project Title | Y
12TPIT0024 | Kendall Autotransformer Replacement | Replace the existing 345/138 kV 336 MVA autotransformer with an 800 MVA autotransformer at the Kendall Substation. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-12-22 |  | 345 | 0 | 0 | 800 | 0 | KENDALL |  | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | CREZ Default project assigned to LCRA TSC
11TPIT0104 | Lon Hill to Upriver 69 kV Modifications | Lon Hill to Upriver 69 kV Hairpin into Hearn Road and Upgrade Lon Hill to Hearn Road section | Schedule Update | AEP GROUP 399 | AEP/ETT/TCC | Michael Glueck 918-599-2653 |  | 2011-12-30 |  | 69 | 0.5 | 0.5 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y
13TPIT0068 | Reconfigure Helotes to Bandera - 138kV Circuit | Reconfigure Helotes - Bandera to Helotes - Grissom 138 kV circuit |  |  | CPS | PM: Bruce Raney | T-0203 | 2011-12-30 |  | 138 | 0.5 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 2 |  |  |  | 5200 5020 5185 | Y |  | There are no transformers associated with this project
11TPIT0136 | Bissett to Aspermont | Rebuild Bissett to Aspermont 69 kV line with 795 ACSR |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-12-31 |  | 69 | 0 | 21.35 | 0 | 0 | STONEWALL | STONEWALL | Tier 4 |  |  |  | 753, 755, 6156 | Y
11TPIT0107 | Happy Valley: Tie 69 kV tap into Steamboat | Happy Valley: Tie 69 kV tap into Steamboat |  | AEP GROUP 354 | AEP/ETT | Teresa Trotman 918-599-2653 | 2092 | 2011-12-31 |  | 69 | 0 | 0.6 | 0 | 0 | TAYLOR | TAYLOR | Tier 4 |  |  |  |  | Y
08TPIT0133 | Rocksprings Station: Install 69 KV Ring Bus | Rocksprings : Install 5-69 KV Breaker Ring Bus and 3.6 MVAR Cap Bank |  | AEP GROUP 377 | AEP/ETT | Brian Johnson 918-599-2653 | 3019 | 2011-12-31 |  | 69 | 0 | 0 | 0 | 3.6 | EDWARDS |  | Tier 4 |  |  |  |  | N
12TPIT0070 | Ballinger to Steamboat, Rebuild portions of 69 kV line | Re-Build Portions of the Ballinger to Abilene South 69 kV line | Circuit Miles Update | AEP GROUP 354 | AEP/ETT | Teresa Trotman 918-599-2653 | 2460 | 2011-12-31 |  | 69 | 0 | 16.7 | 0 | 0 | TAYLOR | TAYLOR | Tier 1 | 2008-06-20 | 2009-03-19 | 2009-08-06 |  | Y
11TPIT0103 | Lon Hiil to Sinton 69 kVLine Modifications | Lon Hiil to Sinton 69 kVLine: Bypass Hearn Road | Schedule Update | AEP GROUP 399 | AEP/TCC | Michael Glueck 918-599-2653 |  | 2011-12-31 |  | 69 | 0 | 0.25 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y
11TPIT0144 | Rough Canyon to Hamilton Road, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | NEW | AEP GROUP 474 | AEP/TCC/ETT | Larry Roberson 918-599-2653 | 2440 | 2011-12-31 |  | 69 | 0 | 12.4 | 0 | 0 | VALVERDE | VALVERDE | CREZ Modified |  |  |  |  | Y
11TPIT0140 | Convert Kirby Substation into a double tap substation | Reconfigure Kirby substation. Kirby will loop through Ckt.37 (existing) and tap from Ckt.90 HOC to Garrott (new). |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-12-31 |  | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47320, 47321, 47322 | Y |  | No autotransformer capacity to be added.
12TPIT0069 | Barney Davis to Nelson Sharpe 138 kV line rebuild | Barney Davis to Nelson Sharpe 138 kV line rebuild | Schedule Update | AEP GROUP 400 | AEP/ETT/TCC | Michael Glueck 918-599-2653 |  | 2011-12-31 |  | 138 | 0 | 22.2 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y
12TPIT0072 | Ferguson to Wirtz | Upgrade the 4.0 mile Ferguson (7126) -Wirtz (7104) 138kV transmission lines to 1433.6 ACSS/TW (2000 Amps) |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-01-01 |  | 138 | 0 | 4 | 0 | 0 | BURNET | LLANO | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
11TPIT0110 | Alberta Switch-AEP Weslaco Switch | Rebuild 8.5 Miles of 138kV line from Alberta Switch to Valverde Substation to AEP Weslaco Switch | Project Speedup due to delay with Alberta Switch-Doedyns | 07TPIT7777 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-01-01 |  | 138 | 0 | 8.5 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8759-8769-8354 | Y
12TPIT0091 | Garvey Road 345 kV Switching Station | Construct new switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R905-E | 2012-01-01 |  | 345 | 0 | 0 | 0 | 0 | ARCHER | ARCHER | Tier 4 |  |  |  | 1702 | Y
10TPIT0045 | Mauermann Rd - New 138kV Substation | Loop new 138kV substation into the existing VH Braunig to Toyota line | Delayed due to resource allocation | T-0087 | CPS | PM:Hector Torres | S-0399 | 2012-02-22 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5297 | Y |  | There are no transformers associated with this project
12TPIT0034 | Illinois #4, Build new three breaker ring bus & add 138/69 kV auto | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | County Location Update, Autotransformer Capacity Update | AEP GROUP 474 | AEP/ETT | Larry Roberson 918-599-2653 | 2365 | 2012-02-28 |  | 138 | 0 | 0 | 37 | 0 | CROCKETT | CROCKETT | CREZ Modified |  |  |  |  | Y
12TPIT0064 | Rough Canyon, Convert station to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line |  | AEP GROUP 474 | AEP/ETT | Larry Roberson 918-599-2653 | 2433 | 2012-02-28 |  | 138 | 0 | 0 | 0 | 0 | VALVERDE | VALVERDE | CREZ Modified |  |  |  |  | Y
10TPIT0089 | Illinois #4 to Hamilton Rd., Convert 69 kV to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | Project Title Update, County Location Update, Cost Update | AEP GROUP 474 | AEP/ETT | Larry Roberson 918-599-2653 | 2364 | 2012-02-28 |  | 138 | 0 | 97.63 | 0 | 0 | CROCKETT | VALVERDE | CREZ Modified |  |  |  |  | Y
11TPIT0041 | Gila 138kV: Construct new 138 kV, 6 breaker GIS Ring Bus | Expand Nueces Bay 138 kV system for interconnection of 700 MW of new generation | Schedule Update | AEP GROUP 399 | AEP/ETT/TCC | Michael Glueck 918-599-2653 |  | 2012-02-28 |  | 138 | 0 | 0 | 0 | 57.6 | NUECES |  | Tier 1 | 2009-03-16 | 2009-10-09 | 2009-12-01 |  | Y
12TPIT0065 | Comstock, Convert station to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line |  | AEP GROUP 474 | AEP/TCC/ETT | Larry Roberson 918-599-2653 | 2401 | 2012-02-28 |  | 138 | 0 | 0 | 0 | 0 | VALVERDE | VALVERDE | CREZ Modified |  |  |  |  | Y
12TPIT0086 | Hamilton Road, expand station | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line |  | AEP GROUP 474 | AEP/TCC/ETT | Larry Roberson 918-599-2653 | 2368 | 2012-02-28 |  | 138 | 0 | 0 | 0 | 0 | VALVERDE | VALVERDE | CREZ Modified |  |  |  |  | Y
10TPIT0088 | Ft. Lancaster to Illinois #4, Convert 69 KV to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | Project Title Update, County Location Update, Cost Update | AEP GROUP 474 | AEP/TNC/ETT | Larry Roberson 918-599-2653 | 2363 | 2012-02-28 |  | 138 | 0 | 17.21 | 0 | 0 | PECOS | CROCKETT | CREZ Modified |  |  |  |  | Y
12TPIT0071 | Carson Creek to MetCenter new 138kV | Establish a new 138kV circuit between Carson Creek and MetCenter with 3000Amp rating. | New Project |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P354 PLAN_117_P370 PLAN_117_P371 | 2012-03-01 |  | 138 | 0.7 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9164, 9175 | N |  | Will add to the base case in this TPIT updates.
11TPIT0009 | Dunlap 138kV substation | Establish a new 138kV Dunlap substation with one 30MVA transformer. The substation will cut into existing Ckt 921 (Austrop - Decker). | Delay |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3230_117_2930 3230_117_2933 3240_117_4930 3240_117_4933 | 2012-03-01 |  | 138 | 0.1 | 0 | 60 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9045 | Y
12TPIT0089 | Knox to Knox | Rebuild Knox to Knox 69 kV line with 795 ACSR |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2012-03-15 |  | 69 | 0 | 3.67 | 0 | 0 | HASKEL | KNOX | Tier 4 |  |  |  | 765, 6114 | Y
07TPIT0251 | Victoria Power Plant: Install 1-28.8 MVAR 69 kV Cap Bank | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. |  | AEP GROUP 389 | AEP/TCC | Dave Goetz 918-599-2653 | 2243 | 2012-03-31 |  | 69 | 0 | 0 | 0 | 28.8 | VICTORIA |  | Tier 4 |  |  |  |  | Y
08TPIT0092 | North Victoria to Victoria: Reconductor 69 kV Line | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. |  | AEP GROUP 389 | AEP/TCC | Dave Goetz 918-599-2653 | 15 | 2012-03-31 |  | 69 | 0 | 3.1 | 0 | 0 | VICTORIA | VICTORIA | Tier 4 |  |  |  |  | Y
07TPIT0086 | Circuit 978 (Seaholm to Warren) Reconductor | Reconductor the last span of the Ckt 978 (Seaholm to Warren) going into Warren substation with bundled 795 ACSR Drake conductor. | Speedup |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P086 | 2012-04-01 |  | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9132, 9286 | Y
09TPIT0032 | Williamson 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Williamson substation. | Delay |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P063 | 2012-04-01 |  | 138 | 0 | 0 | 0 | 31.2 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9295 | Y
11TPIT0042 | Gila to Highway 9 138kV, Re-connect existing Highway 9 to Nueces Bay into Gila, | Expand Nueces Bay 138 kV system for interconnection of 700 MW of new generation |  | AEP GROUP 399 | AEP/TCC | Michael Glueck 918-599-2653 |  | 2012-04-12 |  | 138 | 0 | 3.29 | 0 | 0 | NUECES | NUECES | Tier 1 | 2009-03-17 | 2009-10-09 | 2009-12-01 |  | Y
11TPIT0052 | Riley, Build a new Riley to Oklaunion 345 kV line | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 |  | AEP GROUP 467 | AEP/ETT | Tommy Vannoy 918-599-2653 | 2351 | 2012-04-30 |  | 345 | 3.55 | 0 | 0 | 0 | WILBARGER | WILBARGER | CREZ Modified |  |  |  |  | Y
05TPIT0072 | Mountain Top-Blanco-Devil's Hill | Close the 69-kV switch (SW 458) at the Blanco substation(7482) to loop the load located at the Blanco substation. Upgrade the capacity of the 138-69-kV auto-transformer (T2) at the Devil’s Hill substation(7493) from 20-MVA to 45-MVA. |  |  | PEC | Randy Buchanan (830) 868-6058 | 1005443 | 2012-05-01 |  | 138 | 0 | 0 | 45 | 0 | BLANCO | COMAL | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
10TPIT0018 | Austin Ranch - Colony 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3004-E | 2012-05-01 |  | 138 | 0 | 4.6 | 0 | 0 | DENTON | COLLIN | Tier 4 |  |  |  | 2518, 2378, 12518 | Y | 2009-R16
10TPIT0032 | Arco (TMPA) - Krugerville 138 kV line | Rebuild existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5129-E | 2012-05-01 |  | 138 | 0 | 5.6 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | 2010-06-15 | 1994, 1993 | Y
11TPIT0012 | Euless - Grapevine Ball Street 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5131-E | 2012-05-01 |  | 138 | 0 | 5.9 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2016, 2021 | Y
12TPIT0074 | Coppell Tap - McKamy Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5001-E | 2012-05-01 |  | 138 | 0 | 1.35 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2014, 2025 | Y | No. 2007-R9 | 2007 ERCOT Five-year Transmission Plan Project No. 2007-R9
07TPIT0017 | Handley - Hurst 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M572-E | 2012-05-01 |  | 138 | 0 | 18.7 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1950, 2110, 2109, 1951 | Y
08TPIT0107 | Leon - Flat Creek 138 kV line | Rebuild existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R520A-E | 2012-05-01 |  | 138 | 0 | 19.5 | 0 | 0 | EASTLAND | ERATH | Tier 4 |  |  |  | 1624, 1640 | Y
10TPIT0109 | Burwick Switching Station | Construct new switching station to connect a new wind farm | Generation resource changed schedule |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R583-WA | 2012-05-01 |  | 345 | 0 | 0 | 0 | 0 | JACK |  | Tier 4 |  |  |  | 1456 | Y
11TPIT0096 | Elm Mott Switch circuit breaker | Install 345 kV circuit breaker on line to Tradinghouse |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R737-E | 2012-05-01 |  | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3406 | Y
11TPIT0038 | CSU Northgate Substation | Install (3) Breaker ring to include (2) 138 lines and tap to College Station Utilities |  |  | BTU/CSU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2012-05-06 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
12TPIT0073 | FM 239 Nordheim - New Substation | Construct a new 69-13.09x26.18-KV, 7.0 MVA substation |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-05-15 |  | 69 | 0 | 0 | 0 | 0 | DEWITT |  | Tier 4 |  |  |  | See Project Title | Y
11TPIT0016 | GPLTemp-Shiloh 69kV line and Shiloh 138kV substation rebuild and install a 138 kV/69 kV autotransformer (75 MVA) | Line upgrade and substation rebuild with installing a 138 kV/69 kV autotransformer (75 MVA) at Shiloh substation | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-05-31 |  | 69 | 0 | 2 | 75 | 0 | DALLAS |  | Tier 4 |  |  |  | 808, 830, 854 | Y |  | This project is a line upgrade and substation rebuild and install a 138 kV/69 kV-75MVA autotransformer for serving Plastipak and Shiloh loads
10TPIT0051 | Alamito Creek to Gonzales, Replace existing 69kV line with new 69kV line | Replace Alamito Creek to Gonzales line with 795 ACSR |  | AEP GROUP 358 | AEP/ETT | Jim Eriksen 918-599-2653 | 2170 | 2012-05-31 |  | 69 | 0 | 60 | 0 | 0 | PRESIDIO | PRESIDIO | Tier 1 | 2008-03-21 | 2008-06-10 | 2008-07-15 |  | Y
10TPIT0084 | Magruder: Add 1-14.4 MVAR 69 kV Cap Bank | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. |  | AEP GROUP 389 | AEP/ETT | Dave Goetz 918-599-2653 | 3335 | 2012-05-31 |  | 69 | 0 | 0 | 0 | 14.4 | VICTORIA |  | Tier 4 |  |  |  |  | Y
11TPIT0081 | Plastipak-Shiloh 138 kV line | Line upgrade | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-05-31 |  | 138 | 0 | 1.5 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 808, 830 | Y |  | This project is a line upgrade for serving new load at Plastipak
10TPIT0038 | College-Brand 138 kV line | Line reconductor | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-05-31 |  | 138 | 0 | 4.2 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 829, 827 | Y |  | This project is a line reconductor for solving overload
12TPIT0047 | Zenith - Kluge and Zenith - Addicks: Reconfigure and Upgrade Ckt. 76 and Ckt. 21 | Reconfigure circuits to form Zenith to Gertie tap to Cy Fair tap to Kluge Ckt. 76, Zenith to Gertie tap to Satsuma tap to Addicks Ckt. 76, and Camron to Cy Fair tap to Kluge Ckt. 21. Upgrade Ckt. 76 and Ckt. 21 to increase thermal ratings. |  | 12TPIT0046 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-05-31 |  | 138 | 0 | 6.1 | 0 | 0 | HARRIS | HARRIS | Tier 2 | 2009-02-06 | 2009-09-01 | N/A | 45952, 45712, 45801, 45802, 46302 | Y |  | Part of the 2012 Northwest Houston Reliability Project
06TPIT0057 | Magruder: Add 138/69 kV, 187 MVA, auto, 3 breaker 138 kV ringbus, 1 69 kV lowside breaker | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. |  | AEP GROUP 389 | AEP/ETT/TCC | Dave Goetz 918-599-2653 | 209 | 2012-05-31 |  | 138 | 0 | 0 | 187 | 0 | VICTORIA |  | Tier 4 |  |  |  |  | Y
13TPIT0026 | Tesla 345kv Switching Station | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2393 | 2012-05-31 |  | 345 | 0 | 0 | 0 | 0 | COTTLE | COTTLE | CREZ |  |  |  |  | Y
13TPIT0027 | Tesla, add two 130.9 MVar capacitors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2394 | 2012-05-31 |  | 345 | 0 | 0 | 0 | 261.8 | COTTLE | COTTLE | CREZ |  |  |  |  | Y
13TPIT0028 | Tesla, add two 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2395 | 2012-05-31 |  | 345 | 0 | 0 | 0 | 100 | COTTLE | COTTLE | CREZ |  |  |  |  | Y
11TPIT0077 | Riley, Add two 130.9 MVar capacitors | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 |  | AEP GROUP 467 | AEP/ETT | Tommy Vannoy 918-599-2653 | 2379 | 2012-05-31 |  | 345 | 0 | 0 | 0 | 261.8 | WILBARGER | WILBARGER | CREZ Modified |  |  |  |  | Y
12TPIT0076 | Oklaunion, Expand 345 kV switch station for the addition of the new Oklaunion to Riley circuit #2 | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 |  | AEP GROUP 467 | AEP/ETT | Tommy Vannoy 918-599-2653 | 2452 | 2012-05-31 |  | 345 | 0 | 0 | 0 | 0 | WILBARGER | WILBARGER | CREZ Modified |  |  |  |  | Y
12TPIT0046 | Zenith 138kV | Expand Zenith substation with addition of 345/138kV 800MVA Autotransformer. Build a new 138kV double circuit line from Zenith to Gertie corner. |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-05-31 |  | 345/138 | 10 | 0 | 800 | 0 | HARRIS | HARRIS | Tier 2 | 2009-02-06 | 2009-09-01 | N/A | 44900, 44910, 45801, 45802 | Y |  | Part of the 2012 Northwest Houston Reliability Project
12TPIT0081 | 36th St - New 138kV Substation | Loop new 138kV substation into existing 138kV Merida to Medina Base line and replace exiting Kelly Field #3 138kV substation |  | T-0161 | CPS | PM: Bruce Raney | S-0578 | 2012-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5427 5245 5305 5310 | Y |  | There are no transformers associated with this project
12TPIT0082 | Hotwells - New 138kV Substation | Loop new 138kV substation into existing 138kV Ball Park to Deely line |  | T-0168 | CPS | PM: George Corrigan | S-0615 | 2012-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5227 5255 5110 | Y |  | There are no transformers associated with this project
12TPIT0054 | SWRI to Westside - 138 kV Substation Equipment Upgrade | Replace Existing Substation Equipment at Westside to remove MLSE on the SWRI to Westside 138kV transmission line |  |  | CPS | Blake Williams |  | 2012-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5419 5490 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
09TPIT0037 | Blossom - New 138 kV Substation | Loop new 138 kV substation into the existing 138kV Harmony Hills to Skyline line | Accelarated for Reliability | T-0178 | CPS | PM: Ulrich Skerhut | S-0602 | 2012-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5022 | N |  | There are no transformers associated with this project
08TPIT0034 | McNeil to Summit Reconductor | The proposal of adding the 2nd ckt from McNeil to Summit in not feasible due to right of way issues. New proposal calls for the upgrading of the original circuit to 3000Amp. | Speedup |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P351 PLAN_117_P372 PLAN_117_P373 | 2012-06-01 |  | 138 | 2 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9079, 9279 | Y
12TPIT0090 | Whitney 2nd Auto | Add 75 MVA, 138/69 kV auto |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2012-06-01 |  | 138 | 0 | 0 | 75 | 0 | BOSQUE |  | Tier 4 |  |  |  | 241, 243 | Y
11TPIT0114 | Alberta Switch-Doedyns 138kV Line | Rebuild 3.1 Miles of 138kV line from Alberta Switch to Doedyns Substation | Delay Engineering Design | 07TPIT7777 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-06-01 |  | 138 | 0 | 3.1 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8753 - 8759 | Y
11TPIT0065 | Ector County North Switch (West B) - Moss 138 kV line | Construct 138 kV line with one circuit in place. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C0043-E | 2012-06-01 |  | 138 | 17.5 | 0 | 0 | 0 | ECTOR | ECTOR | CREZ |  |  |  | 11140, 1019 | Y |  | Proposed in-service date is an estimate since the in-service date will not be set until after the Certificate of Convenience and Necessity ("CCN") has been granted by the PUCT. Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0066 | Ector County North Switch (West B) | Construct 138 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C016-E | 2012-06-01 |  | 138 | 0 | 0 | 0 | 0 | ECTOR |  | CREZ |  |  |  | 11140 | Y |  | Proposed in-service date is an estimate since the in-service date will not be set until after the Certificate of Convenience and Necessity ("CCN") has been granted by the PUCT. Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0044 | Hill Country - Install Fourth 345/138 kV Autotransformer | Install 600 MVA autotransformer at Hill Country |  |  | CPS | Blake Williams |  | 2012-06-01 |  | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5211 5210 | Y |  | There is no transmission line additions associated with this project
12TPIT0045 | Brown Switch | Construct 345 kV switching station with shunt reactors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C022-E | 2012-06-01 |  | 345 | 0 | 0 | 0 | -250 | BROWN |  | CREZ |  |  |  | 1444 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0010 | Coppell to Roanoke Reconductor | Reconductor existing Coppell to Roanoke 138kv line with 959ACSS conductor |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2012-06-15 |  | 138 | 0 | 17 | 0 | 0 | TARRANT | DALLAS | Tier 4 |  |  |  | 1852, 661, 556, 555, 648 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
12TPIT0068 | South Bend Switch to Morris Sheppard Rebuild | Rebuild South Bend Switch to Morris Sheppard 69 kV line |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2012-06-15 |  | 138 | 0 | 18.2 | 0 | 0 | YOUNG | PALO PINTO | Tier 4 |  |  |  | 795, 343 | Y
13TPIT0014 | Decatur Capacitor Bank | Install 15mvar capacitor bank at Decatur |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2012-06-15 |  | 138 | 0 | 0 | 0 | 15 | WISE |  | Tier 4 |  |  |  | 583 | Y
07TPIT0042 | 2nd Lewisville Auto | Install (2nd) 345/138 kV autotransformer at Lewisville station |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2012-06-15 |  | 345 | 0 | 0 | 700 | 0 | DENTON |  | Tier 3 |  |  |  | 646, 645 | Y | 2009-R17
11TPIT0057 | Matador to Paducah Clare, Rebuild 69 kV line | Rebuild 69 kV line from Matador to Paducah Clare to Paducah City as 69/138 kV double circuit capable with 795 ACSS |  | AEP GROUP 454 | AEP/ETT | Joe Gilbert 918-599-2653 | 2328 | 2012-06-30 |  | 69 | 0 | 31.2 | 0 | 0 | MOTLEY | COTTLE | Tier 3 | 2010-05-01 | 2010-06-01 | N/A |  | Y
11TPIT0058 | Paducah Clare to Paducah City, Rebuild 69 kV line | Rebuild 69 kV line from Matador to Paducah Clare to Paducah City as 69/138 kV double circuit capable with 795 ACSS |  | AEP GROUP 454 | AEP/ETT | Joe Gilbert 918-599-2653 | 2378 | 2012-06-30 |  | 69 | 0 | 0.68 | 0 | 0 | COTTLE | COTTLE | Tier 4 | 2010-05-03 |  |  |  | Y
05TPIT0079 | Port Aransas: add 3 breaker 69 kv bus and 1-14.4 MVAR 69 kV cap bank | Add 3 breaker 69 kV ring bus on high side and install 1-14.4 MVAR capacitor bank at Port Aransas substation |  | AEP GROUP 029 | AEP/TCC/ETT/LCRA | Michael Glueck 918-599-2653 | 1136 | 2012-06-30 |  | 69 | 0 | 0 | 0 | 14.4 | ARANSAS |  | Tier 4 |  |  |  |  | Y
12TPIT0043 | Bluff Creek - Brown 345 kV line | Construct double-circuit 345 kV line with one circuit |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C076-E | 2012-07-01 |  | 345 | 86.6 | 0 | 0 | 0 | TAYLOR | BROWN | CREZ |  |  |  | 60040, 1444 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0044 | Central Bluff - Brown 345 kV line | Construct double-circuit 345 kV line with one circuit |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C075-E & C076-E | 2012-07-01 |  | 345 | 96.1 | 0 | 0 | 0 | NOLAN | BROWN | CREZ |  |  |  | 11406, 11425, 1444 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0087 | Wilson Substation | Add T2, 138kV-13.09x26.18 dual kV, 40 MVA PWT w/associated bus, structures, panels, etc |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-07-15 |  | 138 | 0 | 0 | 0 | 0 | WILSON |  | Tier 4 |  |  |  | See Project Title | N
13TPIT0023 | Edith Clarke 345kV station | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2387 | 2012-07-31 |  | 345 | 0 | 0 | 0 | 0 | COTTLE | COTTLE | CREZ |  |  |  |  | Y
13TPIT0024 | Edith Clarke, add two 130.9 MVar capacitors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2389 | 2012-07-31 |  | 345 | 0 | 0 | 0 | 261.8 | COTTLE | COTTLE | CREZ |  |  |  |  | Y
13TPIT0025 | Edith Clarke, add four 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2390 | 2012-07-31 |  | 345 | 0 | 0 | 0 | 200 | COTTLE | COTTLE | CREZ |  |  |  |  | Y
13TPIT0066 | E C Mornhinweg | Construct a new 138 kV 795 ACSR transmission line between the GPI switching station (7459) and the new E C Mornhinweg substation (7463). |  |  | NBU | Greg Baumbach (830) 629-8441 gbaumbach@nbutexas.com |  | 2012-08-01 |  | 138 | 2.7 | 0 | 0 | 0 | COMAL | COMAL | Tier 2 | 2009-02-06 | 2009-06-01 | N/A | SEE PROJECT DESCRIPTION | Y
11TPIT0108 | Penascal Wind Phases 3 Generation Interconnect | Penascal Wind Phases 2 and 3 Install ERCOT EPS Metering | Schedule Update | AEP GROUP 489 | AEP/ETT/TCC | John Pulay 918-599-2653 | 3370 | 2012-09-21 |  | 345 | 0 | 0 | 0 | 0 | KENNEDY |  | Tier 4 |  |  |  |  | Y
11TPIT0083 | Glen Rose Hills Substation | This project will build a new 138 kV / 12.47 kV substation near Glen Rose Hills subdivision north of Glen Rose |  |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE02110 | 2012-10-31 |  | 138 | 0 | 0 | 0 | 0 | SOMERVELL |  | Tier 4 |  |  |  | 37705 | Y
09TPIT0125 | East Abilene, Build new 138 kV switch station, terminate new 138 kV Leon line | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line |  | AEP GROUP 479 | AEP/ETT | Larry Roberson 918-599-2653 | 2272 | 2012-10-31 |  | 138 | 0 | 0 | 0 | 0 | EASTLAND |  | CREZ Modified |  |  |  |  | Y
10TPIT0086 | East Abilene to Putnam, Add 138 kV to existing 69 kV line | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line |  | AEP GROUP 466 | AEP/ETT | Larry Roberson 918-599-2653 | 2346 | 2012-10-31 |  | 138 | 0 | 32 | 0 | 0 | NUECES | CALLAHAN | CREZ Modified |  |  |  |  | Y
07TPIT0050 | Decker to Techridge 138kV Circuit Relocation/Reconductor | This project calls for the rerouting of the existing Ckt 975 (Decker to Techridge) from Yager corner to the Techridge substation. The rerouting will adopt 3000 Amps bundled 795 ACSS Drake. | Delay |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P071 | 2012-11-01 |  | 138 | 0 | 4.5 | 0 | 0 | TRAVIS | TRAVIS | Tier 2 | 2009-01-26 | 2009-06-01 | N/A | 9195, 9190 | Y
08TPIT0172 | Gunsight 138 kV Switching Station | Construct new switching station to connect a new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R829-WA | 2012-11-01 |  | 138 | 0 | 0 | 0 | 0 | HOWARD |  | Tier 4 |  |  |  | 1360 | Y
13TPIT0012 | Zorn Autotransformer Addition | Add a new 345-138 kV 478 MVA autotransformer at the Zorn substation (7042). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-11-01 |  | 345 | 0 | 0 | 478 | 0 | GUADALUPE |  | Tier 3 | 2008-01-30 | 2008-06-10 | N/A | SEE PROJECT DESCRIPTION | Y
12TPIT0075 | Knob Creek 345 kV Switching Station | Construct 345 kV switching station to connect a new generator |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R749-E | 2012-11-01 |  | 345 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 13413 | Y
12TPIT0028 | Twin Buttes (76009) to Big Hill (76003) | Construct a new double circuit capable 345 kV transmission line (approximately 31 miles) between the existing LCRA TSC Twin Buttes (76009) and new Big Hill station (76003). The new transmission line will consist of Cumberland conductor to provide a thermal rating of 2988 MVA. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-11-14 |  | 345 | 31 | 0 | 0 | 0 | TOM GREEN | SCHLEICHER | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y
09TPIT0039 | Woodrow to Kings Row 69kV Transmission Line Reconstruction | Reconstruct 4.0 miles of existing 69V transmission line | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600483 | 2012-12-01 |  | 69 | 0 | 4 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 901, 909 | Y
12TPIT0063 | Rebuild Heights-Lamarque 69kV line | This project will rebuild the 69 kV path from Heights to LaMarque. This includes lines 69-H1, 69-H2, and 69-J. Total length of line is approximately 2.8 miles. This project also will add to the system hardening efforts taken after Hurricane Ike in September of 2008. |  |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE07610 | 2012-12-01 |  | 69 | 0 | 2.8 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 38770, 39280, 39310, 39340 | N
07TPIT0096 | Pockrus Substation - Reconstruct 138kV Section of the Station | Reconstruct the 138kV section of the station to install transmission circuit breakers in a ring bus configuration | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600852 | 2012-12-01 |  | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 917 | Y
08TPIT0018 | Uvalde to Castroville, build 138 kV line, double circuit capable | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR | Schedule Update | AEP GROUP 291 | AEP/ETT | Brian Johnson (AEP) 918-599-2653 Hector Torres (CPS) 210-353-2404 | 1522 | 2012-12-01 |  | 138 | 77.5 | 0 | 0 | 0 | UVALDE | MEDINA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 5430, 8234 | Y
11TPIT0040 | Uvalde 138 kV Substation Upgrade | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR | Schedule Update | AEP GROUP 291 | AEP/TCC | Brian Johnson 918-599-2653 |  | 2012-12-01 |  | 138 | 0 | 0 | 0 | 0 | UVALDE |  | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
06TPIT0043 | Sherry - Liggett 138 kV line & Liggett - International Airport 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5042-WA | 2012-12-01 |  | 138 | 0 | 13 | 0 | 0 | TARRANT | DALLAS | Tier 4 |  |  |  | 1920, 2140, 1922, 2124, 2128, 2133, 2137 | Y |  | Sherry - GM section was completed in 2009.
12TPIT0079 | Roanoke Switch - Southlake 138 kV line | Rebuild 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5118 | 2012-12-01 |  | 138 | 0 | 7.1 | 0 | 0 | Denton | Tarrant | Tier 4 |  |  |  | 1852, 2018, 2020 | Y | 2007-R4
12TPIT0039 | Newton Switch | Construct 345 kV switching station | Construction schedule changed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C023-E | 2012-12-01 |  | 345 | 0 | 0 | 0 | 0 | LAMPASAS |  | CREZ |  |  |  | 3690 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0125 | Killeen Switch | Install circuit breakers and second 345/138 kV autotransformer | Construction schedule changed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C006-WA | 2012-12-01 |  | 345 | 0 | 0 | 600 | 0 | BELL |  | CREZ |  |  |  | 3422, 3423 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. The autotransformer will be placed in service in 12/2010.
07TPIT0140 | Trinidad - Watermill 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4045-E | 2012-12-01 |  | 345 | 0 | 52 | 0 | 0 | HENDERSON | DALLAS | Tier 3 |  |  |  | 2427, 3123 | Y
12TPIT0036 | Brown - Newton 345 kV line | Construct double-circuit 345 kV line with one circuit |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C048-E | 2012-12-01 |  | 345 | 98.6 | 0 | 0 | 0 | BROWN | LAMPASAS | CREZ |  |  |  | 1444, 3690 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0037 | Newton - Killeen Switch 345 kV line | Construct double-circuit 345 kV line with one circuit. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C049-E & C006B-E | 2012-12-01 |  | 345 | 27.9 | 0 | 0 | 0 | LAMPASAS | BELL | CREZ |  |  |  | 3690, 3422 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0038 | Brown - Killeen Switch 345 kV line | Add 345 kV circuit to the structures of the Brown - Newton - Killeen Switch line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C048-E & C049-E | 2012-12-01 |  | 345 | 126.5 | 0 | 0 | 0 | BROWN | BELL | CREZ |  |  |  | 1444, 3691, 3422 | Y | 2007-E7f | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. Cost estimate is included in the estimate for Brown - Newton - Killeen Switch 345 kV line.
12TPIT0078 | Southeast Nacogdoches - Lufkin Switch 345 kV line | Construct new 345 kV line, add second circuit to existing structures and add 345 kV circuit breakers at existing switching stations |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R862 | 2012-12-01 |  | 345 | 8 | 13 | 0 | 0 | NACOGDOCHES | ANGELINA | Tier 2 | 2008-07-01 |  | 2008-09-01 | 3117, 3119 | Y | 2007-E4
12TPIT0083 | Firewheel-Lookout 138 kV line | Line upgrade | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-12-15 |  | 138 | 0 | 1.3 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 821, 828 | Y |  | This project is a line reconductor for solving overload
12TPIT0084 | Lookout 138 kV new substation | New load serving | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-12-15 |  | 138 | 0 | 0 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 828 | Y |  | This project is a line reconductor for solving overload
12TPIT0085 | Apollo-Lookout 138 kV line | Line upgrade | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-12-15 |  | 138 | 0 | 2.8 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 802, 828 | Y |  | This project is a line reconductor for solving overload
11TPIT0076 | Cottonwood 345 kV Station and Cotttonwood to Dermott 345 kV line | Establish new 345 kV Cottonwood station and construct a new double circuit 345 kV transmission line WETT new Cottonwood and Oncor's Dermott 345 kV stations. |  |  | Wind Energy Transmission Texas (WETT) | Patsy Baynard (512) 279-7372 Patsy.Baynard@windenergyoftexas.com |  | 2012-12-30 |  | 345 | 71.5 | 0 | 0 | 50 -50 | DICKENS | SCURRY | CREZ |  |  |  | 59904 | Y |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
12TPIT0008 | Kings Row to Denton North 69kV Transmission Line Reconstruction | Reconstruct 2 miles of existing 69V transmission line | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602674 | 2012-12-31 |  | 69 | 0 | 2 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 909, 912 | Y
12TPIT0088 | Kings Row Substation Reconstruction | Completely reconstruct the Kings Row Substation | On schedule | 09TPIT0039 12TPIT0008 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | Not Assigned | 2012-12-31 |  | 69 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 909 | Y
09TPIT0073 | Jupiter-Apollo 69 kV line | Line reconductor | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-12-31 |  | 138 | 0 | 2 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 806, 802 | Y |  | This project is a line reconductor for solving overload
09TPIT0074 | Jupiter-Lawler 69 kV line | Line reconductor | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-12-31 |  | 138 | 0 | 1.5 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 806, 815, 820 | Y |  | This project is a line reconductor for solving overload
09TPIT0076 | Lawler-College 69 kV line | Line reconductor | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-12-31 |  | 138 | 0 | 2 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 803, 815, 820 | Y |  | This project is a line reconductor for solving overload
13TPIT0071 | Bullick Hollow 138kV Substation | Establish a new substation with (2) 50MVA unit transformers to serve the Water Treatment Plant | New Project |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P070 PLAN_117_P355 | 2013-01-01 |  | 138 | 0 | 0 | 100 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9162 | N |  | Will add idev file to the cases
12TPIT0056 | Grelton 345 kV Station and Grelton to Long Draw 345 kV line | Establish new 345 kV Grelton station and construct a new single circuit, double circuit capable 345 kV transmission line between new Grelton and new Long Draw 345 kV stations. |  |  | Wind Energy Transmission Texas (WETT) | Patsy Baynard (512) 279-7372 Patsy.Baynard@windenergyoftexas.com |  | 2013-02-28 |  | 345 | 55.4 | 0 | 0 | 0 | MARTIN | BORDEN | CREZ |  |  |  | 59901 | Y |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
12TPIT0057 | Grelton to Odessa 345 kV line | Construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Grelton and Oncor's existing Odessa 345 kV stations. |  |  | Wind Energy Transmission Texas (WETT) | Patsy Baynard (512) 279-7372 Patsy.Baynard@windenergyoftexas.com |  | 2013-02-28 |  | 345 | 49.9 | 0 | 0 | 0 | MARTIN | SCURRY | CREZ |  |  |  |  | Y |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
12TPIT0058 | Long Draw 345 kV Station and Long Draw to Scurry County South 345 kV line | Establish new 345 kV Long Draw station and construct a new double circuit 345 kV transmission line between WETT's new Long Draw and Oncor's Scurry County South 345 kV stations. |  |  | Wind Energy Transmission Texas (WETT) | Patsy Baynard (512) 279-7372 Patsy.Baynard@windenergyoftexas.com |  | 2013-02-28 |  | 345 | 50.7 | 0 | 0 | 0 | BORDEN | SCURRY | CREZ |  |  |  | 59900 | Y |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
13TPIT0048 | Scurry County (Central A) - West Shackelford (Central C) | CREZ Assigned Project to build West Shackelford (Central C) substation in Shackelford county and the double ckt 345 kV lines from Scurry County sub (Oncor Central A facility) to West Shackelford substation utilizing 2-1590 ACSS/TW "Falcon" conductor. Approximate distance is 90.5 miles. Two 100 MVar (2 x -100) shunt reactors will be place on the line terminals to Sam Switch and Navarro at West Shackelford. |  |  | Lone Star Transmission, LLC | Julius Horvath 512-236-3135 julius.horvath@lonestar-transmission.com |  | 2013-03-01 |  | 345 | 181 | 0 | 0 | -200 | SCURRY | SHACKELFORD | CREZ | N/A | N/A | N/A | West Shackelford 68000 | Y
13TPIT0049 | West Shackelford (Central C) - Sam Switch/Navarro | CREZ Assigned Project to build Sam Switch (Hill County) and Navarro (Navarro County) substations. There will be a double circuit line from West Shackelford (Central C) substation to Sam Switch utilizing a 2-1590 ACSS/TW "Falcon" conductor. At Sam Switch one of the circuits will terminate in the substation and the other will continue to Navarro as a single circuit line utilizing the same 2-1590 ACSS/TW "Falcon" conductor. The towers from Sam Switch to Navarro will be designed so that a second 345kV circuit can be added in the future. Approximate distance from West Shackelford to Sam Switch is 187.2 miles and approximate distance from Sam Switch to Navarro is 33.3 miles. Both lines will be series compensated at about 50% of the reactance in two banks; one approximately at 60 miles from West Shackelford at Romney (Eastland Co) and another at approximately 120 miles from West Shackelford at Kopperl (Bosque Co). There will be four 50 MVar (4 x -50) shunt reactors at the Romney station, two on the east side of the series capacitors and two on the west side. |  |  | Lone Star Transmission, LLC | Julius Horvath 512-236-3135 julius.horvath@lonestar-transmission.com |  | 2013-03-01 |  | 345 | 407.7 | 0 | 0 | -200 | SHACKELFORD | HILL / NAVARRO | CREZ | N/A | N/A | N/A | Romney 1 W 68010 Romney 2 W 68050 Romney 1 E 68020 Romney 2 E 68060 Kopperl 1 W 68030 Kopperl 2 W 68070 Kopperl 1 E 68040 Kopperl 2 E 68080 Sam Switch 68090 Navarro 68091 | Y
12TPIT0049 | LS04 Silverton to Cottonwood | Construct a new 345kV double circuit line from Silverton switching station to WETT's Cottonwod switching station | New | 12TPIT0050 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com | PR09.05163.CAP | 2013-03-01 |  | 345 | 63 | 0 | 0 | 0 | BRISCOE | DICKENS | CREZ |  |  |  | 99103-99104 | Y
12TPIT0050 | Silverton Collection Station | Construct the new 345 kV Silverton switching station.Initial build is 14 element folded breaker and one half bus arrangement. | New | 12TPIT0049 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com | PR09.05159.CAP | 2013-03-01 |  | 345 | 0 | 0 | 0 | 100 -50 | BRISCOE |  | CREZ |  |  |  | 99103 | Y |  | Column P input represents the dual values of capacitance and inductance as designated in the CTOS
13TPIT0051 | Gray to Tesla, build double circuit 345 kV line | Build new Gray Substation (Panhandle B-B) including 150 to 200 MVAR of reactive compensation and 345 kV double circuit line from Gray to Tesla | Revised circuit miles and cost to reflect approved CCN. |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-03-09 |  | 345 | 218 | 0 | 0 | 0 | GRAY | CHILDRESS | CREZ |  |  |  | 79000-60501 & 79000-60503 | Y
13TPIT0052 | Gray Substation (Panhandle B-B), build new collector substation | Build new Gray Substation (Panhandle B-B) including 150 to 200 MVAR of reactive compensation and 345 kV double circuit line from Gray to Tesla | Change based on CREZ Reactive Study |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-03-09 |  | 345 | 0 | 0 | 0 | 0 | GRAY |  | CREZ |  |  |  | 79000 | Y
13TPIT0053 | Gray Substation (Panhandle B-B), build 150 to 200 MVAR of Reactive Compensation | Build new Gray Substation (Panhandle B-B) including 150 to 200 MVAR of reactive compensation and 345 kV double circuit line from Gray to Tesla | Change based on CREZ Reactive Study |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-03-09 |  | 345 | 0 | 0 | 0 | -200 | GRAY |  | CREZ |  |  |  | 79000 | Y
13TPIT0054 | Gray to White Deer, build double circuit 345 kV line | Build 345 kV double circuit line from Gray to White Deer | Revised Trans Circuit Miles to reflect double circuit line. Project Cost from Docket 35665 Final Order. |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-03-11 |  | 345 | 80 | 0 | 0 | 0 | GRAY | CARSON | CREZ |  |  |  | 79000-99201,CKT 1 & 79000-99201,CKT 2 | Y
06TPIT0068 | Hamilton Road to Picacho, reconductor 138 kV line | Reconductor Del Rio 138 kV System | PM update | AEP GROUP 301 | AEP/TCC | Paul Hassink 918-599-2653 | 1544 | 2013-03-30 |  | 138 | 0 | 8.67 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
10TPIT0070 | Magruder to North Victoria: Rebuild 69 kV Line | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. |  | AEP GROUP 389 | AEP/TCC | Dave Goetz 918-599-2653 | 3261 | 2013-03-31 |  | 69 | 0 | 3.7 | 0 | 0 | VICTORIA | VICTORIA | Tier 4 |  |  |  |  | Y
11TPIT0078 | Riley, add four 50 MVar reactors | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 |  | AEP GROUP 467 | AEP/ETT | Tommy Vannoy 918-599-2653 | 2380 | 2013-03-31 |  | 345 | 0 | 0 | 0 | 200 | WILBARGER | WILBARGER | CREZ Modified |  |  |  |  | Y
11TPIT0079 | Riley, Expand 345 kV switch station for the additon of the West Krum to Riley 345 kV double circuit | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 |  | AEP GROUP 467 | AEP/ETT | Tommy Vannoy 918-599-2653 | 2435 | 2013-03-31 |  | 345 | 0 | 0 | 0 | 0 | WILBARGER | WILBARGER | CREZ Modified |  |  |  |  | Y
13TPIT0029 | Big Hill to Kendall 50% Series Compensation | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2398 | 2013-03-31 |  | 345 | 0 | 0 | 0 | 0 | SCHLEICHER | KENDALL | CREZ |  |  |  |  | Y
06TPIT0084 | Hamilton Road to Del Rio reconductor 138 kV line | Reconductor Del Rio 138 kV System | PM update | AEP GROUP 301 | AEP/TCC | Paul Hassink 918-599-2653 | 1545 | 2013-04-30 |  | 138 | 0 | 3 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
13TPIT0067 | Coleto Creek Substation: Interconnect New Generation to the 345 kV Rung Co-located with the Pawnee Line | Add a generation interconnection terminal at the Coleto Creek 345 kV bus. Upgrade protection, disturbance monitoring, communications, and metering for new generation. |  | AEP GROUP 453 | AEP/TCC | Paul Hassink 918-599-2653 | 3341 | 2013-04-30 |  | 345 | 0 | 0 | 0 | 0 | GOLIAD |  | Tier 4 |  |  |  |  | Y
07TPIT0116 | Handley - Duval 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5116-E | 2013-05-01 |  | 69 | 0 | 5.4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1952, 2158 | Y
12TPIT0018 | Bonham Switch 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R556-E | 2013-05-01 |  | 69 | 0 | 0 | 0 | 18.4 | FANNIN |  | Tier 4 |  |  |  | 1761 | Y
07TPIT0210 | Hilltop - White Settlement 69 kV line | Rebuild 4/0 ACSR section of line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5135-E | 2013-05-01 |  | 69 | 0 | 14.33 | 0 | 0 | PARKER | TARRANT | Tier 4 |  |  |  | 502, 1588, 2089 | Y
10TPIT0013 | Apollo to East Richardson | BEPC's portion of the line. |  | 09TPIT0044 | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2013-05-01 |  | 138 | 0 | 1.4 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 802, 2690 | Y |  | mileage shown is for Bepc portion of line
09TPIT0120 | Sun Switch - Golden - Sacroc 138 kV line | Rebuild 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R807-E | 2013-05-01 |  | 138 | 0 | 12.8 | 0 | 0 | SCURRY | SCURRY | Tier 4 |  |  |  | 1064, 1067, 1311 | Y
09TPIT0121 | Sun Switch - Sacroc 138 kV line | Rebuild 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R812-E | 2013-05-01 |  | 138 | 0 | 1.8 | 0 | 0 | SCURRY | SCURRY | Tier 4 |  |  |  | 1064, 1311 | Y
10TPIT0091 | Elm Mott - Waco Northcrest 138 kV line upgrade | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R714-E | 2013-05-01 |  | 138 | 0 | 3.6 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3407, 3575 | Y
11TPIT0032 | NW Carrollton - Collin 138 kV line | Rebuild existing 138 kV line for double-circuit operation. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M368-E | 2013-05-01 |  | 138 | 16.93 | 16.93 | 0 | 0 | DALLAS | COLLIN | Tier 4 |  |  |  | 2363, 2370 | Y | 2009-R13
09TPIT0117 | Stryker Creek - Dialville 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R664-E | 2013-05-01 |  | 138 | 0 | 15.2 | 0 | 0 | CHEROKEE | CHEROKEE | Tier 4 |  |  |  | 3110, 3160 | Y
11TPIT0031 | Celina SE 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3066-E | 2013-05-01 |  | 138 | 0 | 0 | 0 | 36.8 | COLLIN |  | Tier 4 |  |  |  | 2350 | Y
11TPIT0048 | Austin Ranch 138 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3074-E | 2013-05-01 |  | 138 | 0 | 0 | 0 | 55.2 | DENTON |  | Tier 4 |  |  |  | 2378, 2377 | Y
12TPIT0019 | Pleasant Valley second 138/69 kV autotransformer | Install second 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R555-E | 2013-05-01 |  | 138 | 0 | 0 | 100 | 0 | WICHITA |  | Tier 4 |  |  |  | 1450, 1451 | Y
13TPIT0059 | Cedar Crest - Industrial 138 kV line | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4072-E | 2013-05-01 |  | 138 | 0 | 3.2 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2494, 2981, 2976 | Y | 2009-R23
13TPIT0060 | Cedar Hill Switch - Mountain Creek 138 kV line | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4068-E | 2013-05-01 |  | 138 | 0 | 11.4 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2422, 2421, 2412, 2411 | Y
13TPIT0061 | Terrell Switch - North Terrell Tap 138 kV line | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M363-E | 2013-05-01 |  | 138 | 0 | 7.9 | 0 | 0 | KAUFMAN | KAUFMAN | Tier 4 |  |  |  | 2718, 2715, 2721 | Y
09TPIT0044 | E. Richardson - Apollo 138 kV line (Oncor Electric Delivery section) | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3033-WA | 2013-05-01 |  | 138 | 0 | 2.32 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 802, 2690 | N
12TPIT0051 | LS01 Silverton to Nazareth | Construct a new 345kV single circuit line from Silverton switching station to Nazareth switching station. | New | 12TPIT0053 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com | PR09.05157.CAP | 2013-05-01 |  | 345 | 48 | 0 | 0 | 0 | BRISCOE | CASTRO | CREZ |  |  |  | 99103-99101 | Y
12TPIT0053 | Nazareth Collection Station | Construct the new 345 kV Nazareth switching station.Initial build is 7 element ring bus arrangement. | New | 12TPIT0051 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com | PR09.05164.CAP | 2013-05-01 |  | 345 | 0 | 0 | 1200 | -50 | CASTRO |  | CREZ |  |  |  | 99101 | Y
12TPIT0067 | Anna Switch 345/138 kV autotransformer replacement | Replace #1 autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3085-E | 2013-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  | Tier 4 |  |  |  | 2373, 2374 | Y
09TPIT0042 | Collin 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M318-E | 2013-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  | Tier 4 |  |  |  | 2370, 2372 | N | 2009-R15
13TPIT0018 | McCamey C to McCamey D (Bakersfield to Big Hill) | Construct new 113 miles 1590 ACSR 345 kV line from Bakersfiled to Big Hill (McCamey C to McCamey D). |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-05-01 |  | 345 | 112 | 0 | 0 | 0 | PECOS | SCHLEICHER | CREZ |  |  |  | 76002-76003 | Y
06TPIT0083 | Del Rio to Buena Vista, reconductor 138 kV line | Reconductor Del Rio 138 kV System | PM update | AEP GROUP 301 | AEP/TCC | Paul Hassink 918-599-2653 | 1546 | 2013-05-30 |  | 138 | 0 | 3 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
12TPIT0059 | Sand Bluff 345 kV Station and Sand Bluff to Divide 345 kV line | Establish new 345 kV Sand Bluff station and construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Sand Bluff and LCRA TSC's Divide 345 kV stations. |  |  | Wind Energy Transmission Texas (WETT) | Patsy Baynard (512) 279-7372 Patsy.Baynard@windenergyoftexas.com |  | 2013-05-30 |  | 345 | 33 | 0 | 0 | 0 | GLASSCOCK | COKE | CREZ |  |  |  | 59902 | Y |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
12TPIT0060 | Bearkat 345 kV Station and Bearkat to Sand Bluff 345 kV line | Establish new 345 kV Bearkat station and construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Sand Bluff and new Bearkat 345 kV stations. |  |  | Wind Energy Transmission Texas (WETT) | Patsy Baynard (512) 279-7372 Patsy.Baynard@windenergyoftexas.com |  | 2013-05-30 |  | 345 | 29.7 | 0 | 0 | 0 | GLASSCOCK | STERLING | CREZ |  |  |  | 59903 | Y |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
12TPIT0061 | Sand Bluff to Long Draw 345 kV line | Construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Sand Bluff and new Long Draw 345 kV stations. |  |  | Wind Energy Transmission Texas (WETT) | Patsy Baynard (512) 279-7372 Patsy.Baynard@windenergyoftexas.com |  | 2013-05-30 |  | 345 | 72.4 | 0 | 0 | 0 | GLASSCOCK | BORDEN | CREZ |  |  |  |  | Y |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
12TPIT0062 | UTMB Substaion- New Substation | This project will build new 138 kV / 12.47 kV substation to serve proposed UTMB Medical Center at Victory Lakes in League City. |  |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE04512 | 2013-05-31 |  | 138 | 0 | 0 | 0 | 0 | GALVESTON |  | Tier 4 |  |  |  |  | N
07TPIT0024 | Lytle: Add 138/69 kV Auto | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | Schedule Update | AEP GROUP 028 | AEP/ETT | Brian Johnson 918-599-2653 | 74 | 2013-05-31 |  | 138 | 0 | 0 | 93 | 0 | MEDINA |  | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
07TPIT0027 | CPS Lytle to ETT Lytle: Build 138 kV Line and CPS Lytle Substation Upgrades | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | Schedule Update | AEP GROUP 028 CPS S-0046 | AEP/ETT/CPS | Brian Johnson (AEP) 918-599-2653 Hector Torres (CPS) 210-353-2404 | 21 | 2013-05-31 |  | 138 | 4 | 0 | 0 | 0 | BEXAR | MEDINA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 5290, 8962 | Y
13TPIT0022 | Gray to Oklaunion double circuit 345kV line (Tesla to Riley portion) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2384 | 2013-05-31 |  | 345 | 132.2 | 0 | 0 | 0 | GRAY | WILBARGER | CREZ |  |  |  |  | Y
13TPIT0020 | Tesla to Edith Clarke double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2382 | 2013-05-31 |  | 345 | 79.8 | 0 | 0 | 0 | COTTLE | COTTLE | CREZ |  |  |  |  | Y
13TPIT0013 | Perry to Midway Rebuild | Rebuild Perry to Midway with 959ACSS |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2013-06-01 |  | 69 | 0 | 12.4 | 0 | 0 | FALLS | FALLS | Tier 4 |  |  |  | 92185 | Y
13TPIT0069 | Panther Springs - New 138kV Substation | Loop new 138kV substation into existing 138kV Hill Country to Stonegate circuit #1 line |  | T-0172 | CPS | PM: George Corrigan | S-0616 | 2013-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5331 5210 5415 | Y |  | There are no transformers associated with this project
11TPIT0024 | TCC - 138kV Line Reroutes | The following 138kV lines will be rerouted: Cagnon - AMDTP - AMD becomes Cagnon - AMD Cagnon - AMDTP - Pinn becomes Cagnon - Pinn Pinn - SWRI becomes Pinn - Westside Construct a new 138kV line from TCC - SWRI Cagnon - AMD line upgrade to 1590AAC |  | S-0384 | CPS | T: Kevin Phillips | T-0106 | 2013-06-01 |  | 138 | 5.8 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 2 |  |  |  | 5423 5419 5345 5002 5004 5490 | Y |  | There are no transformers associated with this project
12TPIT0009 | Masterson Rd - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to Valley Rd line and the Cagnon to Howard line |  |  | CPS | Blake Williams |  | 2013-06-01 |  | 138 | 20 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5296 | Y |  | There are no transformers associated with this project
13TPIT0011 | Palo Alto - New 138kV Substation | Loop new 138kV substation into the existing 138kV Leon Creek to Chavaneaux line |  |  | CPS | Blake Williams |  | 2013-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5330 | Y |  | There are no transformers associated with this project
08TPIT0044 | Circuit 1013 Double Breaker at Decker Power Plant | Install one 138 kV, 3000 Amp, 63 kA circuit breaker and two switches to connect Ckt 1013 (Decker to McNeil) to the Decker MB2 Bus. | Delay |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P138 | 2013-06-01 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9187, 9188 | N |  | The double breaker configuration will not be reflected in the SSWG models because the planning models are bus based.
11TPIT0026 | Cagnon - Install a Third 345kV Autotransformer | Install one 600 MVA autotransformer. |  |  | CPS | Blake Williams |  | 2013-06-01 |  | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5055 5056 | Y |  | There are no transmission line additions associated with this project
10TPIT0031 | Dunlap 138/345kV Autotransformer Project | Instal one 138/345 kV 672 MVA autotransformer at the Dunlap substation, configuring a Dunlap to Lost Pines 345 kV circuit, add a new 345kV line from Dunlap to Austrop and combine 138kv Dunlap to Decker and Decker to Techridge into one single circuit bypassing Decker. |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P132 | 2013-06-01 |  | 345 | 0 | 0 | 672 | 0 | TRAVIS | TRAVIS | Tier 3 | 2010-04-01 | 2010-06-01 | N/A | 9044, 9045 | Y
13TPIT0037 | Krum West Switch | Construct 345 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C017B-E | 2013-06-01 |  | 345 | 0 | 0 | 0 | 80 -100 | DENTON |  | CREZ |  |  |  | 1730 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0036 | Krum West - Riley (Oklaunion) 345 kV line (Oncor Electric Delivery portion) | Construct double-circuit 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C050-E | 2013-06-01 |  | 345 | 322.8 | 0 | 0 | 0 | DENTON | WILBARGER | CREZ |  |  |  | 1730, 6101 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0039 | Hicks Switch - Willow Creek 345 kV line | Construct double-circuit 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C061-E | 2013-06-01 |  | 345 | 86.6 | 0 | 0 | 0 | TARRANT | WISE | CREZ |  |  |  | 2081, 1421 | Y |  | Proposed in-service date is an estimate since the in-service date will not be set until after the Certificate of Convenience and Necessity ("CCN") has been granted by the PUCT. Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0040 | Willow Creek Switch circuit breakers | Install 345 kV circuit breakers. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C012B-E | 2013-06-01 |  | 345 | 0 | 0 | 0 | 0 | WISE |  | CREZ |  |  |  | 1421 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0038 | Hicks Switch | Construct 345 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C030-E | 2013-06-01 |  | 345 | 0 | 0 | 0 | 0 | TARRANT |  | CREZ |  |  |  | 2081 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0078 | Kendall Autotransformer Addition | Replace the existing 345-138 kV 478MVA autotransformer with an 672 MVA autotransformer at the Kendall substation. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2013-06-01 |  | 345 | 0 | 0 | 672 | 0 | KENDALL |  | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y |  | CREZ Default project assigned to LCRA TSC
10TPIT0083 | Mustang Capacitor Bank | Install 100mvar capacitors at future Mustang sub |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2013-06-15 |  | 138 | 0 | 0 | 0 | 100 | DENTON |  | Tier 4 |  |  |  | 654 | Y
13TPIT0045 | Blumenthal | Construct a new 8.4-mile 138 kV transmission line from a tap point on the Kendall- Mountain Top 138 kV transmission line to the new Blumenthal substation (7418). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2013-06-30 |  | 138 | 8.4 | 0 | 0 | 0 | KENDALL |  | Tier 2 |  |  |  | SEE PROJECT DESCRIPTION | Y
13TPIT0046 | Flatonia-Yoakum Gartner Road | Upgrade and convert the 27.7 mile Flatonia (7248)-Moulton (7236)-Henkhaus (7237)-Shiner (7238)-Yoakum Gartner Road (7242) 2/0 ACSR 69 kV transmission line to 795 ACSR 138 kV. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2013-06-30 |  | 138 | 0 | 27.7 | 0 | 0 | FAYETTE | DEWITT | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y
07TPIT0083 | Picacho to CFE, construct new 138 kV line | Convert Amistad to CFE Amistad 12.5 kV distribution to 138 kV line | PM update | AEP GROUP 301 | AEP/ETT | Paul Hassink 918-599-2653 | 1548 | 2013-06-30 |  | 138 | 8.8 | 0 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
06TPIT0082 | Buena Vista to Picacho, reconductor 138 kV line | Reconductor Del Rio 138 kV System | PM update | AEP GROUP 301 | AEP/TCC | Paul Hassink 918-599-2653 | 1547 | 2013-06-30 |  | 138 | 0 | 3 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
12TPIT0022 | North McCamey Autotransformer Addition | Add two new 345-138 kV 800 MVA autotransformer at the North McCamey substation. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2013-06-30 |  | 345 | 0 | 0 | 1600 | 0 | UPTON |  | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | CREZ Default project assigned to LCRA TSC
13TPIT0019 | Riley to Edith Clarke double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2381 | 2013-06-30 |  | 345 | 85.6 | 0 | 0 | 0 | WILBARGER | COTTLE | CREZ |  |  |  |  | Y
13TPIT0021 | Cottonwood to Edith Clarke double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2383 | 2013-06-30 |  | 345 | 149 | 0 | 0 | 0 | DICKENS | COTTLE | CREZ |  |  |  |  | Y
12TPIT0048 | Hereford Collection Station | Construct the new 345 kV Hereford switching station.Initial build is 7 element folded breaker and one half bus arrangement | New | 13TPIT0042, 13TPIT0043 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com | PR09.05165.CAP | 2013-07-01 |  | 345 | 0 | 0 | 1200 | -50 | DEAF SMITH |  | CREZ |  |  |  | 99102 | Y |  | Filed under PUC Docket # 38290
12TPIT0052 | LS02 Nazareth to Hereford | Construct a new 345kV single circuit line from Nazareth Switching to Hereford switching station | New |  | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com | PR09.05161.CAP | 2013-07-01 |  | 345 | 33 | 0 | 0 | 0 | CASTRO | DEAF SMITH | CREZ |  |  |  | 99101-99102 | Y
12TPIT0007 | FM-725 - New Substation | Build a 138-26.18 kV, 40 MVA substation on the GVEC McQueeney(7606) - Schumansville(7609) 138 kV transmission line |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2013-07-31 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N
13TPIT0042 | LS03 White Deer to Hereford | Construct a new 345kV single circuit line from White Deer switching station to Hereford switching station | New | 12TPIT0048, 13TPIT0043 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com | PR09.05162.CAP | 2013-09-01 |  | 345 | 92 | 0 | 0 | 0 | CARSON | DEAF SMITH | CREZ |  |  |  | 99201-99102 | Y |  | Filed under PUC Docket # 38290
13TPIT0043 | White Deer Collection Station | Construct the new 345 kV White Deer switching station.Initial build is 10 element folded breaker and one half bus arrangement. | New | 12TPIT0048, 13TPIT0042 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com | PR09.05158.CAP | 2013-09-01 |  | 345 | 0 | 0 | 0 | -100 | CARSON |  | CREZ |  |  |  | 99201 | Y |  | Filed under PUC Docket # 38290
10TPIT0048 | Koppe Bridge Substation | Install (4) Breaker ring to include (2) 138 lines and (1) 138/12.5 transformer |  | 10TPIT0049 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2013-09-10 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
10TPIT0049 | Koppe Bridge to Wellborn Transmission | Build (5.8) miles of 138 kV line(s) to serve station |  | 10TPIT0048 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2013-09-10 |  | 138 | 5.8 | 0 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | Y
13TPIT0015 | Wellborn Switching Sub | Install (3) Breaker ring to include (2) 138 lines and (1) 138/69 auto transformer relocated from Greens Prairie |  | 10TPIT0049 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2013-09-10 |  | 138 | 0 | 0 | 20 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
13TPIT0016 | Greens Prairie to Wellborn Transmission | ReBuild-Reconductor (3.75) miles of 69kV line converting to 138 kV to serve Wellborn |  |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2013-09-10 |  | 138 | 0 | 4 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | Y
13TPIT0017 | Greens Prairie Substation | Install (1) Breaker in existing ring bus for a 138 line from Wellborn/Millican Substation(s) |  |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2013-09-10 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32897 | Y
13TPIT0055 | Silverton to Tesla, build double circuit 345 kV line | Build 345 kV double circuit line from Silverton to Tesla | Revised Trans Circuit Miles to reflect double circuit line. Project Cost from Docket 35665 Final Order. |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-09-12 |  | 345 | 170 | 0 | 0 | 0 | BRISCOE | CHILDRESS | CREZ |  |  |  | 99103-79001, 79002-60503 & 99103-60502 | Y
13TPIT0056 | Silverton to Tesla, build series compensation | Add series compenstion to both circuit of the 345 kV double circuit line from Silverton to Tesla | Change based on CREZ Reactive Study and recommendation of ERCOT. Project Cost based on Docket 35665 Final Order |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-09-12 |  | 345 | 0 | 0 | 0 | 0 | BRISCOE | CHILDRESS | CREZ |  |  |  | 79001-79002 & 79003-79004 | Y
13TPIT0050 | LS05 Silverton to White Deer | Construct a new 345kV double circuit line from Silverton switching station to White Deer switching station | New |  | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com | PR09.05160.CAP | 2013-09-30 |  | 345 | 76 | 0 | 0 | 0 | BRISCOE | CARSON | CREZ |  |  |  | 99103-99201 | Y
13TPIT0030 | Dermott to Willow Creek (Dermott to Clear Crossing portion) double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2391 | 2013-09-30 |  | 345 | 189 | 0 | 0 | 0 | SCURRY | HASKELL | CREZ |  |  |  |  | Y
13TPIT0031 | Dermott to Clear Crossing 25% Compensation | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2392 | 2013-09-30 |  | 345 | 0 | 0 | 0 | 0 | SCURRY | HASKELL | CREZ |  |  |  |  | Y
13TPIT0064 | Series reactive compensation for Willow Creek - Clear Crossing - Dermott Switch (Central B) 345 kV line (Oncor Electric Delivery part) | Install series capacitor |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C079-E | 2013-11-01 |  | 345 | 0 | 0 | 0 | 0 | HASKELL |  | CREZ |  |  |  |  | Y |  | Proposed in-service date is an estimate since the in-service date will not be set until after the Certificate of Convenience and Necessity ("CCN") has been granted by the PUCT. Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0070 | Nash Creek Substation | Replace 5.6 MVA with 10 MVA 69-13.09x26.18-KV transformer |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2013-11-30 |  | 69 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N
13TPIT0032 | Edith Clarke to West Shackelford double circuit 345kV line (Edith Clarke to Clear Crossing portion) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2385 | 2013-11-30 |  | 345 | 150.6 | 0 | 0 | 0 | COTTLE | SHACKELFORD | CREZ |  |  |  |  | Y
13TPIT0033 | Edith Clarke to West Shackelford double circuit 345kV line (Clear Crossing to West Shackelford portion) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2386 | 2013-11-30 |  | 345 | 59.6 | 0 | 0 | 0 | COTTLE | SHACKELFORD | CREZ |  |  |  |  | Y
13TPIT0034 | Edith Clarke to West Shackelford 50% compensation | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | AEP GROUP 478 | AEP/ETT | Paul Hassink 918-599-2653 | 2388 | 2013-11-30 |  | 345 | 0 | 0 | 0 | 0 | COTTLE | COTTLE | CREZ |  |  |  |  | Y
13TPIT0063 | Salado 138 kV Switch | Construct 138 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R445B-E | 2013-12-01 |  | 138 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 13640 | Y
13TPIT0072 | Scurry County South Switch (Central A) | Install shunt capacitor |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC0088-E | 2013-12-01 |  | 345 | 0 | 0 | 1200 | 160 | SCURRY |  | CREZ |  |  |  | 11318 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0073 | Killeen Switch | Install shunt capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC0089-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | 160 | BELL |  | CREZ |  |  |  | 3422 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0074 | Willow Creek Switch | Install shunt reactors. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C054B-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | -100 | WISE |  | CREZ |  |  |  | 1421 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0035 | Willow Creek - Clear Crossing - Dermott Switch (Central B) 345 kV line (Oncor Electric Delivery section) | Construct double-circuit 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C054-E | 2013-12-01 |  | 345 | 213.6 | 0 | 0 | 0 | WISE | HASKELL | CREZ |  |  |  | 1421 | Y |  | Proposed in-service date is an estimate since the in-service date will not be set until after the Certificate of Convenience and Necessity ("CCN") has been granted by the PUCT. Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0075 | Graham Switching Station | Install shunt reactor |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC083-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | -200 | YOUNG | YOUNG | CREZ |  |  |  | 1430 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0076 | Parker Switching Station | Install a dynamic reactive device |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC087-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | 300 -265 | PARKER | PARKER | CREZ |  |  |  | 1436 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0020 | Anna Switch - Krum W. Switch 345 kV line | Construct a double-circuit 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C060-E | 2013-12-01 |  | 345 | 102 | 0 | 0 | 0 | DENTON | COLLIN | CREZ |  |  |  | 1730, 2373 | Y |  | Proposed in-service date is an estimate since the in-service date will not be set until after the Certificate of Convenience and Necessity ("CCN") has been granted by the PUCT. Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
13TPIT0041 | Anna Switch circuit breakers | Install 345 kV circuit breakers |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C015-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | 0 | COLLIN |  | CREZ |  |  |  | 1730 | Y |  | Proposed in-service date is an estimate since the in-service date will not be set until after the Certificate of Convenience and Necessity ("CCN") has been granted by the PUCT. Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
09TPIT0053 | Princeton, Climax to New Princeton Station | Build a 138kV line from Climax Station to New Princeton Station to Longneck Station |  |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2013-12-15 |  | 138 | 10 | 0 | 42 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  |  | Y
12TPIT0029 | Big Hill (76003) to Kendall (7046) | Construct a new double circuit 345 kV transmission line (approximately 137 miles) between the new Big Hill (76003) and the existing Kendall station (7046). The new transmission lines will consist of Cumberland conductor to provide a thermal rating of 2988 MVA each. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2013-12-30 |  | 345 | 274 | 0 | 0 | 0 | SCHLEICHER | KENDALL | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y
07TPIT0250 | Foster Field: Install 2-7.2 MVAR 69 kV Cap Banks | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. |  | AEP GROUP 389 | AEP/TCC | Dave Goetz 918-599-2653 | 2047 | 2013-12-31 |  | 69 | 0 | 0 | 0 | 14.4 | VICTORIA |  | Tier 4 |  |  |  |  | Y
11TPIT0084 | South League City Substation-New Substation | Build a new distribution substation in order to accommodate new subdivision growth along the FM 517 and FM 646 corridor in Dickinson, Texas |  |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE02411 | 2013-12-31 |  | 138 | 0 | 0 | 0 | 0 | GALVESTON |  | Tier 4 |  |  |  | 38900 | Y
12TPIT0015 | Barney Davis to Laguna: Construct 138 kV transmission line | Construct new 138 kV line and add tranformation at Laguna to remove contingency overloads during off-peak maintnenance | Schedule Update | AEP GROUP 400 | AEP/ETT | Michael Glueck 918-599-2653 |  | 2013-12-31 |  | 138 | 4.2 | 0 | 0 | 0 | NUECES | NUECES | Tier 1 | 2009-03-26 | 2009-10-09 | 2009-12-01 |  | Y
12TPIT0014 | Laguna: Add 138/69 kV Auto | Construct new 138 kV line and add tranformation at Laguna to remove contingency overloads during off-peak maintnenance | Schedule Update | AEP GROUP 400 | AEP/ETT/TCC | Michael Glueck 918-599-2653 |  | 2013-12-31 |  | 138 | 0 | 0 | 240 | 0 | NUECES |  | Tier 1 | 2009-03-24 | 2009-10-09 | 2009-12-01 |  | Y
13TPIT0077 | Kendall (7147) to Miller Creek (7148) to Paleface (7476) | Upgrade existing Kendall to Miller Creek line to 1433 ACSS/TW (Merrimack) and Miller Creek to Paleface line to 795 ACSR (Drake) |  |  | LCRA TSC | Brad Woods brad.woods@lcra.org 512 369 4104 |  | 2013-12-31 |  | 138 | 0 | 56.88 | 0 | 0 | KENDALL | Burnet | CREZ |  |  |  | SEE PROJECT DESCRIPTION | y
12TPIT0027 | North McCamey (76000) to Bakersfield (76002) | Construct a new double circuit capable 345 kV transmission line (approximately 12 miles) between the LCRA TSC North McCamey (76000) and Bakersfield (76002) stations. The new transmission line will consist of 2x1590 ACSR Falcon conductor to provide a thermal rating of 1678 MVA | Project reassigned by PUCT to STEC from LCRA. |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-12-31 |  | 345 | 15 | 0 | 0 | 0 | UPTON | PECOS | CREZ |  |  |  | 76000-76002 | Y |  | Cost estimates for this project have been included with TPIT project # 12TPIT0026. Both projects will be filed in one PUCT Project # in 2011.
12TPIT0026 | North McCamey (76000) to Odessa EHV (11028) | Construct a new double circuit capable 345 kV transmission line (approximately 50 miles) between the existing LCRA TSC North McCamey (McCamey A) and the existing Oncor Odessa EHV stations. The new transmission line will consist of 2x1590 ACSR Falcon conductor to provide a thermal rating of 1678 MVA. | Project reassigned by PUCT to STEC from LCRA. |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-12-31 |  | 345 | 50 | 0 | 0 | 0 | UPTON | ECTOR | CREZ |  |  |  | 76000-11028 | Y |  | Cost estimates for this project include TPIT project # 12TPIT0027. Both projects will be filed in one PUCT Project # in 2011.
13TPIT0047 | Parkway to EC Mornhinweg | Construct a new 138 kV 795 ACSR transmission line between the new EC Mornhinweg substation (7463) and the Parkway substation (7611). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2014-03-01 |  | 138 | 8 | 0 | 0 | 0 | COMAL | GUADALUPE | Tier 2 | 2009-02-06 | 2009-06-01 | N/A | SEE PROJECT DESCRIPTION | Y
08TPIT0132 | Melon Creek to Tatton: Build 69 KV Line & Tatton Substation Upgrades | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. | Schedule Update | AEP GROUP 100 | AEP/TCC | Paul Hassink 918-599-2653 | 2028 | 2014-03-31 |  | 69 | 7.7 | 0 | 0 | 0 | REFUGIO | ARANSAS | Tier 2 |  |  |  |  | Y
07TPIT0252 | Greta: Install 1-7.2 MVAR 69 kV Cap Bank | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. |  | AEP GROUP 100 | AEP/TCC | Paul Hassink 918-599-2653 | 2045 | 2014-03-31 |  | 69 | 0 | 0 | 0 | 7.2 | REFUGIO |  | Tier 4 |  |  |  |  | Y
08TPIT0131 | Melon Creek: Install 138/69 KV Auto | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. | Schedule Update | AEP GROUP 100 | AEP/TCC | Paul Hassink 918-599-2653 | 2021 | 2014-03-31 |  | 138 | 0 | 0 | 50 | 0 | REFUGIO |  | Tier 4 |  |  |  |  | Y
11TPIT0014 | Muenster - St. Jo (BEC) 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R186B-E | 2014-05-01 |  | 69 | 0 | 7.8 | 0 | 0 | COOKE | COOKE | Tier 4 |  |  |  | 1712, 1716 | Y
14TPIT0008 | Holt - Emma 69 Tap kV line | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8006-E | 2014-05-01 |  | 69 | 0 | 6.2 | 0 | 0 | ECTOR | ANDREWS | Tier 4 |  |  |  | 1262, 1142 | Y | 2009-R5
14TPIT0009 | Odessa North - North Cowden 69 kV line | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8008-E | 2014-05-01 |  | 69 | 0 | 12.4 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1259, 1123 | Y | 2009-R4
10TPIT0027 | West Batesville, Install 138 kV ring bus | West Batesville: Construct bundled 2x795 ACSR 138 kV line, add 138 kV circuit breaker and convert to 4 breaker ring bus |  | AEP GROUP 383 | AEP/ETT | Paul Hassink 918-599-2653 | 2168 | 2014-05-01 |  | 138 | 0 | 0 | 0 | 0 | ZAVALA |  | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | N
10TPIT0028 | Escondido to West Batesville, build 138 kV Line | West Batesville: Construct bundled 2x795 ACSR 138 kV line, add 138 kV circuit breaker and convert to 4 breaker ring bus |  | AEP GROUP 383 | AEP/ETT | Paul Hassink 918-599-2653 | 2169 | 2014-05-01 |  | 138 | 46.2 | 0 | 0 | 0 | MAVERICK | ZAVALA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | N
07TPIT0236 | N. Terrell Tap - Rose Hill 138 kV line | Rebuild existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3059-E | 2014-05-01 |  | 138 | 0 | 8.68 | 0 | 0 | KAUFMAN | KAUFMAN | Tier 4 |  |  |  | 2715, 2717, 2714, 2723, 2719 | Y
08TPIT0153 | Elkton - Athens North Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R651-E | 2014-05-01 |  | 138 | 0 | 29.1 | 0 | 0 | HENDERSON | HENDERSON | Tier 4 | 2007-11-26 |  |  | 3177, 3178, 3172, 3131 | Y
09TPIT0118 | Fisher Road - Wichita Falls 138 kV line | Upgrade existing 138 kV line. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R191-E | 2014-05-01 |  | 138 | 0 | 1.45 | 0 | 0 | WICHITA | WICHITA | Tier 4 |  |  |  | 1427, 1448 | Y
09TPIT0122 | Shamburger - Tyler NW 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6001-E | 2014-05-01 |  | 138 | 0 | 6.3 | 0 | 0 | SMITH | SMITH | Tier 4 |  |  |  | 3104, 3141 | Y | 2009-E6
10TPIT0017 | Allen Switch - Plano Custer - Collin Junction 138 kV line | Upgrade existing double-circuit 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3047-E | 2014-05-01 |  | 138 | 0 | 9 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 2509, 2525, 2510,2526,2524 | Y
14TPIT0010 | Handley - Pantego 138 kV line | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5155-E | 2014-05-01 |  | 138 | 0 | 3.8 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1950, 1951, 2247 | Y
14TPIT0011 | Midland East - Windwood 138 kV line | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8009-E | 2014-05-01 |  | 138 | 0 | 1.7 | 0 | 0 | MIDLAND | MIDLAND | Tier 4 |  |  |  | 1023, 1116 | Y
14TPIT0012 | Mountain Creek - Norwood 138 kV line | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4074-E | 2014-05-01 |  | 138 | 0 | 7.2 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2412, 2804, 2805, 2407 | Y
14TPIT0013 | Norwood - East Levee 138 kV line | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4073-E | 2014-05-01 |  | 138 | 0 | 6.6 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2481, 2405 | Y
14TPIT0014 | NW Carrollton - Lakepointe (TNMP) 138 kV line (Oncor Electric Delivery's section) | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5156-E | 2014-05-01 |  | 138 | 0 | 2.1 | 0 | 0 | DALLAS | DENTON | Tier 4 |  |  |  | 2362, 37010 | Y
14TPIT0015 | Troup - Walnut Grove - Whitehouse 138 kV line | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6002-E | 2014-05-01 |  | 138 | 0 | 9.8 | 0 | 0 | CHEROKEE | SMITH | Tier 4 |  |  |  | 3147, 3227, 3156 | Y
14TPIT0016 | West Mesquite - Prairie Creek 138 kV line | Upgrade existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4069-E | 2014-05-01 |  | 138 | 0 | 2.8 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2754, 2441 | Y | 2009-R19
11TPIT0097 | Norwood Switch autotransformer | Replace #1 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4070-E | 2014-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2405, 2406 | Y
12TPIT0080 | Forney Sw. Sta. Second 600 MVA, 345/138 kV Autotransformer | Add second 345/138 autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4037 | 2014-05-01 |  | 345 | 0 | 0 | 600 | 0 | KAUFMAN |  | Tier 4 | 2008-06-01 | 2008-07-01 |  | 2437, 2438 | Y | 2007-R2
07TPIT0073 | Venus - Webb 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5098-E | 2014-05-01 |  | 345 | 0 | 11.3 | 0 | 0 | ELLIS | DALLAS | Tier 4 |  |  |  | 1906, 1904 | Y
07TPIT0126 | Tricorner - Seagoville Switch 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4044-E | 2014-05-01 |  | 345 | 0 | 9.4 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2432, 2433 | Y
14TPIT0018 | Upgrade North Alvin-Hastings | This project will rebuild North Alvin to Hastings transmission line |  |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com |  | 2014-05-30 |  | 138 | 0 | 1.93 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 39010, 39015 | Y
07TPIT0078 | Devine to Lytle: Rebuild 69 kV Line | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | Schedule Update | AEP GROUP 028 | AEP/ETT | Brian Johnson 918-599-2653 | 1778 | 2014-05-31 |  | 69 | 0 | 7 | 0 | 0 | MEDINA | MEDINA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
07TPIT0077 | Big Foot to Devine: Rebuild 69 kV Line | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | Schedule Update | AEP GROUP 028 | AEP/ETT/TCC | Brian Johnson 918-599-2653 | 1777 | 2014-05-31 |  | 69 | 0 | 6.1 | 0 | 0 | FRIO | MEDINA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
14TPIT0033 | Muenster to Red River | Add 60 MVA 138/69 kV auto at Munester. Build 11 miles of 795 ACSR line to Red River. |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2014-06-01 |  | 69 | 11 | 0 | 60 | 0 | COOKE | COOKE | Tier 2 |  |  |  | 694, 694, 735 | Y
14TPIT0020 | Spencer Interchange to Pockrus 138kV Transmission Line New Construction | Construct 3.25 miles of new 138V transmission line | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | Not Assigned | 2014-06-01 |  | 138 | 3.25 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 982, 917 | N
14TPIT0003 | Ranchtown - New 138 kV Substation | Loop new 138kV substation into the existing 138kV Helotes to Menger Creek line |  | T-0175 | CPS | Blake Williams | S-0567 | 2014-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5200 5358 7663 | Y |  | There are no transformers associated with this project. There is no transmission line additions associated with this project
10TPIT0025 | Rinard Creek 138kV substation | Establish a new 138kV Rinard Creek substation with (2) 30MVA transformers. The substation will cut into existing Ckt 987 (Lytton Springs to Slaughter Lane). |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P151 PLAN_117_P152 | 2014-06-01 |  | 138 | 0.1 | 0 | 30 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9262 | Y
13TPIT0058 | Circuit 941 Summit - Williamson Reconductor | Reconductor the entire circuit from single 795 ACSR to 2000A bundle 795 ACSR conductor. |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_079 | 2014-06-01 |  | 138 | 0 | 3.54 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9279, 9295 | N |  | Will add the ptoject to the base case.
09TPIT0031 | Circuit 972 (McNeil to Howard Lane) Reconductor | Reconductor the last span of the Ckt 972 (McNeil to Howard Lane) going into McNeil substation with bundled 795 ACSR Drake conductor. |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P085 | 2014-06-01 |  | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9079, 9217 | Y
10TPIT0022 | Ckt 918 Oak Hill to Brodie Lane Reconductor | Reconductor the last span of the Ckt 918 going into Oak Hill sub with bundled 795 ACSR Drake capable of 2000 Amperes |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P080 | 2014-06-01 |  | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9169, 9247 | Y
14TPIT0030 | Bellaire - HO Clarke Ckt. 09 | Upgrade substation equipment to increase thermal ratings. |  | 14TPIT0002 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-06-01 |  | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47010, 47050, 47150 | Y |  | Identified as part of ERCOT RPG review of North to Houston Constraint Mitigation Project
14TPIT0031 | Cagnon - Install a Fourth 345kV Autotransformer | Install one 600 MVA autotransformer. |  | T-0176 | CPS | Blake Williams | S-0588 | 2014-06-01 |  | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5056 5055 | Y |  | There are no transmission line additions associated with this project
14TPIT0019 | Orange Grove Switch to Orange Grove Sub upgrade | Upgrade 0.21 miles of 69 kV circuit between Orange Grove Switch and Orange Grove Sub |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-06-14 |  | 69 | 0 | 0.21 | 0 | 0 | JIM WELLS | JIM WELLS | Tier 4 |  |  |  | 5658 - 5662 | Y
14TPIT0032 | Downing to Mountary | Existing 69 kV line. |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2014-06-15 |  | 69 | 0 | 14.64 | 0 | 0 | COMANCHE | COMANCHE | Tier 4 |  |  |  | 281, 294 | Y | 2009-R29
14TPIT0004 | Cushman-Highway 123 | Construct a new 6.2 mile single 795 ACSR 138 kV transmission line (rated 220 MVA) from the new Highway 123 substation (7221) located near the intersection of State Highway 123 and the GVEC Hickory Forest-New Berlin 138 kV (T–529) transmission line to the LCRA TSC Cushman substation. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2014-06-30 |  | 138 | 6.2 | 0 | 0 | 0 | GUADALUPE |  | Tier 2 | 2009-02-06 | 2009-06-01 | N/A | SEE PROJECT DESCRIPTION | Y
10TPIT0074 | Buttercup-Whitestone | Replace under-rated limiting line terminal equipment at Buttercup and Whitestone to increase Buttercup (7531)-Whitestone (7529) to the conductor's rating. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2014-06-30 |  | 138 | 0 | 0 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
05TPIT0065 | Highway 32-Wimberley | Construct a new 795 ACSR (220-MVA) 138-kV double circuit transmission line (approximately four miles) between the Highway 32(7546) and Wimberley(7496) substations. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2014-06-30 |  | 138 | 4 | 0 | 0 | 0 | HAYS | HAYS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | N
14TPIT0021 | Buttercup-Whitestone Upgrade | Upgrade the 2.3-mile Buttercup (7531)-Whitestone (7529) 795 ACSR (220-MVA) 138-kV transmission line to bundled 795 ACSR (440MVA). |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2014-06-30 |  | 138 | 0 | 2.3 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
14TPIT0022 | Sand Dollar 345 kV: Construct GIS 4 Breaker Ring Bus | Las Brisas Energy Center 1200 MW Generator Interconnect | Schedule Update | AEP GROUP 495 | AEP/ETT | Larry Roberson 918-599-2653 | 3388 | 2014-09-30 |  | 345 | 0 | 0 | 0 | 0 | NUECES |  | Tier 3 |  |  |  |  | Y
14TPIT0023 | Nopalito 345 kV: Construct GIS 5 Breaker Ring Bus | Las Brisas Energy Center 1200 MW Generator Interconnect | Schedule Update | AEP GROUP 495 | AEP/ETT | Larry Roberson 918-599-2653 | 3390 | 2014-09-30 |  | 345 | 0 | 0 | 0 | 0 | SAN PATRICIO |  | Tier 3 |  |  |  |  | Y
14TPIT0024 | Lon Hill to Sand Dollar 345 kV: Construct New 345 kV Transmission Line | Las Brisas Energy Center 1200 MW Generator Interconnect | Schedule Update | AEP GROUP 495 | AEP/ETT | Larry Roberson 918-599-2653 | 3389 | 2014-09-30 |  | 345 | 11.5 | 0 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y
14TPIT0025 | Nopalito to Sand Dollar 345 kV: Construct New 345 kV Transmission Line | Las Brisas Energy Center 1200 MW Generator Interconnect | Schedule Update | AEP GROUP 495 | AEP/ETT | Larry Roberson 918-599-2653 | 3391 | 2014-09-30 |  | 345 | 14.5 | 0 | 0 | 0 | NUECES | SAN PATRICIO | Tier 2 |  |  |  |  | Y
14TPIT0026 | Sand Dollar to Las Brisas Energy Center #1 345 kV: Construct New 345 kV Transmission Line | Las Brisas Energy Center 1200 MW Generator Interconnect | Schedule Update | AEP GROUP 495 | AEP/ETT | Larry Roberson 918-599-2653 | 3392 | 2014-09-30 |  | 345 | 2 | 0 | 0 | 0 | NUECES | NUECES | Tier 2 |  |  |  |  | Y
14TPIT0027 | Lon Hill to Whitepoint 345 kV Transmission Line: Hairpin into Nopalito | Las Brisas Energy Center 1200 MW Generator Interconnect | Schedule Update | AEP GROUP 495 | AEP/TCC | Larry Roberson 918-599-2653 | 3398 | 2014-09-30 |  | 345 | 0.1 | 0 | 0 | 0 | SAN PATRICIO |  | Tier 4 |  |  |  |  | Y
14TPIT0028 | Whitepoint to STP 345 kV Transmission Line: Hairpin into Nopalito | Las Brisas Energy Center 1200 MW Generator Interconnect | Schedule Update | AEP GROUP 495 | AEP/TCC | Larry Roberson 918-599-2653 | 3399 | 2014-09-30 |  | 345 | 0.1 | 0 | 0 | 0 | SAN PATRICIO |  | Tier 4 |  |  |  |  | Y
08TPIT0104 | Elgin Switching Station - Elgin 69 kV line conversion to 138 kV | Rebuild existing 69 kV line and convert to 138 kV operation |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R471-E | 2014-12-01 |  | 138 | 0 | 5.9 | 0 | 0 | WILLIAMSON | BASTROP | Tier 4 |  |  |  | 3655, 3650 | Y
12TPIT0025 | Refugio - Tatton: Rebuild Irreparable 69 kV Line | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. | Schedule Update | AEP GROUP 100 | AEP/TCC | Paul Hassink 918-599-2653 | 2027 | 2014-12-31 |  | 69 | 0 | 13.9 | 0 | 0 | REFUGIO | ARANSAS | Tier 4 |  |  |  |  | Y
10TPIT0063 | McQueeney(7605)-Geronimo(7604) 138 kV Line rebuild | Rebuild the existing 69-kV 4/0 transmission line to 138-kV 795 MCM between Geronimo and McQueeney substations on existing right-of-way, and loop-in CMC station. |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2014-12-31 |  | 138 | 0 | 5.5 | 0 | 0 | GUADALUPE | GUADALUPE | Tier 4 |  |  |  | See Project Title | N
14TPIT0006 | Mainland-New Substation | This project is to build a new distribution substation to serve the Mainland area for alleviating future loading from Lamarque, TX |  |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE03814 | 2014-12-31 |  | 138 | 0 | 0 | 0 | 0 | GALVESTON |  | Tier 4 |  |  |  | 39040 | Y
11TPIT0001 | Lobo to Rio Bravo, build 345 kV line energized at 138kV, and Rio Bravo Station Upgrades | Construct 345 kV line from Lobo to Rio Bravo and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer | PM update | AEP GROUP 206 | AEP/ETT | Bill Eakin 918-599-2653 | 880 | 2015-04-01 |  | 345 | 30 | 0 | 0 | 0 | WEBB | WEBB | Tier 1 |  |  |  |  | Y
11TPIT0015 | Sherry - Park Row - Grand Prairie 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5121-E | 2015-05-01 |  | 138 | 0 | 11.4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1919, 1920, 2257, 2258 | Y
11TPIT0050 | Roanoke Switch - Elizabeth Creek 138 kV line | Construct new line. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M509-E | 2015-05-01 |  | 138 | 3.75 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1850, 1852, 1866, 1867 | Y
11TPIT0034 | Sargent Road 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M486-E | 2015-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2946, 2949 | Y
14TPIT0000 | CSU Graham Rd Substation | Install (3) Breaker ring to include (2) 138 lines and tap to College Station Utilities |  |  | BTU/CSU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2015-05-06 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | N
14TPIT0002 | Zenith to Fayetteville 345kV Circuits | Build 345kV double circuit from Zenith to Fayetteville as part of North to Houston Constraint Mitigation Project. | Change in Project Sponsorship and Schedule |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 345 | 120 | 0 | 0 | 0 | HARRIS | FAYETTE | Tier 1 | 2009-07-01 | 2010-07-01 | 2010-08-01 | 44900, 7057 | Y |  | Part of North to Houston Constraint Mitigation Project
15TPIT0002 | Hickory Substation to Locust 69kV Transmission Line Reconstruction | Reconstruct 2.5 miles of existing 69V transmission line | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | Not Assigned | 2015-06-01 |  | 69 | 0 | 2.5 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 910, 914 | N
15TPIT0011 | Shannon to Montague | Rebuild Shannon to Montague 69 kV line with 959 ACSS. |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2015-06-01 |  | 69 | 0 | 23.36 | 0 | 0 | CLAY | MONTAGUE | Tier 4 |  |  |  | 772, 769, 768, 633 | Y
15TPIT0012 | Petteway to Ben Hur | Rebuild Petteway to Ben Hur 69 kV line with 795 ACSR |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2015-06-01 |  | 69 | 0 | 23.59 | 0 | 0 | ROBERTSON | LIMESTONE | Tier 4 |  |  |  | 93, 85, 99 | Y
15TPIT0013 | Seymour to Lake Kemp Switch | Rebuild Semour to Lake Kemp Switch 69 kV line with 795 ACSR |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2015-06-01 |  | 69 | 0 | 6.9 | 0 | 0 | BAYLOR | BAYLOR | Tier 4 |  |  |  | 779, 782 | Y
15TPIT0004 | Converse - New 138kV Substation | Loop new 138kV substation into existing 138kV Deely to Skyline line |  | T-0177 | CPS | Blake Williams | S-0601 | 2015-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5098 5110 5370 | Y |  | There are no transformers associated with this project
15TPIT0005 | Deely to Laredo - 138kV substation equipment upgrade | Upgrade substation equipment at Deely and Laredo to remove existing MLSE on the Deely to Laredo 138kV line |  |  | CPS | Blake Williams | S-0604 | 2015-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5210 5255 | Y |  | There are no transformers associated with this project
15TPIT0006 | Bandera to Broadview - 138kV substation equipment upgrade | Upgrade substation equipment at Broadview to remove existing MLSE on the Bandera to Broadview 138kV line |  |  | CPS | PM: Ulrich Skerhut | S-0603 | 2015-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5020 5040 | Y |  | There are no transformers associated with this project
15TPIT0007 | Green Mountain to Stonegate - 138kV 2nd Circuit | Build second 138kV transmission line from Green Mountain to Stonegate on existing transmission structures |  | S-0608 | CPS | Blake Williams | T-0179 | 2015-06-01 |  | 138 | 11.5 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5180 5415 | Y |  | There are no transformers associated with this project
07TPIT0060 | Howard Lane to Techridge Reconductor | The project calls for Circuit 1004 (Techridge to Howard Lane) to be reconductored using 795 ACSS Drake conductors to increase the capacity to 3000 Amp. |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P067 PLAN_117_P194 | 2015-06-01 |  | 138 | 0 | 1.72 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9190, 9217 | Y
15TPIT0010 | Howard Lane to Jollyville Reconductor | The project calls for Circuit 961 (Techridge to Howard Lane) to be reconductored using 795 ACSS Drake conductors to increase the capacity to 3000 Amp. | New Project |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P350 PLAN_117_P369 | 2015-06-01 |  | 138 | 0 | 1.72 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9217, 9223 | N |  | Will add to the models with idev files
08TPIT0033 | Gilleland to Techridge 138kV Circuit | Establish a new 138kV circuit from Gilleland to Techridge and maintain a normally close tie between AEN and LCRA's switchyard at Gilleland. |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_4276 PLAN_117_P207 | 2015-06-01 |  | 345 | 8 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 1 |  |  | 2004-12-01 | 9053, 9054 | Y
15TPIT0009 | Fayette Power Project-Fayetteville | Loop Fayette Power Project – Salem 345 kV line into Fayetteville and upgrade Fayette Power Project – Fayetteville 345 kV double circuit lines. | Date revised after ERCOT BOD approval | 14TPIT0002 | LCRA TSC | Brad Woods brad.woods@lcra.org 512 369 4104 |  | 2015-06-30 |  | 345 | 0 | 16.4 | 0 | 0 | FAYETTE | FAYETTE | Tier 1 | 2009-07-01 | 2010-07-27 | 2010-08-17 | 7056 | Y |  | Part of North to Houston Constraint Mitigation Project
15TPIT0003 | Sand Dollar to Las Brisas Energy Center #2 345 kV: Construct New 345 kV Transmission Line | Las Brisas Energy Center 1200 MW Generator Interconnect | Schedule Update | AEP GROUP 495 | AEP/ETT | Larry Roberson 918-599-2653 | 3393 | 2015-11-30 |  | 345 | 2 | 0 | 0 | 0 | NUECES | NUECES | Tier 2 |  |  |  |  | Y
15TPIT0008 | Triple R - New Substation | Build a 138-26.18 kV, 40 MVA substation on the GVEC Wilson - Sutherland Springs (T549) 138 kV transmission line |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2015-12-30 |  | 138 | 0 | 0 | 0 | 0 | WILSON |  | Tier 4 |  |  |  | See Project Title | N
13TPIT0065 | Upgrade PHRobison-South Shore 138kV Line | This project will rebuild 5.6 miles of 138 kV transmission line from Centerpoint's PH Robinson Substation to TNMP's South Shore Substation |  |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE08410 | 2015-12-31 |  | 138 | 0 | 5.6 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 38890, 42015 | Y
08TPIT0005 | Frontera, add SS with 345/138 kV autotransformer | Addition North Edinburg to Frontera to South McAllen 345 kV line with bundled 1590 ACSR conductor and double circuit capable structures and 345/138 kV substation at Frontera |  | AEP GROUP 065 | AEP/ETT | Paul Hassink 918-599-2653 | 1061 | 2016-03-31 |  | 345 | 0 | 0 | 675 | 0 | HIDALGO |  | Tier 1 |  |  |  |  | Y
11TPIT0002 | Sol to Rio Bravo, build 345 kV line | Construct 345 kV line from Rio Bravo to Sol to N Edinburg and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 065 | AEP/ETT | Paul Hassink 918-599-2653 | 630 | 2016-03-31 |  | 345 | 122.4 | 0 | 0 | 0 | WEBB | HIDALGO | Tier 1 |  |  |  |  | Y
11TPIT0003 | Rio Bravo, 345 kV SS with 345/138 kV autotransformer | Construct 345 kV line from Lobo to Rio Bravo and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 206 | AEP/ETT | Paul Hassink 918-599-2653 | 1309 | 2016-03-31 |  | 345 | 0 | 0 | 675 | 0 | WEBB |  | Tier 1 |  |  |  |  | Y
13TPIT0005 | Sol, Build 345 KV SS | Construct 345 kV line from Rio Bravo to Sol to N Edinburg and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 065 | AEP/ETT | Paul Hassink 918-599-2653 | 631 | 2016-03-31 |  | 345 | 0 | 0 | 0 | 0 | HIDALGO |  | Tier 1 |  |  |  |  | Y
13TPIT0006 | N. Edinburg to Sol: Build 345 KV Line | Construct 345 kV line from Rio Bravo to Sol to N Edinburg and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 065 | AEP/ETT | Paul Hassink 918-599-2653 | 3064 | 2016-03-31 |  | 345 | 15 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 1 |  |  |  |  | Y
13TPIT0007 | Frontera to Sol: Build 345 KV Line | Frontera to Sol: Build 12.4 Miles of 2-1590 ACSR double circuit 345 KV |  | AEP GROUP 065 | AEP/ETT | Paul Hassink 918-599-2653 | 288 | 2016-03-31 |  | 345 | 12.4 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 1 |  |  |  |  | Y
16TPIT0000 | Sol : Add 50% series cap compensation | Construct 345 kV line from Rio Bravo to Sol to N Edinburg and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 065 | AEP/ETT | Paul Hassink 918-599-2653 | 629 | 2016-03-31 |  | 345 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 1 |  |  |  |  | Y
07TPIT0069 | Sterrett - Sardis 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M361-E | 2016-05-01 |  | 138 | 0 | 1.95 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 2317, 203 | N
10TPIT0019 | Everman - Cleburne Switch 138 kV line sections | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3034-E | 2016-05-01 |  | 138 | 0 | 8.5 | 0 | 0 | TARRANT | JOHNSON | Tier 4 |  |  |  | 2279, 2210, 2209, 2208, 1883 | N
11TPIT0033 | Saginaw - American MFG Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5070-E | 2016-05-01 |  | 138 | 0 | 1.37 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2146, 1957 | N
16TPIT0002 | Barton - Oran 138 kV line series reactor | Install 9-ohm series reactor |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R565 | 2016-05-01 |  | 138 | 0 | 0 | 0 | 0 | Jack | Palo Pinto | Tier 4 |  |  |  | 1599, 1571 | N | 2007- E7d
07TPIT0234 | Collin Switch - NW. Carrollton 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3061-E | 2016-05-01 |  | 345 | 0 | 19.3 | 0 | 0 | COLLIN | DALLAS | Tier 4 | 2006-10-01 | 2007-02-01 | N/A | 2372, 2361 | N |  | The ERCOT Staff determined this project is not economically justified in their February 2007 study.
09TPIT0024 | Electra - KMA Tap 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R185-E | 2016-05-15 |  | 69 | 0 | 9.9 | 0 | 0 | WICHITA | WICHITA | Tier 4 |  |  |  | 1538, 1536 | N
07TPIT0014 | Plano West - Richardson Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M364-E | 2016-05-15 |  | 138 | 0 | 1.9 | 0 | 0 | COLLIN | DALLAS | Tier 4 |  |  |  | 2673, 2685 | N
12TPIT0002 | South McAllen 345 kV Station Upgrade and build 138kV line to South McAllen 138kV | Add Frontera to South McAllen 345 kV line with bundled 1590 ACSR and double circuit capable structures and 345/138 kV substations at Frontera and South McAllen |  | AEP GROUP 236 | AEP/ETT | Paul Hassink 918-599-2653 | 1276 | 2016-05-31 |  | 138 | 0 | 0.5 | 0 | 0 | HIDALGO |  | Tier 1 |  |  |  |  | Y
08TPIT0006 | South McAllen, new SS with 345/138 kV autotransformer | Add Frontera to South McAllen 345 kV line with bundled 1590 ACSR and double circuit capable structures and 345/138 kV substations at Frontera and South McAllen |  | AEP GROUP 236 | AEP/ETT | Paul Hassink 918-599-2653 | 293 | 2016-05-31 |  | 345 | 0 | 0 | 675 | 0 | HIDALGO |  | Tier 1 |  |  |  |  | Y
13TPIT0000 | Frontera to South McAllen, build 345 KV line | Add Frontera to South McAllen 345 kV line with bundled 1590 ACSR and double circuit capable structures and 345/138 kV substations at Frontera and South McAllen |  | AEP GROUP 236 | AEP/ETT | Paul Hassink 918-599-2653 | 292 | 2016-05-31 |  | 345 | 12.18 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 1 |  |  |  |  | Y
10TPIT0001 | Trumbo - New 138 kV Substation | Loop new 138 kV substation into the existing 138kV Leon Creek to Pleasanton Rd line | Accelarated by Disribution Planning | T-0082 | CPS | Blake Williams | S-0181 | 2016-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5429 | Y |  | There are no transformers associated with this project
11TPIT0011 | Northeast 138kV Substation | Establish a 138kV substation with (2) 30MVA transformers and 4 distribution circuits with underground get-a-ways. The station will cut into existing Gilleland - Techridge line. | Original Project title is "East Substation" |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P142 PLAN_117_P143 PLAN_117_P144 | 2016-06-01 |  | 138 | 0.1 | 0 | 60 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9195 | Y
11TPIT0008 | Rainey St 138kV substation | Establish a new 138kV Rainey St substation with (2) 50MVA transformers. The substation will cut into existing Ckt 1015 (Pedernales to Seaholm). |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P158 PLAN_117_P166 PLAN_117_P167 | 2016-06-01 |  | 138 | 0.1 | 0 | 100 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9261 | Y
11TPIT0017 | Wormser to Santa Nino: Reconductor 138 KV Line | Construct 345 kV line from Lobo to Rio Bravo and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer | Schedule update | AEP GROUP 206 | AEP/TCC | Paul Hassink 918-599-2653 | 2209 | 2016-06-01 |  | 138 | 0 | 3.25 | 0 | 0 | WEBB | WEBB | Tier 1 |  |  |  |  | Y
11TPIT0004 | Rio Bravo to Wormser, Reconductor 138 kV line | Construct 345 kV line from Lobo to Rio Bravo and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer | Schedule update | AEP GROUP 206 | AEP/TCC | Paul Hassink 918-599-2653 | 1305 | 2016-06-01 |  | 138 | 0 | 9.86 | 0 | 0 | WEBB | WEBB | Tier 1 |  |  |  |  | Y
15TPIT0000 | Bird Pond Substation | Install (3) Breaker ring to include (2) 138 lines and (1) 138/12.5 transformer |  |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2016-06-11 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | N
10TPIT0062 | Weil Road (Marion South) - New Substation | Build a 138-26.18 kV 40 MVA substation on the GVEC Marion(7178)-Cibolo(7608) 138 kV transmission line near the Marion Interchange |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2016-06-30 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N
09TPIT0047 | N. Waco - NE. Waco 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R477-E | 2017-05-01 |  | 138 | 0 | 1.9 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3551, 3552 | N
06TPIT0143 | Temple Switch - Temple SE 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R448-E | 2017-05-01 |  | 138 | 0 | 4.4 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3415, 3612, 3602, 3611 | N
08TPIT0109 | Payne - Collin Switching Station 138 kV line | Rebuild existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R519-E | 2017-05-01 |  | 138 | 0 | 31.75 | 0 | 0 | GRAYSON | COLLIN | Tier 3 | 2008-01-07 |  |  | 1758, 1757, 2350, 2366, 2349, 2364, 2370 | N | 2009-R12
10TPIT0053 | Kaufman South 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3064-E | 2017-05-01 |  | 138 | 0 | 0 | 0 | 55.2 | KAUFMAN |  | Tier 4 |  |  |  | 2728 | N
10TPIT0054 | Royse 138/69 kV autotransformer | Install larger autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3065-E | 2017-05-01 |  | 138 | 0 | 0 | 120 | 0 | ROCKWALL |  | Tier 4 |  |  |  | 2462, 2463 | N
00TPITno06 | Loma Alta - Ranchito or la Palma 345-kV line | Install 345-kV line from Loma Alta to La Palma or Ranchito |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2017-07-01 |  | 345 | 25 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 2 |  |  |  |  | N
00TPITno07 | Loma Alta - Rio Hondo 345-kV line | Install 345-kV line from Loma Alta to Rio Hondo |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2017-07-01 |  | 345 | 35 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 2 |  |  |  |  | N
00TPITno10 | Loma Alta 345kV station and autotransformer | Construct a 345 substation and connect to the existing Loma Alta 138 substation. |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2017-07-01 |  | 345 | 0 | 0 | 600 | 0 | CAMERON |  | Tier 4 |  |  |  |  | N
13TPIT0001 | Ranchito: Build 138 kV station with 138 KV Auto and Ring Bus | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/ETT | Paul Hassink 918-599-2653 | 1329 | 2017-12-01 |  | 138 | 0 | 0 | 187 | 0 | CAMERON |  | Tier 1 |  |  |  |  | Y
00TPITno15 | Ranchito, New SS with 345/138 kV autotransformer | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/ETT | Paul Hassink 918-599-2653 | 1059 | 2017-12-01 |  | 345 | 0 | 0 | 675 | 0 | CAMERON |  | Tier 1 |  |  |  |  | Y
11TPIT0036 | Caddo - New Substation | Construct a new 69-13.09x26.18-KV, 10 MVA substation |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2017-12-31 |  | 138 | 0 | 0 | 0 | 0 | WILSON |  | Tier 4 |  |  |  | See Project Title | N
00TPITno19 | Ranchito to South McAllen, new 345 kV line | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/ETT | Paul Hassink 918-599-2653 | 295 | 2017-12-31 |  | 345 | 38 | 0 | 0 | 0 | CAMERON | HIDALGO | Tier 1 |  |  |  |  | Y
13TPIT0002 | Villa Cavazos to Military Highway: Reconductor 138 KV Line | Construct 345 kV line from LaPalma to Villa Cavazos to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 1332 | 2018-03-31 |  | 138 | 0 | 10 | 0 | 0 | CAMERON | CAMERON | Tier 1 |  |  |  |  | Y
06TPIT0092 | Wichita Falls Switch - Wichita Falls Basin 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R168A-E | 2018-05-01 |  | 69 | 0 | 1 | 0 | 0 | ARCHER | WICHITA | Tier 4 |  |  |  | 1449, 1508 | N
08TPIT0110 | Temple - Little River 69 kV line | Rebuild existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R097-E | 2018-05-01 |  | 69 | 0 | 7.4 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3645, 3644 | N
09TPIT0068 | W. Weatherford - Weatherford 69 kV line | Rebuild existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R515-E | 2018-05-01 |  | 69 | 0 | 7.5 | 0 | 0 | PARKER | PARKER | Tier 4 |  |  |  | 1586, 1585 | N
12TPIT0003 | LaPalma to Villa Cavazos: Reconductor 138 KV Line | Construct 345 kV line from LaPalma to Villa Cavazos to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 1519 | 2018-05-01 |  | 138 | 0 | 10.5 | 0 | 0 | CAMERON | CAMERON | Tier 1 |  |  |  |  | Y
07TPIT0115 | Elgin Switch - Taylor 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R026-E | 2018-05-01 |  | 138 | 0 | 11.4 | 0 | 0 | BASTROP | BASTROP | Tier 4 |  |  |  | 3650, 3658 | N
08TPIT0069 | Lake Creek - East Waco 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R470-E | 2018-05-01 |  | 138 | 0 | 10.5 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3410, 3452, 3438 | N
14TPIT0029 | Lake Creek - Robinson 138 kV line | Rebuild 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R476 | 2018-05-01 |  | 138 | 0 | 8.3 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3410, 3567 | N | 2007-R8
06TPIT0036 | Ennis Switch - Ennis 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M280-E | 2018-05-01 |  | 138 | 0 | 6.32 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 2324, 2326 | N
06TPIT0042 | Lake Wichita Switch - Wichita Falls Switch 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R168-E | 2018-05-01 |  | 138 | 0 | 6.3 | 0 | 0 | ARCHER | WICHITA | Tier 4 |  |  |  | 1447, 1449 | N
06TPIT0047 | Elkton - Tyler West 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R323-E | 2018-05-01 |  | 138 | 0 | 4.98 | 0 | 0 | SMITH | SMITH | Tier 4 |  |  |  | 3106, 3139 | N
07TPIT0012 | Trinity Switch - Richland 138 kV line | Upgrade existing 138 kV line |  | M5014-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5069-E | 2018-05-01 |  | 138 | 0 | 0.5 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2096, 2100 | N
07TPIT0119 | Lavon Switch - Allen Switch 138 kV line | Create a new 138 kV line by reconfiguring existing lines and adding circuit to existing structures |  | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375B-E | 2018-05-01 |  | 138 | 8.9 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 2475, 2477, 2509 | N
07TPIT0122 | Royse - Dalrock 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3035-E | 2018-05-01 |  | 138 | 0 | 6.8 | 0 | 0 | ROCKWALL | ROCKWALL | Tier 4 |  |  |  | 2472, 2733, 2735 | N
07TPIT0138 | Oates (GPL) - Garland Bobtown Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M322-E | 2018-05-01 |  | 138 | 0 | 1.5 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 831, 2739 | N
08TPIT0007 | Austin Ranch - Hebron 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3002-E | 2018-05-01 |  | 138 | 0 | 0.7 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  | 2376, 2377 | N
08TPIT0111 | Lufkin Switching Station - Texas Foundries Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R389-E | 2018-05-01 |  | 138 | 0 | 0.73 | 0 | 0 | ANGELINA | ANGELINA | Tier 4 |  |  |  | 3326, 3327, 3328 | N
09TPIT0043 | Coppell - North Lake 138 kV line | Construct 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M549-E | 2018-05-01 |  | 138 | 4.8 | 0 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2015, 2386 | N
09TPIT0046 | N. Midlothian - Midlothian TXI Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3031-E | 2018-05-01 |  | 138 | 0 | 6.2 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 2310, 2311, 2313 | N
09TPIT0050 | Rowlett - Garland Bobtown Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3032-E | 2018-05-01 |  | 138 | 0 | 4.1 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2736, 2739 | N
09TPIT0051 | Salado Switch - Cedar Valley Switch (BEC) 138 kV line and switching stations | Establish two new 138 kV switching stations and connect them with a new 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R469-E | 2018-05-01 |  | 138 | 7 | 0 | 0 | 0 | BELL | BELL | Tier 2 |  |  |  | 117, 3640 | N
09TPIT0066 | Boggy Creek 138 kV Switching Station and associated line | Construct 138 kV switching station and add second circuit to a 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R488-E | 2018-05-01 |  | 138 | 3.5 | 0 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3424, 3415, 3425, 13645 | N
09TPIT0067 | Bonham Switching Station 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R516-E | 2018-05-01 |  | 138 | 0 | 0 | 100 | 0 | FANNIN |  | Tier 4 |  |  |  | 1760, 1761 | N
10TPIT0009 | Trinity Switch - Hurst 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5040-E | 2018-05-01 |  | 138 | 0 | 4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2096, 2115 | N
10TPIT0034 | Leon Switch #2 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R517-E | 2018-05-01 |  | 138 | 0 | 0 | 100 | 0 | EASTLAND |  | Tier 4 |  |  |  | 1624, 1626 | N
11TPIT0027 | East Richardson Switch - Ben Davis Switch (TMPA) 138 kV line | Create a new 138 kV line by reconfiguring existing lines |  | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375D-E | 2018-05-01 |  | 138 | 0 | 0 | 0 | 0 | COLLIN | DALLAS | Tier 4 |  |  |  | 968, 2690 | N
11TPIT0028 | Allen Switch - West Plano Switch 138 kV line | Create a new 138 kV line by reconfiguring existing lines and adding circuit to existing structures |  | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375C-E | 2018-05-01 |  | 138 | 3.5 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 2510, 2691, 2673 | N
00TPIT0004 | DeCordova - Benbrook 345 kV line upgrade | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5034-E | 2018-05-01 |  | 345 | 0 | 27 | 0 | 0 | HOOD | TARRANT | Tier 4 |  |  |  | 1873, 1890 | N
07TPIT0001 | Liggett - Trinity Switch 345 kV line | Construct Liggett - Trinity 345 kV line |  | M5014-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5015-E | 2018-05-01 |  | 345 | 12.8 | 0 | 0 | 0 | DALLAS | TARRANT | Tier 2 |  |  |  | 2095, 2097 | N
07TPIT0002 | Trinity Switch 345/138 kV autotransformer | Create Trinity Switch and install a 600 MVA 345/138 kV autotransformer |  | M5015-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5014-E | 2018-05-01 |  | 345 | 0 | 0 | 600 | 0 | TARRANT |  | Tier 4 |  |  |  | 2096, 2097 | N
07TPIT0118 | Lavon 345/138 kV Switching Station | Construct 345/138 kV switching station |  | M375B, M375C | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375A-E | 2018-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  | Tier 4 |  |  |  | 2475, 2476 | N
08TPIT0071 | North Lake 345/138 kV autotransformer | Install a 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3020-E | 2018-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2334, 2333 | N
00TPITno14 | LaPalma to Ranchito, new 345 kV line | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/ETT | Paul Hassink 918-599-2653 | 1060 | 2018-05-31 |  | 345 | 10 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 1 |  |  |  |  | Y
12TPIT0004 | Sulpher Springs - New 138kV Substation | Loop new 138kV substation into the existing 138kV OW Sommers to Kirby line |  |  | CPS | Blake Williams | S-0385 | 2018-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5416 | Y |  | There are no transformers associated with this project
18TPIT0000 | Ranchito to Villa Cavazos: Build Double circuit 138kV Line | Construct 345 kV line from LaPalma to Villa Cavazos to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/ETT | Paul Hassink 918-599-2653 | 1333 | 2018-06-01 |  | 138 | 5 | 0 | 0 | 0 | HIDALGO | CAMERON | Tier 1 |  |  |  |  | Y
11TPIT0037 | Santa Clara - New Substation | Build a new 138-26.18 kV 40 MVA substation on the GVEC McQueeney(7606)-Cibolo(7608) 138 kV transmission line |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2018-06-30 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N
18TPIT0001 | Wiederstein Substation | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2018-12-15 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N
13TPIT0062 | Cedar Hill Switch second 345/138 kV autotransformer | Install autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4071-E | 2019-05-01 |  | 345 | 0 | 0 | 504 | 0 | DALLAS |  | Tier 4 |  |  |  | 2420, 2422, 2421 | N
19TPIT0000 | Weser substation | Replace 5.6 MVA with 69-13.09 kV, 20 MVA transformer |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2019-06-15 |  | 69 | 0 | 0 | 0 | 0 | GOLIAD |  | Tier 4 |  |  |  | See Project Title | Y
20TPIT0000 | Parkway Substation | Replace T1, 20 MVA with a 40 MVA 138-13.09 kV transformer |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2020-05-15 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N
09TPIT0011 | Cagnon to Hill Country - 345kV 2nd Circuit | Build second 345 kV line from Cagnon to Hill Country. The circuit will be installed on existing transmission structures |  |  | CPS | Blake Williams | T-0053 | 2020-06-01 |  | 345 | 19.5 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5056 5211 | N |  | There are no transformers associated with this project
09TPIT0012 | Hill Country to Skyline - 345 kV 2nd Circuit | Build second 345 kV line from Hillcountry to Skyline. The second circuit will be installed on existing transmission structures |  |  | CPS | Blake Williams | T-0052 | 2020-06-01 |  | 345 | 11 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5211 5371 | N |  | There are no transformers associated with this project
12TPIT0006 | Olmos(7613) - New Substation | Build a 138-13.08 kV 22.4 MVA substation on the Olmos switching station site |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2020-11-30 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | Y
22TPIT0000 | Parkway Substation | Replace T2, 20 MVA with a 40 MVA 138-13.09 kV transformer |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2022-05-15 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N

## TPITCompletedNoCost12012010
DECEMBER BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) COMPLETED PROJECTS As Of 09/01/2010.
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Requested Additional Information (Optional) | Other (Optional)
09TPIT0033 | Gatesville to Fort Gates Switch Rebuild | Rebuild existiing Gatesville to Fort Gates Switch 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-06-01 | 2008-01-01 | 69 | 0 | 7.5 | 0 | 0 | CORYELL | CORYELL |  |  |  |  | 157250 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0182 | Hilltop Lakes to Petteway Rebuild | Rebuild the existing Hilltop Lakes Switch to Petteway 69KV line with 795 and 138KV construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-01-01 | 2008-01-01 | 69 | 0 | 8.28 | 0 | 0 | ROBERTSON | ROBERTSON |  |  |  |  | 43,93 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0256 | Bethel Capacitor Bank | Install 7.2 mvar of capacitors at Bethel |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-12-01 | 2008-01-01 | 69 | 0 | 0 | 0 | 7.2 | ELLIS | [5 empty] | 204 | Y |  | There are no circuit breakers, transmission line or transformer capacity associated with this project
08TPIT0064 | Hood to Decordova Rebuild | Rebuild existing Hood to Decordova 138kv line | Brazos to rebuild TXUED portion of line |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-01-01 | 138 | 0 | 2.2 | 0 | 0 | HOOD | HOOD |  |  |  |  | 2277363 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
12TPIT0001 | Texas Research Park - New Substation | Install new 138kV substation. May be part of T-0049 or T-0072. |  | S-0225 | CPS | PM: Janna Junkin 210-353-2524 | T-0072 | 2007-12-14 | 2008-01-09 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5430 | Y |  | There are no transformers associated with this project
08TPIT0170 | Jewett - Seaway Teague 138 kV line | Upgrade existing 138 kV line |  | R478A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R478-WACF | 2008-05-01 | 2008-01-16 | 138 | 0 | 10.75 | 0 | 0 | LEON | FREESTONE |  | 2007-02-13 | 2007-03-06 | N/A |  | Y
07TPIT0179 | Paducah: Add a 20 MVAR 138 KV Shunt Reactor | Replace 69/138 kV auto at Paducah with an 90 MVA 69/138 kV with LTC and add 20 MVAR 138 kV shunt reactor | IN-SERVICE | AEP GROUP 289 | AEP/TNC | Brett Madison 918-599-2653 | 1994 | 2008-01-18 | 2008-01-18 | 138 | 0 | 0 | 0 | -20 | COTTLE | [6 empty] | Y
08TPIT0144 | Glasscock Capacitor Bank Addition | Add a 138 kV 31.2 MVAR capacitor bank at Glasscock (7523). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2008-06-30 | 2008-01-24 | 138 | 0 | 0 | 0 | 31.2 | WILLIAMSON | [5 empty] | SEE PROJECT DESCRIPTION | Y
07TPIT0101 | Hi-Line to Stewart Rd tap, upgrade 69 kV line to 138 kV | Add Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Stewart Road 69 kV to 138 kV and convert Hidalgo and Dyer substations to 138 kV | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1791 | 2008-05-01 | 2008-01-25 | 69 | 0 | 3 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
05TPIT0075 | San Diego, add 69 kV breakers and 1 - 7.2 MVAR 69 kV cap | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2043 | 2007-11-30 | 2008-01-25 | 69 | 0 | 0 | 0 | 7.2 | JIM WELLS | [6 empty] | Y
06TPIT0059 | Stewart Road, build 138/69 kV SS with 2-28.8 MVar caps | Construct a new Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1318 | 2008-01-25 | 2008-01-25 | 138 | 0 | 0 | 93 | 57.6 | HIDALGO | [6 empty] | Y
06TPIT0120 | Stewart Rd to Hi-Line , build 138/69 kV double circuit line | Construct a new Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1319 | 2008-01-25 | 2008-01-25 | 138 | 3 | 0 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
07TPIT0127 | Bandera to Hamilton Wolfe to Med. Center - Reconductor | Reconductor existing 138 kV line with 1-1272 ACSR. Phase 1: Med. Center to Hamilton Wolfe (Dec 07) Phase 2: Bandera to Hamilton Wolfe (Feb 08) | Distribution Conflicts & Budget Delays | T-0084 | CPS | PM: Ulrich Skerhut 210-353-2923 | T-0084 | 2008-02-08 | 2008-02-08 | 138 | 0 | 1.7 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5020 5300 5187 | Y |  | There are no transformers associated with this project
06TPIT0170 | College Station Post Oak Substation to Southwood Valley Substation Line Reconducter | Reconducter College Station Post Oak substation to Southwood Valley Substation with 1033 ACSS | Material Deliveries |  | COCS | Garry Lange 979 764 3682 glange@cstx.gov |  | 2008-02-08 | 2008-02-08 | 138 | 0 | 3 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | Y |  | Transmission Rebuilt on Line
05TPIT0256 | College Station Switch Station to Post Oak Substation Line Reconducter | Reconductor College Station Switch Station to Post Oak Station with 1033 ACSS | Material Deliveries |  | COCS | Garry Lange 979 764 3682 glange@cstx.gov |  | 2008-02-07 | 2008-02-08 | 138 | 0 | 1.7 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | Y |  | Transmission Rebuilt on Line
08TPIT0161 | Tomball - Tomball Distribution Tap ckt.81 | Verified equipment rating at Tomball to increase emergency rating. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2008-05-31 | 2008-02-15 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46510, 46512 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
05TPIT0077 | North Padre to Mustang Island, rebuild 69 kV line | Rebuild North Padre (8856) to Port Aransas (8436) 69 kV transmission line from 4/0 ACSR to 795 ACSS |  | AEP GROUP 029 | LCRA TSC / AEP | Brad Woods (512) 369-4104 brad.woods@lcra.org | 140, LCRA#1003910 | 2008-02-25 | 2008-02-25 | 69 | 0 | 6.7 | 0 | 0 | NUECES | NUECES |  |  |  |  | SEE PROJECT DESCRIPTION | Y
07TPIT0155 | Putnam, Add 138 kV phase shift transformer | Putnam, Add 138 kV phase shift transformer on the Abilene South to Putnam 138 kV line | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Dave Goetz 918-599-2653 | 2148 | 2008-03-10 | 2008-02-28 | 138 | 0 | 0 | 150 | 0 | CALLAHAN | [6 empty] | Y
06TPIT0104 | Convert Circuit 822 (Burleson to Cardinal Lane) and 824 (Cardinal Lane to Seaholm) from 69kV to 138kV. | Convert the 69kV circuit 822 (Burleson to Cardinal Lane) and Circuit 824 (Cardinal Lane to Seaholm) to 138kV capable of carrying at least 3000 Amps. | The reconductoring of both Circuit 822 and 824 is now complete. They will still operate at the 69kV level and switch to 138kV after the new Cardinal Lane substation completion in June 2008. |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | 3230_117_4268 3230_117_4269 3230_117_4274 3230_117_4275 | 2008-02-08 | 2008-03-01 | 138 | 0 | 5.7 | 0 | 0 | TRAVIS | TRAVIS |  |  |  |  | 9120,9179,9299, 9132 | Y
08TPIT0016 | Covington to Grandview Upgrade or Rebuild | Rebuild Covington to Grandview |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-03-01 | 138 | 0 | 9.9 | 0 | 0 | JOHNSON | JOHNSON |  |  |  |  | 444443436 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0187 | Olefin Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R684-WACF - R686-WACF | 2008-05-01 | 2008-03-05 | 138 | 0 | 0 | 0 | 0 | ECTOR | [6 empty] | Y
08TPIT0036 | Austrop to Decker Reconductor Last Three Spans of the circuit. | Reconductor the remaining three spans of Circuit 921 (Austrop to Decker) coming into the Decker Plant switchyard with triple bundle 795 ACSR Drake conductors. | Comments: The three spans have been replaced but the rerating will not be done until the breakers are changed out before Summer 2009. |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | PLAN_117_P003 | 2008-03-01 | 2008-03-08 | 138 | 0 | 0.58 | 0 | 0 | TRAVIS | TRAVIS |  |  |  |  | 9187, 7328 | Y
00TPITno00 | Airport - Waterport 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-03-09 | 2008-03-09 | 138 | 0 | 8.8 | 0 | 0 | CAMERON | [5 empty] | 59460, 59450 | Y
00TPITno18 | Waterport 138-kV Substation | Convert Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-03-09 | 2008-03-09 | 138 | 0 | 0 | 28 | 0 | CAMERON | [5 empty] | 59450 | Y |  | `
07TPIT0105 | Airport Substation138-kV Substation | Convert Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-03-09 | 2008-03-09 | 138 | 0 | 0 | 28 | 0 | CAMERON | [5 empty] | 59460 | Y |  | The existing 138/69-kV and a 69/12.5-kV transformers will remain.
07TPIT0114 | E. Mesquite - W. Mesquite 138 kV line | Upgrade existing 138 kV line |  | M4038 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4041-WACF | 2008-04-30 | 2008-03-14 | 138 | 0 | 2.7 | 0 | 0 | DALLAS | DALLAS |  |  |  |  | 2754, 2756 | Y
08TPIT0099 | Sandow Switch circuit breaker installation | Install 138 kV circuit breakers and terminate existing 138 kV lines |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R701-WACF | 2008-11-01 | 2008-03-17 | 138 | 0 | 0 | 0 | 0 | MILAM | [5 empty] | 13431, 13432, 13430, 13429 | Y
08TPIT0201 | Disconnect and remove Simson 69kV Substation from CenterPoint Energy's system. | Disconnected and removed customer owned Simson substation from CNP's ckt.23 Deepwater - S.R. Bertron. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-03-15 | 2008-03-18 | 69 | 0.02 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40470, 41460,41415 | Y |  | 1)_No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. 2)_PSS/E bus #41460 will be removed from the base cases.
08TPIT0194 | Lane City: Upgrade Series Reactor to 2000 Amps | Upgrade Lane City substation bus and series reactors | IN-SERVICE | AEP GROUP 387 | AEP/TCC | Dave Goetz 918-599-2653 | 2234 | 2008-03-08 | 2008-03-24 | 138 | 0 | 0 | 0 | 0 | WHARTON | [6 empty] | Y
07TPIT0117 | Seaway Teague - W. Fairfield 138 kV line | Upgrade existing 138 kV line |  | R478 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R478A-WACF | 2008-05-15 | 2008-03-25 | 138 | 0 | 13 | 0 | 0 | FREESTONE | FREESTONE |  | 2007-02-13 | 2007-03-06 | N/A | 3392, 3501, 3503 | Y
08TPIT0159 | Satsuma - Gertie ckt.76 | Verified conductors clearance to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2008-05-31 | 2008-03-26 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46302, 45802 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
08TPIT0181 | Gail Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R801-WACF & R804-WACF | 2008-05-01 | 2008-03-29 | 138 | 0 | 0 | 0 | 0 | BORDEN | [6 empty] | Y
07TPIT0085 | Hi-Line to Hidalgo, upgrade 69 kV line to 138 kV | Add Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Stewart Road 69 kV to 138 kV and convert Hidalgo and Dyer substations to 138 kV | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1792 | 2008-03-31 | 2008-03-31 | 69 | 0 | 2 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
08TPIT0113 | Flatonia Autotransformer Addition | Add a new 138-69 kV 45 MVA autotransformer at the Flatonia substation (7248). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2008-06-30 | 2008-03-31 | 138 | 0 | 0 | 30 | 0 | FAYETTE | [5 empty] | SEE PROJECT DESCRIPTION | Y
09TPIT0040 | Jack Creek Sub: new 345 sub near Kurten | New 345 KV sub with one 600 MVA 345-138 autotransformer | On Schedule |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T06012 | 2008-05-07 | 2008-03-31 | 345 | 0 | 0 | 600 | 0 | BRAZOS |  |  | 2005-09-01 | 2005-11-01 | 2006-01-01 | ? | Y
09TPIT0017 | Pancake to Gatesville Rebuild | Rebuild existing Pancake to Gatesville with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-06-01 | 2008-04-01 | 69 | 0 | 4 | 0 | 0 | CORYELL | CORYELL |  |  |  |  | 157158 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0039 | Hasse to Downing Upgrade/Rebuild | Rebuild or Upgrade existing Hasse to Downing line with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-04-01 | 69 | 0 | 7.3 | 0 | 0 | COMANCHE | COMANCHE |  |  |  |  | 277281 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0199 | Capote Substation (7598)- Convert to 138 kV Operation | 138 kV conversion involves switching, relocation of jumpers and other minor work. |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2008-04-01 | 2008-04-01 | 138 | 0 | 0 | 0 | 0 | GUADALUPE | [5 empty] | See Project Title | Y
10TPIT0014 | Olney Auto | Increase 138/69 autotransformer capacity at Olney |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 | 2008-04-01 | 138 | 0 | 0 | 0 | 0 | YOUNT | [5 empty] | 788787 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
09TPIT0034 | Bunker to Hood Rebuild | Rebuild existing Bunker to Hood 138kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-06-01 | 2008-04-01 | 138 | 0 | 9.1 | 0 | 0 | HOOD | HOOD |  |  |  |  | 363352306 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0180 | Exxon Sharon Ridge Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R802-WA & R803-WA | 2008-05-01 | 2008-04-01 | 138 | 0 | 0 | 0 | 0 | SCURRY | [6 empty] | Y
07TPIT0121 | Morgan Creek 345/138 kV autotransformer | Install third 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R608-WACF | 2007-12-01 | 2008-04-01 | 345 | 0 | 0 | 300 | 0 | MITCHELL |  |  | 2006-09-20 | 2006-10-18 | N/A | 1030, 1032 | Y
08TPIT0197 | Reconfigure ckt.03 EXXON - S.R. Bertron and ckt.88 Baytown - Rohmas substation. | Reconfigured ckt.03 EXXON - S.R. Bertron and ckt.88 Baytown - Rohmas substation to create two new circuits ckt.03 EXXON - Baytown and ckt.88 S.R. Bertron - Rohmas to ensure reliable service to the customers in the Baytown area. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-04-10 | 2008-04-03 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40570, 40170, 41405, 41350 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
08TPIT0183 | Key Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R698-WACF & R805-WACF | 2008-05-01 | 2008-04-05 | 138 | 0 | 0 | 0 | 0 | DAWSON | [6 empty] | Y
08TPIT0189 | Benbrook Switch terminal equipment upgrade | Upgrade 345 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5120-WACF | 2008-05-01 | 2008-04-07 | 345 | 0 | 0 | 0 | 0 | TARRANT | [6 empty] | Y
08TPIT0100 | Twin Oak circuit breakers | Install 345 kV circuit breakers to connect a new power plant |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R498-WACF | 2008-06-01 | 2008-04-08 | 345 | 0 | 0 | 0 | 0 | ROBERTSON | [5 empty] | 3400, 13691, 13692 | Y
09TPIT0089 | Waterport - Loma Alta 138-kV Circuit | Add a new 138-kV circuit to Loma Alta Substation |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-04-11 | 2008-04-11 | 138 | 0 | 4.29 | 0 | 0 | CAMERON | [5 empty] | 59450, 5962 | Y
07TPIT0154 | Putnam, Replace existing 69/138 kV Autotransformer | Putnam, replace 69/138 kV Autotransformer with 90 MVA | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Dave Goetz 918-599-2653 | 2147 | 2008-04-30 | 2008-04-11 | 138 | 0 | 0 | 90 | 0 | CALLAHAN | [6 empty] | Y
08TPIT0143 | Lampasas-Adamsville-Evant | Upgrade the Lampasas(7064)-Adamsville(7066)-Evant(7068) 138 kV transmission line (T-128) from 4/0 ACSR (84 MVA) to 795 ACSR (220 MVA |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2008-06-30 | 2008-04-15 | 138 | 0 | 26 | 0 | 0 | LAMPASAS | CORYELL |  | 2007-02-19 | 2007-03-12 | N/A | SEE PROJECT DESCRIPTION | Y
08TPIT0046 | Nolanville - Harker Heights 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R050-WACF | 2008-05-15 | 2008-04-15 | 138 | 0 | 7 | 0 | 0 | BELL | BELL |  |  |  |  | 3617, 3618 | Y
06TPIT0110 | Hidalgo to S McAllen, upgrade 69 kV line | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substatio | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1315 | 2008-06-30 | 2008-04-18 | 138 | 0 | 3.7 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
06TPIT0132 | Hidalgo, upgrade 2 transformers & distribution equipment | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1707 | 2008-05-31 | 2008-04-18 | 138 | 0 | 0 | 0 | 0 | HIDALGO | [6 empty] | Y
04TPIT0148 | Walnut-Fairdale 69 kV line | Line upgrade |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-04-30 | 2008-04-30 | 69 | 0 | 2 | 0 | 0 | DALLAS | [5 empty] | 823, 803 | Y
08TPIT0141 | Manvel | Installed new 69kV 7.2 MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-05-31 | 2008-04-30 | 69 | 0 | 0 | 0 | 7.2 | BRAZORIA | BRAZORIA |  |  |  |  | 44440 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
06TPIT0099 | Fairdale load 69 kV to 138 kV voltage conversion | Converts voltage for its load |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-04-30 | 2008-04-30 | 138 | 0 | 0 | 0 | 0 | DALLAS | [5 empty] | 803 | Y
08TPIT0017 | Olney to Shannon Rebuild | Rebuild the existing Olney to Shannon 69KV line with 795 138KV construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-05-01 | 69 | 0 | 28.5 | 0 | 0 | YOUNG | CLAY |  |  |  |  | 788776772 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0185 | Leon Switch terminal equipment upgrade | Upgrade 69 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R541-E | 2008-05-01 | 2008-05-01 | 69 | 0 | 0 | 0 | 0 | EASTLAND | [6 empty] | Y
07TPIT0139 | Temple Pecan Creek - Lake Creek 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R408A-WACF | 2008-06-01 | 2008-05-01 | 138 | 0 | 28.5 | 0 | 0 | BELL | MCLENNAN |  | 2007-04-23 | 2007-05-21 | N/A | 3410, 3420 | Y
07TPIT0241 | Drumright 138 kV Switching Station | Construct 138 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R671-WACF | 2008-05-31 | 2008-05-01 | 138 | 0 | 0 | 0 | 0 | GLASSCOCK | [5 empty] | 1335, 1336, 1331, 1328 | Y
08TPIT0178 | China Grove Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R687-WACF to R690-WACF | 2008-05-01 | 2008-05-01 | 138 | 0 | 0 | 0 | 0 | MITCHELL | [6 empty] | Y
06TPIT0054 | Rangerville, add 7.2 Mvar cap | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1324 | 2008-05-08 | 2008-05-08 | 69 | 0 | 0 | 0 | 7.2 | CAMERON | [6 empty] | Y
06TPIT0144 | Add dynamic reactive device Phase 1 | Added dynamic reactive device at Bellaire South 138 kV bus | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-06-30 | 2008-05-12 | 138 | 0 | 0 | 0 | 140 | HARRIS | HARRIS |  | 2006-03-08 | 2006-07-12 | 2006-08-30 | 47016 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. IDEV reflects addition of the SVC model.
09TPIT0028 | Goldthwaite | Upgrade the 138-69 kV 25 MVA auto-transformer (T1) at the Goldthwaite substation(7070) to 45 MVA. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org | Not yet assigned | 2008-06-29 | 2008-05-13 | 138 | 0 | 0 | 45 | 0 | MILLS | [5 empty] | SEE PROJECT DESCRIPTION | Y
08TPIT0139 | Longshore 345 kV Switching Station | Construct 345 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R682-WACF | 2008-05-15 | 2008-05-14 | 345 | 0 | 0.22 | 0 | 0 | HOWARD | [5 empty] | 1030, 1058, 1029 | Y
07TPIT0174 | Morris 138 kV, add 1-28.8 MVAR Cap Bank | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2040 | 2008-05-15 | 2008-05-15 | 138 | 0 | 0 | 0 | 28.8 | Val VERDE | Val VERDE | [5 empty] | Y
06TPIT0228 | Athens load conversion and second 138 kV line | Convert load to 138 kV service and add second 138 kV source |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R369-WAC | 2008-05-01 | 2008-05-15 | 138 | 2 | 0 | 0 | 0 | HENDERSON | HENDERSON |  |  |  |  | 3239, 3238 | Y
06TPIT0050 | Cagnon to Lytle - New 138 kV line | Build new 138 kV line from Cagnon to Lytle. This project has been broken out into 3 phases. Phase 1: Cagnon - TX Research (Dec07) Phase 2: TX Research - Lytle (May08) | 12 Step Public Review Caused Delay of Start | T-0072 | CPS | PM: Ulrich Skerhut 210-353-2923 | T-0011 | 2008-05-15 | 2008-05-16 | 138 | 21.7 | 0 | 0 | 0 | BEXAR | MEDINA |  |  |  |  | 5055 5083 5290 | Y |  | There are no transformers associated with this project
08TPIT0186 | Mustang Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R699-WACF | 2008-05-01 | 2008-05-16 | 138 | 0 | 0 | 0 | 0 | ANDREWS | [6 empty] | Y
06TPIT0245 | Bluff Creek, Install 1 - 57.6 Mvar Cap Bank | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Ashley Beasley 918-599-2653 | 2125 | 2008-05-15 | 2008-05-20 | 138 | 0 | 0 | 0 | 57.6 | TAYLOR | [6 empty] | Y
08TPIT0188 | Paul Davis Tap terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R695-WACF & R800-WACF | 2008-05-01 | 2008-05-20 | 138 | 0 | 0 | 0 | 0 | DAWSON | [6 empty] | Y
08TPIT0182 | Graham Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R542-WACF | 2008-05-01 | 2008-05-21 | 138 | 0 | 0 | 0 | 0 | YOUNG | [6 empty] | Y
07TPIT0075 | Add dynamic reactive device Phase 2 | Added dynamic reactive device at Crosby 138 kV bus | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-06-30 | 2008-05-23 | 138 | 0 | 0 | 0 | 140 | HARRIS | HARRIS |  | 2006-03-08 | 2006-07-12 | 2006-08-30 | 40392 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. IDEV reflects addition of the SVC model.
06TPIT0024 | Seaton - Poage 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R045-WACF | 2008-05-15 | 2008-05-30 | 69 | 0 | 11.9 | 0 | 0 | BELL | BELL |  |  |  |  | 131, 3635 | Y
06TPIT0095 | Walnut-Fairdale line 69 kV to 138 kV voltage conversion | Converts voltage for the line |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-05-30 | 2008-05-30 | 138 | 0 | 1.92 | 0 | 0 | DALLAS | [5 empty] | 823, 803 | Y
07TPIT0162 | S.R. Bertron - Fairmont ckt.06 | Raised conductors and partially reconductored ckt.06 to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-05-31 | 2008-05-30 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 41400, 41310, 41631, 42610 | Y |  | No transformer capacity to be added.
05TPIT0143 | Weslaco SS, add 2-43.2 MVAR capacitor, cut-in Pharr to Harlingen SS 138 kV Line | Install capacitor banks at various locations in the East Valley area | IN-SERVICE | AEP GROUP 293 | AEP/TCC | Rich Haley 918-599-2653 | 1648 | 2008-09-30 | 2008-05-30 | 138 | 0 | 0 | 0 | 86.4 | CAMERON | [6 empty] | Y
08TPIT0191 | Olmito, Construct 138 kV Distribution Substation | Olmito: Construct a new substation with cut-in, between Military Highway and Palo Alto 138kV line | IN-SERVICE | AEP GROUP 255 | AEP/TCC | Rich Haley 918-599-2653 |  | 2008-08-29 | 2008-05-30 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
08TPIT0192 | Military Highway to Palo Alto 138kV line, cut-in Olmito at 138kV | Olmito: Construct a new substation with cut-in, between Military Highway and Palo Alto 138kV line | IN-SERVICE | AEP GROUP 255 | AEP/TCC | Rich Haley 918-599-2653 |  | 2008-08-29 | 2008-05-30 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
07TPIT0247 | Hillje 69 kV Substation | Construct Hillje Substation in the 69 kV line between Round Mott Switch and Louise. | IN-SERVICE |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2008-05-31 | 2008-05-31 | 69 | 0 | 0 | 0 | 0 | WHARTON |  |  | N/A |  |  | 5532 | Y
06TPIT0097 | Walnut 69 kV to 138 kV voltage conversion | Converts voltage for the substation |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-05-31 | 2008-05-31 | 138 | 0 | 0 | 0 | 0 | DALLAS | [5 empty] | 823 | Y
05TPIT0021 | Copperas Cove - Ding Dong (BEC) 138 kV line (Oncor Electric Delivery portion) | Construct 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R036A-WAC | 2008-07-01 | 2008-06-01 | 138 | 15.7 | 0 | 0 | 0 | CORYELL | BELL |  |  |  |  | 3630, 115, 3628, 3630 | Y
08TPIT0148 | Eskota Switching Station | Install 138 kV breaker to connect new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R806-WACF | 2008-07-01 | 2008-06-01 | 138 | 0 | 0 | 0 | 0 | HOWARD | [5 empty] | 1030, 1058, 1029 | Y
07TPIT0135 | Abilene Elm Creek to Abilene Shelton Street, Rebuild 69 kV line | Re-build 2.62 miles Abilene Elm Creek to Shelton 69 kV line @ 795 ACSS | IN-SERVICE | AEP GROUP 341 | AEP/TNC | John Pulay 918-599-2653 | 1989 | 2008-06-30 | 2008-06-02 | 69 | 0 | 2.62 | 0 | 0 | TAYLOR | TAYLOR | [5 empty] | Y
08TPIT0198 | Praxair Texas City #2 Station- TNMP 69-A Tap | TNMP will tap its existing 69kV line along SH146 to provide service to Praxair Texas City #2 Station | Line construction has been completed. Working on SCADA and Meter install. |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com |  | 2008-05-08 | 2008-06-08 | 69 | 0 | 0 | 60 | 0 | GALVESTON | GALVESTON |  |  |  |  | 39345, 39346 | Y
07TPIT0261 | County Rd 101 | Build 1.23 miles of 138 kV for retail service | Customer will be ready to take power on Oct-08 |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com |  | 2008-10-01 | 2008-06-08 | 138 | 1.23 | 0 | 0 | 0 | REEVES | REEVES |  |  |  |  | 6657, 38375 | Y
09TPIT0078 | Loma Alta 138-kV Substation | Facilitate substation for a new 138/12.5-kV transformer | The Load has been installed instead on the 69-kV Bus. The substation upgrade to 138kV portion was part of another project. |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-06-02 | 2008-06-09 | 138 | 0 | 0 | 28 | 0 | CAMERON | [5 empty] | 5943 | Y
08TPIT0195 | Bandera - Add 69kV Breaker | Add 69kV Breaker to Bandera 69kV Bus |  |  | Bandera Electric | Brian Bartos | 115770 | 2008-06-08 | 2008-06-11 | 69 | 0 | 0 | 0 | 0 | BANDERA | BANDERA | [5 empty] | Y
08TPIT0119 | East Bernard - Orchard - Fort Bend ckt.60 | Reconductored 138kV ckt.60 East Bernard to Fort Bend and upgraded substations limiting equipment to increase thermal ratings. | IN-SERVICE |  | CNP | Danh Huynh; Dhuynh@garlandpower-light.org |  | 2008-06-30 | 2008-06-24 | 138 | 0 | 18.33 | 0 | 0 | WHARTON | FORT BEND |  |  |  |  | 44190, 44540, 44300 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added.
06TPIT0015 | Airline to Naval Base, rebuild 69 kV Line | Rebuild Airline to Naval Base 69 kV transmission line from 477 MCM to 795 ACSR |  | AEP GROUP 029 | LCRA TSC / AEP | Danh Huynh; Dhuynh@garlandpower-light.org | 3, LCRA#1003909 | 2008-06-15 | 2008-06-27 | 69 | 0 | 8 | 0 | 0 | NUECES | NUECES | [5 empty] | Y
05TPIT0044 | Asherton, add 14.4 MVAR cap on 138kV & 1-14.4 MVAR Cap on 69 kV | Install a 150 MVA PST at North Laredo substation with capacitors at Asherton and North Laredo. | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Danh Huynh; Dhuynh@garlandpower-light.org | 1451 | 2008-05-08 | 2008-06-30 | 138 | 0 | 0 | 0 | 28.8 | DIMMIT | [6 empty] | Y
07TPIT0065 | Gainesville - Muenster 69 kV line and Muenster 69 kV capacitors | Upgrade existing 69 kV line and install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R186-WACF | 2008-08-15 | 2008-07-01 | 69 | 0 | 13.84 | 0 | 18.4 | COOKE | MONTAGUE |  |  |  |  | 1709, 1712, 1716 | Y
08TPIT0166 | Texas City 69F Reroute | Reroute 1.4 miles of 69 kV transmission line to outside of BP's Texas City Refinery | Construction has started for this project |  | TNMP | Danh Huynh; Dhuynh@garlandpower-light.org |  | 2008-07-08 | 2008-07-08 | 69 | 0 | 1.4 | 0 | 0 | GALVESTON | GALVESTON | [5 empty] | Y
06TPIT0165 | MVEC W. Edinburg-MVEC Palmhurst | Rebuild 138kV line from W. Edinburg to Palmhurst Substations | Material Issues | 04TPTI0025 | STEC | Doug Evans 361-485-6459 devans@stec.org | 791294 | 2008-12-08 | 2008-07-08 | 138 | 0 | 3.5 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
08TPIT0208 | TXDOT FM88 | Relocate 138kV line from MVEC Weslaco to AEP Weslaco Switch |  | 08TPIT0207 | STEC | Doug Evans 361-485-6459 devans@stec.org | 1189902 | 2008-09-08 | 2008-07-08 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | N |  | TXDOT Project to relocate line due to road widening. The line did not change.
07TPIT0195 | Texas Gulf-New Gulf tap ckt.04 | Verified conductors clearance to increase thermal ratings. | IN-SERVICE |  | CNP | Danh Huynh; Dhuynh@garlandpower-light.org |  | 2008-12-01 | 2008-07-15 | 138 | 0 | 0 | 0 | 0 | WHARTON | WHARTON |  |  |  |  | 43340, 43011 | Y |  | 1) No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. 2) IDEV reflects change in project in-service date.
08TPIT0118 | South Lane City - New Gulf tap - Texas Gulf ckt.60 | Raised conductors to increase thermal ratings to 90/120deg C. | IN-SERVICE |  | CNP | Danh Huynh; Dhuynh@garlandpower-light.org |  | 2008-07-30 | 2008-07-15 | 138 | 0 | 10.56 | 0 | 0 | WHARTON | WHARTON |  |  |  |  | 43190, 43012, 43340 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
08TPIT0160 | Greens Bayou - Normandy Tap ckt.77 | Verified conductors clearance to increase thermal ratings. | IN-SERVICE |  | CNP | Danh Huynh; Dhuynh@garlandpower-light.org |  | 2008-07-30 | 2008-07-30 | 138 | 0 | 8.95 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40716, 41171 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
08TPIT0114 | Plastipak 138 kV new substation | New load serving |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-07-31 | 2008-07-31 | 138 | 0 | 0 | 0 | 0 | DALLAS | [5 empty] | 808 | Y
08TPIT0115 | Plastipak-Fairdale 138 kV line | Line upgrade |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-07-31 | 2008-07-31 | 138 | 0 | 1.5 | 0 | 0 | DALLAS | [5 empty] | 808, 805 | Y
06TPIT0018 | Maypearl 69 kV capacitor | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R423-WACF | 2008-08-15 | 2008-08-01 | 69 | 0 | 0 | 0 | 27.6 | ELLIS | [5 empty] | 3536 | Y
08TPIT0089 | Mill Creek - Gay Hill | Increase the line-to-ground clearance on the Mill Creek (7565) - Gay Hill (7572) 138 kV transmission line as necessary to increase the capacity of this circuit to its full conductor rating of 128 MVA. |  |  | BBEC | Eric Kocian (979) 542-4150 eric.kocian@bluebonnet.coop |  | 2008-08-02 | 2008-08-02 | 138 | 0 | 9.1 | 0 | 0 | WASHINGTON | WASHINGTON |  |  |  |  | SEE PROJECT DESCRIPTION | Y | SEE PROJECT DESCRIPTION
08TPIT0177 | Keller Wall Price 138 kV Capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5126-WACF | 2008-08-01 | 2008-08-04 | 138 | 0 | 0 | 0 | 110.4 | TARRANT | [6 empty] | Y
07TPIT0130 | Buda-Centex-Lehigh-Kyle-Canyon | Upgrade the 3.5-mile Lehigh-Buda(7498) 4/0-ACSR 69-kV transmission line to a 69/138 kV double circuit transmission line. One circuit will be 795 ACSR 69 KV and the other circuit will be bundled 795 ACSR 138 kV. The 69 kV circuit will terminate at Buda(7 |  | 06TPIT0224 | PEC | Randy Buchanan (830) 868-6058 |  | 2008-10-29 | 2008-08-08 | 138 | 3.5 | 12.2 | 0 | 0 | HAYS | [5 empty] | SEE PROJECT DESCRIPTION | Y | The name of Kohler's Crossing Substaion has been changed to Lehigh Substation
07TPIT0090 | Greenville: Construct new Shelby sub with 138-69 auto and re-route Royse line into new sub | Construct a new substation with a 138-69 kV autotransformer and route Royse line into sub | Construction Delays |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05012 | 2008-08-08 | 2008-08-08 | 138 | 4 | 0 | 150 | 0 | HUNT | HUNT |  |  |  |  | 960, 961 | Y
09TPIT0036 | Castroville - New 138kV Substation | Loop new 138kV substation into the existing 138kV TX Research to Lytle line | Design/Build contract has been awarded | T-0072 | CPS | PM: Ulrich Skerhut | S-0185 | 2008-09-01 | 2008-08-29 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5083 | Y |  | There are no transformers associated with this project
08TPIT0207 | TXDOT Hwy 511 | Relocate 138kV line from Central Ave to East Rio Hondo Substation |  | 08TPIT0208 | STEC | Doug Evans 361-485-6459 devans@stec.org | 975628 | 2008-08-08 | 2008-08-31 | 138 | 0.75 | 0.19 | 0 | 0 | CAMERON | CAMERON | [5 empty] | Y |  | TXDOT Project to relocate line due to road widening
08TPIT0203 | Uprate White Baker to Rio Pecos | Rebuild existing 69kV line from White Baker to Rio Pecos to accommodate 300MW generation for 138kV interconnection at White Baker substation. Work will include changing out poles for clearance, and reconductoring from White Baker to Rio Pecos with 795 ACSS conductor. Building a new entrance to AEP Rio Pecos Plant to the 138kV bay. |  |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com | NTE 07207 | 2008-09-08 | 2008-09-08 | 69 | 0 | 14 | 0 | 0 | PECOS | CROCKETT |  |  |  |  | 38430, 6601 | Y
08TPIT0204 | White Baker Substation - Sherbino | Build new 138kV station at White Baker. The station will have 138kV ringbus section to serve Orion (BP) Sherbino Mesa Project and 69kV section to serve Northern Natural to White Baker. |  |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com | NTE 07207 | 2008-09-08 | 2008-09-08 | 138 | 0 | 0 | 70 | 0 | PECOS | PECOS |  |  |  |  | 38430, 38420 | Y
08TPIT0123 | Long Creek Switching Station circuit breakers | Install 345 kV circuit breakers |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R620B-WACF | 2008-08-01 | 2008-09-08 | 345 | 0 | 0 | 0 | 0 | SHACKELFORD | [5 empty] | 6230, 1435, 1437, 1430 | Y
09TPIT0091 | Giddings Capacitor Bank Addition | Add a 138 kV 31.2 MVAR capacitor bank at the Giddings (7302). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-06-30 | 2008-09-26 | 138 | 0 | 0 | 0 | 31.2 | LEE | [5 empty] | SEE PROJECT DESCRIPTION | Y
09TPIT0184b | La Marque to West Galveston Ckt. 13 removed and distribution load converted to be served from 138kV. | Disconnected both 138/69kV autotransfomers at West Galveston and Ckt.13 from La Marque to West Galveston. Converted distribution load from 69kV to 138kV. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-09-30 | 2008-09-30 | 138 | 0 | 0 | -183 | 0 | GALVESTON | GALVESTON |  |  |  |  | 43400, 43410, 42860 | Y |  | 1) Part of the Post-Ike Galveston area recovery plan. 2) Distribution load moved from bus 43410 to bus 43400. 3) Transformer capacity to be removed and no transmission circuits to be built, rebuilt or reconductored. 4) West Galveston 138kV ring bus to be rebuilt by May 2009 to reflect the pre-storm configuration @West Galveston.
08TPIT0134 | Ajo, Build 345 KV SS | Build 345 kV switching station with shunt reactors in the Nelson Sharpe to Rio Hondo 345 kV line and 345kV line from Ajo to IPP's | IN-SERVICE | AEP GROUP 343 | AEP/TCC | John Pulay 918-599-2653 | 2052 | 2008-09-30 | 2008-09-30 | 345 | 0 | 0 | 0 | -200 | KENEDY | [6 empty] | Y
09TPIT0168 | Temple Switch terminal equipment | Replace terminal equipment on circuit to Temple Pecan Creek. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R723-E | 2009-05-01 | 2008-10-01 | 138 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 3415 | Y
08TPIT0149 | Willow Valley 138 kV Switching Station | Construct new switching station to connect a new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R813-WACF | 2008-10-01 | 2008-10-03 | 138 | 0 | 0.23 | 0 | 0 | SCURRY | [5 empty] | 1048 | Y
09TPIT0090 | Williamson County Capacitor Bank Additions | Add one 138 kV 31.2 MVAR capacitor bank at Avery Ranch(7534) and add one 138 kV 31.2 MVAR capacitor bank at Buttercup (7531). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-06-30 | 2008-10-22 | 138 | 0 | 0 | 0 | 62.4 | WILLIAMSON | [5 empty] | SEE PROJECT DESCRIPTION | Y
07TPIT0233 | Anna Switch - Collin Switch 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3060-WACF | 2008-12-01 | 2008-10-30 | 345 | 0 | 13.2 | 0 | 0 | COLLIN | COLLIN | Tier 4 | 2006-10-10 | 2007-02-01 | 2007-04-01 | 2373, 2372 | Y
09TPIT0142 | Spur: Add 138 kV Terminal, upgrade relaying | Interconnect McAdoo Wind Farm at Spur substation, add 138 kV terminal, upgrade relaying, at Aspermont and Spur. | IN-SERVICE | AEP GROUP 395 | AEP/TNC | Dave Goetz 918-599-2653 | 3086 | 2008-11-30 | 2008-10-31 | 138 | 0 | 0 | 0 | 0 | DICKENS | [6 empty] | Y
08TPIT0154 | Cook Field Road 345 kV Switching Station | Construct new switching station to connect a new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R817-WACF | 2008-10-31 | 2008-10-31 | 345 | 0 | 0 | 0 | 0 | SHACKELFORD | [6 empty] | Y
08TPIT0137 | North Padre: Add 1-14.4 MVAR Cap Bank | North Padre: Add 1-14.4 MVAR 69KV Cap Bank and Termination Upgrades | IN-SERVICE | AEP GROUP 029 | AEP/TCC | Michael Glueck 918-599-2653 | 205 | 2008-11-03 | 2008-11-03 | 69 | 0 | 0 | 0 | 14.4 | ARANSAS |  | Tier 4 |  |  |  |  | Y
08TPIT0174 | Tonkawa 345 kV Switching Station | Install 345 kV breakers to connect new wind farms |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R821-WACF | 2008-11-01 | 2008-11-05 | 345 | 0 | 0 | 0 | 0 | SCURRY | [5 empty] | 1048 | Y
08TPIT0179 | DeCordova terminal equipment upgrade | Upgrade 138 kV terminal equipment on 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5142-WACF | 2008-12-15 | 2008-11-10 | 138 | 0 | 0 | 0 | 0 | HOOD | [6 empty] | Y
06TPIT0081 | Airline to Laguna, rebuild 69 kV line | Rebuild Airline (8487) to Laguna (8494) 69 kV transmission line from 477 ACSR to 795 ACSR. |  | AEP GROUP 029 | LCRA TSC / AEP | Brad Woods (512) 369-4104 brad.woods@lcra.org | 4, LCRA#1003908 | 2008-11-11 | 2008-11-12 | 69 | 0 | 6.4 | 0 | 0 | NUECES | NUECES | Tier 4 |  |  |  |  | Y
08TPIT0083 | Clyde to Putnam, Rebuild 69 kV line | Rebuild the Clyde to Putnam 69 kV line | IN-SERVICE | AEP GROUP 354 | AEP/TNC | John Pulay 918-599-2653 | 2143 | 2008-11-30 | 2008-11-13 | 69 | 0 | 19.08 | 0 | 0 | CALLAHAN | CALLAHAN | [5 empty] | Y
08TPIT0209 | Victoria: Generation Interconnect | Interconnect new generation at the Victoria substation, install a phase shifting transformer at Thomaston substation, and rebuild Magruder to North Victoria 69 kV Line | IN-SERVICE | AEP GROUP 402 | AEP/TCC | Dave Goetz 918-599-2653 | 3111 | 2008-11-15 | 2008-11-15 | 138 | 0 | 0 | 0 | 0 | VICTORIA |  | Tier 4 |  |  |  |  | Y |  | As of November, 2008, AEP transmission interconnection facilities are in-service. As of mid-January, 2009, the generating units at Victoria Plant are not yet commercially available.
08TPIT0205 | Longshore 345 kV Switching Station | Expand 345 kV switching station to connect additional wind farms |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R682B-WACF | 2008-11-21 | 2008-11-24 | 345 | 0 | 0 | 0 | 0 | HOWARD | [5 empty] | 1058 | Y
08TPIT0147 | Ajo to IPP, build 345 kV line | Build 345 kV switching station in the Nelson Sharpe to Rio Hondo 345 kV line and 345kV line from Ajo to IPP's | IN-SERVICE | AEP GROUP 343 | AEP/TCC | John Pulay 918-599-2653 | 2223 | 2008-11-30 | 2008-11-30 | 345 | 21.6 | 0 | 0 | 0 | KENEDY | KENEDY | [5 empty] | Y
09TPIT0150 | Graham terminal equipment | Replace terminal equipment on circuit to Paint Creek. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R848-E | 2009-05-01 | 2008-12-01 | 138 | 0 | 0 | 0 | 0 | YOUNG | [5 empty] | 1431, 1371 | Y
08TPIT0184 | Lamesa Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment on lines to Holt Switch and Bluff Creek Switch. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R691-WACF - R694-WACF, R696-WACF & R697-WACF | 2008-11-15 | 2008-12-01 | 138 | 0 | 0 | 0 | 0 | DAWSON | [5 empty] | 1163 | Y
11TPIT0007 | Cibolo Creek - New 138kV Substation | Loop new 138kV substation into the existing 138kV Stonegate to Green Mountain line | Design/Build contract has been awarded | T-0110 | CPS | S: Bill Wards PM Ulrich Skerhut | S-0271 | 2008-12-01 | 2008-12-04 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5093 | Y |  | There are no transformers associated with this project
09TPIT0169 | Tradinghouse terminal equipment | Replace terminal equipment on circuit to Lake Creek. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R716-WACF | 2008-12-01 | 2008-12-06 | 345 | 0 | 0 | 0 | 0 | MCLENNAN | [5 empty] | 3405 | Y
08TPIT0175 | Comanche Peak capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R547-WACF | 2008-12-01 | 2008-12-11 | 138 | 0 | 0 | 0 | 18.4 | SOMERVELL | [5 empty] | 2278 | Y
08TPIT0084 | Ballinger, Add distribution transformer and cap | Ballinger, Add 138/13.02 kV transformer, 14.4 Mvar 69 kV cap | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2149 | 2008-12-31 | 2008-12-15 | 138 | 0 | 0 | 0 | 14.4 | RUNNELS | [6 empty] | Y
08TPIT0103 | Eastland 69 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R512-WACF | 2008-12-01 | 2008-12-16 | 69 | 0 | 0 | 0 | 9.2 | EASTLAND | [5 empty] | 1622 | Y
09TPIT0041 | Collin - Custer (BEC) 138 kV line (Oncor Electric Delivery section) | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3029-WACF | 2015-05-15 | 2008-12-16 | 138 | 0 | 3.5 | 0 | 0 | COLLIN | COLLIN |  |  |  |  | 2370, 655 | N
08TPIT0176 | Custer (BEC) 138 kV loop line reconfigure | Convert 138 kV loop line into two radial lines |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3029-WA | 2008-12-01 | 2008-12-16 | 138 | 0 | 0 | 0 | 0 | COLLIN | [5 empty] | 2566, 2567 | Y
08TPIT0142 | Elm Grove 138 kV new substation and load serving (load belongs to Oncor), and its 138 kV connections to Olinger and to Ben Davis | Elm Grove 138 kV new substation and load serving (load belongs to Oncor) |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-12-15 | 2008-12-17 | 138 | 0 | 20.1 | 0 | 0 | DALLAS | [5 empty] | 818, 2705, 968 | Y
09TPIT0111 | Bluff Creek to Oak Creek, Rebuild line | Rebuild the Bluff Creek to Oak Creek with 2X795 ACSS | IN-SERVICE | AEP GROUP 391 | AEP/TNC | Ashley Beasley 918-599-2653 | 2259 | 2009-01-31 | 2008-12-19 | 138 | 0 | 20.8 | 0 | 0 | TAYLOR | COKE | [5 empty] | Y
08TPIT0102 | Crandall 138 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3045-WACF | 2008-12-01 | 2008-12-19 | 138 | 0 | 0 | 0 | 55.2 | KAUFMAN | [5 empty] | 2727 | Y
07TPIT0124 | Seagoville Switch 345/138 kV autotransformer | Replace the existing 345/138 kV autotransformer |  | M4042 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4038-WACF | 2008-12-01 | 2008-12-19 | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 | 2006-09-27 | 2006-10-19 | N/A | 2433, 2434 | Y
08TPIT0140 | Brownwood Switch - Goldthwaite 138 kV line | Reconductor existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R540-WACF | 2008-12-01 | 2008-12-22 | 138 | 0 | 29.54 | 0 | 0 | BROWN | MILLS |  |  |  |  | 1655, 7070 | Y
08TPIT0171 | No Trees 138 kV Switching Station | Construct new switching station to connect a new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R822-WACF | 2008-12-01 | 2008-12-22 | 138 | 0 | 0 | 0 | 0 | WINKLER | [5 empty] | 1146 | Y
06TPIT0235 | Rice 69 kV capacitor | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3025-WACF | 2008-12-01 | 2008-12-29 | 69 | 0 | 0 | 0 | 18.4 | NAVARRO | [5 empty] | 2347 | Y
08TPIT0106 | Gorman 69 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R514-WACF | 2008-12-01 | 2008-12-29 | 69 | 0 | 0 | 0 | 9.2 | EASTLAND | [5 empty] | 1630 | Y
08TPIT0112 | Tonkawa 345 kV Switching Station shunt reactor | Install 345 kV shunt reactor |  | R677 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R673B-WACF | 2008-12-01 | 2008-12-29 | 345 | 0 | 0 | 0 | -100 | SCURRY | [5 empty] | 1048 | Y
08TPIT0190 | New Berlin(7612)-Olmos(7613) (Wilson Tap) | Rebuild New Berlin(7612)-Olmos (Wilson Tap)(7613) 4/0 ACSR 69-kV transmission line to 795 ACSR and convert to 138-kV. Construct Olmos 69/138 kV switching station. Relocate the New Berlin Autotransformer to Olmos switching station. |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2008-12-01 | 2008-12-31 | 138 | 0 | 6.1 | 0 | 0 | WILSON | [5 empty] | See Project Title | Y
06TPIT0232 | Forney - Lake Hubbard 138 kV line | Upgrade existing 138 kV line to operate at an elevated conductor temperature |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4040-WA | 2008-12-15 | 2008-12-31 | 138 | 0 | 7.58 | 0 | 0 | KAUFMAN | DALLAS |  |  |  |  | 2438, 2934, 2402 | Y |  | Temporary upgrade completed in 2007 will be made permanent in 2008.
07TPIT0123 | Seagoville Switch - Lawson Rd. 138 kV line | Upgrade existing 138 kV line |  | M4038 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4042-WACF | 2008-12-01 | 2008-12-31 | 138 | 0 | 2.5 | 0 | 0 | DALLAS | DALLAS |  |  |  |  | 2434, 2779 | Y
08TPIT0173 | Lavon Switch second 138 kV capacitor installation | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3069-WACF | 2008-12-01 | 2008-12-31 | 138 | 0 | 0 | 0 | 36.8 | COLLIN | [5 empty] | 2694 | Y
08TPIT0050 | Gustine to Hamilton Rebuild | Rebuild Hamilton to Gustine 69kv line with 795 and 138kv construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-05-01 | 2009-01-01 | 69 | 0 | 17.1 | 0 | 0 | COMANCHE | HAMILTON |  |  |  |  | 258, 279 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0062 | Bell County to Schwertner Rebuild | Rebuild Bell County to Schwertner 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-11-01 | 2009-01-01 | 69 | 0 | 13.7 | 0 | 0 | BELL | WILLIAMSON |  |  |  |  | 133114122 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
10TPIT0040 | Temple Switch - Bell County 138 kV line | Upgrade existing 138 kV line |  | R494 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R704A-E | 2010-05-01 | 2009-01-01 | 138 | 0 | 8.2 | 0 | 0 | WILLIAMSON | WILLIAMSON |  | 2006-11-01 |  | 2007-07-01 | 3666, 3673, 3658 | Y
09TPIT0164 | Scurry Chevron terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R844-E | 2009-01-01 | 2009-01-01 | 138 | 0 | 0 | 0 | 0 | SCURRY | [5 empty] | 1312 | Y
08TPIT0196 | Construct Bender 138kV Substation | Serve substation by looping into Ckt.86 Barhill to Crosby | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-11-30 | 2009-01-05 | 138 | 0.2 | 0 | 0 | 0 | CHAMBERS |  | Tier 4 |  |  |  | 40155 | Y |  | No transformer capacity added.
08TPIT0073 | Convert Cardinal Lane substation and Zilker Demolition | Rebuild Cardinal Lane substation as a 138kV substation and decommission Zilker substation and relocate the Seaholm cap bank to Cardinal Lane substation. | The final 4th unit has been installed and the circuit breakers are also installed. |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | 3230_117_2884 3240_117_4884 3240_117_2859 3240_117_4859 PLAN_117_P133 PLAN_117_P139 | 2009-01-01 | 2009-01-09 | 138 | 0 | 0 | 90 | 0 | TRAVIS | TRAVIS |  |  |  |  | 9120,9179,9299, 9132 | Y
08TPIT0117 | New Gulf tap - Pledger tap - West Columbia Ckt.04 | Raise conductors, partially rebuild Ckt.04 and upgrade limiting equipment at West Columbia to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-12-31 | 2009-01-16 | 138 | 0 | 27.47 | 0 | 0 | WHARTON | WHARTON | Tier 4 |  |  |  | 43340, 43011, 43120, 43380 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added.
08TPIT0108 | Lufkin E. - Lufkin S. 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R388-WACF | 2009-01-01 | 2009-01-23 | 138 | 0 | 6.3 | 0 | 0 | ANGELINA | ANGELINA | Tier 4 |  |  |  | 3326 | Y
08TPIT0155 | Jefferson - College Tap - Pasadena Ckt.06 | Reconductor 138kV Ckt.06 Jefferson to College Tap to Pasadena to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-12-31 | 2009-01-24 | 138 | 0 | 4.73 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 41240, 42312 | Y |  | No transformer capacity added.
09TPIT0205 | Austrop SPS | Establish a Special Protection System for the Austrop 138/345kV autotransformers. | For the overload of one Austrop autotransformer due to the loss of the other Austrop autotransformer, the SPS will open circuit 921 or circuits 921 and 920 if necessary |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com |  | 2009-01-29 | 2009-01-29 | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  |  | 9040, 7328 | Y
07TPIT0230 | Tyler GE - Tyler Omen Road 138 kV line | Rebuild existing 138 kV line |  | R384 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R386-WACF | 2009-05-01 | 2009-01-30 | 138 | 0 | 2.4 | 0 | 0 | SMITH | SMITH | Tier 4 | 2007-09-01 | 2008-01-01 | 2008-03-01 | 3213, 3212 | Y
06TPIT0179 | West Denton Sub: Expand 138 bus, add terminal for DME's line to R.G. Wells Sub | Expand 138 kV breaker and a half substation for new line to Denton's RD Wells Interchange and Substation | Delayed due to problems with site acquisition |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05006 | 2008-12-08 | 2009-02-01 | 138 | 0 | 0 | 0 | 0 | DENTON |  | Tier 4 |  |  |  | 986 | Y
08TPIT0098 | Gabriel to Schwertner Rebuild | Rebuild existing Gabriel to Schwertner |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-05-01 | 2009-02-17 | 69 | 0 | 9.4 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | 122, 123, 7345 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0088 | TCC - New 138kV Substation | Install new 138kV substation and connect to AMD |  | T-0106 | CPS | PM: Janna Junkin | S-0269 | 2009-02-28 | 2009-02-19 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5423 | Y |  | Underground transmission being installed at customer cost.
09TPIT0059 | Lago Vista-Nameless | Replace under-rated limiting line terminal equipment at Lago Vista to increase Lago Vista (7352)-Nameless (7526) to the conductor's rating. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2010-12-01 | 2009-02-19 | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
06TPIT0046 | Tyler NE - Tyler East 138 kV line | Upgrade existing 138 kV line |  | R384 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R337B-WACF | 2009-05-01 | 2009-02-25 | 138 | 0 | 3.74 | 0 | 0 | SMITH | SMITH | Tier 4 | 2007-09-11 | 2008-01-01 | 2008-03-01 | 3210, 3211 | Y
06TPIT0098 | Newman 138 kV new switching substation and installing a 138 kV/69 kV autotransformer (168 MVA) | Install a 138 kV/69 kV autotransformer (168 MVA) at Newman substation |  |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2009-03-02 | 2009-03-02 | 138 | 0 | 0 | 168 | 0 | DALLAS |  | Tier 4 |  |  |  | 849, 814 | Y
06TPIT0100 | Newman-Walnut line 69 kV to 138 kV voltage conversion | Converts voltage for the line |  |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2009-03-02 | 2009-03-02 | 138 | 0 | 0.55 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 814, 823 | Y
09TPIT0154 | Lake Creek terminal equipment | Replace terminal equipment on circuit to Temple Pecan Creek. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R725-WACF | 2009-05-01 | 2009-03-06 | 138 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3410 | Y
09TPIT0181 | Lake Creek terminal equipment | Replace terminal equipment on circuit to Temple Switch. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R730-WACF | 2009-05-01 | 2009-03-06 | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3409 | Y
07TPIT0076 | Friendship-Escarpment-Manchaca | Construct a new 795 ACSR 138-kV transmission line (approximately eight miles) between the Friendship(7507) and Manchaca(7504) substations. Construct a new 138-26.18-kV 22.4-MVA distribution substation to serve the load requirements in the area south of Austin. The new Escarpment(7672) substation will be cut midway into the new 138-kV Friendship-Manchaca transmission line. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org | 1006535 | 2009-03-16 | 2009-03-26 | 138 | 8 | 0 | 0 | 0 | TRAVIS | HAYS | Tier 2 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | The name of the new substation was changed from HWY 45 to Escarpment.
09TPIT0162 | Odessa terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R871-WACF | 2009-05-01 | 2009-03-26 | 138 | 0 | 0 | 0 | 0 | ECTOR |  | Tier 4 |  |  |  | 1127 | Y
07TPIT0172 | Freer 69 kV, add 1-7.2 MVAR Cap Bank | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2035 | 2009-03-27 | 2009-03-27 | 69 | 0 | 0 | 0 | 7.2 | Val VERDE | Val VERDE | Tier 4 |  |  |  |  | Y
09TPIT0198 | Alliance Substation | Replace terminal equipment at substation in the Roanoke Switch - Eagle Mountain 345 kV line. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C031-E | 2009-06-01 | 2009-03-27 | 345 | 0 | 0 | 0 | 0 | TARRANT |  | CREZ |  |  |  | 1855 | Y |  | CREZ default project
07TPIT0262 | Abilene South to Putnam, ugrades to improve ratings | Abilene South to Putnam 138 kV line, upgrades to improve rating | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Dave Goetz 918-599-2653 | 2171 | 2009-03-31 | 2009-03-31 | 138 | 0 | 35.3 | 0 | 0 | TAYLOR | CALLAHAN | Tier 4 |  |  |  |  | Y
08TPIT0206 | Leon Switch #5 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R553-WACF | 2009-05-01 | 2009-04-01 | 138 | 0 | 0 | 100 | 0 | EASTLAND |  | Tier 4 |  |  |  | 1624, 1626 | Y
09TPIT0159 | Midland West terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R843-WACF | 2009-05-01 | 2009-04-03 | 138 | 0 | 0 | 0 | 0 | MIDLAND |  | Tier 4 |  |  |  | 1117 | Y
09TPIT0063 | Whitney to Bosque Reconductor | Reconductor existing Whitney to Bosque 138kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-04-01 | 2009-04-06 | 138 | 0 | 13.4 | 0 | 0 | BOSQUE | MCLENNAN | Tier 4 |  |  |  | 241181177 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
09TPIT0172 | Wichita Falls Switch terminal equipment | Replace terminal equipment on circuit to Wichita Falls South. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R576-WACF | 2009-05-01 | 2009-04-08 | 138 | 0 | 0 | 0 | 0 | WICHITA |  | Tier 4 |  |  |  | 1448 | Y
07TPIT0132 | West Denton Re-route 138 KV Line Exits | Relocate 138 lines and add new line to R.D. Wells Interchange and Substation | Delayed due to line routing issues in Denton | 06TPIT0179 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T06014 | 2009-05-08 | 2009-04-09 | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  | 988 | Y
09TPIT0187 | T.H. Wharton - T.H. Wharton tap Ckt.81 | Move tap to T.H. Wharton (THW) distribution transformer TR5 from ckt.81 THW - Bammel to ckt.81 THW - Fairbanks. Upgrade the newly created THW - THW tap section. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-05-31 | 2009-04-09 | 138 | 0 | 0.05 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 45515, 45511 | Y |  | No transformer capacity to be added.
09TPIT0182 | Tradinghouse terminal equipment | Replace terminal equipment on circuit to Temple Pecan Creek. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R731-WACF | 2009-05-01 | 2009-04-16 | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3405 | Y
09TPIT0029 | Hilltop Lakes Sw. to Hearne Rebuild | Rebuild existing Hilltop Lakes to Hearne |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-03-01 | 2009-04-17 | 69 | 0 | 14.5 | 0 | 0 | ROBERTSON | ROBERTSON | Tier 4 |  |  |  | 36,53,57,43 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0152 | Big Spring - Chalk - McDonald 69 kV line | Rebuild existing 69 kV line for double-circuit operation with one 138 kV circuit and one 69 kV circuit |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R645-WAC | 2009-05-01 | 2009-04-17 | 138 | 17.6 | 17.6 | 0 | 0 | HOWARD | HOWARD | Tier 3 | 2007-09-01 | 2008-01-18 | N/A | 1323, 1352, 1333 | Y |  | Big Spring - Signal Mountain section wll be completed by 12/2008.
07TPIT0231 | Tyler Grande 345/138 kV Switching Station | Construct switching station and install a 345/138 kV autotransformer |  | R387, R337B & R386 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R384-WACF | 2009-05-15 | 2009-04-20 | 345 | 0 | 0 | 600 | 0 | SMITH |  | Tier 3 | 2007-09-01 | 2008-01-01 | 2008-03-01 | 3102, 3196 | Y
07TPIT0016 | Saginaw - Euless/Roanoke Switch 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M507-WAC | 2009-05-01 | 2009-04-22 | 138 | 0 | 17.4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1957, 2039, 2040, 2041, 2042, 2043, 2044, 2047 | Y
07TPIT0158 | Sandow Switch - Salty - Thorndale North - Taylor 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R485-WACF | 2009-05-01 | 2009-04-22 | 138 | 0 | 21.86 | 0 | 0 | MILAM | WILLIAMSON | Tier 4 | 2007-04-23 | 2007-08-01 | N/A | 3430, 3661, 3659, 3658 | Y |  | Sandow Switch - Thorndale N section will be completed in 12/2008.
08TPIT0157 | Blodgett - Garrott Ckt.37 | Raise conductors to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2009-03-30 | 2009-04-23 | 138 | 0 | 1.64 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47521, 47660 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0087 | Singleton Switching Station | Build a new 345 kV Singleton substation. Loop Ckt.1 Jewett - T.H. Wharton, Ckt.1 Jewett - Tomball, Ckt.75 Gibbons Creek - Roans Prairie and Ckt.99 Gibbons creek - Obrien into the new substation. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-04-30 | 2009-04-24 | 345 | 0 | 0.5 | 0 | 0 | GRIMES |  | Tier 3 | 2007-01-08 | 2007-07-16 | 2007-08-21 | 44645 | Y |  | 1)_Part of Houston Area Constraint Mitigation Project, Phase II. 2)_No transformer capacity to be added.
09TPIT0157 | Tri Gas (Liquid Air) terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R869-WACF | 2009-05-01 | 2009-04-30 | 138 | 0 | 0 | 0 | 0 | ECTOR |  | Tier 4 |  |  |  | 1128 | Y
09TPIT0062 | West Weatherford to Shady Grove Rebuild | Rebuild existing West Weatherford to Shady Grove 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-05-01 | 2009-05-01 | 69 | 0 | 2.35 | 0 | 0 | PARKER | PARKER | Tier 4 |  |  |  | 515, 1585 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
09TPIT0186 | Dunlavy - Heights Ckt.31 | Upgrade Dunlavy - Heights 69kV Ckt.31 to increase thermal ratings. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-05-31 | 2009-05-01 | 69 | 0 | 2.35 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47580, 47680 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
06TPIT0113 | McNeil autotransformer replacement | With the completion of 138kV conversion of circuit 822 and 824, the Seaholm auto will replace the autotransformer at the McNeil substation. | COMPLETE |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P049 | 2009-05-07 | 2009-05-01 | 138 | 0 | 0 | 200 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9079, 9080 | Y
09TPIT0184a | Alvin Auto Substation 138/69kV Autotransformer | Add new 83MVA Autotransformer (A1) at Alvin Auto substation |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-05-31 | 2009-05-01 | 138 | 0 | 0 | 83 | 0 | BRAZORIA |  | Tier 4 |  |  |  | 42130, 42140 | Y |  | 1) Part of the Post-Ike Galveston area recovery plan. 2) 83MVA Autotransformer A1 to be moved from West Galveston to Alvin Auto substation and a new 69kV bus #42140 will be added to the base cases 3). No transmission circuits to be built, rebuilt or reconductored.
08TPIT8889 | STEC Southmost Substation Approach Span | Build 0.42 Mile Approach Spans into Southmost Substation |  | 08TPIT8888 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2009-05-09 | 2009-05-01 | 138 | 0.42 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  |  | Y
09TPIT0147 | China Grove terminal equipment | Replace terminal equipment on circuit to Paint Creek. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R864-E | 2009-05-01 | 2009-05-01 | 138 | 0 | 0 | 0 | 0 | MITCHELL |  | Tier 4 |  |  |  | 1318 | Y
09TPIT0165 | Shamburger Switch terminal equipment | Replace terminal equipment on circuit to Tyler Grande. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R866-E | 2009-05-01 | 2009-05-01 | 138 | 0 | 0 | 0 | 0 | SMITH |  | Tier 4 |  |  |  | 3104, 3210 | Y
10TPIT0035 | Roanoke Switching Station #1 345/138 kV autotransformer replacement | Replace existing 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5122-WACF | 2009-05-01 | 2009-05-01 | 345 | 0 | 0 | 600 | 0 | DENTON |  | Tier 4 | 2007-12-31 | 2008-02-26 | N/A | 1850, 1851 | Y
09TPIT0092 | VH Braunig to Streich to OW Sommers - 138kV Transmission Line Reroute | Open VH Braunig tie breakers in order to reduce fault current Braunig E - Streich becomes Braunig W - Streich Sommers - Streich becomes Deely - Streich Braunig - OW Sommers upgrade substation equipment to 3000A |  | S-0369 | CPS | T: Adam Marin S: Keith Calle | T-0122 | 2009-05-04 | 2009-05-08 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5025 5110 5395 5417 | Y |  | There are no transformers associated with this project
09TPIT0025 | Second Concord 345/138 Autotransformer | Install second 300MVA 345/138KV auto at Concord |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-09-01 | 2009-05-09 | 345 | 0 | 0 | 300 | 0 | JOHNSON |  | Tier 4 |  |  |  | 393, 394 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
10TPIT0046 | Austin to Tuttle - 138kV Transmission Line Rebuild | Reconductor existing 138 kV line |  | S-0396 | CPS | T: Kevin Phillips PM: Ulrich Skerhut | T-0127 | 2009-05-30 | 2009-05-10 | 138 | 0 | 2 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5005 5435 | Y |  | There are no transformers associated with this project
09TPIT0144 | Collin Switch 138 kV capacitors | Install capacitors | Project is taking more time than expected. |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3081-WACF | 2009-07-01 | 2009-05-15 | 138 | 0 | 0 | 0 | 110.4 | COLLIN |  | Tier 4 |  |  |  | 2370 | Y
09TPIT0139 | Johnson Switch | Add 345 kV circuit breakers |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3070-WACF | 2009-05-01 | 2009-05-18 | 345 | 0 | 0 | 0 | 0 | JOHNSON |  | Tier 4 |  |  |  | 1902 | Y
09TPIT0099 | Villa Cavazos, Convert 69 kV distribution substation to 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line | IN-SERVICE | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 3065 | 2009-06-30 | 2009-05-20 | 138 | 0 | 0 | 0 | 0 | CAMERON |  | Tier 4 |  |  |  |  | Y
09TPIT0100 | La Palma to Military Highway 138kV line, cut-in Villa Cavazos at 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line | IN-SERVICE | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 3071 | 2009-06-30 | 2009-05-20 | 138 | 0.1 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  |  | Y
09TPIT0088 | East Bernard - Wallis - Sealy - Peters Ckt.65 | Raise conductors and partially rebuild Ckt.65 to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-05-04 | 2009-05-22 | 138 | 0 | 25.28 | 0 | 0 | WHARTON | AUSTIN | Tier 4 |  |  |  | 44190, 44740, 44640, 46220 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added
09TPIT0055 | Skyline to Dresden - 138kV Line Upgrade | Upgrade small section from 556AA to 795ACSS/TW |  |  | CPS | T: Adam Marin | T-0128 | 2009-05-16 | 2009-05-23 | 138 | 0 | 1 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5130 5370 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
07TPIT0232 | Tyler Grande - Tyler S. 138 kV line | Rebuild existing 138 kV line for double-circuit operation |  | R384 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R387-WA | 2009-05-15 | 2009-05-28 | 138 | 2.32 | 2.32 | 0 | 0 | SMITH | SMITH | Tier 4 | 2007-09-01 | 2008-01-01 | 2008-03-01 | 3196, 3218 | Y
09TPIT0094 | Westover Hills - New 138kV Substation | Install new 138kV substation and connect to VLSI |  | T-0121 | CPS | T: LeeRoy Perez S: Keith Calle | S-0328 | 2009-05-29 | 2009-05-29 | 138 | 1.7 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5467 5488 | Y |  | There are no transformers associated with this project
09TPIT0197 | Sacroc terminal equipment | Replace terminal equipment on circuit to Snyder. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R870-WACF | 2009-05-01 | 2009-05-29 | 138 | 0 | 0 | 0 | 0 | SCURRY |  | Tier 4 |  |  |  | 1311 | Y
07TPIT0137 | Abilene Plant to Clyde, Rebuild 69/138 kV Dbld Crkt Capable | Re-build 13 miles Abilene Plant to Clyde Dbl Crkt 69/138 KV line @ 795 ACSR - Energize @ 69 kV | IN-SERVICE | AEP GROUP 341 | AEP/TNC | John Pulay 918-599-2653 | 1697 | 2009-05-31 | 2009-05-31 | 69 | 0 | 13 | 0 | 0 | TAYLOR | CALLAHAN | Tier 4 |  |  |  |  | Y
09TPIT0146 | Chalk terminal equipment | Replace terminal equipment on circuit to Garden City. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R839-E | 2009-05-23 | 2009-06-01 | 69 | 0 | 0 | 0 | 0 | HOWARD |  | Tier 4 |  |  |  | 1352 | Y
09TPIT0149 | Garden City terminal equipment | Replace terminal equipment on circuit to Chalk. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R840-E | 2009-05-01 | 2009-06-01 | 69 | 0 | 0 | 0 | 0 | GLASSCOCK |  | Tier 4 |  |  |  | 1218 | Y
09TPIT0166 | Snyder terminal equipment | Replace terminal equipment on circuit to China Grove. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R865-E | 2009-05-01 | 2009-06-01 | 69 | 0 | 0 | 0 | 0 | SCURRY |  | Tier 4 |  |  |  | 1305 | Y
09TPIT0167 | Spraberry terminal equipment | Replace terminal equipment on circuit to Big Spring Switch. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R872-E | 2009-05-01 | 2009-06-01 | 69 | 0 | 0 | 0 | 0 | MIDLAND |  | Tier 4 |  |  |  | 1330 | Y
09TPIT0052 | Justin Lane 138/69 kV substation | Establish a new substation at Justin Lane site and install (2) 30MVA transformers. The substation will cut into the existing Ckt 811 (McNeil to Koenig Lane). | COMPLETE |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3240_117_4855 PLAN_117_P042 PLAN_117_P135 | 2009-05-11 | 2009-06-01 | 138 | 0.5 | 0 | 60 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9225 | Y
09TPIT0109 | Nicole, Four Position Ring | Provide inteconnection at new Nicole substation | IN-SERVICE | AEP GROUP 390 | AEP/ETT | Leo York | 3115 | 2009-06-01 | 2009-06-01 | 138 | 0 | 0 | 0 | 0 | COKE |  | Tier 4 |  |  |  |  | Y
08TPIT0169 | Cut Bluff Creek to Oak Creek into Nicole | Provide inteconnection at new Nicole substation | IN-SERVICE | AEP GROUP 390 | AEP/TNC | Ashley Beasley 918-599-2653 | 3116 | 2009-06-01 | 2009-06-01 | 138 | 0 | 2 | 0 | 0 | COKE | COKE | Tier 4 |  |  |  |  | Y
09TPIT0110 | Cut Red Creek 138 kV line into Nicole | Provide inteconnection at new Nicole substation | IN-SERVICE | AEP GROUP 390 | AEP/TNC | Ashley Beasley 918-599-2653 | 3114 | 2009-06-01 | 2009-06-01 | 138 | 0 | 38 | 0 | 0 | COKE | TOM GREEN | Tier 4 |  |  |  |  | Y
07TPIT0092 | Denton West to RD Wells 138kV Transmission Line | Construct 4.6 miles of new 138kV transmission line | On schedule | 07TPIT0091, 0094, 0095, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600129 | 2009-06-01 | 2009-06-02 | 138 | 4.6 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 986, 930 | Y
06TPIT0030 | West Waco - Lorena - Eddy 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R093-WACF | 2009-05-01 | 2009-06-03 | 69 | 0 | 16.3 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3437, 3577, 3580 | Y |  | The Waco West to Lorena section will be reconstructed by 12/31/2008.
07TPIT0094 | RD Wells Substation | Install three 25MVA, 138kV to 13.2kV substation transformers served from the RD Wells 138kV bus | On schedule | 07TPIT0091, 0092, 0095, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600126 | 2009-06-02 | 2009-06-03 | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 932 | Y
09TPIT0006 | Lobo, build 138/69 kV substation | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV | IN-SERVICE | AEP GROUP 216 | AEP/ETT | Bill Eakin 918-599-2653 | 1306 | 2009-12-31 | 2009-06-09 | 138 | 0 | 0 | 93 | 0 | WEBB |  | Tier 1 | 2003-09-15 | 2004-02-19 | 2004-03-08 |  | Y
09TPIT0114 | San Angelo Power Station, Reconfigure Station | San Angleo Power Station, Reconfigure Station to separate wind from load circuits | IN-SERVICE | AEP GROUP 429 | AEP/TNC | Brett Madison 918-599-2653 | #N/A | 2009-06-10 | 2009-06-10 | 138 | 0 | 0 | 0 | 0 | TOM GREEN |  | Tier 4 |  |  |  |  | Y
09TPIT0210 | San Angelo Power Station, to Menard 138 kV line improvements | Rebuild part of SAPS to Menard 138 kV line by replacing structures | IN-SERVICE | AEP GROUP 471 | AEP/TNC | Brett Madison 918-599-2653 | 2353 | 2009-06-10 | 2009-06-10 | 138 | 0 | 0 | 0 | 0 | TOM GREEN | MENARD | Tier 4 |  |  |  |  | Y
09TPIT0161 | Moss Switch terminal equipment | Replace terminal equipment on circuit to Odessa EHV. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R846-WACF | 2009-05-01 | 2009-06-12 | 138 | 0 | 0 | 0 | 0 | ECTOR |  | Tier 4 |  |  |  | 1019 | Y
09TPIT0155 | Lake Creek terminal equipment | Replace terminal equipment on circuit to Tradinghouse. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R715-WACF | 2009-06-01 | 2009-06-12 | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3409 | Y
09TPIT0082 | Jewett - Big Brown 345 kV circuit #1 | Upgrade circuit breaker and associated equipment at Big Brown to increase emergency rating of line. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R707-E | 2009-05-01 | 2009-06-16 | 345 | 0 | 0 | 0 | 0 | FREESTONE |  | Tier 4 |  |  |  | 3390, 3380 | Y |  | 1)_Part of Houston Area Constraint Mitigation Project, Phase II. 2)_No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0151 | Graham terminal equipment | Replace terminal equipment on circuit to Navy Kickapoo. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R554-WACF | 2009-05-01 | 2009-06-18 | 69 | 0 | 0 | 0 | 0 | YOUNG |  | Tier 4 |  |  |  | 1602 | Y
09TPIT0145 | Shamburger Switch 138 kV capacitors | Install capacitors | Project is taking more time than expected. |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R860-WACF | 2009-07-01 | 2009-06-23 | 138 | 0 | 0 | 0 | 110.4 | SMITH |  | Tier 4 |  |  |  | 3104 | Y
09TPIT0131 | Interconnect a new combined cycle plant at Cedar Bayou. | Add a new combined cycle plant at the NRG Cedar Bayou site connected to the Cedar Bayou substation. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-06-30 | 2009-06-24 | 345 | 0 | 0 | 0 | 0 | CHAMBERS |  | Tier 4 |  |  |  | 40000, 48583, 48584, 48585, 40001 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
08TPIT0138 | Aransas Pass: Add 1-28.8 MVAR Cap Bank | Aransas Pass: Add 3-69 KV Breakers, Add 1-28.8 MVAR 69 KV Cap Bank |  | AEP GROUP 029 | AEP/TCC | Michael Glueck 918-599-2653 | 1192 | 2009-06-30 | 2009-06-26 | 69 | 0 | 0 | 0 | 28.8 | ARANSAS |  | Tier 4 |  |  |  |  | Y
09TPIT0143 | Anna Switch 138 kV capacitors | Install capacitors | Project is taking more time than expected. |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3080-WACF | 2009-07-01 | 2009-06-26 | 138 | 0 | 0 | 0 | 110.4 | COLLIN |  | Tier 4 |  |  |  | 2374 | Y
09TPIT0048 | Poage - Temple Taylors Valley - Bell County 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R472-WACF | 2009-05-01 | 2009-06-29 | 69 | 0 | 3.4 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3635, 3636 | Y
09TPIT0136 | Northern Natural 2 Mvar Capacitor bank | Install 2 Mvar 69 kV Cap Bank at Northern Natural |  |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2009-06-30 | 2009-06-30 | 69 | 0 | 0 | 0 | 2 | PECOS | PECOS | Tier 4 |  |  |  | 38440 | Y
09TPIT0056 | McNeil-Gilleland | Replace under-rated limiting line terminal equipment to increase McNeil (7334)-Gilleland (7336) to the conductor's rating. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-06-30 | 2009-06-30 | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | $ for this project is included with the Fayetteville-Willow Springs and Jollyville-Avery Ranch projects.
09TPIT0070 | Fayetteville-Willow Springs | Replace under-rated limiting line terminal equipment to increase Fayetteville (7286)-Willow Springs (7273) to the conductor's rating. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-06-30 | 2009-06-30 | 138 | 0 | 0 | 0 | 0 | FAYETTE |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | $ for this project is included with theMcNeil-Gilleland and Jollyville-Avery Ranch projects.
09TPIT0071 | Avery Ranch-Jollyville | Replace under-rated limiting line terminal equipment to increase Avery Ranch (7534)-Jollyville (9223) to the conductor's rating. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-06-30 | 2009-06-30 | 138 | 0 | 0 | 0 | 0 | WILLIAMSON |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | $ for this project is included with the McNeil-Gilleland and Fayetteville-Willow Springs projects.
08TPIT0024 | Wilson(7615)-CPS Sutherland Springs(5418) | Construct a new 795 ACSR (220-MVA) 138-kV transmission line between the Wilson(7615) and Floresville Sutherland Springs(5418) substations. |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2009-07-31 | 2009-06-30 | 138 | 10.98 | 0 | 0 | 0 | WILSON | WILSON | Tier 3 |  |  |  | See Project Title | Y
07TPIT0151 | Yellowjacket, New 138/69 Station | Yellowjacket, Build new 138 kV Switch Station Station: Five postion ring with 2-90 MVA Auto 138/69 (LTC), 138 KV 28.8 MVAR Capacitor and 1- 10 MVA distribution bank | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2138 | 2009-06-30 | 2009-06-30 | 138 | 0 | 0 | 90 | 28.8 | MENARD |  | Tier 4 |  |  |  |  | Y
09TPIT0174 | Lufkin Switch - Aspen Power 138 kV line | Construct second 138 kV circuit on an existing line to connect a new power plant. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R850-WAC | 2009-08-01 | 2009-06-30 | 138 | 1.9 | 0 | 0 | 0 | ANGELINA | ANGELINA | Tier 4 |  |  |  | 3118, 3268 | Y
07TPIT0070 | Taylor - Taylor West - Hutto Switch 138 kV line | Upgrade existing 138 kV line | Will attempt accelerating project if construction clearance can be obtained. |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R457-WACF | 2009-07-01 | 2009-06-30 | 138 | 0 | 10.07 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  | 2007-08-01 | N/A | 3666, 3673, 3658 | Y
09TPIT0123 | Parkdale SVC installation | Install two +300 Mvar/-265 Mvar SVCs |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4056-WACF | 2009-06-15 | 2009-06-30 | 138 | 0 | 0 | 0 | 600 | DALLAS |  | Tier 1 | 2007-02-01 |  | 2007-08-01 | 2440, 12440, 12448, 12449 | Y
09TPIT0065 | Spruce 2 - Power Plant Loop | Install 345kV connection between the Spruce 2 GSU and the existing Spruce 345kV switchyard |  | S-0138 | CPS | T: LeeRoy Perez S: Joe Rodriguez | T-0075 | 2009-06-15 | 2009-06-30 | 345 | 0.07 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5400 | Y |  | There are no transformers associated with this project
09TPIT0160 | Morgan Creek terminal equipment | Replace terminal equipment on circuits Odessa EHV and Quail Switch. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R833-WACF, R841-WACF & R842-WACF | 2009-05-01 | 2009-06-30 | 345 | 0 | 0 | 0 | 0 | MITCHELL |  | Tier 4 |  |  |  | 1030 | Y
11TPIT0049 | Morgan Creek terminal equipment | Replace terminal equipment on line to Twin Buttes. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C071-E | 2009-05-01 | 2009-06-30 | 345 | 0 | 0 | 0 | 0 | MITCHELL |  | CREZ |  |  |  | 1030 | Y | IF zero ($) no dates are needed | CREZ default project Existing terminal equipment is adequate.
05TPIT0118 | Hidden Valley 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Hidden Valley substation. | COMPLETE |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3230_117_1442 | 2009-07-01 | 2009-07-01 | 138 | 0 | 0 | 0 | 31.2 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9207 | Y
09TPIT0180 | Barney Davis: Expand substation for Generator interconnects | Barney Davis interconnection of 360 MW of new generation | IN-SERVICE | AEP GROUP 400 | AEP/TCC | Michael Glueck 918-599-2653 |  | 2009-07-01 | 2009-07-01 | 138 | 0 | 0 | 0 | 0 | NUECES |  | Tier 4 | 2009-03-22 | 2009-10-09 | 2009-12-01 |  | Y
06TPIT0166 | MVEC Palmhurst-MVEC Merett | Rebuild 138kV line from Palmhurst to Merett Substations |  | 06TPIT0165 | STEC | Doug Evans 361-485-6459 devans@stec.org | 984501 | 2009-10-09 | 2009-07-09 | 138 | 0 | 4.2 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8774-8752 | Y
08TPIT8888 | STEC Southmost Substation | Build New 138kV Substation |  | 08TPIT8889 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2009-05-09 | 2009-07-09 | 138 | 0 | 0 | 0 | 0 | CAMERON |  | Tier 4 |  |  |  | 8789 | Y
10TPIT0057 | Benbrook series reactors | Install a 2-ohm 138 kV series reactor on autotransformer A and B. | ERCOT's approval process for this project took more time than expected which delayed the start of construction. |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5068-WACF & M5139-WACF | 2009-07-01 | 2009-07-09 | 138 | 0 | 0 | 0 | 0 | TARRANT |  | Tier 4 |  |  |  | 1874,1870, 1869, 1875 | N
09TPIT0206 | Warvue Co-Generation | Interconnect a new co-generation plant at Warvue substation. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-05-31 | 2009-07-14 | 138 | 0 | 0 | 0 | 0 | CHAMBERS |  | Tier 4 |  |  |  | 48940, 41700 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
08TPIT0082 | Live Oak, Add 69/138 kV Auto | Add second Auto 138/69 (LTC) at Live Oak 50 MVA - Expand to a four position ring bus | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2130 | 2009-07-16 | 2009-07-16 | 138 | 0 | 0 | 50 | 0 | SCHLEICHER |  | Tier 4 |  |  |  |  | Y
09TPIT0216 | Lynpol Substation | Disconnect customer owned Lynpol substation from CNP's Ckt. 94 Fairmont - Himont. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-07-31 | 2009-07-31 | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 42910 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0202 | Construct Betka 138kV Substation | Serve substation by looping into Ckt.66 Hockley to Freeman. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-06-30 | 2009-07-31 | 138 | 1.74 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 45675 | Y |  | No transformer capacity added.
09TPIT0138 | Hillsboro - Alvarado 69 kV line | Rebuild existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R489-WACF | 2009-09-01 | 2009-08-19 | 69 | 0 | 27.2 | 0 | 0 | HILL | JOHNSON | Tier 4 | 2008-05-01 | 2008-06-10 | N/A | 3523, 3532, 3533, 3537, 2298 | Y
09TPIT0156 | Leon Switch terminal equipment | Replace terminal equipment on circuit to Putnam. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R577-E | 2009-12-01 | 2009-08-19 | 138 | 0 | 0 | 0 | 0 | EASTLAND |  | Tier 4 |  |  |  | 1624 | Y
05TPIT0069 | Waller-Prairie View-Seaway-Macedonia | Upgrade the 22.0-mile Waller(7272)-Macedonia(7671) 138-kV transmission line from 477 ACSR (159-MVA) to 959 ACSS (392-MVA). |  |  | SBEC | Billy Marricle (979) 865-3171 bmarricle@sbec.org | 1004653 | 2009-09-01 | 2009-08-20 | 138 | 0 | 22 | 0 | 0 | WALLER | WALLER | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
12TPIT0020 | Kendall CTEC to Kendall | The existing LCRA TSC 138 kV transmission line (approximately 0.23 miles) between the Kendall CTEC (7147) and LCRA TSC Kendall (7152) stations will be rebuilt. The rebuilt transmission line will consist of 1X795 ACSR conductor to provide a thermal rating of 220 MVA. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-12-01 | 2009-09-01 | 138 | 0 | 0.23 | 0 | 0 | KENDALL | KENDALL | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | CREZ Default project assigned to LCRA TSC
09TPIT0204 | Pelican Tap | Pelican 138 kV: Papalote Creek 180 MW Windfarm Direct Interconnect | IN-SERVICE | AEP GROUP 397 | AEP/TCC | Tommy Vannoy 918-599-2653 | 3095 | 2009-09-01 | 2009-09-01 | 138 | 0 | 0 | 0 | 0 | San Patricio |  | Tier 4 |  |  |  |  | N
09TPIT0128 | Zorillo: Build 345kV Station | Build 345 kV switching station in the Nelson Sharpe to Rio Hondo 345 kV line and 345kV line from Ajo to IPP's |  | AEP GROUP 343 | AEP/TCC | John Pulay 918-599-2653 | 2222 | 2009-08-03 | 2009-09-01 | 345 | 0 | 0 | 0 | 0 | KENEDY |  | Tier 4 |  |  |  |  | Y
09TPIT0069 | Rattlesnake Road 345 kV Switching Station | Construct 345 kV switching station to connect a new power plant. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R499-WA | 2009-09-01 | 2009-09-01 | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3397, 3398, 3399 | Y
09TPIT0212 | SAPS: Reconfigure to double bus, double breaker, reterminate 69/138 kV Auto | Rebuild part of SAPS to Menard 138 kV line by replacing structures and Move SAPS auto and add DCRS at North Brady | IN-SERVICE | AEP GROUP 472 | AEP/TNC | Brett Madison 918-599-2653 | 2356 | 2009-09-30 | 2009-09-15 | 138 | 0 | 0 | 0 | 0 | TOM GREEN | TOM GREEN | Tier 4 |  |  |  |  | Y
10TPIT0094 | Britmore - Addicks Ckt.09 | Upgrade limiting equipment at 138kV Addicks and Britmoore substations to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-09-30 | 2009-09-22 | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 44120, 45610 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0106 | Perry Auto | Increase 138/69 autotransformer capacity at Perry |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-11-03 | 2009-09-24 | 138 | 0 | 0 | 100 | 0 | FALLS |  | Tier 4 |  |  |  | 91,92 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
07TPIT0225 | Bennett Road Switching Station | Construct 138 kV switching station |  | R510A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R510B-WACF | 2009-12-01 | 2009-10-01 | 138 | 0 | 0 | 0 | 0 | WISE |  | Tier 3 |  |  |  | 1582, 1565, 1566, 1568 | Y
09TPIT0220 | Graham terminal equipment upgrade | Upgrade 345 kV terminal equipment on lines to Long Creek and Parker |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R575-WACF | 2009-12-01 | 2009-10-01 | 345 | 0 | 0 | 0 | 0 | YOUNG |  | Tier 4 |  |  |  | 1430, 1436, 1435 | Y
09TPIT0218 | Graham Switch terminal equipment | Replace terminal equipment on line to Bowman |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R575-WA | 2009-10-01 | 2009-10-01 | 345 | 0 | 0 | 0 | 0 | YOUNG |  | Tier 4 |  |  |  | 1430 | Y
09TPIT0219 | Morgan Creek terminal equipment | Replace terminal equipment on line to Twin Buttes. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C071-E | 2009-10-01 | 2009-10-01 | 345 | 0 | 0 | 0 | 0 | MITCHELL |  | Tier 4 |  |  |  | 1030 | Y
09TPIT0095 | Cagnon - 138kV Capacitor Bank Addition | 80 MVAR Capacitor Addition at Cagnon |  |  | CPS | S: Ricardo Renteria | S-0362 | 2009-08-17 | 2009-10-07 | 138 | 0 | 0 | 0 | 80 | BEXAR | BEXAR | Tier 4 |  |  |  | 5055 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
09TPIT0191 | Reactor Banks | Install 25 MVAR reactor Banks at Jack County, Rhome, Bowie, and Spring |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-11-02 | 2009-10-08 | 138 | 0 | 0 | 0 | -100 | COOKE, MONTAGUE, JACK, WISE |  | Tier 4 |  |  |  | 579576620684 | N |  | Substation Project
07TPIT0152 | Abilene South, 2nd 69/138 kV Auto | Abilene South, add 2nd 69/138 kV 90 MVA Autotransformer | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2134 | 2009-09-30 | 2009-10-10 | 138 | 0 | 0 | 90 | 0 | TAYLOR |  | Tier 4 |  |  |  |  | Y
09TPIT0137 | Hill Country - 138kV Capacitor Bank Addition | Remove one existing back-to-back 50.4MVAR capacitor bank at Harmony Hills and relocate to the 138kV Hill Country bus |  |  | CPS | S: David Riethmeyer | S-0520 | 2009-09-30 | 2009-10-12 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5209 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
07TPIT0153 | Yellowjacket, Add 2nd 69/138 kV Auto | Yellowjacket, Build new 138 kV Switch Station Station: Five postion ring with 2-90 MVA Auto 138/69 (LTC), 138 KV 28.8 MVAR Capacitor and 1- 10 MVA distribution bank, | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2123 | 2009-12-31 | 2009-10-13 | 138 | 0 | 0 | 90 | 0 | MENARD |  | Tier 4 |  |  |  |  | Y
09TPIT0126 | Sonora 69 kV: Mitigation | Open the Friend Ranch to Sonora 69 kV line when the Friend Ranch to Sonora 138 kV line trips to keep the 69 kV line from overloading | IN-SERVICE | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2265 | 2009-12-31 | 2009-10-15 | 138 | 0 | 0 | 0 | 0 | SUTTON |  | Tier 4 |  |  |  |  | Y
09TPIT0097 | Hunt Lane - New 138kV substation | Build a new two-terminal 138kV substation to replace Marbach. |  | T-0126 | CPS | PM:Hector Torres | S-0398 | 2009-10-16 | 2009-10-23 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5234 | Y |  | There are no transformers associated with this project
09TPIT0141 | Abilene South, Replace 138/69 kV Auto | Abilene South, add 2nd 69/138 kV 90 MVA Autotransformer | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2134 | 2009-09-30 | 2009-10-23 | 138 | 0 | 0 | 90 | 0 | TAYLOR |  | Tier 4 |  |  |  |  | Y
09TPIT0171 | Tyler South terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R835-WA | 2009-12-01 | 2009-10-24 | 138 | 0 | 0 | 0 | 0 | SMITH |  | Tier 4 |  |  |  | 3218 | Y
07TPIT0224 | Decatur - Bennett Rd - Wise County 138 kV line | Rebuild existing 138 kV line |  | R510A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R511-WACF | 2009-11-01 | 2009-10-28 | 138 | 0 | 12.6 | 0 | 0 | WISE | WISE | Tier 3 |  |  |  | 1582, 1566 | Y
08TPIT0049 | Second Whitney 345/138 Autotransformer | Install second 450MVA 345/138KV auto at Whitney |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-09-01 | 2009-10-28 | 345 | 0 | 0 | 450 | 0 | BOSQUE |  | Tier 4 |  |  |  | 240, 241 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
09TPIT0208 | Install an intermediate pole and jumpers to connect Langford to SAPS/ELO 138 kV line | Interconnect Langford Wind Farm at Santiago, upgrade relaying | IN-SERVICE | AEP GROUP 461 | AEP/TNC | Terry Weeks 918-599-2653 | 2335 | 2009-10-01 | 2009-10-29 | 138 | 0 | 0 | 0 | 0 | TOM GREEN | TOM GREEN | Tier 4 |  |  |  |  | Y
09TPIT0209 | Lighthouse Electric Co-Op distribution station | Muleta tap located on the Matador to Turkey 69 kV line | IN-SERVICE | AEP GROUP 470 | AEP/ETT | Dave Goetz 918-599-2653 | 2352 | 2009-11-30 | 2009-10-30 | 69 | 0 | 0 | 0 | 0 | MOTLEY | MOTLEY | Tier 4 |  |  |  |  | Y
09TPIT0096 | Floresville - 138kV Capacitor Bank Addition | Install a new circuit breaker and 18 MVAR capacitor bank at the Elmendorf substation in conjunction with a 21.6 MVAR capacitor bank at Floresville |  |  | CPS | S: David Riethmeyer | S-0364 | 2009-11-30 | 2009-10-30 | 138 | 0 | 0 | 0 | 10 | BEXAR | BEXAR | Tier 4 |  |  |  | 5155 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
09TPIT0199 | Champion Creek Switching Station | Construct a 345 kV switching station to connect a new wind farm. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8000-WACF | 2009-12-01 | 2009-10-30 | 345 | 0 | 0 | 0 | 0 | MITCHELL |  | Tier 4 |  |  |  | 1414 | Y
09TPIT0027 | Fox to Hilltop 138KV Conversion | Convert existing Fox to North Texas 69KV line to 138KV operation. Rebuild Fox to Brock line with double circuit construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-30 | 2009-11-03 | 138 | 0 | 3.7 | 0 | 0 | PARKER | PARKER | Tier 4 |  |  |  | 501, 495, 498, 487, 478 | Y |  | There is no reactive or transformer capability associated with this project
09TPIT0201 | IH20 15 Mvar Capacitor bank | Install 15 Mvar 69 kV Cap Bank at IH20 |  |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2009-11-15 | 2009-11-09 | 69 | 0 | 0 | 0 | 15 | REEVES | REEVES | Tier 4 |  |  |  | 38040 | Y
09TPIT0129 | Paducah 69/138 kV Station, Replace the existing 69/138 kV auto | Replace 69/138 kV auto at Paducah with an 90 MVA 69/138 kV with LTC and add 20 MVAR 138 kV shunt reactor | IN-SERVICE | AEP GROUP 289 | AEP/TNC | Brett Madison 918-599-2653 | 1436 | 2009-11-10 | 2009-11-10 | 138 | 0 | 0 | 90 | 0 | COTTLE |  | Tier 4 |  |  |  |  | Y
09TPIT0193 | J.K. Spruce to Pawnee - 345 kV Substation Equipment Upgrade | Replace Substation Equipment at J.K. Spruce in order to remove an existing MLSE |  |  | CPS | S: Cory Kaldacek | S-0543 | 2009-11-01 | 2009-11-15 | 345 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5400 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
09TPIT0192 | Krum | Convert to 138 kV operation |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-11-01 | 2009-11-16 | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  | 670 | Y
09TPIT0148 | Falcon Seaboard terminal equipment | Replace terminal equipment on circuit to Midland East. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R837-WA | 2009-12-01 | 2009-11-17 | 345 | 0 | 0 | 0 | 0 | HOWARD |  | Tier 4 |  |  |  | 1025 | Y
10TPIT0105 | Parker Switch - Everman 345 kV line | Construct 345 kV line on existing structures. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C035-WA | 2009-11-01 | 2009-11-17 | 345 | 86.3 | 0 | 0 | 0 | PARKER | TARRANT | CREZ |  |  |  | 1436, 1882, 1886, 1430, 1873 | Y |  | Project schedule details can be found in PUCT MCPR Docket No. 36146.
09TPIT0222 | Everman Switch | Install 345 kV breakers at Everman. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C035-WA | 2009-11-01 | 2009-11-17 | 345 | 0 | 0 | 0 | 0 | TARRANT |  | CREZ |  |  |  |  | Y |  | Project schedule details can be found in PUCT MCPR Docket No. 36146.
09TPIT0223 | Parker Switch | Upgrade Parker bus arrangement and connect Graham - Benbrook 345 kV line to Parker. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C035-WA | 2009-11-01 | 2009-11-17 | 345 | 0 | 0 | 0 | 0 | PARKER |  | CREZ |  |  |  |  | Y |  | Project schedule details can be found in PUCT MCPR Docket No. 36146.
09TPIT0007 | Spruce to Skyline - 345kV 2nd Circuit | Build second 345kV line from Spruce to Skyline on existing transmission structures |  | S-0127 | CPS | T: LeeRoy Perez S: Joe Rodriguez | T-0050 | 2009-11-13 | 2009-11-19 | 345 | 20.77 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 | 2007-05-08 | 2007-05-31 | N/A | 5371 5400 | Y |  | There are no transformers associated with this project
10TPIT0029 | Robertson to Watson Chapel Rebuild | Rebuild existing Robertson to Watson Chapel 138kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 | 2009-11-23 | 138 | 0 | 21.6 | 0 | 0 | ROBERTSON | LEON | Tier 4 |  |  |  | 32,33 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
10TPIT0120 | Live Oak-Gillespie | Replace under-rated limiting line terminal equipment at Live Oak and Gillespie to increase Live Oak (7412)-Rutherford (7130) to the conductor's rating. |  |  | CTEC | David Peterson 830-992-2250 david.peterson@ctec.coop |  | 2010-06-30 | 2009-11-24 | 69 | 0 | 0 | 0 | 0 | GILLESPIE |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
09TPIT0005 | Laredo Plant to Lobo, upgrade 69 kV to 138 kV line | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV | IN-SERVICE | AEP GROUP 216 | AEP/ETT | Bill Eakin 918-599-2653 | 1303 | 2009-11-29 | 2009-11-29 | 138 | 0 | 16.5 | 0 | 0 | WEBB | WEBB | Tier 1 | 2003-09-15 | 2004-02-19 | 2004-03-08 |  | Y
09TPIT0134 | York Creek (Galle) - New Substation | Construct a new 138-kV 22.4 MVA substation on the LCRA Zorn-Luling 138-kV transmission line. |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2009-11-30 | 2009-11-30 | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | 7227 | Y
09TPIT0200 | Caterpillar - New Substation | Build a 138-12.5 KV (2) 12-16-20 MVA substation on the existing GVEC 138 KV transmission line between Seguin-West and CMC (SMI) substations. |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2009-11-30 | 2009-11-30 | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N
09TPIT0188 | Tomball - Tomball Tap Ckt.66 | Reconductor Tomball - Tomball Tap Ckt.66 |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-11-30 | 2009-12-01 | 138 | 0 | 0.11 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 46510, 46511 | Y |  | No transformer capacity to be added.
10TPIT0136 | Bell County - Salado 138 kV line | Increase the operating temperature of the line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2009-12-01 | 2009-12-01 | 138 | 0 | 7 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3640, 3425 | Y
09TPIT0221 | Eagle Mountain - Alliance - Roanoke Switch terminal equipment | Upgrade 345 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2009-12-01 | 2009-12-01 | 345 | 0 | 0 | 0 | 0 | TARRANT |  | CREZ |  |  |  |  | Y
09TPIT0224 | Jacksboro Switch | Install 345 kV circuit breakers |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C039-WA | 2009-12-01 | 2009-12-01 | 345 | 0 | 0 | 0 | 0 | JACK |  | CREZ |  |  |  | 1429 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
09TPIT0158 | Midland East terminal equipment | Replace terminal equipment on circuit to Moss. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R838-WACF | 2009-12-01 | 2009-12-07 | 345 | 0 | 0 | 0 | 0 | MIDLAND |  | Tier 4 |  |  |  | 1022 | Y
09TPIT0213 | White Baker Station Serve OXY Century Plant | In White Baker Station add 138kV breaker and line position to serve new customer, OXY Century Plant. |  |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2009-12-09 | 2009-12-09 | 138 | 0 | 0 | 0 | 0 | PECOS |  | Tier 4 |  |  |  | 38431 | Y
07TPIT0253 | West Childress to Henry: Rebuild Dbl Ckt 138/69 kV Line | Rebuild Dbl Crkt 138/69 Line from West Chilldress to Childress 20th Street to connect BEC's Henry Substation (11/09) | IN-SERVICE | AEP GROUP 403 | AEP/BEC | John Pulay 918-599-2653 | 2279 | 2009-12-10 | 2009-12-10 | 69 | 1 | 0 | 0 | 0 | CHILDRESS | CHILDRESS | Tier 4 |  |  |  |  | Y
10TPIT0067 | Holbrook - New 138kV Substation | Loop new 138kV substation into the existing 138kV Coliseum to Kirby line |  | T-0136 | CPS | S: Keith Calle | S-0226 | 2010-01-29 | 2009-12-10 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5218 | Y |  | There are no transformers associated with this project
09TPIT0108 | Rio Pecos, Add SVC at Rio Pecos | Reconfigure Rio Pecos to add SVC and 2nd 138/69 kV auto | IN-SERVICE | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2227 | 2009-12-11 | 2009-12-11 | 69 | 0 | 0 | 0 | 90 | PECOS |  | Tier 4 |  |  |  |  | Y
09TPIT0195 | Raymond Barker to Verde Creek | The existing LCRA TSC 138 kV transmission line (approximately 1.9 miles) between the LCRA TSC Raymond Barker (7158) and Bandera Electric Cooperative (BEC) Verde Creek (7146) stations will be rebuilt. The rebuilt transmission line will consist of 2X795 ACSR conductor to provide a thermal rating of 440 MVA. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-12-16 | 2009-12-11 | 138 | 0 | 1.9 | 0 | 0 | KERR | KERR | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | CREZ Default project assigned to LCRA TSC
09TPIT0107 | Rio Pecos, Add 2nd 138/69 kV Auto & reconfig 69 kV bus | Reconfigure Rio Pecos to add SVC and 2nd 138/69 kV auto | IN-SERVICE | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2232 | 2009-12-11 | 2009-12-11 | 138 | 0 | 0 | 68 | 0 | PECOS |  | Tier 4 |  |  |  |  | Y
10TPIT0055 | Eagle Mountain 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C001-WA | 2009-12-01 | 2009-12-16 | 345 | 0 | 0 | 517 | 0 | TARRANT |  | CREZ | 2007-12-31 | 2008-02-26 | N/A | 11865, 11864 | Y |  | Project schedule details can be found in PUCT MCPR Docket No. 36146.
05TPIT0117 | HiCross to Slaughter Lane 138kV circuit | Establish a new 138kV circuit from HiCross to Slaughter Lane substation | COMPLETE |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P225 PLAN_117_P251 | 2009-11-09 | 2009-12-18 | 138 | 2.2 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 2 | 2008-11-25 | 2008-12-17 | 2009-02-06 | 9147,9292,9267, 9075 | Y
09TPIT0183 | Needle 69kV Substation | Disconnect customer owned Needle 69kV substation from 69kV Ckt.43 Crosby to Mont Belvieu and serve from distribution voltage. |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-12-31 | 2009-12-19 | 69 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 41140 | Y |  | 1) No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. 2) Bus #41140 will be removed from the base cases.
06TPIT0014 | LaPalma to Loma Alta, cut-in Los Fresnos at 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line | IN-SERVICE | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 645 | 2009-12-31 | 2009-12-22 | 138 | 0.1 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  |  | Y
06TPIT0133 | Los Fresnos, Convert 69 kV distribution substation to 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line | IN-SERVICE | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 1708 | 2009-12-31 | 2009-12-22 | 138 | 0 | 0 | 0 | 0 | CAMERON |  | Tier 4 |  |  |  |  | Y
07TPIT0238 | Krum - Allison - Decatur 138 kV line | Rebuild and convert 69 kV line to 138 kV operation |  | R510B & R511 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R510A-WACF | 2009-11-01 | 2009-12-28 | 138 | 0 | 19 | 0 | 0 | DENTON | WISE | Tier 3 | 2008-01-14 | 2008-05-19 | N/A | 1582, 1568, 1987, 1990, 1986 | Y
09TPIT0038 | Ben Davis Sub: Replace 138 kV Breakers due to interrupting rating | Replace existing circuit breakers due to interrupting rating |  |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T07005 | 2009-12-30 | 2009-12-31 | 138 | 0 | 0 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 968 | Y
08TPIT0200 | Interconnection between TNMP and BP Alternative Energy North America Inc | BP's one 244 MW steam turbine generating unit will be interconnected with TNMP's 138kV system at Greenbelt Switching Station in Texas City, TX | Most of the breakers have been installed. Remaining breakers are scheduled for delivery and installation |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com |  | 2009-12-30 | 2009-12-31 | 138 | 0 | 0 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  |  | N
08TPIT0156 | H.O. Clarke - Brays Ckt.09 | Raise conductors and upgrade limiting equipment at H.O. Clarke and Brays to increase thermal ratings. |  | 07TPIT0263 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-12-31 | 2010-01-05 | 138 | 0 | 2.62 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47150, 47050 | Y |  | 1) No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
07TPIT0098 | Replace five poles, Hickory - Locust 69kV Transmission Line | Replace five poles in an existing 69kV transmission line | On Schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600774 | 2010-03-31 | 2010-01-10 | 69 | 0 | 0.25 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 910, 914 | Y
10TPIT0097 | Salt Creek Reactor | Install 25 MVAR reactor at Salt Creek |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 | 2010-01-19 | 138 | 0 | 0 | 0 | -25 | KENT | KENT | Tier 4 |  |  |  | 743 | N
06TPIT0037 | Carrollton East - Renner 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M448-WA | 2009-12-01 | 2010-01-19 | 138 | 0 | 6.9 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2356, 2611, 2578, 2582 | Y |  | Carrollton East - Farmers Branch Gillis Rd section will be completed in 12/2008.
06TPIT0080 | Medina Lake-CPS (Part 1) | Construct a new 138-kV 795 ACSR transmission line (approximately 20 miles in length) from the BEC Medina Lake substation (7432) to the future CPS Energy Talley Road substation (5422), then continuing on to the CPS Energy Texas Research Park substation (5430). | LCRA projected completion date is March 2010. CPS Energy completed on September 23, 2009. | 07TPIT0034 CPS S-0275 | CPS / LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org PM:Hector Torres (210) 353-2404 HVTorres@cpsenergy.com | CPS T-0049 | 2010-01-08 | 2010-01-21 | 138 | 20.7 | 0 | 0 | 0 | BANDERA | BEXAR | Tier 2 | 2007-10-03 | 2007-11-03 |  | 5430 7432 | Y |  | CPS and LCRA have filed update letter with ERCOT. BEC is proposing a new load serving substation between Medina Lake and CPS.
09TPIT0175 | Reconfigure Ckt.03 Lynch - Cedar Bayou. | Reconfigure Ckt.03 Lynch - Cedar Bayou substation to create two new circuits Ckt.03 Lynch - EXXON and Ckt.03 Baytown - Cedar Bayou substation per customers request. |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-01-31 | 2010-01-22 | 138 | 0.7 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 41010, 40011, 40015, 40170, 40570 | Y |  | No transformer capacity to be added.
08TPIT0135 | Yellowjacket, Install 150 MVA Phase Shifting Transformer | Yellowjacket, Install 150 MVA 138 kV Phase Shifting Transformer on the SAPS 138 kV line | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2219 | 2010-01-28 | 2010-01-28 | 138 | 0 | 0 | 150 | 0 | MENARD |  | Tier 4 |  |  |  |  | Y
09TPIT0127 | Menard to San Angelo Power Station 138 kV Hairpin into Yellowjacket | Yellowjacket, Build new 138 kV Switch Station Station: Five postion ring with 2-90 MVA Auto 138/69 (LTC), 138 KV 28.8 MVAR Capacitor and 1- 10 MVA distribution bank | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2154 | 2010-01-28 | 2010-01-28 | 138 | 2 | 0 | 0 | 0 | MENARD | TOM GREEN | Tier 4 |  |  |  |  | Y
09TPIT0211 | San Angelo Power Station to Menard 138 kV line improvements | Rebuild part of SAPS to Menard 138 kV line by replacing structures and Move SAPS auto and add DCRS at North Brady | IN-SERVICE | AEP GROUP 472 | AEP/TNC | Brett Madison 918-599-2653 | 2359 | 2010-01-28 | 2010-01-28 | 138 | 0 | 0 | 0 | 0 | TOM GREEN | MENARD | Tier 4 |  |  |  |  | Y
10TPIT0134 | Gonzales, Build new 69 kV station | Add 2nd 138/69 kV autotransformer at Alamito Creek, and install a NaS Battery at Gonzales | IN-SERVICE | AEP GROUP 358 | AEP/ETT | Brett Madison 918-599-2653 | 1182 | 2010-02-01 | 2010-02-01 | 69 | 0 | 0 | 0 | 0 | PRESIDIO |  | Tier 4 |  |  |  |  | Y
10TPIT0153 | Graham terminal equipment | Upgrade terminal equipment on 345 kV line to Bowman |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C070-E | 2010-05-01 | 2010-02-01 | 345 | 0 | 0 | 0 | 0 | YOUNG |  | Tier 4 |  |  |  | 1430 | Y
06TPIT0247 | Salt Dome 69kV Substation | Construct a new Salt Dome substation in the STEC N. Clemville to S. Clemville circut. | Tie is delayed to verify load. Load customer delays and changing load level. Project scope may be reduced before actual construction. Name Changed from "United Brine" to "Salt Dome" |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2009-12-09 | 2010-02-10 | 69 | 0.1 | 0 | 0 | 0 | JACKSON |  | Tier 4 | 2006-03-23 | 2006-04-17 | N/A | 5551 | Y
08TPIT0167 | Friend Ranch, Add 2nd 138 kV 28.8 Mvar Shunt Capacitor | Reconfigure Rio Pecos to add SVC and 2nd 138/69 kV auto (available when needed) | IN-SERVICE | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2264 | 2010-02-28 | 2010-02-28 | 138 | 0 | 0 | 0 | 28.8 | CROCKETT |  | Tier 4 |  |  |  |  | Y
08TPIT0193 | Sonora to Hamilton 138 kV Line: Apply a dynamic rating with new structures | Raise necessary structures to increase MVA rating of Sonora to Hamilton 138 kV line | IN-SERVICE | AEP GROUP 386 | AEP/TNC/TCC | Brett Madison 918-599-2653 | 2231 | 2010-02-28 | 2010-02-28 | 138 | 0 | 0 | 0 | 0 | SUTTON | VAL VERDE | Tier 4 |  |  |  |  | Y
10TPIT0077 | Hamilton to Pancake Rebuild | Rebuild Hamilton to Pancake with 795ACSR, 138KV |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-08-01 | 2010-03-01 | 69 | 0 | 21.9 | 0 | 0 | HAMILTON | CORYELL | Tier 4 |  |  |  | 158258 | Y
06TPIT0077 | Rim Rock-Jack Furman | Construct a new 336 ACSR 138 kV transmission line (approximately 7.5 miles) between the existing Rim Rock substation (7143) and a new 138 kV switching substation (Jack Furman)(7141). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org | 1002912 | 2010-06-30 | 2010-03-01 | 138 | 7.5 | 0 | 0 | 0 | KERR |  | Tier 2 | 2005-09-01 | 2205-09-01 |  | SEE PROJECT DESCRIPTION | Y |  | The name of the new substation was changed from Goat Creek to Jack Furman.
09TPIT0178 | Fox to Granbury 138KV Conversion | Convert exisitng Fox to Granbury 69KV line to 138KV operation |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-11-01 | 2010-03-04 | 138 | 3 | 0 | 0 | 0 | PARKER | HOOD | Tier 4 |  |  |  | 306487478 | Y
10TPIT0146 | Seward Junction-Leander | Relocate two (2) structures( #84 #85) for Hwy 183A Roadwork |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2010-03-10 | 2010-03-05 | 138 | 0 | 0 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | N
10TPIT0092 | Crockett Cap Bank | Increase reactive capacity to 107.2 MVAR at 138kV Crockett substation. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-05 | 138 | 0 | 0 | 0 | 100 | HARRIS |  | Tier 4 |  |  |  | 47570, 47571 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
08TPIT0146 | Firerock, Add Phase Shifting Transformer | Firerock, Build new station and Add Phase Shifting Transformer East of Santa Anna on the Brownwood line | IN-SERVICE | AEP GROUP 391 | AEP/ETT | Ashley Beasley 918-599-2653 | 2269 | 2010-03-18 | 2010-03-07 | 138 | 0 | 0 | 150 | 0 | COLEMAN |  | Tier 4 |  |  |  |  | Y
09TPIT0004 | Laredo Plant to Lobo, rebuild 138 kV line | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV | IN-SERVICE | AEP GROUP 216 | AEP/ETT | Bill Eakin 918-599-2653 | 1304 | 2010-03-07 | 2010-03-07 | 138 | 0 | 15 | 0 | 0 | WEBB | WEBB | Tier 1 | 2003-09-15 | 2004-02-19 | 2004-03-08 |  | Y
10TPIT0002 | Lobo, build 345 kV for 675MVA autotransformer | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV | IN-SERVICE | AEP GROUP 216 | AEP/ETT | Bill Eakin 918-599-2653 | 1720 | 2010-03-07 | 2010-03-07 | 345 | 0 | 0 | 675 | 0 | WEBB |  | Tier 1 | 2003-09-15 | 2004-02-19 | 2004-03-08 |  | Y
09TPIT0003 | Lobo to San Miguel, build 345 kV line | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and con | IN-SERVICE | AEP GROUP 216 | AEP/ETT/TCC | Bill Eakin 918-599-2653 | 633 | 2010-03-07 | 2010-03-07 | 345 | 72 | 0 | 0 | 0 | WEBB | ATASCOSA | Tier 1 | 2003-09-15 | 2004-02-19 | 2004-03-08 |  | Y |  | Associated with STEC project 10TPIT0075
07TPIT0248 | San Miguel 345 kV line terminal for San Miguel to Lobo 345 kV line | Breakers, bus, relaying for San Miguel to Lobo 345 kV line termination | Previous 2007 date entry was a typo. Work is planned for 2009. Changed responsibility to STEC and AEP | 09TPIT0003 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-03-01 | 2010-03-10 | 345 | 0 | 0 | 0 | 0 | ATASCOSA |  | Tier 4 |  |  |  | 5901 | Y
10TPIT0075 | San Miguel to Lobo 345 kV line | Construct a 113.8 miles 345 kV line from San Miguel to Lobo. Joint project with AEP. STEC portion 41.8 miles | Previous 2007 date entry was a typo. Work is planned for 2009. Changed responsibility to STEC and AEP | 09TPIT0003 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-03-01 | 2010-03-10 | 345 | 41.8 | 0 | 0 | 0 | ATASCOSA | WEBB | Tier 1 | 2009-10-03 | 2009-02-04 | 2009-03-04 | 5901-80219 | Y
10TPIT0149 | Tomball - Tomball Tap Ckt.66 - Substation Equipment | Upgrade limiting equipment at Tomball substation to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-16 | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 46510, 46511 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0104 | Gonzales, add NaS Battery | Add 2nd 138/69 kV autotransformer at Alamito Creek, and install a Nas Battery at Gonzales | IN-SERVICE | AEP GROUP 358 | AEP/ETT | Brett Madison 918-599-2653 | 2281 | 2010-03-17 | 2010-03-17 | 69 | 0 | 0 | 0 | 0 | PRESIDIO |  | Tier 1 | 2008-03-21 | 2008-06-10 | 2008-07-15 |  | Y
08TPIT0086 | Exeter - New 138kV Substation | Construct new 138kV substation to replace Terrell Hills substation |  | T-0088 | CPS | PM: Ulrich Skerhut | S-0230 | 2010-03-02 | 2010-03-19 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5143 | Y |  | There are no transformers associated with this project
10TPIT0111 | Sandow Switch - Sandow Third 138 kV line | Build new 138 kv line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R732-WACF | 2010-03-01 | 2010-03-20 | 138 | 1 | 0 | 0 | 0 | MILAM | MILAM | Tier 2 |  | 2009-03-01 |  | 13430, 3430, 13434 | Y
10TPIT0112 | Sandow Switch Third 345/138 kV autotransformer | Install third 345/138 kV autotransformer and remove small autotransformer from service. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R736-WACF | 2010-03-01 | 2010-03-20 | 345 | 0 | 0 | 600 | 0 | MILAM |  | Tier 2 |  | 2009-03-01 |  | 3429, 13430 | Y
10TPIT0151 | Benbrook terminal equipment | Upgrade terminal equipment on 345 kV line to Parker |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5154-WACF | 2010-05-01 | 2010-03-21 | 345 | 0 | 0 | 0 | 0 | TARRANT |  | Tier 4 |  |  |  | 1873, 1869, 1870, 1436 | Y
10TPIT0152 | Parker terminal equipment | Upgrade terminal equipment on 345 kV line to Benbrook |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R586-WACF | 2010-05-01 | 2010-03-21 | 345 | 0 | 0 | 0 | 0 | PARKER |  | Tier 4 |  |  |  | 1436, 1873, 1869, 1870 | Y
10TPIT0143 | Childress 20th St to Henry: Rebuild Dbl Ckt 138/69 kV Line | Rebuild Dbl Crkt 138/69 Line from West Chilldress to Childress 20th Street to connect BEC's Henry Substation (11/09) | IN-SERVICE | AEP GROUP 403 | AEP/BEC | John Pulay 918-599-2653 | 2279 | 2010-03-21 | 2010-03-21 | 69 | 1 | 0 | 0 | 0 | CHILDRESS | CHILDRESS | Tier 4 |  |  |  |  | Y
09TPIT0084 | Tomball - Rothwood - Rayford Ckt.66 | Upgrade 138 kV Ckt.66 Tomball - Rothwood to increase thermal ratings | IN-SERVICE | 09TPIT0086 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-25 | 138 | 0 | 13 | 0 | 0 | HARRIS | MONTGOMERY | Tier 3 | 2008-03-26 | 2008-04-14 | 2008-05-20 | 46510, 46295, 46261 | Y | “Please see Requested Info in 09tpit0086” | Added as part of 2007 ERCOT 5 year plan projects. Energization dates for projects associated with Rothwood substation have been updated to match the current construction schedule.
09TPIT0085 | Convert Rayford 138 kV substation. | Convert Rayford from a double tap substation to a loop tap configuration substation. | IN-SERVICE | 09TPIT0086 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-25 | 138 | 0 | 0 | 0 | 0 | MONTGOMERY |  | Tier 3 | 2008-03-26 | 2008-04-14 | 2008-05-20 | 46261, 46262 | Y |  | Added as part of 2007 ERCOT 5 year plan projects. Energization dates for projects associated with Rothwood substation have been updated to match the current construction schedule.
10TPIT0071 | Rayford - Westfield Ckt.66 | Upgrade 138 kV Ckt.66 Rayford - Westfield to increase thermal ratings | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-25 | 138 | 0 | 9.14 | 0 | 0 | MONTGOMERY | HARRIS | Tier 4 |  |  |  | 46261, 46051 | Y |  | No transformer capacity to be added. Energization dates for projects associated with Rothwood substation have been updated to match the current construction schedule.
10TPIT0093 | Tomball - Westfield Ckt.81 | Upgrade 138 kV Ckt.81 Tomball - Westfield to increase thermal ratings | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-25 | 138 | 0 | 8.31 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 46510, 46512, 46052 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. Energization dates for projects associated with Rothwood substation have been updated to match the current construction schedule.
09TPIT0086 | Rothwood 345/138 kV substation | Build a new 345/138 kV Rothwood substation. Loop Ckt.74 Kuykendahl to King and 138 kV Ckt.66 Rayford tap section into the new substation. Add one 800 MVA 345/138 kV autotransformer at Rothwood substation. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-25 | 345 | 0.4 | 0 | 800 | 0 | HARRIS |  | Tier 3 | 2008-03-27 | 2008-04-14 | 2008-05-20 | 46290, 46295 | Y | (Q) I’ve been reviewing the SSWG cases and ERCOT’s 08/01/2008 TPIT to get a better understanding of the projects related to the new Rothwood 345/138 kV substation. In the 2010/2011 SSWG cases, as released, there are still significant overloads on the 138 kV branch from Rothwood to Rayford (46290-46261) for loss of branches 46512-46052 and 46570-45910. (A) Branches 46512-46052 and 46570-45910 do not share a common tower currently and will not share a common tower after the Rothwood project is complete; therefore, they are not included in the ERCOT contingency files posted with the SSWG cases. Furthermore, after the Rothwood project is finished, the circuit segment 46512-46052 will be part of a multi-section line with the circuit designation 46510-46570-&1 (Q) This overload is like the original 2009 overload of the Tomball – Rayford (46510-46261)138 kV line that results in unserved energy that this project is designed to fix. (A) The contingency that caused the unserved energy in the 5 year plan was the loss of the 345 kV double circuit line into Tomball overloading North Belt to Westfield (Q) The latest TPIT lists line upgrade projects on the 138 kV line from Tomball – Rothwood – Rayford going in in 2010. I do not believe that this project is captured in the 2010 or 2011 case. (A) It is captured in the cases; however, the scope of the upgrade had yet to be finalized; therefore, we only modeled bundling the Tomball to Rothwood to Rayford segments with 2-795ACSR. Our own studies on the 08DSB cases from June show a need to upgrade above this capacity because of single contingencies and the soon to be updated TPIT update will reflect these changes. (Q) Can any of you provide the ratings of the lines once the upgrades are complete? The current SSWG case currently has a ratings of 371/455/455 MVA for both 2010 and 2011 (A) The ckt 66 Tomball – Rothwood ratings are expected be 440/526/562. Ckt 66 Rothwood – Rayford ratings are expected to be at least 398/455/893. Final ratings on these segments are still to be determined. (Q) As a side note, the line upgrades associated with the branches from CWESFLD_ 138D – TRSWIG_138A and TRSWIG_138A – Humble__138F are not included in the case. We’ve already included those ratings in our cases though, I have no requests related to those branches. (Q) Additionally, there is an approximately 250% growth in load at Rayford, bus 46261, between 2009 and 2010. I just wanted to verify that this was correct. (A) The reason for the large increase in load is that with the Rothwood project Rayford is being converted from a double tap station to a loop-thru station. The model is adjusted accordingly by eliminating bus 46262 and moving its load (86.2 MW) to bus 46261 for a total of (67.5 + 86.2 MW). | Added as part of 2007 ERCOT 5 year plan projects. Energization dates for projects associated with Rothwood substation have been updated to match the current construction schedule.
08TPIT0079 | Steamboat, new 69 kV switching station | Build new Steamboat 69 kV switch station | IN-SERVICE | AEP GROUP 341 | AEP/TNC | Brett Madison 918-599-2653 | 2074 | 2010-03-31 | 2010-03-31 | 69 | 0 | 0 | 0 | 0 | TAYLOR |  | Tier 4 |  |  |  |  | Y
10TPIT0052 | Big Lake, Add 150 MVA Phase Shifting Transformer | Install a 138 kV Phase Shifting Transformer at Big Lake | IN-SERVICE | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2228 | 2010-03-31 | 2010-03-31 | 138 | 0 | 0 | 150 | 0 | REAGAN |  | Tier 4 |  |  |  |  | Y
10TPIT0058 | Lytton Springs Autotransformer Addition | Add a new 345-138 kV 478 MVA autotransformer at the Lytton Springs substation (9074). Terminate the Mendoza (7325) - Turnersville (7500) 138 kV transmission line (T-382) into the Lytton Springs substation 138 kV bus (9075), creating the new Turnersville (7500) - Lytton Springs (9075) and Mendoza (7325) - Lytton Springs (9075) 138 kV transmission lines. Upgrade the new Turnersville (7500) - Lytton Springs (9075) 138 kV transmission line from 795 ACSR (220MVA) to 1433 ACSS/TW (507 MVA). Upgrade the new Mendoza (7325) - Lytton Springs (9075) 138 kV transmission line from 795 ACSR (220 MVA) to bundled 795 ACSR (440 MVA). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-05-11 | 2010-04-01 | 345 | 0 | 7 | 478 | 0 | CALDWELL |  | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y
10TPIT0121 | Lolita: Replace Limiting Switches and Jumpers on Formosa to Lolita 138 kV Line | Upgrade generator disturbance monitoring, metering, and communications at the Formosa 138 kV substation. Add generator monitoring, protection, and communications at the Formosa CFB Plant. | In-Service | AEP GROUP 437 | AEP/TCC | Paul Hassink 918-599-2653 | 3336 | 2010-04-09 | 2010-04-09 | 138 | 0 | 11.84 | 0 | 0 | CALHOUN | JACKSON | Tier 4 |  |  |  |  | Y
09TPIT0196 | Pearsall to Moore SS 138 kV Line | Upgrade 12 miles composite core 1020 ACCC-TW 138 kV line conductor from Pearsall to Moore Switching Station. | Upgrade 138 kV line for new generation at Pearsall |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-04-01 | 2010-04-10 | 138 | 0 | 12 | 0 | 0 | FRIO | FRIO | Tier 4 |  |  |  | 5895-5827 | Y
10TPIT0150 | Elgin Switch terminal equipment | Upgrade 138 kV terminal equipment on line to Gilleland |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R734-WACF | 2010-05-01 | 2010-04-17 | 138 | 0 | 0 | 0 | 0 | WILLIAMSON |  | Tier 4 |  |  |  | 3650 | Y
10TPIT0110 | Sandow Switch - Elgin Switch 138 kV line | Rebuild existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R733-WACF | 2010-04-01 | 2010-04-17 | 138 | 0 | 21.8 | 0 | 0 | MILAM | WILLIAMSON | Tier 2 | 2008-07-07 | 2008-08-04 | 2009-03-31 | 13430, 3650 | Y
10TPIT0139 | Salado Switch | Add 345 kV breakers |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C007-WA | 2010-06-01 | 2010-04-17 | 345 | 0 | 0 | 0 | 0 | BELL |  | CREZ |  |  |  | 3699 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
08TPIT0158 | Baytown - Haney Ckt.66 | Reconductor and upgrade limiting equipment at Baytown to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-04-30 | 2010-04-29 | 138 | 0 | 7.1 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 40170, 40172, 40790 | Y |  | No transformer capacity to be added.
06TPIT0198 | Hickory Substation 69kV Bay Addition | Construct new 69kV bays to allow tie in of the new Iron Horse to Hickory transmission line | On Schedule | 07TPIT0095 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600128 | 2010-06-01 | 2010-05-01 | 69 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 910 | Y
07TPIT0095 | RD Wells to Hickory 69kV Transmission Line | Construct 1.6 miles of new 138kV transmission line to be operated at 69kV | On schedule | 07TPIT0091, 0092, 0094, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600130 | 2010-04-10 | 2010-05-01 | 69 | 1.6 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 932, 910 | Y
07TPIT0097 | Reconstruct 1.2 miles - Hickory to North Lakes 69kV Transmission Line | Reconstruct 1.2 miles of existing 69V transmission line | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600775 | 2010-03-01 | 2010-05-01 | 69 | 0 | 1.2 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 910, 915 | Y
07TPIT0091 | RD Wells 138kV to 69kV Interchange | Construct a new 138kV to 69 kV 150MVA interchange | On schedule | 07TPIT0092, 0094,0095, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600005 | 2010-04-10 | 2010-05-01 | 138 | 0 | 0 | 168 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 930, 932 | Y
10TPIT0099 | Goldthwaite to Evant | The existing LCRA TSC 138 kV transmission line (approximately 24 miles) between the LCRA TSC Goldthwaite (7070) and Evant (7068) stations will be rebuilt. The rebuilt transmission line will consist of 1X795 ACSR conductor to provide a thermal rating of 220 MVA. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-05-30 | 2010-05-01 | 138 | 0 | 24 | 0 | 0 | MILLS | LAMPASAS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | CREZ Default project assigned to LCRA TSC
10TPIT0131 | Elgin-Gilleland Creek | Upgrade the conductor on the 12.9-mile Elgin (3650)-Gilleland Creek (7336) 138 kV transmission line from 795 ACSR (220 MVA) to 1433 ACSS/TW (507 MVA). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-05-28 | 2010-05-01 | 138 | 0 | 12.9 | 0 | 0 | TRAVIS | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
08TPIT0128 | Stanton East - Big Spring Switch 138 kV line and Stanton East 138/69 kV autotransformer | Rebuild and convert an existing 69 kV line to a 138 kV line and install a 138/69 kV autotransformer at Stanton East |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8002-WACF | 2010-05-01 | 2010-05-01 | 138 | 0 | 21.6 | 60 | 0 | MARTIN | HOWARD | Tier 4 | 2008-12-12 | 2009-03-27 | 2009-07-21 | 1229, 1326, 1322, 1323 | Y
09TPIT0215 | Seadrift 69 kV substation | Construct new 69 kV substation connected to new line from Port O'Connor substation. Will tie to AEP Union Carbide in future. | Acquiring Right-Of-Way Easements | 05TPIT0092 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-04-30 | 2010-05-10 | 69 | 0 | 0 | 0 | 0 | CALHOUN |  | Tier 2 |  | 2001-06-22 | 2001-07-09 | 5598 | Y
10TPIT0124 | Port O'Conner to Seadrift 69 kV line | Construct new 12.4miles 795 MCM ACSR 69 kV line between the new Seadrift station and STEC's Port O'Connor substation. | In construction | 05TPIT0092 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-04-30 | 2010-05-10 | 69 | 12.4 | 0 | 0 | 0 | CALHOUN | CALHOUN | Tier 2 |  | 2001-06-22 | 2001-07-09 | 5596-5598 | Y
08TPIT0116 | CenterPoint Energy/TNMP Alvin interconnection | Build a new 345 kV, 3 breaker ring bus Meadow substation looped into Ckt.99 P.H. Robinson - Oasis. Move 345/138 kV autotransformer from PH Robinson to new Meadow substation for interconnection with TNMP 138 kV North Alvin bus. | IN-SERVICE | 07TPIT0161 | CNP, TNMP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-06-30 | 2010-05-17 | 345 | 0.1 | 0 | 500 | 0 | BRAZORIA |  | Tier 4 | 2006-07-25 | 2006-11-06 | 2007-01-16 | 43030, 42000, 42015 | Y |  | 1)_TNMP and CenterPoint Energy jointly studied project. 2)_No transmission circuits to be built, rebuilt or reconductored. 3) See Project #07TPIT0161 for reason for delay. 4) Moving P.H. Robinson Auto #3 (500MVA) to Meadow Substation 5) Meadow substation was formerly known as South Alvin.
09TPIT0013 | Skyline - Install a Third 345kV Autotransformer | Install one 600 MVA autotransformer at Skyline. |  |  | CPS | S: Joe Rodriguez | S-0182 | 2010-05-26 | 2010-05-25 | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR | Tier 4 | 2007-03-29 | 2007-04-20 | N/A | 5370 5371 | Y |  | There is no transmission line additions associated with this project
10TPIT0130 | Hondo -138 kV Capacitor Bank | Install 18 MVAR Capacitor at the Hondo substation |  |  | CPS | S: Thomas Fryer | S-0569 | 2010-05-28 | 2010-05-27 | 138 | 0 | 0 | 0 | 18 | BEXAR | BEXAR | Tier 4 |  |  |  | 5225 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
07TPIT0161 | Centerpoint Energy/TNMP Alvin Interconnection Project | Install 138 kV switching station on Alvin-Hastings transmission line and interconnect with Centerpoint 345-138 kV auto-transformer near Alvin. | Difficulties in acquistion of land of switching station site has delayed the project. | 08TPIT0116 | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | GCEC 27517, 27519 | 2010-05-01 | 2010-05-31 | 138 | 0 | 0 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 4 | 2006-07-06 | 2006-11-06 | 2007-01-07 | 39015 | Y | Autotransformer for this project is being relocated from PH Robinson.
10TPIT0116 | North Brady, Move DRCS from Rio Pecos to N Brady | Rebuild part of SAPS to Menard 138 kV line by replacing structures and Move SAPS auto and add DCRS at North Brady | IN-SERVICE | AEP GROUP 472 | AEP/TNC | Rue Galyean 918-599-2653 | 2358 | 2010-06-01 | 2010-06-01 | 69 | 0 | 0 | 0 | 0 | MCCULLOCH | MCCULLOCH | Tier 4 |  |  |  |  | Y
10TPIT0129 | Merida to Sommers - 138 kV Substation Equipment Upgrade | Replace Substation Equipment at Merida to remove MLSE on the Merida to Sommers 138kV transmission line |  |  | CPS | S: David Riethmeyer | S-0565 | 2010-06-01 | 2010-06-01 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5310 5395 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
10TPIT0127 | Austin to Tuttle - 138 kV Substation Equipment Upgrade | Replace Substation Equipment at Austin to remove MLSE on the Austin to Tuttle 138kV transmission lines |  |  | CPS | S: Keith Calle | S-0396 | 2010-06-01 | 2010-06-01 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5005 5435 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
10TPIT0107 | McNeil-Marshall Ford | Replace under-rated limiting line terminal equipment to increase McNeil (7334)-Marshall Ford (7356) to the conductor's rating. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-06-30 | 2010-06-01 | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
10TPIT0072 | Fayetteville-Willow Springs-New Bremen-Bellville South | Rebuild the 28-mile Fayetteville (7286)-Willow Springs (7273)-New Bremen (7271)-Bellville South (7270) 138 kV transmission line (T-216). Upgrade the conductor along the entire line to 1433 ACSS (450 MVA). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-06-01 | 2010-06-01 | 138 | 0 | 28.2 | 0 | 0 | FAYETTE | AUSTIN | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y
11TPIT0046 | Twin Buttes (76009) to Coleman/Brown County Line | Add the second 345 kV circuit (approximately 88 miles) to existing transmission line, double circuit capable structures, between the LCRA TSC Twin Buttes station (76009) and the Oncor Brown station (1444). Circuit ownership changes with Oncor at the Coleman/Brown County line. The new circuit will consist of Cumberland conductor to provide a thermal rating of 2988 MVA. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-06-29 | 2010-06-01 | 345 | 88 | 0 | 0 | 0 | TOM GREEN | COLEMAN | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | N |  | CREZ Default project assigned to LCRA TSC
11TPIT0045 | Divide to Twin Buttes | Add the second 345 kV transmission line (approximately 31 miles) to existing double circuit capable structures between the LCRA TSC Divide (76090) and Twin Buttes (76009) stations. The new transmission line will consist of 2x1590 ACSR Falcon ACSS Merrimack conductor to provide a thermal rating of 1678 MVA. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-06-04 | 2010-06-01 | 345 | 31 | 0 | 0 | 0 | COKE | TOM GREEN | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | CREZ Default project assigned to LCRA TSC
10TPIT0102 | Bowman - Jacksboro Switch 345 kV line | Rebuild existing 345 kV line. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C041-WA | 2010-06-01 | 2010-06-01 | 345 | 0 | 46.7 | 0 | 0 | ARCHER | JACK | CREZ |  |  |  | 1422, 1429 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
09TPIT0124 | Jacksboro Switch - Willow Creek 345 kV line | Rebuild 345 kV line for double-circuit operation. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C039-WA | 2010-06-01 | 2010-06-01 | 345 | 19.1 | 19.1 | 0 | 0 | JACK | WISE | CREZ |  |  |  | 1429, 1421 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. Cost is included in Willow Creek - Parker project.
10TPIT0156 | NW Carrollton Switch | Add 345 kV breaker. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C0008E | 2010-06-01 | 2010-06-01 | 345 | 0 | 0 | 0 | 0 | DALLAS |  | CREZ |  |  |  | 1730 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0106 | Killeen Switch - Salado Switch 345 kV line | Construct 345 kV line on existing structures |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C036-WA | 2010-03-01 | 2010-06-01 | 345 | 15.7 | 0 | 0 | 0 | BELL | BELL | CREZ |  |  |  | 3422, 3699 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0056 | Renner SVC Phase I | Install one static var compensator (+300 Mvar/-265 Mvar) |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4058-WA | 2010-06-02 | 2010-06-02 | 138 | 0 | 0 | 0 | 600 | DALLAS |  | Tier 1 | 2008-10-16 |  | 2009-02-01 | 12356, 12357 | Y |  | The first phase of the project was approved on 8/19/2008, and the second phase was approved on 2/2/2009. Phase I will go into service in May 2010, and Phase II will go into service in May 2011.
10TPIT0068 | Broadview to Fredericksburg Rd - 138kV line upgrade | Upgrade the existing Broadview to Fredericksburg Rd 138kV transmission line |  |  | CPS | PM: Ulrich Skerhut | T-0133 | 2010-06-07 | 2010-06-08 | 138 | 0 | 2.3 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5040 5170 | Y |  | There are no transformers associated with this project
11TPIT0025 | Anderson to Westover Hills - New 138kV Transmission Line | Build new 138kV line from Anderson - Westover Hills |  | S-0439 | CPS | T: LeeRoy Perez PM: Bruce Raney | T-0200 | 2010-06-01 | 2010-06-08 | 138 | 1.8 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 2 | 2008-08-01 | 2008-10-01 |  | 5003 5488 | Y |  | There are no transformers associated with this project
08TPIT0067 | Fort Worth Substation | Construct new 25MVA, 138kV to 13.2kV substation adjacent to TMPA's 138kV transmission line where it intersects US377 | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600821 | 2010-06-01 | 2010-06-10 | 138 | 0 | 4 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 919 | Y
06TPIT0010 | W. Levee - Norwood 345 kV line | Construct W. Levee - Norwood 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M477-WAC | 2010-06-01 | 2010-06-10 | 345 | 6.5 | 0 | 0 | 0 | DALLAS | DALLAS | Tier 3 | 2003-10-01 | 2004-02-01 | 2004-04-01 | 2398, 2406 | Y
10TPIT0144 | Tombstone: Build new 138 kV Box Bay structure | Interconnect Occidental Petroleum into new Tombstone station | IN-SERVICE | AEP GROUP 473 | AEP/ETT | Brett Madison 918-599-2653 | 2360 | 2010-06-15 | 2010-06-15 | 138 | 0 | 0 | 0 | 0 | PECOS | PECOS | Tier 4 |  |  |  |  | Y
08TPIT0003 | Hutto Switch - Salado Switch 345 kV line | Construct Hutto Switch - Salado Switch 345 kV line and Salado 345 kV Switching Station |  | R456 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R445-WA | 2010-06-01 | 2010-06-15 | 345 | 73.8 | 0 | 0 | 0 | WILLIAMSON | BELL | Tier 1 |  |  | 2004-12-18 | 3699, 3696 | Y
10TPIT0008 | Hutto Switch and 345/138 kV autotransformer | Create 345 kV switching station and install a 345/138 kV autotransformer |  | R445 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R456-WA | 2010-06-01 | 2010-06-15 | 345 | 0 | 0 | 600 | 0 | WILLIAMSON |  | Tier 1 |  |  | 2004-12-18 | 3696, 3666 | Y
10TPIT0098 | Henderson Ranch Switching Station | Construct new switching station to connect a new power plant |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R580-WA | 2010-06-01 | 2010-06-17 | 345 | 0 | 0 | 0 | 0 | JACK |  | Tier 4 |  |  |  | 1443 | Y
10TPIT0042 | Ables Springs 138 kV line and point of interconnection (Oncor Electric Delivery portion only) | Construct 138 kV line and point of interconnection |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3055-WA | 2010-07-01 | 2010-06-21 | 138 | 15.67 | 4.97 | 0 | 0 | KAUFMAN | HUNT | Tier 2 | 2007-01-05 | 2007-05-01 | N/A | 12469, 12470 | Y |  | The point of interconnection and eastern line were placed into service in May 2010.
10TPIT0128 | Sommers to Kirby & Sommers to Beck to Kirby - 138 kV Substation Equipment Upgrade | Replace Substation Equipment at O.W. Sommers, Beck Rd. and Kirby to remove MLSE on the Sommers to Kirby & Sommers to Beck to Kirby 138kV transmission lines |  |  | CPS | S: Ricardo Renteria | S-0561 | 2010-06-30 | 2010-06-30 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5395 5035 5250 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
07TPIT0043 | Wynn Joyce-Miller line 69 kV to 138 kV voltage conversion | Converts voltage for the line |  |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 2.81 | 0 | 0 | DALLAS | [5 empty] | 811, 824 | Y
07TPIT0044 | Miller 69 kV to 138 kV voltage conversion | Converts voltage for the substation |  |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 0 | 0 | 0 | DALLAS | [5 empty] | 824 | Y
07TPIT0046 | Newman-Miller line 69 kV to 138 kV voltage conversion | Converts voltage for the line |  |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 2.27 | 0 | 0 | DALLAS | [5 empty] | 814, 824 | Y
07TPIT0047 | Centerville-Miller line 69 kV to 138 kV voltage conversion | Converts voltage for the line |  |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 2.68 | 0 | 0 | DALLAS | [5 empty] | 810, 824 | Y
09TPIT0185 | Quanum to Airpro to Shell Ckt.85 | Upgrade limiting equipment at Airpro substation to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 41330, 40070, 41450 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
10TPIT0145 | Pelican 138 kV: Add second tap for generation interconnect | Cotton Wind Farm Interconnect Facilities | IN SERVICE | AEP GROUP 397 | AEP/ETT | Tommy Vannoy 918-599-2653 |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 0 | 0 | 0 | SAN PATRICIO |  | Tier 4 |  |  |  |  | Y
10TPIT0137 | Krum Tap 138 kV Switching Station | Construct 138 kV switching station |  | R510D-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R510C-WACF | 2010-06-01 | 2010-06-30 | 138 | 0 | 1 | 0 | 0 | DENTON |  | Tier 3 | 2008-01-14 | 2008-05-19 | N/A | 1582, 1568, 1987, 1990, 1986 | Y
10TPIT0138 | Krum Tap 138 kV line | Rebuild existing 138 kV line |  | R510C-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R510D-WA | 2010-06-01 | 2010-06-30 | 138 | 0 | 3.3 | 0 | 0 | DENTON | DENTON | Tier 3 | 2008-01-14 | 2008-05-19 | N/A | 1987, 1986 | Y
09TPIT0194 | Taylor Expansion | Close in 138kV ring bus at Taylor Substation | New |  | SU | Dwight Yarbrough, 956-687-5600, dyarbrough@sharylandUtilties.com | PR08.05149.CAP | 2010-07-01 | 2010-07-15 | 138 | 0.2 | 0 | 0 | 0 | HIDALGO |  | Tier 4 |  |  |  | 8821 | Y |  | CCN 30192
09TPIT0190 | Spunky to Georges Creek and New Hope Rebuilds | Rebuild Spunky to New Hope and Spunky to Georges Creek with 795 ACSR conductor |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-09-15 | 2010-07-16 | 69 | 0 | 10.2 | 0 | 0 | JOHNSON | SOMERVELL | Tier 4 |  |  |  | 357384387 | Y
09TPIT0179 | SLU Taylor Road Substation: Loop station into line | Hairpin SLU Taylor Substation into South McAllen to Frontera 138kV Line | IN-SERVICE | AEP GROUP 458 | AEP/TCC/SLU | Rich Haley 918-599-2653 | 3326 | 2010-07-23 | 2010-07-23 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  |  | Y
10TPIT0155 | Cedar Hill Switch 345/138 kV autotransformer | Replace failed autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4083A-E | 2010-08-01 | 2010-08-01 | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2420,2422, 2421 | Y
09TPIT0083 | P.H. Robinson - Oasis Ckt.99 | Raise conductors and upgrade in-series equipment at P.H. Robinson to increase thermal rating. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-06-30 | 2010-08-17 | 345 | 0 | 20.45 | 0 | 0 | GALVESTON | BRAZORIA | Tier 4 |  |  |  | 42000, 43035 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
10TPIT0117 | TECO Generation | Interconnect a new generation plant at TECO substation. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-09-30 | 2010-08-24 | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 48865, 47430 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. Commercial operation scheduled for June 2010
05TPIT0092 | Seadrift to AEP Union Carbide 69 kV line | Construct new 12.4 miles 795 MCM ACSR 69 kV line between the AEP Union Carbide station and STEC's new Seadrift substation. | Construction delays- weather |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-09-01 | 2010-09-01 | 69 | 12.4 | 0 | 0 | 0 | CALHOUN | CALHOUN | Tier 2 |  | 2001-06-22 | 2001-07-09 | 5598-80135 | Y
10TPIT0140 | Second Hasse 138 / 69 Autotransformer | Install 40 MVA 138 / 69 kV autotransformer at Hasse |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2010-09-23 | 2010-09-22 | 138 | 0 | 0 | 40 | 0 | COMANCHE |  | Tier 4 |  |  |  | 277, 1649 | Y
10TPIT0135 | La Quinta: Temporary Connection into Falfurrias to Lobo 138kV Line | Construct new 138kV La Quinta Substation to directly interconnect 150MW Cedro Hill Wind Farm | IN SERVICE | AEP GROUP 398 | AEP/ETT | Tommy Vannoy 918-599-2653 | 3353 | 2010-09-27 | 2010-09-27 | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB | Tier 4 |  |  |  |  | Y
09TPIT0133 | Jim Christal Substation 138kV Reconstruction | Reconstruct 138kV section of the station installing five 138kV circuit breakers to break the Denton West to Denton North transmission line into two sections | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602153 | 2010-11-01 | 2010-10-01 | 69 | 0 | 2 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 916 | Y
09TPIT0135 | CSU Dowling Road Substation | Install (3) Breaker ring to include (2) 138 lines and tap to College Station Utilities |  |  | BTU/CSU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Randy Trimble, 979-821-5728, rtrimble@btutilities.com |  | 2010-09-01 | 2010-10-01 | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
10TPIT0100 | Tippett (76001) to North McCamey (76032) | Add the second 138 kV transmission line (approximately 15 miles) to existing double circuit capable structures between the LCRA TSC North McCamey station (76032) and the new Tippett station (76001). The new transmission line will consist of 2X795 ACSR conductor to provide a thermal rating of 448 MVA. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-10-01 | 2010-10-10 | 138 | 15 | 0 | 0 | 0 | UPTON | UPTON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | CREZ Default project assigned to LCRA TSC
10TPIT0147 | San Miguel to Pawnee 138 kV reroute | Reroute San Miguel to Pawnee 138 kV circuit to parallel 345 kV circuit per PUCT order |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-11-01 | 2010-10-10 | 138 | 0 | 11 | 0 | 0 | ATASCOSA | KARNES | Tier 4 |  |  |  | 5902-5727 | Y
10TPIT0113 | Odessa EHV Third 345/138 kV autotransformer | Install 345/138 kV autotransformer and tertiary shunt reactors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8004-WA | 2010-12-15 | 2010-11-01 | 345 | 0 | 0 | 504 | -75 | ECTOR |  | Tier 4 |  |  | 2009-07-21 | 1027, 1028 | Y | 2009-R6 | ERCOT BOD approved this project as part of the RMR exit strategy for Permian Basin generation.
09TPIT0170 | Tyler Bullard Road terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R836-WA | 2010-10-01 | 2010-11-02 | 138 | 0 | 0 | 0 | 0 | SMITH |  | Tier 4 |  |  |  | 3219 | Y | 2009-R37
10TPIT0118 | Bandera-Verde Creek Rebuild | Rebuild and upgrade the 15 mile Bandera - Verde Creek 336 ACSR 138kV transmission line to 2- 795 ACSR 138kV. |  |  | Bandera Electric | Brian D. Bartos (830) 796-6074 b.bartos@banderaelectric.com | 134142 | 2010-11-10 | 2010-11-10 | 138 | 0 | 15 | 0 | 0 | BANDERA | KENDALL | CREZ |  |  |  |  | N |  | The project will now to bundle the 795 conductor per ERCOT recommendation.
10TPIT0119 | Add 2nd Autotransformer at Bandera | Install a second 24/32/40 MVA 138/69kV autotransformer at Bandera Substation. |  |  | Bandera Electric | Brian D. Bartos (830) 796-6074 b.bartos@banderaelectric.com | 151272 | 2010-11-10 | 2010-11-10 | 138 | 0 | 0 | 40 | 0 | BANDERA | BANDERA | CREZ |  |  |  |  | N
07TPIT0034 | Medina Lake-Pipe Creek Rebuild (formally (Medina Lake-CPS Cagnon (Part 2)) | Rebuild and upgrade the 7.8 mile Pipe Creek (7437) - Medina Lake (7432) 1/0 ACSR 69kV transmission line to 795 ACSR 138kV. |  | 06TPIT0080 | Bandera Electric | Brian D. Bartos (830) 796-6074 b.bartos@banderaelectric.com | 57596 | 2010-11-10 | 2010-11-10 | 138 | 0 | 7.8 | 0 | 0 | BANDERA | BANDERA | Tier 4 | 2003-10-01 | 2003-11-01 |  | See Project Description | Y |  | This project was formally known as Medina Lake - CPS Cagnon (Part 2). Submissions to ERCOT RPG for review where concurrent with Medina Lake - CPS Cagnon (Part 1)
09TPIT0018 | Reagor Springs to India Rebuild/Upgrade | Upgrade/rebuild existing Reagor Springs. to India line |  |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2010-11-16 | 2010-11-11 | 69 | 0 | 17 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 210, 214, 215 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project

## TPITCancelledNoCost12012010
DECEMBER BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) CANCELLED PROJECTS As Of 09/01/2010
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) (only in completed tab) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location of Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Requested Additional Information (Optional) | Other (Optional)
14TPIT0001 | Circuit 3121/3122 Lytton-Holman-Fayette Reconductor | Replace conductor, insulator and hardware from Lytton Springs to Holman to Fayette. | Cancelled |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P083 | 2015-06-01 |  | 345 | 0 | 61.4 | 0 | 0 | BASTROP | CALDWELL | Tier 4 |  |  |  | 7055,9073,9074 | Y
13TPIT0010 | Decker Plant to Dessau Rebuild | Replace each triple lattice structures with two double circuit structures and reconductor to 3000 Amps. |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P198 | 2016-06-01 |  | 138 | 0 | 12 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9187, 9271, 9193 | Y
15TPIT0001 | Holly to Brackenridge to Harris to Holly Reconductor | Reconductor with bundle 795 ACSR and convert the existing (remaining) 69 kV loop to 138 kV operation. | Under Evaluation |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P073\ | 2016-10-01 |  | 138 | 0 | 8.57 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9252 | Y
07TPIT0048 | Bergstrom to Carson Creek 138kV circuit | Establish a new 138kV transmission circuit from Bergstrom to Carson Creek substation with bundled 795 ACSR Drake conductors. | Under Evaluation |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P074 PLAN_117_P031 PLAN_117_P168 | 2016-12-01 |  | 138 | 2.3 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 2 |  |  |  | 9163, 9175 | Y
07TPIT0049 | Bergstrom to Sand Hill 138kV circuit | Establish a new 138kV transmission circuit from Bergstrom to Sand Hill switchyard with bundled 795 ACSR Drake conductors. | Under Evaluation |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P075 PLAN_117_P169 PLAN_117_P056 | 2016-12-01 |  | 138 | 4 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9163, 9216 | Y
13TPIT0008 | Burleson to Fiesta to Central Austin to Koenig to Northland 138kV conversion | Convert the existing 69kV circuits from Burleson to Northland to 138kV operation. The circuits will be rated at 2000 Amps. | Under Evaluation |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P103 | 2016-12-01 |  | 138 | 0 | 8 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9120, 9121, 9244, 9269, 9227, 9128, 9129 | Y
13TPIT0009 | Koenig Lane to Justin Lane to McNeil 138kV conversion | Convert the existing 69 kV circuits from Koenig to Justin Lane to McNeil to 138kV operation. | Under Evaluation |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P116 | 2016-12-01 |  | 138 | 0 | 5.25 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9227, 9079 | Y
10TPIT0003 | Hidden Valley to Lakeway New 138kV Circuit (new) | Establish a new 138kV transmission circuit between Lakeway and Hidden Valley substation. | Under Evaluation |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | N/A | 2017-12-01 |  | 138 | 4 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 2 |  |  |  | 9207, 9235 | N
10TPIT0004 | Lakeway to Trading Post New 138kV Circuit (new) | Establish a new 138kV transmission circuit between Lakeway and Trading Post substation. | Under Evaluation |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | N/A | 2017-12-01 |  | 138 | 3.8 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 2 |  |  |  | 9282, 9235 | N
10TPIT0005 | Patton Lane to Trading Post New 138kV | Establish a new 138kV transmission circuit between Trading Post and Patton Lane substation. | Under Evaluation |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P055 PLAN_117_P076 PLAN_117_P156 | 2017-12-01 |  | 138 | 12 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 2 |  |  |  | 9282, 9253 | Y
12TPIT0030 | Kendall (7046) to Gillespie (7131) | Construct a new double circuit capable 345 kV transmission line (approximately 29 miles) between the Kendall station and the Gillespie station. The new 345 kV transmission line will consist of 2x1590 ACSR Falcon conductor to provide a thermal rating of 1678 MVA |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2013-05-01 |  | 345 | 29 | 0 | 0 | 0 | KERR | GILLESPIE | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y
12TPIT0031 | Gillespie (7131) to Newton (3690) | Construct a new double circuit capable 345 kV transmission line (approximately 105 miles) between the Gillespie station (7131) and the Newton station (99632). The new transmission line will consist of 2x1590 ACSR Falcon conductor to provide a thermal rating of 1678 MVA. Upgrade the Eckert (7122)-Nebo (7124) 69 kV transmission line (T-126) to 138 kV operation (approximately one (1) mile). Move the line tap to the LCRA TSC Gillespie-Horseshoe Bay 138 kV transmission line (T-448). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2014-10-01 |  | 345 | 105 | 0 | 0 | 0 | GILLESPIE | LAMPASAS | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y
12TPIT0023 | Gillespie Autotransformer Addition | Add one new 345-138 kV 672 MVA autotransformer at the Gillespie substation. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-06-01 |  | 345 | 0 | 0 | 672 | 0 | GILLESPIE |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  | CREZ Default project assigned to LCRA TSC

## TPIT5YearPlanProjects
Project Number | Project Name | Proposed in-service year | Status of Project | Associated TPIT ERCOT Project Number(s) | Notes
2009-R1 | Moss-Westover 138-kV line upgrade | 2011 | Planning Stage |  |  | Planning Stage
2009-R2 | Crane 69-kV bus tie upgrade | 2011 | Design Stage | 11TPIT0120 | Pegasus 138 kV Tap and Point of Interconnection project replaces this project. | In RPG Process
2009-R3 | Ackerly-Lamesa upgrades | 2011 | In RPG Process | 11TPIT0060 |  | Canceled
2009-R4 | Odessa North-North Cowden 69-kV line upgrade | 2011 | Planning Stage | 14TPIT0009 |  | In Construction
2009-R5 | Holt-Emma Tap 69-kV line upgrade | 2011 | Planning Stage | 14TPIT0008 |  | Design Stage
2009-R6 | Odessa EHV third 345/138-kV autotransformer addition | 2011 | In Construction | 10TPIT0113 |  | CCN
2009-R7 | Close San Angelo Power Station 138-kV bus tie | 2010 |  |  |  | In Service
2009-R8 | Abilene South-Ballinger upgrades | 2010
2009-R9 | Montague-Johnson Switch-Bowie 69-kV line upgrade | 2011 | Planning Stage
2009-R10 | Olney-Rice Switch 138-kV line upgrade | 2011 | Planning Stage | 10TPIT0141
2009-R11 | Denton area 138-kV line upgrades | 2011
2009-R12 | Payne-M&M POI 138-kV line upgrades | 2012 | Planning Stage | 08TPIT0109
2009-R13 | Add a second Carrollton Northwest-Collin Switch 138-kV line project | 2013 | Planning Stage | 11TPIT0032
2009-R14 | Frisco-Collin Switch 138-kV line upgrade | 2012 | Design Stage | 08TPIT0068
2009-R15 | Collin Switch second 345/138-kV autotransformer addition | 2013 | Planning Stage | 09TPIT0042
2009-R16 | Austin Ranch #1-Colony 138-kV line upgrade | 2010 | Planning Stage | 10TPIT0018
2009-R17 | Lewisville second 345/138-kV autotransformer addition | 2012 | Planning Stage | 07TPIT0042
2009-R18 | Highland TNP-West TNP 138-kV line uprate | 2013
2009-R19 | Mesquite West-Mesquite Western Electric-Prairie Creek 138-kV line upgrade | 2012 | Planning Stage | 14TPIT0016
2009-R20 | Garland area 138-kV line upgrades | 2011
2009-R21 | West Levee 138-kV bus split | 2011 | Planning Stage
2009-R22 | Sargent Road-St. Augustine 138-kV line upgrade | 2011 | Planning Stage
2009-R23 | Industrial East-Compton-Cedar Crest East 138-kV line upgrade | 2011 | Planning Stage | 13TPIT0059
2009-R24 | Cedar Crest-South Oak Cliff 138-kV line upgrade | 2012 | Planning Stage
2009-R25 | Mayfield-Cedar Hill 138-kV line upgrade | 2011 | Planning Stage
2009-R26 | Cedar Hill second 345/138-kV autotransformer addition | 2011 | Planning Stage | 13TPIT0062 | Addition of a second autotransformer has been deferred because the existing autotransformer failed and was replaced by a larger autotransformer.
2009-R27 | Randol Mill-Hemphill 138-kV line terminal equipment upgrade | 2011 | Planning Stage
2009-R28 | Hicks 345/138-kV autotransformer and 138-kV line project | 2013 | Planning Stage
2009-R29 | Downing-Mountary 69-kV line upgrade | 2014 | Planning Stage
2009-R30 | Robinson-Robinson Northwest 138-kV line upgrade | 2012 | Planning Stage
2009-R31 | Belton-Belton Southwest 138-kV line upgrade | 2011 | Planning Stage
2009-R32 | Killeen Switch-Killeen South-Killeen Fort Hood Tap 138-kV line upgrade | 2011 | Planning Stage |  | Killeen Switch - Killeen South 138 kV line upgrade is planned for 2011. The Killeen South - Killeen Fort Hood Tap 138 kV line upgrade is under study.
2009-R33 | Hutto Switch second 345/138-kV autotransformer addition | 2013 | Planning Stage
2009-R34 | Gilleland Creek 138-kV bus tie upgrade | 2014
2009-R35 | Whitestone-Buttercup 138-kV line upgrade | 2013
2009-R36 | McNeil-Summit-Williamson 138-kV line upgrade | 2013 | Planning Stage | 08TPIT0034 | McNeil to Summit upgrade is scheduled for May 2012
2009-R37 | Elkton-Tyler Bullard-Tyler Loop 138-kV line terminal equipment upgrade | 2014 | Planning Stage | 09TPIT0170
2009-R38 | PH Robinson-Alta Loma 138-kV line upgrade | 2012 | Design Stage | 10TPIT0126
2009-R39 | Alvin area 138-kV line reliability upgrades | 2013
2009-R40 | Galveston area 138-kV line upgrades | 2011 | Design Stage | 11TPIT0074
2009-R41 | Texas City Water-Intercity-Lamarque 69-kV line upgrade | 2011
2009-E1 | Scurry County upgrades | 2014
2009-E2 | Midland East-Stanton West 138-kV line upgrade | 2014 | Planning Stage
2009-E3 | Close Sonora Atlantic-Sonora 69-kV line | 2010
2009-E4 | Seagoville-Kleburg Tap 138-kV line upgrade | 2014 | Planning Stage
2009-E5 | Tyler Bullard-Tyler Loop 138-kV line upgrade | 2010 | Design Stage | 09TPIT0170
2009-E6 | Shamburger-Tyler Northwest 138-kV line upgrade | 2014 | Planning Stage | 09TPIT0122
2009-E7 | Alvin area 138-kV line economic upgrades | 2010
2009-E8 | Oasis-Meadow 345-kV line upgrade | 2011 | Design Stage | 11TPIT0113
2009-E9 | Kenedy Switch Station #1-Kenedy Substation second 69-kV line addition | 2014
2009-E10 | HEC-Aderhold Substation 138-kV line upgrade | 2014
2009-E11 | South McAllen-Las Milpas 138-kV line series upgrade | 2014

## TransmissionOwnerProjContacts
TRANSMISSION OWNER | TPIT DISTRIBUTION | Primary Contact | Primary Email Address | Primary Phone | Secondary Contacts | Secondary Email Addresses | Secondary PHONE
AEP | Primary & Secondary | Bob Healey | bhealey@aep.com | Bob Healey: 918 599 2249 | Glen Reed; David Kidd; Brad Myers; Sugam Patel | gareed@aep.com; dekidd@aep.com; rlbentz@aep.com; naward@aep.com; smdsouza@aep.com; camatthes@aep.com; blmyers@aep.com; sgpatel@aep.com; pcbelkin@aep.com | David Kidd: 918 599 2637 Glen Reed: 918 599 2664 Brad Myers: 918 599 2690
AUSTIN ENERGY | Primary & Secondary | Ken Chui | ken.chui@austinenergy.com; | Ken: 512 322 6745 | Armke, James; Mathew, Biju; Ebrahimian, Reza; Hunt, Dandy | James.Armke@austinenergy.com; biju.mathew@austinenergy.com; reza.ebrahimian@austinenergy.com; dandy.hunt@austinenergy.com; | James: 512 322 6705 Biju: 512 322 6381 Reza: 512 322 6740 Dandy: 512 322 6748
Bandera Electric | Primary | Lee Pressler | l.pressler@banderaelectric.com | Lee: 830 796 6079 | Brian Bartos | b.bartos@banderaelectric.com | Brian: 830 796 6074
BEPC (BRAZOS ELECTRIC) | Primary & Secondary | Brion Ryan | bryan@brazoselectric.com | Brion: 254 750 6353 | David Albers; Dwight Beckman | dalbers@brazoselectric.com; dbeckman@brazoselectric.com | David: 254 750 6358 Dwight: 254 750 6373
BPUB | Primary | Ramon Sanz | rsanz@brownsville-pub.com; | Ramon: 956 983 6203 | James McCann | jmccann@brownsville-pub.com; | James: 956 983 6204
BTU | Primary & Secondary | James Tanneberger | jtanneberger@btutilities.com | James: 979 821 5763 | Randy Trimble | rtrimble@btutilities.com | Randy: 979-821-5728 979-229-3154 (cell)
CNP | Primary & Secondary | Wayne Kemper | wayne.kemper@centrpointenergy.com | Wayne: 713 207 2192 | Wesley Woitt; Paul Rocha; Hanson John; Cody Mann; Karolyn Skalany | wesley.woitt@centerpointenergy.com; paul.rocha@centerpointenergy.com; john.hanson@centerpointenergy.com; cody.mann@centerpointenergy.com; karolyn.skalany@centerpointenergy.com | Wesley Woitt: 713-207-2760 Paul Rocha: 713-207-2768 John Hanson: 713-207-2754 Cody Mann: 713-207-3149 Karolyn Skalany: 713-207-3614
COCS | Primary | Tony Michalsky | tmichalsky@cstx.gov; | Tony: 979 764 3438 | Aguie Palmisano; Timothy Crabb; David Massey; David Roye | apalmisano@cstx.gov; tcrabb@cstx.gov; dmassey@cstx.gov; droye@cstx.gov; | Augie 979 764 3447 Timothy 979 764 3439 David 979 764 3493 David R 979 764 5021
CPS | Primary & Secondary | Basileo Rocha | bdrocha@cpsenergy.com; | Basileo: 210 353 4933 | Kenneth Bowen Blake Williams | kbowen@cpsenergy.com; bawilliams@cpsenergy.com; | Kenneth: 210 353 4142 Blake: 210 353 3557
CTT (Cross Texas Transmission) | Primary & Secondary | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310 | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310
DENTON | Primary & Secondary | Chuck Sears | Chuck.Sears@cityofdenton.com; | Chuck: 940 349 7111 | Brent Heath | brent.heath@cityofdenton.com; | Brent: 940 349 7180
GARLAND | Primary & Secondary | Danh Huynh | Dhuynh@garlandpower-light.org | Danh: 972 205 3826 | Grubbs, David; Fred Sherman; Steve Zaragoza | Dgrubbs@garlandpower-light.org; FredS@gplops.org; stevez@gplops.org | David: 972 205 2664 Fred: 972 205 3184 Steve: 972-205-3098
Golden Spread EC | Primary & Secondary | Shane McMinn | smcminn@gsec.coop; | Shane: 806 379 7766 | Shane McMinn | smcminn@gsec.coop; | Shane: 806 379 7766
LCRA TSC; PEC; SBEC; GVEC; City of Georgetown; BBEC,CTEC, NBU | Primary & Secondary | Christina Doerr | christina.doerr@lcra.org; | Christina: 512 369 4514 | Sergio Garza | sergio.garza@lcra.org; | Sergio: 512 369 4149 Brad: 512 369 4104
Lone Star | Primary & Secondary | Julius Horvath | julius.horvath@lonestar-transmission.com | Julius: 512-236-3135 | Dan Mayers | d.j.mayers@nexteraenergy.com | Dan: 561 694 4732
ONCOR | Primary & Secondary | Mike Juricek | Michael.Juricek@oncor.com; | Mike: 214 743 6671 | Larry Reiter, Travis Besier | Travis.Besier@oncor.com; Larry.Reiter@oncor.com; | Larry: 214 743 6672 Travis: 214 486 4917
Sharyland Utilities | Primary & Secondary | Mark Caskey | mcaskey@sharylandutilities.com | Mark: 214 978 8243 | Michael Glass, Dwight Yarbrough | mglass@sharylandutilities.com; dyarbrough@sharylandutilities.com | Michael: 956 687 5600, Dwight: 956 687 5600
STEC | Primary & Secondary | Doug Evans | devans@stec.org | Doug: 361 485 6459 | Cory Allen Loretta Gallaga | cory@stec.org; lgallaga@stec.org; | Cory: 866 225 5683 X2531 Loretta: 956 514 1289
TMPA | Primary & Secondary | Eric Schroeder | eschroeder@texasmpa.org; | Eric: 936 873 1124 | Frank Owens | fowens@texasmpa.org; | Frank: 936 873 1120
TNMP | Primary & Secondary | Mohammed Uddin | Mohammad.Uddin@tnmp.com; | Mohammad: 409 948 8451 x232 | Aars, Alton; McDaniel, Rex | Rex.McDaniel@tnmp.com; Alton.Aars@tnmp.com; | Rex:409 948 8451 X238 Alton:972 420 4189
Wind Energy Texas Transmission (WETT) | Primary & Secondary | Patsy Baynard | patsy.baynard@windenergyoftexas.com | Patsy: 512 279 7372 | Paul Steckley | Paul.Steckley@BrookfieldPower.com | Paul 508 251 7690