## Read Me
TPIT TEMPLATE CHANGES
COLUMNS DROPPED
04/10/2007
Structure Type – Drop
Conductor Type – Drop
Circuit Breakers – Drop
Brief Description of Problem Being solved by this Project – Drop
Project Status – Drop
ERCOT Primary Planning Region (North, South or West) – Drop
ERCOT Secondary Planning Region (if located in both regions) – Drop
Is this project Right-of Way New or Existing – Drop
Has IDEV OR Update been submitted to updated Base Cases? – Drop
OTHER CHANGES
Projects past 2 years will not be included in TPIT
Projects past 2 years will be archived and posted
Circuit Miles will change from one column to two columns – 1. New, 2. Rebuilt, Reconductored or upgraded
Clarify - Projected Inservice Date & Actual Inservice Date
Highlight Header whether optional or required
Transmission Owner Project Contact Manager – Create a New Tab
05/01/2008
TPIT Five Year Plan Project Tab added
02/01/2009
New Column “S”: Planning Charter Tier
Any project that would be built by an entity that is exempt (e.g. a municipal utility) from getting a CCN for transmission projects but would require a CCN if it were to be built by a regulated entity will be treated as if the project would require a CCN for the purpose of defining the Tier of the project.
There will be a drop down box with a choice for you to choose from Tier 1, Tier 2, Tier 3 or Tier 4.
Tier 1 - This category is for all projects whose estimated capital cost is $50 million or greater. - RPG Review and Comment & ERCOT Independent Review &ERCOT BOD Endorsement
Tier 2 - This category consists of projects with estimated capital costs less than $50 million requiring a CCN. - RPG Review and Comment & ERCOT Independent Review
Tier 3 - This category consists of projects with estimated capital costs between $15 million and $50 million not requiring a CCN. –RPG Review and Comment
Tier 4 - This category consists of: small system upgrades whose estimated capital cost is less than or equal to $15 million and that do not require a CCN, as well as certain “neutral” projects. Neutral Projects are: the addition of, or upgrades to, radial transmission lines; the addition of equipment that does not affect the transfer capability of a line; repair and replacement-in-kind projects; that are directly associated with the interconnection of new generation; and to add static reactive devices. A project, irrespective of estimated capital cost, to serve a new load is considered to be a Neutral Project even if a CCN is required, unless such project would create a new transmission line connection between two stations (other than looping an existing line into the new load serving station). -No ERCOT Review
CREZ - This category is for all CREZ projects that are being developed as they were described in CREZ hearing. These projects are not expected to undergo further individual review.
CREZ Modified - This category is for all CREZ projects that are being developed as they were described in CREZ hearing. These projects are not expected to undergo further individual review.
02/01/2009
TPIT Five Year Plan Project Tab
New Selection (In-Service) added to drop down box
For any additional questions please contact Jan Grisham at 512-248-3140 or via email at jgrisham@ercot.com

## ERCOTTPITPast2Years
TRANSMISISON OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) PROJECTS PAST 2 YEARS (1999 - 2008)
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Requested Additional Information (Optional) | Other (Optional)
No Project Number Will Be Developed | DECORDOVA - CLEBURNE SWITCH 138 KV LINE UPGRADE CAPACITY |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-01-01 | 138 | 21.83 |  | 0
No Project Number Will Be Developed | ARGYLE-LEWISVILLE HIGHLANDS (TNP) 138 KV : INST. LINE MONITOR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-01-22 | 138 | 0 |  | 0
No Project Number Will Be Developed | CORINTH - DENTON (TMPA): INSTALL CAT-1 DEVICE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-01-22 | 138 | 0 |  | 0
99TPIT0001 | Alberta Switch to Doedyns Substation | Built new 138 kV line to serve the proposed Doedyns Substation |  |  | MVEC | Loretta C. Gallaga (956) 463-1584 lgalla@magicvalley.coop |  |  | 1999-02-01 | 138 | 3.14 |  | 14 | 0 | Hidalgo | Hidalgo
No Project Number Will Be Developed | HOLNAM SUB: ESTABLISH POINT OF DELIVERY FOR BEPCO |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-03-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | BETO, POD 138-25 KV: CONSTRUCT 138 KV POD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-03-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | E. LEVEE SW STA.: INSTALL 55 MVAR CAPACITOR BANK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-05-13 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | NW. CARROLLTON - LAKEPOINTE (TNMP) 138 KV LINE UPGRADE CAPACITY |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 2.4 |  | 0
No Project Number Will Be Developed | WHITESBORO SE.: ADD CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 7.2
No Project Number Will Be Developed | ROUND ROCK: ADD 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 18.4
No Project Number Will Be Developed | KILLEEN SWITCH: ADD 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 18.4
No Project Number Will Be Developed | KILLEEN CLEAR CREEK: ADD 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 18.4
No Project Number Will Be Developed | TEX HARVEY SUB.: ADD 9.2 MVAR CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 9.2
No Project Number Will Be Developed | LAMESA SUB.: ADD 18.4 MVAR CAPACITOR BANK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 18.4
No Project Number Will Be Developed | BONHAM SW: INSTALL 36.4 MVAR CAPACITOR BANK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 36.8
No Project Number Will Be Developed | LIGGETT: ADD 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 36.8
No Project Number Will Be Developed | MIDLOTHIAN S.: ADD 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | ALLEN SWITCH: ADD 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | NORWOOD SWITCH: ADD 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | PAYNE - NW SHERMAN 138 KV LINE UPGRADE CAPACITY |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 4.6 |  | 0
No Project Number Will Be Developed | PARKDALE: ADD 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | COLLIN: ADD 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | LAKE CREEK: ADD 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-01 | 138 | 0 |  | 0 | 36.8
No Project Number Will Be Developed | ROUND ROCK SOUTH: INSTALL 36.4 MVAR CAPACITOR BANK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-06-15 | 138 | 0 |  | 0 | 36.8
No Project Number Will Be Developed | SHERMAN NW - PERRIN TAP 138 KV RECONDUCTOR 795 MCM ACSR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-09-22 | 138 | 3.8 |  | 0
No Project Number Will Be Developed | ROYSE SW.:RECONNECT THE 345KV AUTO ON THE 345KV FORNEY LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-10-19 | 345 | 0 |  | 0
No Project Number Will Be Developed | Elsa-Weslaco 138 kV Conversion | Convert from 69 kV to 138 kV and reconductor to 795 MCM ACSR the existing section of the CPL N. Ediburg-Weslaco 69 kV from Elsa Substation 4.4 miles south to the MVEC 138 kV line. |  | AEP GROUP 000 | AEP/TCC |  | 21242014 | 1999-10-22 | 1999-10-22 | 138 | 4.4 |  | 0 |  | Hildago
No Project Number Will Be Developed | Hall Acres-South McAllen 138 kV Line Reconductor | Reconductor and rebuild approximately 3.7 miles of existing 138 kV transmission line from Hall Acres Substation to South McAllen Substation. The old line is 336 MCM aluminum conductors on wood poles and it will be reconductored with 795 MCM aluminum conductors on steel poles. |  | AEP GROUP 000 | AEP/TCC |  | 20399062 | 1999-11-01 | 1999-11-01 | 138 | 3.7 |  | 0 |  | Hildago
No Project Number Will Be Developed | Frontera Interconnect 138 kV line upgrades | Convert Bates to Pharr 69 kV line to 138 kV. Reonductor Bates to Goodwin 69 kV, Bates to Garza 138 kV, Bates to Edinburg 138 kV, S. Mcallen to Hall Acres 138 kV, and Bates to Sharyland 138 kV. |  | AEP Group 000 | AEP/TCC |  | PC98029 PC98030 | 1999-11-01 | 1999-11-01 | 138 | 73.71 |  | 0 |  |  | HIDALGO
No Project Number Will Be Developed | Frontera Interconnect 69 kV line upgrades | Convert Bates to Pharr 69 kV line to 138 kV. Reonductor Bates to Goodwin 69 kV, Bates to Garza 138 kV, Bates to Edinburg 138 kV, S. Mcallen to Hall Acres 138 kV, and Bates to Sharyland 138 kV. |  | AEP Group 000 | AEP/TCC |  | PC98029 PC98030 | 1999-11-01 | 1999-11-01 | 69 | 4.14 |  | 0 |  | HIDALGO | HIDALGO
No Project Number Will Be Developed | VENUS SW.:INSTALL 2-345 KV LINE TERMINALS FOR ANP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-11-03 | 345 | 0 |  | 0
No Project Number Will Be Developed | VALLEY-WOLF 138 KV LINE- FCEC-ECTOR SUBSTATION POD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | MONTICELLO SES:RELAY MODIFICATIONS FOR PARIS SS EXPANS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-11-26 | 345 | 0 |  | 0
No Project Number Will Be Developed | VALLEY SES:RELAY MODIFICATIONS FOR PARIS SS EXPANSION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-11-26 | 345 | 0 |  | 0
No Project Number Will Be Developed | PARIS SW: ESTABLISH RING BUS WITH FOUR 345KV CBS TO SERVE PAN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-11-26 | 345 | 0 |  | 0
No Project Number Will Be Developed | Bates-Goodwin 69 kV Line Reconductor | Reconductor and rebuild approximately 4.0 miles of existing 69kV transmission line from J.L. Bates Substation to Goodwin Substation. The old line is 336 MCM Aluminum conductor on wood poles and will be 795 MCM on steel poles. |  | AEP GROUP 000 | AEP/TCC |  | 20399145 | 1999-11-30 | 1999-11-30 | 69 | 4 |  | 0 |  | Hildago
No Project Number Will Be Developed | PFLUGERVILLE 138 KV LOOP LINE: INSTALL SECTIONALIZING SWITCHE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-12-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | PAYNE SW STA.: REPLACE 138 KV CB 1680 & UPGRADE TERM EQUIPMEN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-12-22 | 138 | 0 |  | 0
No Project Number Will Be Developed | VALLEY SW: REPLACE 138 KV CB 3340 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 1999-12-22 | 138 | 0 |  | 0
No Project Number Will Be Developed | STERRETT-MG INDUSTRIES 138 KV TAP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-02-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | WAXAHACHIE-OCF 69 KV LINE SECTION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-02-01 | 69 | 0 |  | 0
No Project Number Will Be Developed | WHITESBORO, SOUTHEAST: ADD 7.2 MVAR OF 15 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-02-10 | 138 | 0 |  | 0 | 7.2
No Project Number Will Be Developed | MG INDUSTRIES:ESTABLISH 138 KV POD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-02-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | HEC-Elsa 138 kV line rebuild | Convert to 138 kV and Reconductor with 795 MCM existing 69 kv line from HEC Plant to Elsa Sub. |  | AEP GROUP 000 | AEP/TCC |  | 21361332 | 2000-02-15 | 2000-02-15 | 138 | 14.8 |  | 0 |  | Hildago
No Project Number Will Be Developed | ELM MOTT: UPGDE WACO N LN TERM FOR ELM MOTT-WACO TAP 138 LN U |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-02-24 | 138 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT: REPLACE CARRIER EQUIPMENT FOR NORWOOD LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-02-28 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORWOOD SW UPGRADE DENTON LINE TERM FOR NORWOOD-DENTON LINE R |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-03-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | VALLEY-PAYNE NORTH 138 KV LINE - UPGRADE CAPACITY |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-03-01 | 138 | 15.9 |  | 0
No Project Number Will Be Developed | TEMPLE SW.-TEMPLE 138 KV LINE: LINE CHANGES TO UPGRADE CAPACI |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-03-02 | 138 | 1.6 |  | 0
No Project Number Will Be Developed | BELLMEAD- UPGRADE LINE SWITCHES AS PART OF THE ELM MOTT-WACO |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-03-08 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORTHCREST TAP: UPGDE LN SWS AS PART OF THE ELM MOTT-WACO TAP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-03-16 | 138 | 0 |  | 0
No Project Number Will Be Developed | KIRKLAND PARK-CENTERVILLE 138 KV LINE CHANGES FOR SERIES REAC |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-03-27 | 138 | 0 |  | 0
No Project Number Will Be Developed | VALLEY S.E.S REPLACE BKR. #4054 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-03-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | LEWISVILLE SW (BEC) STA-INSTALL NW CARROLLTON LINE TERMINAL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-04-14 | 345 | 0 |  | 0
No Project Number Will Be Developed | MIDLOTHIAN TXI: INSTALL POWER DONUT LINE MONITORING SYSTEM |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-04-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | PARKDALE SW - UPGDE GRNVL AVE TERM CB340/660 FOR PARKDALE-GN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-05-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | CENTERVILLE SWITCHING STATION: INSTALL 138 KV SERIES REACTORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-05-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | Cut-in the Asherton-Laredo Road 138kV circuit into the Dilley-Wormser 138kV circuit | Build 1.75 miles of double circuit 795 ACSR 138kV transmision line from the Asherton-Laredo Road 138kV circuit to the Dilley-Wormser 138kV circuit at their closest points. |  | AEP GROUP 000 | AEP/TCC |  |  | 2000-05-01 | 2000-05-01 | 138 | 1.75 |  | 0 |  | Webb
No Project Number Will Be Developed | North Laredo 138kV switching substation | Build a new 138kV switching substation with a four breaker expandable ring bus somewhere in the construction zone of the new transmission line. The station shall have the Asherton circuit and the Dilley circuit at opposite points on the ring. |  | AEP GROUP 000 | AEP/TCC |  |  | 2000-05-01 | 2000-05-01 | 138 | 0 |  | 0 |  | Webb
No Project Number Will Be Developed | Frontera Interconnect 138 kV substation upgrades | Convert Bates to Pharr 69 kV line to 138 kV. Reonductor Bates to Goodwin 69 kV, Bates to Garza 138 kV, Bates to Edinburg 138 kV, S. Mcallen to Hall Acres 138 kV, and Bates to Sharyland 138 kV. |  | AEP Group 000 | AEP/TCC |  | PC98029 PC98030 | 2000-05-01 | 2000-05-01 | 138 | 0 |  | 0 |  | Hidalgo
No Project Number Will Be Developed | North Padre Tap | North Padre Tap-replace 3.8 miles of 69 kv with new, double circuit 138kv energized at 69kV. |  | AEP GROUP 000 | AEP/TCC |  | 20257714 20367623 | 2000-05-16 | 2000-05-16 | 69 | 3.8 |  | 0 |  | Nueces
No Project Number Will Be Developed | UPGRADE PAYNE-SHERMAN LINE MATERIAL (REF. NO. R159) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-05-18 | 138 | 4.3 |  | 0
No Project Number Will Be Developed | EVERMAN UPGDE LN TERM EQ: REPLACE CB 6150, SWS 6149, 6151 AND |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-05-20 | 345 | 0 |  | 0
No Project Number Will Be Developed | PAYNE SW: UPGDE EQ CB 1000 & 3480 FOR PAYNE SW 2-VALLEY LN UP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-05-25 | 138 | 0 |  | 0
No Project Number Will Be Developed | VALLEY-PAYNE 138 KV SOUTH CIRCUIT LINE UPGRADE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-05-25 | 138 | 16.3 |  | 0
No Project Number Will Be Developed | FARMERS BRANCH GILLIS RD: MTR AND COM NORTHLAKE-RENNER 138 LI |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-05-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | FPP-Lytton Sprgs 345 kV Line |  |  |  | LCRA TSC |  |  | 2000-06-01 | 2000-06-01 | 345 | 63 |  | 0 | 0
No Project Number Will Be Developed | NORTH LAKE: UPGRADE CB230/CB540 AS PART OF NLK-NWC 138KV LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-06-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | NW CARROLLTON-GAINSVILLE 138KV: CHANGES FOR BRAZOS LEWISVIL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-06-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORTH LAKE: INSTALL 55 MVAR CAPACITOR BANK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-06-01 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | AEP/CFE Asynchronous Interconnection at Eagle Pass | Install a 36 MW asynchronous tie at AEP Eagle Pass Substation on the existing 138 kV transmission line from Eagle Pass to CFE's Nava Substation. |  | AEP Group 000 | AEP/TCC |  | PC98056 | 2000-06-01 | 2000-06-01 | 138 | 0 |  | 36 |  | Maverick
No Project Number Will Be Developed | Military Hwy 138-kV STATCOM | Install a STATCOM device at Military Highway that will provide a dynamic reactive resource of -/+150 MVAR at 138 kV or -50/+100 thyristor switched reactors and capacitors (TSR/TSC) units at N. Edinburg and Rio Hondo. |  | AEP Group 000 | AEP/TCC |  | PC99008 | 2000-06-01 | 2000-06-01 | 138 | 0 |  | 0 | -/+150 | Cameron
No Project Number Will Be Developed | EUREKA POD CONNECT TRINIDAD -HILLSBORO 138KV |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-06-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | ROANOKE SW: INSTALL 55 MVAR CAPACITOR BANK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-06-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | HEC 138 kV Hairpin | Loop the existing 138 kV N. Edinburgh to S. E. Edinburgh line Approx. 3000 ft into two terminals at the Duke SW. Station. |  | AEP GROUP 000 | AEP/TCC |  | 21211500 | 2000-06-19 | 2000-06-19 | 138 | 0.6 |  | 0 |  | Hildago
No Project Number Will Be Developed | PAYNE SUB UPGRADE EQ ON CB #1080 FOR PAYNE SW-SHERMAN LINE MT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-06-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORWOOD 138KV SW STA: INSTALL 2 LINE TERM FOR NWC-LIGGETT LIN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-06-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | PLANO-CUSTER ROAD: ADD SWITCHES TO SW. TRANSFORMERS BETWEEN B |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-07-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | NW CARROLLTON: INSTALL NEW 138KV LINE TERMINAL TO LEWISVILLE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-07-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | WAXAHACHIE OCF:RELOCATE 69 KV BREAKER FROM STERRETT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-07-15 | 69 | 0 |  | 0
No Project Number Will Be Developed | Harlingen #1-West Harlingen 69 kV Line Reconductor | Reconductor and rebuild approximately 2.6 miles of existing 69kV transmission line from Harlingen #1 Substation to West Harlingen Substation. The old line is 336 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM aluminum conductor on steel poles |  | AEP GROUP 000 | AEP/TCC |  | 21739057 | 2000-07-15 | 2000-07-15 | 69 | 2.6 |  | 0 |  | Cameron
No Project Number Will Be Developed | N W CARROLLTON-LEWISVILLE SW: INST 7.5 MI OF 2ND CKT TO BEPC |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-08-15 | 138 | 7.5 |  | 0
No Project Number Will Be Developed | San Benito-West Harlingen 69 kV Line Reconductor | Reconductor and rebuild approximately 7.8 miles of existing 69kV transmission line from San Benito Substaiton to West Harlingen Substation. The old line is 336 MCM ACSR on wood 'H' frame structures and will be reconductored with 795 MCM ACSR conductor on steel poles |  | AEP GROUP 000 | AEP/TCC |  | 21738800 | 2000-08-16 | 2000-08-16 | 69 | 7.8 |  | 0 |  | Cameron
No Project Number Will Be Developed | VALLEY-PARIS 138 KV:CHANGES TO ACCOMMODATE PANDA COGEN (NON-R |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-09-28 | 138 | 0 |  | 0
No Project Number Will Be Developed | NW CARROLLTON - REPLACE CARRIER EQUIPMENT FOR NORWOOD LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-02 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORTH LAKE-NW CARROLLTON CKTS 1 & 2 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-04 | 138 | 0 |  | 0
No Project Number Will Be Developed | NW CARROLLTON- UPGRADE CB2480/CB2590 AS PART OF NWC-NLK 138KV |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | ROYSE CITY-TRINIDAD 138KV: INST. SWITCHES FOR FEC NW TERRELL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | EVERMAN-HANDLEY 138 KV TAP: RELOCATE STRUCTURE 9/6 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-16 | 138 | 0 |  | 0
No Project Number Will Be Developed | ROYSE SW: PURCHASE SPARE 345 KV, 600 MVA AUTOTRANSFORMER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-24 | 345 | 0 |  | 0
No Project Number Will Be Developed | MARTIN LAKE: INSTALL TRANSFER TRIP PANEL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-29 | 345 | 0 |  | 0
No Project Number Will Be Developed | NACOGDOCHES S.E.: CHANGE PHASING ON MT. ENTERPRISE LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-29 | 345 | 0 |  | 0
No Project Number Will Be Developed | STRYKER CREEK: REMOVE TRINIDAD-MARTIN LAKE BKR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-29 | 345 | 0 |  | 0
No Project Number Will Be Developed | MT. ENTERPRISE 345 KV SW: CONSTRUCT 4 CB RING BUS STATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-29 | 345 | 0 |  | 0
No Project Number Will Be Developed | TRINIDAD: INSTALL TRANSFER TRIP PANEL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-29 | 138 | 0 |  | 0
No Project Number Will Be Developed | GREENVILLE AVE SW UPGDE KIRKLAND LNE TERM FOR BLACKWELL-KIRKL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | GREENVILLE AVE SW - UPGRADE THE PARKDALE LINE TERMINALS CB032 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-10-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | STRYKER CREEK-MT ENTERPRISE SW: ROUTE LINE INTO MT. ENTERPRIS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | MT. ENTERPRISE SW.-TENASKA GATEWAY SW. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | MARTIN LAKE-MT ENTERPRISE SW: ROUTE LINE INTO MT. ENTERPRISE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | MT.ENTERPRISE SW-NACOGDOCHES 345 KV LINE: CHANGES/ MT.ENTERPP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-01 | 345 | 4 |  | 0
No Project Number Will Be Developed | VENUS SW STATION REPLACE 1-345KV WAVE TRAP ON CB #4490 AND |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-02 | 345 | 0 |  | 0
No Project Number Will Be Developed | Reconductor the San Benito to West Harlingen 69 kV line from 336 ACSR to 795 ACSR (7.69 miles). |  |  |  | AEP/TCC |  |  | 2001-04-01 | 2000-11-04 | 69 | 7.69 |  | 0
No Project Number Will Be Developed | Calpine-N. Edinburg 138 kV Bus Connection | Connect 3-Calpine Generators to 138 kV Bus at N. Edinburg Sub using 3-1590 mcm ACSR circuits on single steel poles, 2 spans each, apprximately 1000 ft each circuit |  | AEP GROUP 000 | AEP/TCC |  | 21907017 | 2000-11-10 | 2000-11-10 | 138 | 0.6 |  | 0 |  | Hildago
No Project Number Will Be Developed | ROYSE-VALLEY 345 KV LINE: CONNECT TO FARMERSVILLE SWITCHING S |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | MONTICELLO: INSTALL FARMERSVILLE #2 TERMINAL & RPL CB 4650 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | FARMERSVILLE 345KV SW STA |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | VALLEY: INSTALL TRANSFER-TRIP & CHANGE LINE TRAP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | KIRKLAND PARK RPL CB/LN TERM EQ FOR KIRKLAND PARK-NORTHHAVEN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | MORGAN CREEK: RPL 138 KV CB 1250 & 1270 AND 2-345KV LINE TRAP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | EVERMAN - CENTURY(CEDAR HILL) 345: RELOCATION AT EVERMAN SW |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | DECORDOVA BEND: UPGRADE CB 4410 LN TERM & AUTOTRANSFORMER BUS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-11-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | MORGAN CREEK-ODESSA 345 KV |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | ODESSA EHV-PANDA ODESSA ECTOR 345KV TIE: 345KV MERCHANT PLAN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | Pasadena Cogen facility interconnection project, upgraded infrastructure. |  |  |  | CNP |  |  |  | 2000-12-01 | 345 | 7.34 |  | 0 | [10 empty] | No transformer capacity added.
No Project Number Will Be Developed | HANDLEY SW: REPLACE 138KV CBS 4200 & 4210 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | WORTHAM POD-TRANSFORMER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | MONTICELLO-FARMERSVILLE SW 345 KV: ADD SECOND CIRCUIT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-07 | 345 | 80.8 |  | 0
No Project Number Will Be Developed | ODESSA EHV SW STA: CONNECT PANDA-TIE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-10 | 345 | 0 |  | 0
No Project Number Will Be Developed | COMMERCE-PARIS COOPER-ENLOE POD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-20 | 138 | 0 |  | 0
No Project Number Will Be Developed | Mines Road-North Laredo Switch Tap 138 kV Reconductor | Reconductor and rebuild approximately 2 miles of existing 138 kV transmission line from Mines Road Substation to the tap point for the North Laredo Switch Station. The old line is 336 MCM ACSR conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. |  | AEP GROUP 000 | AEP/TCC |  | 22170041 | 2000-12-20 | 2000-12-20 | 138 | 2 |  | 0 |  | Webb
No Project Number Will Be Developed | SULPHUR SPRINGS-SULPHUR SPRINGS SW 138 KV LINE UPGRADE (REF. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-21 | 138 | 3.2 |  | 0
No Project Number Will Be Developed | DUBLIN-STEPHENVILLE 138KV LINE UPGRADE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-22 | 138 | 12 |  | 0
No Project Number Will Be Developed | TEMPLE-BELTON 138KV: RECONDUCTOR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-29 | 138 | 5 |  | 0
No Project Number Will Be Developed | LIGGETT 345KV LINE STRUCTURE REPLACEMENT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | ALLEN NORTH,138-25 KV SUBSTATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | Reconductor the West Harlingen to Harlingen #1 69 kV line from 336 ACSR to 795 ACSR (2.2 miles). |  |  |  | AEP/TCC |  |  | 2001-04-01 | 2000-12-30 | 69 | 2.2 |  | 0
No Project Number Will Be Developed | NORTHAVEN RPL CB & LN TERM EQ FOR KIRKLAND PARK-NORTHAVEN 138 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-31 | 138 | 0 |  | 0
No Project Number Will Be Developed | ELM MOTT - E WACO 138 KV UPGRADE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2000-12-31 | 138 | 9.5 |  | 0
No Project Number Will Be Developed | TRINIDAD - LIGGETT 138 KV: RELOCATE AT DESOTO SW |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-02-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | EVERMAN SW - MANSFIELD 138 KV UPGRADE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-02-04 | 138 | 7.7 |  | 0
No Project Number Will Be Developed | Milo-Mines Road 138 kV Reconductor | Reconductor and rebuild approximately 3 miles of existing 138 kV transmission line from Milo Substation to Mines Road Substation. The old line is 336 MCM ACSR conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. |  | AEP GROUP 000 | AEP/TCC |  | 22169991 | 2001-02-10 | 2001-02-10 | 138 | 3 |  | 0 |  | Webb
No Project Number Will Be Developed | RIVERCREST - CLARKSVILLE SHERRY SUB POD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-02-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | NW CARROLLTON - CARROLLTON TARPLEY RD 138KV UPGRADE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-02-21 | 138 | 9.3 |  | 0
No Project Number Will Be Developed | ENNIS SW: UPGRADE RELAYING FOR ENNIS WEST |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | STERRETT: UPGRADE RELAYING FOR ENNIS WEST |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | ENNIS WEST, 138 KV SW: PROVIDE TRACTEBEL INTE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | WEST WEATHERFORD SUB: INSTALL 69 KV BREAKER FOR BRAZOS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-01 | 69 | 0 |  | 0
No Project Number Will Be Developed | VALLEY SW: 345KV BREAKER #4090 REPLACEMENT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-02 | 345 | 0 |  | 0
No Project Number Will Be Developed | BOWMAN SW: REPLACE 345 KV WAVE TRAP ON CB 6050 AND SWITCHES |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-06 | 345 | 0 |  | 0
No Project Number Will Be Developed | Bates-Garza 138 kV line Reconductor | Reconductor and rebuild approximately 12 miles of existing 138 kV transmission line from Bates Power Plant to Structure #87 on the Bates/Garza 138 kV transmission line. The existing line is 336 MCM Aluminum conductor on wood "H" frame structures and will be reconductored with 795 MCM ACSR on single circuit steel poles. |  | AEP GROUP 000 | AEP/TCC |  | 22151899 | 2001-03-10 | 2001-03-10 | 138 | 12 |  | 0 |  | Hildago
No Project Number Will Be Developed | ABRAMS ROAD SUB - UPGRADE PARKDALE-GREENVILLE SWITCHES AB014 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | COOLIDGE: INSTALL CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-15 | 138 | 0 |  | 0 | 7.2
No Project Number Will Be Developed | GRAHAM SW: REPLACE 1-345KV WAVE TRAP ON CB #6310 & SW |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | WAXAHACHIE-S. ENNIS: MODIF. FOR ENNIS WEST SW 138 KV |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | DENTON DR SW: UPGRADE NORWOOD LINE TERM FOR NORWOOD-DENTON DR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | WORTHAM-SIMSBORO 69 KV LINE - LOWER FOR LIMESTONE-WATERMILL 3 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-15 | 69 | 0 |  | 0
No Project Number Will Be Developed | CHEYENNE T A P : SWITCH #2813 & #2815 UPGRADE TO 1200 AMP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-16 | 138 | 0 |  | 0
No Project Number Will Be Developed | CAMP BOWIE SUBSTATION CUT-IN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-23 | 138 | 0 |  | 0
No Project Number Will Be Developed | MOSS SW: RPL 138KV CB 3900, 3930, & 3950 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-23 | 138 | 0 |  | 0
No Project Number Will Be Developed | IRON BRIDGE TAP: PROVIDE ENTERPRISE POD FOR TVEC |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-25 | 138 | 0 |  | 0
No Project Number Will Be Developed | SOUTH ROUND ROCK SUB: INSTALL DEADEND |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | TAYLOR-ROUND ROCK 138 KV: IMPROVE TIE TO LCRA |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-03-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | VALLEY SW: UPGRADE EQ CB 3380 FOR PAYNE SW 2 - VALLEY LN UPGD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-04-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORTHAVEN: ADD 138KV 55.2 MVAR REACTIVE COMPENSATION & MODIFY |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-04-01 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | Upgrade 69 kV bus and switches at the East Harrison, San Benito, West Harlingen, & Harlingen #1 Substations |  |  |  | AEP/TCC |  |  | 2001-04-01 | 2001-04-01 | 69 | 0 |  | 0
No Project Number Will Be Developed | CHEYENNE TAP: UPGRADE SW #2813 TO 1200A |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-04-03 | 138 | 0 |  | 0
No Project Number Will Be Developed | East Harrison- Harlingen #1 69 kV Line Reconductor | Reconductor and rebuild approximately 4.0 miles of existing 69 kV transmission line from East Harrison Substation to Harlingen #1 Substation. The old line is 336 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM aluminum conductor on steel poles. |  | AEP GROUP 000 | AEP/TCC |  | 21739138 | 2001-04-06 | 2001-04-06 | 69 | 4 |  | 0 |  | Cameron
No Project Number Will Be Developed | Reconductor Harlingen #1 to East Harrison 69 kV line from 336 ACSR to 795 ACSR (3.7miles). |  |  |  | AEP/TCC |  |  | 2001-04-01 | 2001-04-06 | 69 | 3.7 |  | 0
No Project Number Will Be Developed | EVERMAN SW. 345 KV LOOP LINE FROM THE DECORDOVA-SHERRY 345 KV |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-04-07 | 345 | 0.4 |  | 0
No Project Number Will Be Developed | CLIMAX POD: PROVIDE POD FOR FANNIN CO. IN PAYNE-ROYSE CITY 13 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-04-10 | 138 | 0 |  | 0
No Project Number Will Be Developed | BLACKWELL - KIRKLAND 138 KV, REBUILD W/ BUNDLED 1033 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-04-21 | 138 | 3.8 |  | 0
No Project Number Will Be Developed | DENTON AVENUE: REPLACE 69 KV CB #400 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-04-30 | 69 | 0 |  | 0
No Project Number Will Be Developed | 345 kV Series Capacitors | Install series capacitor 345 kV line compensation on the Lon Hill to N. Edinburg and the Lon Hill to Rio Hondo 345 kV transmission lines at 50% compensation with SSR mitigation. These devices will be located at N. Edinburg and Rio Hondo 345 kV Substation. |  | AEP Group 000 | AEP/TCC |  | PC990013 | 2001-05-01 | 2001-05-01 | 345 | 0 |  | 0 |  | Nueces
No Project Number Will Be Developed | HUTTO SW: ESTABLISH STATION W/4-138KV CIRCUIT BREAKERS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | Dupont SS-Whitepoint SS 138 kV-2nd CRKT | Install Second 795 MCM ACSR circuit on the existing couble circuit steel structures between Dupont SS and Whitepoint SS. |  | AEP GROUP 000 | AEP/TCC |  | 21886771 | 2001-05-01 | 2001-05-01 | 138 | 8.2 |  | 0 |  | San Patricio
No Project Number Will Be Developed | Laredo Plant-Milo 138 kV Reconductor | Reconductor and rebuild approximately 3 miles of existing 138kV transmission line from Laredo Plant to Milo Substation. The old line is 336 MCM ACSR conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. |  | AEP GROUP 000 | AEP/TCC |  | 22169942 | 2001-05-01 | 2001-05-01 | 138 | 3 |  | 0 |  | Webb
No Project Number Will Be Developed | Lon Hill/STP-Whitepoint 345 kV | Install 10.1 Miles of double circuit steel single pole (2) 795 MCM 345 kV from Lon Hill-Stp Line to Whitepoint Switching Station. |  | AEP GROUP 000 | AEP/TCC |  | 21723155 21924105 22636844 22636846 | 2001-05-01 | 2001-05-01 | 138 | 10.1 |  | 0 |  | San Patricio
No Project Number Will Be Developed | BIG BROWN-TRINIDAD 345 KV LINE - CHANGES FOR RICHLAND CHAMBER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-03 | 345 | 0 |  | 0
No Project Number Will Be Developed | NORTH LAKE ADD 55MVAR CAP BANK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-07 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | HUBBARD SUB. - MODIFY 138KV LINE AUTO THROWOVER SCHEME |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-08 | 138 | 0 |  | 0
No Project Number Will Be Developed | GREENVILLE AVE SW: ADD TWO 138 KV 55MVAR CAP BANKS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-11 | 138 | 0 |  | 0 | 110.4
No Project Number Will Be Developed | WATERMILL:INSTALL THREE 345KV CBS TO LIMESTONE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-14 | 345 | 0 |  | 0
No Project Number Will Be Developed | LIMESTONE-WATERMILL 345 KV LINE - REV 1 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-14 | 345 | 177.4 |  | 0
No Project Number Will Be Developed | PFLUGERVILLE 138 KV LOOP LINE: CONNECT HUTTO SWITCHING STATIO |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-14 | 138 | 0 |  | 0
No Project Number Will Be Developed | CHINA GROVE, REPLACE OVERDUTIED CB #1040 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | JENKINS SUB RPL 2 LNE SW AS PART OF BLACKWELL-KIRKLAND PARK R |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | BELTON SUB - UPGRADE SOUTH TEMPLE LINE TO 1482 AMPS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT: 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0 | 18.4
No Project Number Will Be Developed | HANDLEY, ADD 138KV 55.2 MVAR REACTIVE COMPENSATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | HANDLEY: 138KV REACTIVE COMPENSATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | EAST LEVEE 55 MVAR CAPACITOR BANK ADDITION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0 | 55.22
No Project Number Will Be Developed | WEST LEVEE SUBSTATION 55.2 MVAR CAPACITOR BANK ADDITION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | ROYSE SUBSTATION - ADD 55 MVAR CAP BANK TO N BUS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | CENTERVILLE SWITCHING STATION: INSTALL 138 KV CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | ANNA SW: ADD 138KV, 55.2 MVAR REACTIVE COMPENSATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | NORWOOD TPL 55MVAR CAPACITOR BANK ADDITION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | COLLIN 138KV YARD: ADD 55MVAR CAP BANK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | CARROLLTON EAST: NEW 138KV SWITCHING STATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | TAYLOR-ROUND ROCK 138 KV: CONNECT TO HUTTO SWITCHING STATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-16 | 138 | 0 |  | 0
No Project Number Will Be Developed | ADDISON 138KV LOOP W/CARROLLTON NW-RENNER & NORTHLAKE-RENNER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-20 | 138 | 0 |  | 0
No Project Number Will Be Developed | ADDISON, ADD 138KV CARROLLTON EAST LINE TRANSFER SCHEME |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-21 | 138 | 0 |  | 0
No Project Number Will Be Developed | MOSS - RECONDUCTOR PERMIAN BASIN - MOSS 138KV LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-25 | 138 | 0 |  | 0
No Project Number Will Be Developed | ODESSA EHV RECONFIG. ODESSA 138KV SUBSTATION AND UPGRADE TERM |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-05-31 | 138 | 0 |  | 0
No Project Number Will Be Developed | NW CARROLLTON- UPGRADE LINE TERMINAL - CB2620 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | FPP-Lost Pines-Austrop 345 kV Line | Established a 2nd 345kV circuit from Austrop to Fayette next to the existing 345kV circuit. Both 345kV circuit have been cut into the Lost Pines switching station. |  | N/A | Austin Energy | James Armke (512) 322-6705 james.armke@austinenergy.com | N/A | 2001-06-01 | 2001-06-01 | 345 | 57 |  | 0 |  | TRAVIS | TRAVIS |  |  |  |  | 7056,9040,9041 | Y
No Project Number Will Be Developed | RENNER DPL, MODIFY CB#055 RELAY |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | MESQUITE FORNEY RD - THORNTON 138KV BUNDLE 0.4 MI 636 ACSR(RE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-01 | 138 | 0.4 |  | 0
No Project Number Will Be Developed | PERMIAN BASIN, UPGRADE 138KV LINE TERMINAL & WAVE TRAP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | KIRKLAND PK - NORTHAVEN 138 KV: REBUILD W/ BUNDLED 1033(3.2 M |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | North Laredo 138 kV Line Hairpin | Construct a new 138 kV transmission line from a tap point on the Laredo Plant-Asherton 138 kV transmission line to the North Laredo Switch Station. The new line will be 2.7 miles of double circuit 138 kV and conductored with 795 MCM aluminum conductor on steel poles. |  | AEP GROUP 000 | AEP/TCC |  | 22053072 | 2001-06-01 | 2001-06-01 | 138 | 2.7 |  | 0 |  | Webb
No Project Number Will Be Developed | Laredo 138-kV STATCOM | Install a STATCOM device at Laredo that will provide a dynamic reactive resource of -/+150 MVAR at 138 kV |  | AEP Group 000 | AEP/TCC |  | PC99008 | 2001-06-01 | 2001-06-01 | 138 | 0 |  | 0 | -/+150 | Webb
No Project Number Will Be Developed | MIDLAND WEST - REPLACE LINE SWITCH FOR T.I.E. ODESSA INTERCON |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-04 | 138 | 0 |  | 0
No Project Number Will Be Developed | ODESSA NORTH - REPLACE LINE SWITCH FOR T.I.E. ODESSA INTERCO |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-04 | 138 | 0 |  | 0
No Project Number Will Be Developed | PFLUGERVILLE SOUTH SW 138 KV: INSTALL (4) 138 KV LINE -CANCEL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | MIDLAND WEST: RPL 138KV SWITCH #2265 W/ 1200A |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-06 | 138 | 0 |  | 0
No Project Number Will Be Developed | WEST PLANO, ADD 138KV 55.2 MVAR REACTIVE COMPENSATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-07 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | ROUND ROCK SE 138KV LOOP - CONSTRUCT PROJECT (REF. NO. R067) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-10 | 138 | 0 |  | 0
No Project Number Will Be Developed | ROYSE-LAVON-W.PLANO 138 KV TAP TO NW.WYLIE SUBSTATION (FEC) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-11 | 138 | 0 |  | 0
No Project Number Will Be Developed | VENUS SW. - INSTALL DIGITAL METERING (ANP MERCHANT PLANT) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | SPRABERRY: UPRATE TERMINAL CB #2800 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | PLANO ALMA; REPLACE AIR SW # 5871 WITH 2000 A SW WITH VAC INT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | PARKDALE - GREENVILLLE 138 KV, REBUILD W/ BUNDLED 1033 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-06-22 | 138 | 13.1 |  | 0
No Project Number Will Be Developed | OVERTON SUB: REPL. AUTOTRANSFORMER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-07-01 | 138 | 0 |  | 50
No Project Number Will Be Developed | PFLUGERVILLE SUB ADD 138KV AIR SW |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-07-17 | 138 | 0 |  | 0
No Project Number Will Be Developed | STONEY POINT P.O.D (PAYNE - ROYSE CITY 138 KV) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-07-19 | 138 | 0 |  | 0
No Project Number Will Be Developed | PFLUGERVILLE - GILLELAND (LCRA) 138 KV LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-07-25 | 138 | 8 |  | 0
No Project Number Will Be Developed | Lon Hill/Rincon-Whitepoint 138 kV | Install 3.2 miles of double circuit concrete poles with bundled 795 MCM 138 kV line from Lon Hill-Rincon 138 kV Line to Whitepoint Switching Station. |  | AEP GROUP 000 | AEP/TCC |  | 21725417 21924122 22636843 22636845 | 2001-07-31 | 2001-07-31 | 138 | 3.2 |  | 0 |  | San Patricio
No Project Number Will Be Developed | Nueces Bay/Portland/Whitepoint 138 kV | Install 2.7 Miles of double circuit concrete poles (2) 795 MCM 138 kV line from Lon Hill-Rincon 138 kV to the Whitepoint Switching Station. |  | AEP GROUP 000 | AEP/TCC |  | 21725420 21886729 22636841 22636842 | 2001-09-28 | 2001-09-28 | 138 | 2.7 |  | 0 |  | San Patricio
No Project Number Will Be Developed | KIRKLAND PARK UPGDE GNVL AVE LINE TERM RPL LN SWS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-09-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT-COLLIN 138 KV LINE: MATHESON-TRIGAS 138 KV TAP LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-10-12 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORWOOD - DENTON DR 138 KV, REBUILD W/BUNDLED 1033 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-10-12 | 138 | 7.6 |  | 0
No Project Number Will Be Developed | MATHESON TRI-GAS: INSTALL METER ENCLOSURE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-10-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | DUBLIN-BROWNWOOD 138KV SHILOH POD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-10-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | DUBLIN - BROWNWOOD 138KV:INSTALL SWITCHES AT BEPC HASSE TAP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-10-27 | 138 | 0 |  | 0
No Project Number Will Be Developed | WESTOVER - REPLACE LINE SWITCH FOR T.I.E. ODESSA INTERCO |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-10-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | SHERRY BREAKER ADDITION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-10-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | ESKOTA SWITCH - INSTALL 138KV LINE TERMINAL TO TRENT WIND FAR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-10-31 | 138 | 0 |  | 0
No Project Number Will Be Developed | TRINIDAD SES - REVISE CARRIER ON 2-345KV LINES FOR RICHLAND C |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | BIG BROWN- REVISE CARRIER ON 2-345KV LINES FOR RICHLAND CHAMB |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | DESOTO : REPLACE 138 KV CB # 1600 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-02 | 138 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT SW: INSTALL 2ND 600 MVA AUTO (M531) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-07 | 345 | 0 |  | 600
No Project Number Will Be Developed | VENUS-ALVARADO 138 KV LINE: GRIFFITH POD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-08 | 138 | 0 |  | 0
No Project Number Will Be Developed | WOLF HOLLOW 345 KV SW. - PROVIDE AES INTERCONNECTION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-09 | 345 | 0 |  | 0
No Project Number Will Be Developed | BENBROOK - REVISE CARRIER FOR WOLF HOLLOW LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-09 | 138 | 0 |  | 0
No Project Number Will Be Developed | Lon Hill - Whitepoint Tap rebuild | Rebuild 16.0 miles of existing 138 kV line with bundled 795 ACSR 26/7 conductor. |  | AEP GROUP 000 | AEP/TCC |  | 21886673 | 2001-11-09 | 2001-11-09 | 138 | 16 |  | 0 |  | San Patricio
No Project Number Will Be Developed | WOLF HOLLOW : DECORDOVA-COMANCHE PEAK 345 KV MOD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-15 | 345 | 0 |  | 0
No Project Number Will Be Developed | CENTERVILLE SUB: ADD 3-345KV BKRS AND ONE 138KV 55.2MVAR CAP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-15 | 345 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | ESKOTA - 138 KV CIRCUIT TO TRENT WIND FARM |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | TEMPLE SW - BELTON 138 KV LINE HFRAME RELOCATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | MINERVA REPLACE 138/69KV AUTOTRANSFORMER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-15 | 138 | 0 |  | 50
No Project Number Will Be Developed | SAGINAW: ADD 138KV 55.2 MVAR REACTIVE COMPENSATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-11-30 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | EVERMAN LOOP FROM DECORDOVA-SHERRY 345KV LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | Channelview Equistar cogen facility interconnection project, built new 345kV Sheldon substation and upgraded infrastructure. |  |  |  | CNP |  |  |  | 2001-12-01 | 345 | 27.79 |  | 0 | [10 empty] | No transformer capacity added.
No Project Number Will Be Developed | Built new 345/35 kV Kuykendahl distribution substation |  |  |  | CNP |  |  |  | 2001-12-01 | 345 | 0.16 |  | 0 | [10 empty] | No transformer capacity added.
No Project Number Will Be Developed | Whitepoint 345/138 kV substation | Build a new 345/138 kV substation at Whitepoint and tie the existing Lon Hill to Rincon and the Dupont SS - Portland - Nueces Bay 138 kV lines into the substation. Build a new circuit from Whitepoint 138 kV to Dupont SS on the existing double circuit structures (Dupont SS to Whitepoint 138 kV line) and upgrade the Dupont SS - Portland - Whitepoint 138 kV line to bundled 795 ACSR capable of 411/479 MVA under normal and emergency conditions. Upgrade the Whitepoint to Lon Hill 138 kV line to bundled 795. Construct 8 miles of double circuit 345 kV from Whitepoint to the intersection of the Lon Hill to STP 345 kV line. The conductor will be bundle 795 ACSR capable of 1011/1176 MVA under normal and emergency conditions. |  | AEP Group 000 | AEP/TCC |  | PC99017 | 2001-12-01 | 2001-12-01 | 345 | 0 |  | 600 |  | Nueces
No Project Number Will Be Developed | Highway 9-Arcadia 69 kV Upgrade | Convert existing 69 kV line from Highway 9 to Acradia Substation to 138 kV and reconductor with 1590 MCM ACSR. 1.1 Miles of wood single pole will be replaced with either concrete or steel single poles. |  | AEP GROUP 000 | AEP/TCC |  | 21884738 | 2001-12-01 | 2001-12-01 | 138 | 1.1 |  | 0 |  | Nueces
No Project Number Will Be Developed | SOUTH ROUND ROCK PERMENENT INSTALLATION OF 138KV CAP BANKS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-04 | 138 | 0 |  | 0
No Project Number Will Be Developed | CULBERSON WIND POD AUTOMATIC ISOLATION SCHEME |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-07 | 138 | 0 |  | 0
No Project Number Will Be Developed | MASON AUTOMATIC ISOLATION SCHEME |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-07 | 138 | 0 |  | 0
No Project Number Will Be Developed | ELMAR AUTOMATIC ISOLATION SCHEME |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-07 | 138 | 0 |  | 0
No Project Number Will Be Developed | DFW SOUTHWEST: UPGRADE 138KV LINE EQUIPMENT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-11 | 138 | 0 |  | 0
No Project Number Will Be Developed | TEMPLE SW: REPLACE BUSHING CTS - BREAKER #2550 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-14 | 138 | 0 |  | 0
No Project Number Will Be Developed | STRYKER CREEK SW: REPLACE WAVE TRAP ON CB #3140.. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORTH LAKE - RENNER 138KV (FARMERS BRANCH GILLIS RD SUB) UPGR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | Arcadia-Southside 69 kV Upgrade | Convert Existing 69 kV line on wood single pole to 138 kV from Arcadia to Southside Station. Three spans of double circuit wood H frame into the Southside Substation will be rebuilt with steel single pole double circuit. |  | AEP GROUP 000 | AEP/TCC |  | 21884756 | 2001-12-15 | 2001-12-15 | 138 | 2.9 |  | 0 |  | Nueces
No Project Number Will Be Developed | TWIN OAKS 345KV SWYD - REPLACE CARRIER EQUIP. - GIBBONS LINES |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-31 | 345 | 0 |  | 0
No Project Number Will Be Developed | TEXAS INSTRUMENTS CONVERT DALLAS TI - KP LINE CB 042 TO POTT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-31 | 138 | 0 |  | 0
No Project Number Will Be Developed | STEPHENVILLE SW: UPGDE DUBLIN LN TERM FOR STPHNVL-COMANCHE 13 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-31 | 138 | 0 |  | 0
No Project Number Will Be Developed | RENNER CONVERT DALLAS TI - RENNER LINE CB 036 TO POTT RELAY S |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-31 | 138 | 0 |  | 0
No Project Number Will Be Developed | TEXAS INSTRUMENTS CONVERT DALLAS TI - RENNER LINE CB 022 TO P |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2001-12-31 | 138 | 0 |  | 0
02TPIT0002 | 29th Street Relocation & Reconductoring | Replaced existing 559 AAAC wood pole line with 795 ACSR on concrete poles |  |  | MVEC | Loretta C. Gallaga (956) 463-1584 lgalla@magicvalley.coop |  |  | 2002-01-01 | 138 | 1 |  | 0 | 0 | Hidalgo | Hidalgo
02TPIT0001 | AEPTC to Aderhold Substation | Built double circuit line to serve new Aderhold Substation |  |  | MVEC | Loretta C. Gallaga (956) 463-1584 lgalla@magicvalley.coop |  |  | 2002-01-01 | 138 | 1.6 |  | 14 | 0 | Hidalgo | Hidalgo
No Project Number Will Be Developed | Southside-Holly 69 kV Upgrade | Convert existing 69 kV line on wood single pole to 138 kV from Holly Substation to Southside Substation. Three spans of double circuit wood H frame in the Southside Station will be rebuilt with steel or concrete single pole double circuit. |  | AEP GROUP 000 | AEP/TCC |  | 21884765 | 2002-01-15 | 2002-01-15 | 138 | 1.8 |  | 0 |  | Nueces
No Project Number Will Be Developed | Arcadia Westside 69 kV Upgrade | Convert existing 69 kV line on wood H frame double circuit structures to double circuit steel and or concrete 138 kV structures and reconductor with 1590 MCM ACSR. |  | AEP GROUP 000 | AEP/TCC |  | 21884824 | 2002-01-30 | 2002-01-30 | 138 | 2.8 |  | 0 |  | Nueces
No Project Number Will Be Developed | TEMPLE SW - SANDOW 138 KV LINE: HIGH TEMPERATURE OPERATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-01-31 | 138 | 38.8 |  | 0
No Project Number Will Be Developed | Citgo NOP-Hwy 9 138 kV Line | Construct 0.6 miles of new 138 kV transmission and rebuild 1.06 miles of 69 kV to 138 kV between Citgo North Oak Park Substation and Highway 9 Substation. Constructed on single poles with 1590 mcm ACSR. |  | AEP GROUP 000 | LCRA TSC / AEP |  | 21722914 21722933 21882535 24666186 24686714 25041161 40060866 | 2002-02-01 | 2002-02-01 | 138 | 1.7 |  | 0 | 0 | Corpus | Nueces
No Project Number Will Be Developed | Citgo NOP-Nueces Bay 138 kV cable | Install 0.6 miles of underground cable from Citgo NOP substation to Nueces Bay Substation in conduit, 138 kV, 2-1000 kcmil Cu per phase in 4 conduits. |  | AEP Group 000 | LCRA TSC / AEP |  | 21722970 | 2002-02-01 | 2002-02-01 | 138 | 0.6 |  | 0 | 0 | Corpus | Nueces
No Project Number Will Be Developed | Citgo NOP substation | Interconnect CCEC Generator |  | AEP GROUP 000 | AEP/TCC |  | 21722914 21722933 21882535 24666186 24686714 25041161 40060866 | 2002-02-01 | 2002-02-01 | 138 | 0 |  | 0 |  | Nueces
No Project Number Will Be Developed | Citgo NOP-Nueces Bay 138 kV cable terminations | Install 0.6 miles of underground cable from Citgo NOP substation to Nueces Bay Substation in conduit, 138 kV, 2-1000 kcmil Cu per phase in 4 conduits. |  | AEP Group 000 | AEP/TCC |  | 21722970 | 2002-02-01 | 2002-02-01 | 138 | 0 |  | 0 |  | Corpus Christi | Nueces
No Project Number Will Be Developed | TEMPLE SOUTH SUB. REPLACE SWITCHES 2430, 2426 & 2428 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-02-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | Portland - Whitepoint Tap rebuild | Rebuild 3.18 miles of existing 138 kV transmission line with bundled 795 ACSR 26/7 conductor. |  | AEP GROUP 000 | AEP/TCC |  | 21886701 | 2002-02-15 | 2002-02-15 | 138 | 3.2 |  | 0 |  | San Patricio
No Project Number Will Be Developed | Falcon-Lopeno 138 kV Line Reconductor | Reconductor and rebuild approximately 10 miles of existing 138kV transmission line from Falcon Substation to Lopeno Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors |  | AEP Group 000 | AEP/TCC |  | 22169662 | 2002-02-15 | 2002-02-21 | 138 | 10 |  | 0 |  | Starr | Zapata
No Project Number Will Be Developed | Falfurrias- Rachal 138 kV Line Reconductor | Reconductor and rebuild approximately 25.1 miles of existing 138kV transmission line from Falfurrias Substation to Rachal Substation. The old line is 477 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM aluminum con |  | AEP Group 000 | AEP/TCC |  | 22169896 | 2002-02-22 | 2002-02-22 | 138 | 25.1 |  | 0 |  | Brooks County, Tx
No Project Number Will Be Developed | EAGLE MTN - REPLACE OVERDUTIED CB #580 & #590 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-03-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | WATERMILL SW, REPLACE SWITCHES #321 AND #323 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-03-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | HACKBERRY - 138KV, 110.4MVAR CAPACITOR BANKS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-03-15 | 138 | 0 |  | 0 | 110.4
No Project Number Will Be Developed | MOUNTAIN CREEK SES. REPLACE SWITCHES ON CB #660. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-04-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | VENUS SW: INSTALL SPECIAL PROTECTION SYSTEM |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-04-29 | 345 | 0 |  | 0
02TPIT0011 | San Miguel-Pawnee 345 kV line and switching station | Construct a 345 kV line from San Miguel to Pawnee. Construct switching station with 345/138 kV auto at Pawnee. |  |  | STEC | John Moore, 361-485-6137, jmoore@stec.org |  | 2002-05-01 | 2002-05-01 | 345 | 30.66 |  | 0 |  | ATASCOSA | BEE |  |  |  |  | 5901-5725 | Y
No Project Number Will Be Developed | MEDILL TERMINATION STATION REPLACE SWITCH #121 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | SEAGOVILLE SW. REPLACE SWITCHES, WAVE TRAP & CTS ON CB #3625. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | EVERMAN REPLACE OVERDUTIED CB 6160 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | DECORDOVA BEND REPLACE OVERDUTIED CB 4400 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-02 | 345 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT-EULESS: RECONDUCTOR 138 KV U.G. LINE(1/2 IN 2001 1/2 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-02 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORTHAVEN - REPLACE OVERDUTIED 138KV CB032 & CB042 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-08 | 138 | 0 |  | 0
No Project Number Will Be Developed | E MESQUITE-SEAGOVILLE SW 138 KV:REPLACE SWITCHES AT THE BALCH |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | CEDAR HILL; REMOVE TRANSFER TRIP RECEIVE PANEL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-15 | 345 | 0 |  | 0
No Project Number Will Be Developed | CEDAR HILL SWITCHING STATION- ADD 138KV, 55MVAR CAPACITOR BAN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | PLANO TENNYSON - ADD 110.4 MVAR CAPACITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-15 | 138 | 0 |  | 0 | 110.4
No Project Number Will Be Developed | LAKE HUBBARD - 138KV, 110.4MVAR CAPACITOR BANKS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-15 | 138 | 0 |  | 0 | 110.4
No Project Number Will Be Developed | WICHITA FALLS - GRAHAM 138 KV REROUTE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-28 | 138 | 0 |  | 0
No Project Number Will Be Developed | GRAHAM - WICHITA FALLS 138 KV REROUTE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-28 | 138 | 0 |  | 0
No Project Number Will Be Developed | MCKINNEY-ANNA SWITCH 138 KV: ADD DAMPERS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT - 138KV 55.2MVAR REACTIVE COMPENSATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-31 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | CARROLLTON EAST - ADD 138KV 110.4 MVAR REACTIVE COMPENSATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-05-31 | 138 | 0 |  | 0 | 110.4
No Project Number Will Be Developed | COMANCHE PEAK: REVISE RELAYING FOR WOLF HOLLOW LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-06-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | MONTICELLO-INSTALL SPECIAL PROTECTION SCHEME TO CB 3770 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-06-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | SHAMBURGER SW. REMOVE 1-345KV AIR SW. #5347. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-06-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | SANDOW:UPGRADE TERMINAL CAPACITY |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-06-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | RAISE VENUS-LIGGET: HIGH TEMPERATURE OPERATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-06-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | Portland - Dupont SS rebuild | Rebuild 7.67 miles of existing 138 kV transmission line with bundled 795 ACSR 26/7 conductor. |  | AEP GROUP 000 | AEP/TCC |  | 21927493 | 2002-06-01 | 2002-06-01 | 138 | 7.7 |  | 0 |  | San Patricio
No Project Number Will Be Developed | ROYSE-LAVON-WEST PLANO 138 KV: RELOCATE STRUCTURE 14/1 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-06-23 | 138 | 0 |  | 0
No Project Number Will Be Developed | BENBROOK REPLACE 345 KV SWITCHES #6439,#6441 AND WAVE TRAP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-06-25 | 345 | 0 |  | 0
No Project Number Will Be Developed | CRANE: UPGRADE STATION FOR 900 AMP OPERATION CB #3510 AND #35 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-06-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | ST. JO SUBSTATION REPLACE 69KV C.T.S ( TNP ) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-07-01 | 69 | 0 |  | 0
No Project Number Will Be Developed | FORNEY SWITCHING STATION - PROVIDE INTERCONNECTION TO FPLE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-07-10 | 345 | 0 |  | 0
No Project Number Will Be Developed | MEXIA: INSTALL 30 MVA 138/69 KV AUTO |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-08-01 | 138 | 0 |  | 30
No Project Number Will Be Developed | GROESBECK POD: INSTALL NEW RELAY PANEL ON CB 3085 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-08-26 | 138 | 0 |  | 0
No Project Number Will Be Developed | WILLOW CREEK SWITCH 345 KV LINE MODIFICATIONS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-09-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | FARMERSVILLE-VALLEY JUNCTION 345 KV: INSTALL CIRCUIT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-09-17 | 345 | 2.5 |  | 0
No Project Number Will Be Developed | VALLEY JUNCTION-ANNA SW 345 KV LINE: CONSTRUCT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-09-17 | 345 | 20.6 |  | 0
No Project Number Will Be Developed | MORGAN CREEK BRK ADDITION FOR SAN ANGELO LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-09-25 | 345 | 0 |  | 0
No Project Number Will Be Developed | VALLEY-NORTHWEST CARROLLTON 345 KV: ADJUSTMENTS FOR ANNA SWIT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-09-27 | 345 | 0 |  | 0
No Project Number Will Be Developed | FARMERSVILLE: ESTABLISH 345KV ANNA TERMINAL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-09-28 | 345 | 0 |  | 0
No Project Number Will Be Developed | N.W. CARROLTON ADD TRANSFER TRIP RELAYING TO 345 KV CB 3300 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-09-29 | 345 | 0 |  | 0
No Project Number Will Be Developed | WILLOW CREEK - TRACTEBEL WEST 345 KV CKT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-09-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | WILLOW CREEK - TRACTEBEL EAST 345 KV CKT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-09-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | FORNEY SW - FPLE SWITCHYARD SOUTH CIRCUIT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-09-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | FORNEY SW - FPLE SWITCHYARD NORTH CIRCUIT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-09-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | MORGAN CREEK - TWIN BUTTES 345KV LINE: CONSTRUCT (REF. NO. R2 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-01 | 345 | 25 |  | 0
No Project Number Will Be Developed | COMANCHE SW- RED CREEK SW 345KV LINE: CONSTRUCT (REF. NO. R28 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-01 | 345 | 45 |  | 0
No Project Number Will Be Developed | BOWMAN-EVERMAN 345 KV LINE(NEAR OLD GRANDBURY RD. AND ATCHISO |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-06 | 345 | 0 |  | 0
No Project Number Will Be Developed | PARKER-ROANOKE 345 KV : SUPPLEMENT TO 96T62022 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-10 | 345 | 0 |  | 0
No Project Number Will Be Developed | Garza- Falcon 138 kV Line Reconductor | Reconductor and rebuild approximately 27.3 miles of existing 138kV transmission line from Garza Substation to Falcon Substation. The old line is 336 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM aluminum conducto |  | AEP Group 000 | AEP/TCC |  | 22169585 | 2002-10-10 | 2002-10-10 | 138 | 27.3 |  | 0 |  | Starr County, Texas
No Project Number Will Be Developed | EVERMAN ADD TRANSFER TRIP PANEL DUE TO NEW SHERRY AUTO # 2 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-11 | 345 | 0 |  | 0
No Project Number Will Be Developed | BOWMAN - EVERMAN 345KV LINE CHG TO PARKER - EVERMAN (REF. NO. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-11 | 345 | 0 |  | 0
No Project Number Will Be Developed | BOWMAN - EVERMAN 345KV LINE CHG TO BOWMAN - PARKER (REF. NO. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-11 | 345 | 0 |  | 0
No Project Number Will Be Developed | BOWMAN - EVERMAN 345 KV LINE RECONFIGURATION AT JACKSBORO SW |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-17 | 345 | 0 |  | 0
No Project Number Will Be Developed | GRAHAM-JACKSBORO 345 KV: CONSTRUCT LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-17 | 345 | 35 |  | 0
No Project Number Will Be Developed | BOWMAN: UPGRADE 345KV CB 6040 LINE TUNER EQUIPMENT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-17 | 138 | 0 |  | 0
No Project Number Will Be Developed | PARKER SW: ADD NEW WILLOW CREEK 345KV POSITION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-18 | 345 | 0 |  | 0
No Project Number Will Be Developed | GRAHAM SW. STATION - ADD JACKSBORO 345KV TERMINAL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-18 | 345 | 0 |  | 0
No Project Number Will Be Developed | JACKSBORO SW. STA.; 3-345KV LINE TERMINALS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-18 | 345 | 0 |  | 0
No Project Number Will Be Developed | WILLOW CREEK - TRACTEBEL WISE INTERCONNECT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-10-21 | 345 | 0 |  | 0
No Project Number Will Be Developed | HANDLEY SES WAVE TRAP (CB 4110) & CTS ON CB #4130 &4110. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-11-02 | 138 | 0 |  | 0
No Project Number Will Be Developed | WEDGWOOD BYPASS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-11-12 | 138 | 0 |  | 0
No Project Number Will Be Developed | COMANCHE SW. 3 BKR RING FOR SAN ANGELO LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-11-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | COMANCHE PEAK - COMANCHE SW. 345KV REROUTE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-11-15 | 345 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT-NORWOOD 138KV REROUTE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-11-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | CHAMBERSVILLE P.O.D. 138 KV |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-11-22 | 138 | 0 |  | 0
No Project Number Will Be Developed | ANNA SWITCHING STATION: RECONFIGURE 345KV |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-11-26 | 345 | 0 |  | 0
No Project Number Will Be Developed | CEDAR HILL SW. - REPLACE OVERDUTY 345KV CB #325 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-01 | 345 | 0 |  | 0
No Project Number Will Be Developed | Reconductored 345kV circuit 97 Cedar Bayou to King to North Belt, circuit 99 Cedar Bayou to North Belt and circuit 97 T.H. Wharton to North Belt and upgraded equipment. |  |  |  | CNP |  |  |  | 2002-12-01 | 345 | 57.8 |  | 0 | [10 empty] | No transformer capacity added.
No Project Number Will Be Developed | Channel Energy Center generating facility interconnection project, built new 345kV Deepwater substation and upgraded infrastructure. |  |  |  | CNP |  |  |  | 2002-12-01 | 345 | 24.69 |  | 0 | [7 empty] | 48591, 48593, 48594, 40450, 41000 |  |  | No transformer capacity added.
No Project Number Will Be Developed | Deer Park Energy generating facility interconnection project, built new 345kV Center substation and upgraded infrastructure. |  |  |  | CNP |  |  |  | 2002-12-01 | 345 | 29.15 |  | 0 | [10 empty] | No transformer capacity added.
No Project Number Will Be Developed | Calpine Baytown Energy Center cogen facility interconnection project, built new 345kV Chamber substation. |  |  |  | CNP |  |  |  | 2002-12-01 | 345 | 28.9 |  | 0 | [10 empty] | No transformer capacity added.
No Project Number Will Be Developed | Brazos Valley Energy cogen facility interconnection project, built new 345kV Smithers substation. |  |  |  | CNP |  |  |  | 2002-12-01 | 345 | 0.98 |  | 0 | [10 empty] | No transformer capacity added.
No Project Number Will Be Developed | Galveston area improvements project, built a new 138kV line from West Galveston to Stewart substation. |  |  |  | CNP |  |  |  | 2002-12-01 | 138 | 13.96 |  | 0 | [10 empty] | No transformer capacity added.
No Project Number Will Be Developed | Build new 138/35kV Sienna distribution substation |  |  |  | CNP |  |  |  | 2002-12-01 | 138 | 5.4 |  | 0 | [10 empty] | No transformer capacity added.
No Project Number Will Be Developed | Reconductored Circuit 66 Atascocita to Crosby and upgraded equipment at Atascocita and Crosby. |  |  |  | CNP |  |  |  | 2002-12-01 | 138 | 12.67 |  | 0 | [10 empty] | No transformer capacity added.
No Project Number Will Be Developed | VENUS-LIGGETT 345 KV LINE: RECONDUCTOR 795 SECTION WITH ACSS/ |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-13 | 345 | 12.4 |  | 0
No Project Number Will Be Developed | BONHAM: ADD 138KV TERMINAL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-18 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORWOOD: RELAY MODIFICATIONS TO CONVERT VENUS LINE TO LIGGETT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-19 | 138 | 0 |  | 0
No Project Number Will Be Developed | ROANOKE SW: INSTALL SPECIAL PROTECTION SYSTEM |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-19 | 138 | 0 |  | 0
No Project Number Will Be Developed | BONHAM SW-EXPLORER (POI) 138 KV LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-19 | 138 | 0 |  | 0
No Project Number Will Be Developed | WOLF HOLLOW SPS ADDITION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-23 | 138 | 0 |  | 0
No Project Number Will Be Developed | BENBROOK SPECIAL PROTECTION PANELS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-23 | 138 | 0 |  | 0
No Project Number Will Be Developed | PAYNE-BONHAM 69 KV LINE - REBUILD FOR EXPLORER POD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-29 | 69 | 0 |  | 0
No Project Number Will Be Developed | DESOTO 345 KV: PURCHASE & STORE, AUTO 345/141.5 KV, 600 MV |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | WINK-NORTH ANDREWS 138 KV: SPAN SINK HOLE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | FORNEY-ROYSE-FARMERSVILLE 345KV LINE(TIED-ROYSE AUTOXFMR M450 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2002-12-31 | 345 | 0 |  | 0
03TPIT0001 | Tomball - Rayford ckt.81 | Verified equipment rating at both substations to increase thermal ratings. |  |  | CNP |  |  | 2003-01-01 | 2003-01-01 | 138 | 0 |  | 0 |  | HARRIS | MONTGOMERY |  |  |  |  | 46510, 46261 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | Coleto Creek-Pawnee 345 kV | New 345 kV line between Coleto Creek Power Station and new STEC Pawnee Switching Station |  | AEP Group 000 | LCRA TSC / AEP |  | 21071518 | 2003-09-30 | 2003-01-07 | 345 | 107.8 |  | 0 | 0 | Goliad | Karnes
No Project Number Will Be Developed | Citgo NOP-Lon Hill 138 kV | Construct a new 138 kV transmission line from Citgo NOP to Lon Hill Sub in three secgments, 1.6 miles of single circuit single pole, 2.8 miles of double circuit single pole and 10. Miles of single circuit single pole. |  | AEP Group 000 | LCRA TSC / AEP |  | 21722984 | 2002-12-31 | 2003-01-14 | 138 | 14.7 |  | 0 | 0 | Corpus | Nueces
No Project Number Will Be Developed | Citgo NOP-Lon Hill 138 kV terminations | Construct a new 138 kV transmission line from Citgo NOP to Lon Hill Sub in three secgments, 1.6 miles of single circuit single pole, 2.8 miles of double circuit single pole and 10. Miles of single circuit single pole. |  | AEP Group 000 | AEP/TCC |  | 21722984 | 2002-12-31 | 2003-01-14 | 138 | 0 |  | 0 |  | Corpus Christi | Nueces
No Project Number Will Be Developed | GRAPELAND MAGNOLIA 138 KV POI - EXPLORER PIPELINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-01-23 | 138 | 0 |  | 0
03TPIT0002 | Sherry 345/138 kV autotransformer | Install a (2nd) 345/138 kV autotransformer (600 MVA) at Sherry |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M591 | 2003-02-01 | 2003-02-01 | 345 | 0 |  | 600 |  | TARRANT | [5 empty] | 1934, 1919 | Y
No Project Number Will Be Developed | Lopeno-Zapata 138 kV Line Reconductor | Reconductor and rebuild approximately 20.3 miles of existing 138kV transmission line from Zapata Substation to Lopeno Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductor |  | AEP Group 000 | AEP/TCC |  | 22169764 | 2003-01-30 | 2003-02-01 | 138 | 20.3 |  | 0 |  | Hidalgo | Hidalgo
No Project Number Will Be Developed | BRYAN AVE SWITCH REPLACE 69KY CB #180 SW #179 & 181 TO 800A |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-02-10 | 138 | 0 |  | 0
No Project Number Will Be Developed | OAKHILL MODIFY SWITCHES #4046,4045,#44044 LOAD SECTIONAL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-02-10 | 138 | 0 |  | 0
03TPIT0003 | Connect Deussen 138kV customer substation | Looped into Chamon - Humble ckt.94 |  |  | CNP |  |  | 2003-02-10 | 2003-02-10 | 138 | 2.78 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 40475 | Y |  | No transformer capacity added.
No Project Number Will Be Developed | ANNA-MCKINNEY 138 KV LINE: INSTALL CAT-1 MONITORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-02-21 | 138 | 0 |  | 0
No Project Number Will Be Developed | N McCamey- McCamey - Tippett | Rebuild 13.46 miles of 69kV line to 138 kV |  | AEP Group 000 | LCRA TSC / AEP |  | 24028549 24908005 40079168 | 2003-02-21 | 2003-02-21 | 138 | 13.46 |  | 0 | 0 | Corpus | Nueces
03TPIT0005 | Reconfigure Kenny 138kV Substation | Radially Tapped from Cedar Bayou West bus ckt.14. De-energize Tap to Kenny on Cedar Bayou - Baytown ckt.03. |  |  | CNP |  |  | 2003-02-28 | 2003-02-28 | 138 | 0 |  | 0 |  | CHAMBERS | CHAMBERS |  |  |  |  | 40870, 40871 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
03TPIT0004 | T.H. Wharton - Fairbanks ckt.81 | Upgraded limiting equipment at T.H. Wharton substation to increase thermal ratings. |  |  | CNP |  |  | 2003-02-28 | 2003-02-28 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 45515, 45760 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | PARKDALE: REPLACE BREAKER P290 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-03-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | JEWETT-CENTERVILLE 138 KV: RECONDUCTOR FOR GRAPELAND EXPLORER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-03-01 | 138 | 7.1 |  | 0
No Project Number Will Be Developed | North Edinburg - McColl 2.6 mile 138kv transmission line reconductor | Reconductor the approximately 2.6 miles of existing 138kv double circuit from North Edinburg to McColl. The old line is 795 ACSR conductor and the new line will be 795 ACSS conductor. Poles and insulators remain the same. |  | AEP Group 000 | AEP/TCC |  | 40103754 | 2003-02-24 | 2003-03-01 | 138 | 2.6 |  | 0 |  | Hidalgo | Hidalgo
No Project Number Will Be Developed | WEDGWOOD SWITCHING STATION: UPGRADE STATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-03-10 | 138 | 0 |  | 0
No Project Number Will Be Developed | North Edinburg- Rachal 138 kV Line Reconductor | Reconductor and rebuild approximately 37.8 miles of existing 138kV transmission line from North Edinburg Substation to Rachal Substation. The old line is 477 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM aluminum |  | AEP Group 000 | AEP/TCC |  | 22169873 | 2003-03-10 | 2003-03-18 | 138 | 37.8 |  | 0 |  | Brooks County, Tx | Hildago
No Project Number Will Be Developed | TRINIDAD: REPLACE SW #4019 & SW #4021 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-03-21 | 138 | 0 |  | 0
No Project Number Will Be Developed | VENUS: REPLACE 345KV CB 4480 AND UPGRADE LIGGET 345KV LINE TE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-03-25 | 345 | 0 |  | 0
03TPIT0013 | Anna - Collin 345 kV line | Upgrade Anna - Collin 345 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R108 | 2003-05-01 | 2003-04-01 | 345 | 13 |  | 0 |  | COLLIN | COLLIN |  |  |  |  | 2373, 2372 | Y
03TPIT0012 | Centerville Switch 345/138 kV autotransformer | Install a (2nd) 345/138 kV autotransformer (600 MVA) at Centerville Switch |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M460 | 2003-05-01 | 2003-04-01 | 345 | 0 |  | 600 |  | DALLAS | [5 empty] | 2453, 2450 | Y
03TPIT0007 | Royse 345 kV bus | Install a (2nd) 345 kV bus at Royse |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M450 | 2003-04-01 | 2003-04-01 | 345 | 0 |  | 0 |  | ROCKWALL | [5 empty] | 2478 | Y
03TPIT0006 | Royse 345/138 kV autotransformer | Install a (2nd) 345/138 kV autotransformer (600 MVA) at Royse |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M450 | 2003-04-01 | 2003-04-01 | 345 | 0 |  | 600 |  | ROCKWALL | [5 empty] | 2474, 2473 | Y |  | Installed cost included significant associated station work.
No Project Number Will Be Developed | PRIMROSE TAP 138KV (NORTH CIRCUIT): BUNDLE CONDUCTOR AT WWSW |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-01 | 138 | 2.2 |  | 0
No Project Number Will Be Developed | BENBROOK-FOREST HILL NO 1 138KV: BUNDLE CONDUCTOR AT WWSW |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | PRIMROSE TAP 138KV (SOUTH CIRCUIT): BUNDLE CONDUCTOR AT WWSW |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-01 | 138 | 2.2 |  | 0
No Project Number Will Be Developed | BENBROOK-FOREST HILL NO 2 138KV: BUNDLE CONDUCTOR AT WWSW |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | WEDGWOOD TAP 138KV (NORTH CIRCUIT ): BUNDLE CONDUCTOR AT WWSW |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | WEDGWOOD TAP 138KV (SOUTH CIRCUIT): BUNDLE CONDUCTOR AT WWSW |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | EULESS-ROANOKE 138KV MCPHERSON BEPCO POI |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT-COLLIN 138KV BRIDGES POD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | FOREST HILL SW: REPLACE SWITCHES #4029,#4031,& #CB370 & SWITC |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-04 | 138 | 0 |  | 0
No Project Number Will Be Developed | ANNA SWITCHING STATION-COLLIN SWITCHING STATION 345 KV: UPGRA |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-08 | 345 | 13.2 |  | 0
03TPIT0008 | Karsten | Increased reactive capability to 100 MVAR |  |  | CNP |  |  | 2003-04-10 | 2003-04-10 | 138 | 0 |  | 0 | 40 | BRAZORIA | BRAZORIA |  |  |  |  | 44410 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | ANNA SWITCHING STATION:MODIFY RELAYING FOR COLLIN SES |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-11 | 345 | 0 |  | 0
No Project Number Will Be Developed | N.W. CARROLLTON: UPGRADE 345KV CB#3300 LINE TERMINAL EQUIP. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-11 | 345 | 0 |  | 0
No Project Number Will Be Developed | TRADINGHOUSE: REPLACE CB #3920 & SW #3918 & #3921 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-11 | 345 | 0 |  | 0
No Project Number Will Be Developed | MESQUITE EAST - REPLACE SW #2729, SW #2731 & LINE TRAP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-12 | 138 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT- HACKBERRY 138KV CONSTRUCT (REF. NO. M526) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-15 | 138 | 6.9 |  | 0
No Project Number Will Be Developed | ROANOKE - 138KV, 110.4MVAR CAPACITOR BANK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-17 | 138 | 0 |  | 0 | 110.4
03TPIT0009 | Fort Bend | Increased reactive capability to 93.3 MVAR |  |  | CNP |  |  | 2003-04-17 | 2003-04-17 | 138 | 0 |  | 0 | 33.33 | FORT BEND | FORT BEND |  |  |  |  | 44300 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | HILLSBORO-BLUM 138KV BLANTON POI |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-24 | 138 | 0 |  | 0
No Project Number Will Be Developed | RIVERCREST: REPLACE BREAKER 2920 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-25 | 138 | 0 |  | 0
No Project Number Will Be Developed | MESQUITE WEST: REPLACE SWS #251, #252 AND#254 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-26 | 138 | 0 |  | 0
03TPIT0011 | STP - W. A. Parish ckt. 39 | Raised conductors and upgraded substation equipment to increase thermal ratings, and swapped WAP line position at STP with Austin Energy Holman ckt.1 |  |  | CNP, AEP, Austin, San Antonio |  |  | 2003-04-30 | 2003-04-30 | 345 | 0.1 |  | 0 |  | MATAGORDA | FORT BEND |  |  |  |  | 5915, 44000 | Y |  | No transformer capacity added.
No Project Number Will Be Developed | TATE SPRINGS MODIFY SWITCHES #4066,#4065,4064, AND #4063 LOAD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-04-30 | 138 | 0 |  | 0
03TPIT0010 | Flewellen | Installed new 138kV 80 MVAR capacitor bank. |  |  | CNP |  |  | 2003-04-30 | 2003-04-30 | 138 | 0.1 |  | 0 | 80 | FORT BEND | FORT BEND |  |  |  |  | 44231 | Y |  | No transformer capacity added.
No Project Number Will Be Developed | ROYSE SWITCHING STATION: INSTALL 2ND AUTOTRANSFORMER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-01 | 345 | 0 |  | 600
03TPIT0014 | Forney - Centerville Switch 345 kV line | Upgrade capacity of line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M459 | 2003-05-01 | 2003-05-01 | 345 | 15 |  | 0 |  | KAUFMAN | DALLAS |  |  |  |  | 2437, 2453 | Y
No Project Number Will Be Developed | EAST RICHARDSON-LAVON 138KV: CONNECT THE NEW NTMWD LAVON PUMP |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | TEMPLE SW-KILLEEN SW 345KV:CONNECT BEPC BELL COUNTY SWITCHING |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | LAVON PUMP NO.2 (NTMWD) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | ROYSE - ROCKWALL 138 KV LINE REBUILD (M379) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-04 | 138 | 7.2 |  | 0
No Project Number Will Be Developed | LIGGETT-EULESS 138KV REBUILD (REF. NO. M552) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-06 | 138 | 7.8 |  | 0
No Project Number Will Be Developed | FORNEY-CENTERVILLE 345 KV LINE: RECONDUCTOR WITH ACSS/TW FOR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-09 | 345 | 14.9 |  | 0
No Project Number Will Be Developed | Tippet to W Yates Tap | Rebuild 9.98 miles of 69kV to 138kV |  | AEP Group 000 | LCRA TSC / AEP |  | 24028557 24907990 40079274 | 2003-05-12 | 2003-05-12 | 138 | 9.98 |  | 0 | 0 | Pecose | Crockett
No Project Number Will Be Developed | LIGGETT SWITCH STATION - UPGRADE 345KV VENUS & TWO 138KV HACK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-15 | 345 | 0 |  | 0
No Project Number Will Be Developed | SHERRY SWITCHING STATION: PURCHASE 345/141.5 KV, 600 MVA AUTO |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-15 | 345 | 0 |  | 600 | 110.4
No Project Number Will Be Developed | SAGINAW: 138KV 110.4MVAR REACTIVE COMPENSATION(M5019) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-15 | 138 | 0 |  | 0 | 110.4
No Project Number Will Be Developed | Rio Bravo-Zapata 138 kV Line Reconductor | Reconductor and rebuild approximately 30.8 miles of existing 138kV transmission line from Zapata Substation to Rio Bravo Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conduc |  | AEP Group 000 | AEP/TCC |  | 22169796 | 2003-04-15 | 2003-05-15 | 138 | 30.8 |  | 0 |  | ZAPATA | WEBB
No Project Number Will Be Developed | Chase Field Line Tap | Construct 4.3 miles of new 69kv 795 MCM 26/2 ACSR transmission line from the Chase Field Substation to a Tap point on the Skidmore to Beeville transmission line near Beeville Tx. using single pole construction |  | AEP Group 000 | AEP/TCC |  | 21074391 | 2003-03-31 | 2003-05-16 | 69 | 4.3 |  | 0 |  | Bee County, Tx
No Project Number Will Be Developed | BRAND-KIMBER MORGAN BULLSEYE 138KV:CONSTRUCT NEW LINE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-19 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORWOOD-AMELIA 138 KV LINE: UT SOUTHWEST MED. CTR. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-27 | 138 | 0 |  | 0
No Project Number Will Be Developed | ROUND ROCK 138 KV LOOP FROM LCRA MC NEIL-CHIEF BRADY - BUNDLE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-28 | 138 | 0.1 |  | 0
No Project Number Will Be Developed | COLLIN 345 KV: ESTABLISH SWITCHING STATION (M377) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | BENBROOK: REPLACE LINE TRAP ON 138KV CB #4320 (M5023) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-05-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | BOWMAN - EVERMAN 345 KV LINE RECONFIGURATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-06-01 | 345 | 0 |  | 0
03TPIT0017 | Collin 345/138 kV autotransformer | Install a 600 MVA 345/138 kV autotransformer at Collin |  | R108 | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M377 | 2003-06-01 | 2003-06-01 | 345 | 0 |  | 0 |  | COLLIN | [5 empty] | 2372, 2370 | Y
03TPIT0016 | Rocky Creek 345/138 kV autotransformer | Install a 600 MVA 345/138 kV autotransformer at Rocky Creek |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M046 | 2003-06-01 | 2003-06-01 | 345 | 0 |  | 600 |  | TARRANT | [5 empty] | 1880, 1881 | Y
03TPIT0018 | San Miguel-San Miguel 138 kV bus tie | Reconductor the 138 kV 795 ACSR tie between buses at San Miguel. |  |  | STEC | John Moore, 361-485-6137, jmoore@stec.org |  | 2003-06-05 | 2003-06-05 | 138 | 0.44 |  | 0 |  | ATASCOSA | ATASCOSA |  |  |  |  | 5704-5706 | Y
No Project Number Will Be Developed | DECATUR-ORAN 69 KV: INSTALL AIRCRAFT OBSTRUCTION MARKER BALLS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-06-13 | 69 | 0 |  | 0
No Project Number Will Be Developed | BOWEN MODIFY SWITCHES #4137,#4136 AND #4138 LOAD SECTIONALIZI |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-06-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | HANDLEY: 138KV REACTIVE COMPENSATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-06-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | SMITHFIELD SUBSTATION - INSTALL 138KV CAPACITOR BANKS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-06-15 | 138 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | ROCKY CREEK - PRIMROSE 138 KV LINE (CCN ESTIMATE W/ CONCRETE) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-06-20 | 138 | 5.8 |  | 0
No Project Number Will Be Developed | Lon Hill Power Station to Nueces Bay Power Station | Install a new 138 kV line in four segments from Lon C Hill Power Plant to Nueces Bay Power Plant. Segment 1-5.4 miles of double circuit single pole, Segment 2-0.2 miles of single circuit single pole, Segment 3-3.2 Miles of single circuit single pole, Segm |  | AEP Group 000 | LCRA TSC / AEP |  | 21723002 | 2002-05-15 | 2003-06-20 | 138 | 17.2 |  | 0 | 0 | Corpus | Nueces
No Project Number Will Be Developed | Lon Hill Power Station to Nueces Bay Power Station terminations | Install a new 138 kV line in four segments from Lon C Hill Power Plant to Nueces Bay Power Plant. Segment 1-5.4 miles of double circuit single pole, Segment 2-0.2 miles of single circuit single pole, Segment 3-3.2 Miles of single circuit single pole, Segm |  | AEP Group 000 | AEP/TCC |  | 21723002 | 2002-05-15 | 2003-06-20 | 138 | 0 |  | 0 |  | Corpus Christi | NUECES
No Project Number Will Be Developed | ROCKY CREEK: ESTABLISH 345/138 KV SWITCHING STATION |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-06-23 | 345 | 0 |  | 600
03TPIT0019 | Jeanetta 345/138 kV autotransformer | Added second 345/138 kV, 600 MVA autotransformer (A3) @Jeanetta |  |  | CNP |  |  | 2003-06-26 | 2003-06-26 | 345 | 0 |  | 600 |  | HARRIS | HARRIS |  |  |  |  | 47300 , 47310 | Y |  | No transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | JEWETT SWITCHING STATION: REPLACE KD-11 RELAY WITH MDAR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-06-30 | 345 | 0 |  | 0
No Project Number Will Be Developed | PAYNE - ROYSE 138 KV: WHITE MOUND SUBSTATION P.O.D. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-06-30 | 138 | 0 |  | 0
03TPIT0015 | Lewisville Switch 345/138 kV autotransformer | Install a 345/138 kV autotransformer at Lewisville Switch. Construct 345 kv switching station at Lewisville. Loop Roanoke - Northwest Carrollton 345 kV line into Lewisville station |  |  | Brazos | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2003-06-01 | 2003-07-01 | 345 | 0 |  | 700 | 100 | DENTON |  |  |  | 2001-07-01 | 2001-08-01 | 646645 | Y |  | There is no transmission line associated with this project
No Project Number Will Be Developed | LAKE HUBBARD: 138KV CAPACITOR BANK ADDITIONS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-07-01 | 138 | 0 |  | 0 | 110.4
No Project Number Will Be Developed | ENNIS WEST SWITCHING STATION-ENNIS SWITCHING STATION 138 KV: |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-07-07 | 138 | 11 |  | 0
03TPIT0020 | West Columbia | Increased reactive capability to 100 MVAR |  |  | CNP |  |  | 2003-07-14 | 2003-07-14 | 138 | 0 |  | 0 | 40 | BRAZORIA | BRAZORIA |  |  |  |  | 42330 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | N McCamey - LCRA Crane | Rebuild 25 miles of existing N McCamey to McElroy 69kV to 138kV |  | AEP Group 001 | LCRA TSC / AEP |  | 40066293 | 2003-07-15 | 2003-07-15 | 138 | 25 |  | 0 | 0 |  | Upton
03TPIT0021 | Clodine - O'Brien ckt.25 | Upgraded limiting equipment at Clodine and O'Brien substations to increase thermal ratings |  |  | CNP |  |  | 2003-07-30 | 2003-07-30 | 138 | 0 |  | 0 |  | HARRIS | FORT BEND |  |  |  |  | 44150, 44511 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | FORNEY SW: REPLACE 345KV CB 4510 & UPGRADE CENTERVILLE TERMIN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-08-01 | 345 | 0 |  | 0
03TPIT0024 | P.H. Robinson 345/138 kV autotransformer | Added fourth 345/138 kV, 800MVA autotransformer (A4) @P.H. Robinson |  |  | CNP |  |  | 2003-09-30 | 2003-08-12 | 345 | 0 |  | 800 |  | GALVESTON | GALVESTON |  |  |  |  | 42000 , 42010 | Y |  | No transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | CENTERVILLE SWITCHING STATION: INSTALL AUTOTRANSFORMER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-08-15 | 345 | 0 |  | 600
03TPIT0028 | Gibbons Creek - Obrien ckt.99 | Raised conductors and upgrade substation equipment to increase thermal ratings |  |  | CNP, TMPA |  |  | 2003-10-30 | 2003-08-20 | 345 | 0 |  | 0 |  | GRIMES | FORT BEND |  |  |  |  | 967 , 44500 | Y |  | Data shown includes only CNP portion of the line. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | SUN-BRAND 138KV:RELOCATE FOR KINDER MORGAN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-08-28 | 138 | 0 |  | 0
03TPIT0022 | Peters 138/69 kV autotransformer | Replaced 20 MVA autotransformer (A1) @Peters with 42 MVA auto |  |  | CNP |  |  | 2003-08-29 | 2003-08-29 | 138 | 0 |  | 42 |  | AUSTIN | AUSTIN |  |  |  |  | 46220, 46230 | Y |  | No transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | TEMPLE SWITCHING STATION - INSTALL LINE SECTIONALIZER SCHEME |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-09-01 | 138 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT-NORWOOD 138 KV LINE: REPLACE FOUNDATIONS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-09-03 | 138 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT-NORWOOD 138 KV: REPLACE CORRODED FOUNDATIONS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-09-03 | 138 | 0 |  | 0
No Project Number Will Be Developed | LIGGETT-NORWOOD 138 KV: DOUBLE CIRCUIT RECONDUCTOR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-09-03 | 138 | 0 |  | 0
No Project Number Will Be Developed | EULESS SWITCH - UPGRADE LIGGETT 138KV TERMINAL EQUIPMENT FOR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-09-04 | 138 | 0 |  | 0
No Project Number Will Be Developed | WEST LEVEE: REPLACE OVERDUTIED 138 KV CB #62 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-09-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | HACKBERRY SUBSTATION TRANSFER 138KV BKR #5230 TO WEST LEVEE S |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-09-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORWOOD-DENTON-BOWIE 138KV: RAISE SECTION FOR HIGH TEMP OPERA |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-09-06 | 138 | 0 |  | 0
No Project Number Will Be Developed | SEAGOVILLE SWITCHING STATION: REPLACE KD-11 RELAY WITH MDAR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-09-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | SULPHUR SPRINGS: REPLACE BREAKER 2580 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-09-18 | 138 | 0 |  | 0
No Project Number Will Be Developed | COLLIN 138KV SWITCHYARD ADD AUTO, STRAIN BUS, REPL 2-138 KV |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-09-18 | 138 | 0 |  | 600
03TPIT0023 | Agri - South Channel ckt.16 | Upgraded 1200Amp limiting equipment to increase thermal ratings. |  |  | CNP |  |  | 2003-09-30 | 2003-09-30 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 40051, 41380 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | MONTICELLO: INSTALL 1 36.8 MVAR CAPACITOR BANK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-09 | 138 | 0 |  | 0 | 36.8
No Project Number Will Be Developed | Southeast Edinburg - Magic Valley Pharr 1.62 mile 138kv transmission line reconductor | Reconductor the approximately 1.62 miles of existing 138kv from Southeast Edinburg to Magic Valley Pharr. The old line is 795 ACSR conductor and the new line will be 795 ACSS conductor. Poles will remain the same. |  | AEP Group 000 | AEP/TCC |  | 40083321 40174856 | 2003-10-25 | 2003-10-10 | 138 | 1.62 |  | 0 |  | HIDALGO
No Project Number Will Be Developed | CARSWELL AFB: REPLACE REVENUE METERS, PF METERI |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | CRYOVAC: REPLACE REVENUE METERS, PF METERIN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | SFA UNIVERSITY: REPLACE REVENUE METERS, PF METERI |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | GUARDIAN GLASS: REPLACE REVENUE METERS, PF METER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | KILLEEN CLEAR CREEK: REPLACE REVENUE METERS, PF METERIN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | KELLY TIRE: REPLACE REVENUE METERS, PF METERIN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | TYLER PIPE: REPLACE REVENUE METERS, PF METER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | BLACKFOOT: REPLACE REVENUE METERS, PF METER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | COSDEN: REPLACE REVENUE METERS, PF METERING |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | CHAPARRAL STEEL: REPLACE REVENUE METERS, PF METERING |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-13 | 138 | 0 |  | 0
No Project Number Will Be Developed | ESKOTA-SOUTH ABILENE 138KV: REBUILD |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-13 | 138 | 5 |  | 0
No Project Number Will Be Developed | WOLF HOLLOW: MODIFY RELAYING FOR ROCKY CREEK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-15 | 345 | 0 |  | 0
No Project Number Will Be Developed | ROYSE - NW CARROLLTON 345 KV LINE MODS FOR PLANO-TENN 138 KV |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | ROUND ROCK-ROUND ROCK SOUTH 138KV LINE - UPGRADE (R441) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-20 | 138 | 3.32 |  | 0
03TPIT0025 | Garden Villas - Pasadena ckt.06 | Raised conductors to increase thermal ratings. |  |  | CNP |  |  | 2003-10-30 | 2003-10-20 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 42680, 42500, 43040 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | CORSICANA MOBIL TAP: REPLACE REVENUE METERS, PF METER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-21 | 138 | 0 |  | 0
No Project Number Will Be Developed | EAGLE MTN COMPRESSOR: REPLACE REVENUE METERS, PF METER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-21 | 138 | 0 |  | 0
No Project Number Will Be Developed | GATESVILLE TDC: REPLACE REVENUE METERS, PF METER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-21 | 138 | 0 |  | 0
No Project Number Will Be Developed | ROUND ROCK WESTINGHOUSE: REPLACE REVENUE METERS, PF METER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-21 | 138 | 0 |  | 0
No Project Number Will Be Developed | HUNTSMAN: REPLACE REVENUE METERS, PF |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-21 | 138 | 0 |  | 0
No Project Number Will Be Developed | SOUTHERLAND: UPGRADE TERMINAL EQUIPMENT (REF:466) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-24 | 138 | 0 |  | 0
No Project Number Will Be Developed | MORGAN CR-MULBERRY CR 345 KV LINE-CHANGES FOR BITTER CR. SW.S |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-28 | 345 | 0 |  | 0
03TPIT0030 | North Belt - Gears ckt.95 | Bundled 138 kV North Belt - Gears ckt.95 and upgraded in-series equipment at North Belt substations. |  |  | CNP |  |  | 2003-10-30 | 2003-10-30 | 138 | 4.28 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 46110, 45862, 45782 | Y |  | Cost included in North Belt - Gears ckt.67 Project #03TPIT0029. No transformer capacity added.
03TPIT0029 | North Belt - Gears ckt.67 | Bundled 138 kV North Belt - Gears ckt.67 and upgraded equipment at North Belt substations. |  |  | CNP |  |  | 2003-10-30 | 2003-10-30 | 138 | 4.28 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 46110, 45861, 45781 | Y |  | No transformer capacity added.
03TPIT0027 | Westwood - Fondren ckt.25 | Verified conductors clearance to increase thermal ratings. |  |  | CNP |  |  | 2003-10-30 | 2003-10-30 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 47462, 47100 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
03TPIT0026 | Garden Villas - Witter Tap ckt.94 | Raised conductors to increase thermal ratings. |  |  | CNP |  |  | 2003-10-30 | 2003-10-30 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 42680, 42311, 41711 | Y |  | Cost included in Garden Villas - Pasadena Ckt 06 Project #03TPIT0025. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | DWU EASTSIDE FILTRATION PLANT: PROVIDE METERING FOR POD. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-10-31 | 138 | 0 |  | 0
04TPIT0071 | Round Rock - Round Rock Westinghouse 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R440 | 2004-06-01 | 2003-10-31 | 138 | 3.3 |  | 0 |  | TRAVIS | WILLIAMSON |  |  |  |  | 3668, 3669 | Y
04TPIT0040 | Valley - Anna 345 kV line upgrade | Upgrade Valley - Anna 345 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R167 | 2004-05-01 | 2003-11-01 | 345 | 27 |  | 0 |  | FANNIN | COLLIN |  |  |  |  | 1690, 2373 | Y
No Project Number Will Be Developed | ROUND ROCK - ROUND ROCK WESTINGHOUSE 138 KV (R440) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-01 | 138 | 2.9 |  | 0
03TPIT0031 | Greenville - Blackwell 138 kV line | Upgrade Greenville - Blackwell 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M436 | 2003-11-01 | 2003-11-01 | 138 | 3.8 |  | 0 |  | DALLAS | DALLAS |  |  |  |  | 2882, 2884, 2883, 2885 | Y
03TPIT0036 | Hockley - Freeman ckt.66 | Raised conductors to increase thermal ratings. |  |  | CNP |  |  | 2003-12-01 | 2003-11-01 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 45880, 45770 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | CADDO MILLS EXPLORER: REPLACE REVENUE METERS, PF ME |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | DENISON DAM: REPLACE REVENUE METERS, PF ME |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | TERRELL AIRCO: REPLACE REVENUE METERS, PF METER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | KIMBERLY CLARK: REPLACE REVENUE METERS, PF METERIN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | IRON BRIDGE PUMP: REPLACE REVENUE METERS, PF METER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | MESQUITE WESTERN ELECTRIC: REPLACE REVENUE METERS, PF METER |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | MIDLOTHIAN NORTH TEXAS CEMENT: REPLACE REVENUE METERS, PF MET |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | PLANO TENNYSON: REPLACE REVENUE METERS, PF METERIN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | FORT HOOD MAIN: REPLACE REVENUE METERS, PF METERING |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | AIR PRODUCTS: REPLACE REVENUE METERS, |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | TRINITY RIVER AUTHORITY: REPLACE REVENUE METERS, PF METERI |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | NUCOR STEEL: REPLACE REVENUE METERS, PF METERING |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | MIDLOTHIAN TXI: REPLACE REVENUE METERS, PF METERING |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | CHAMPION PAPER: REPLACE REVENUE METERS, PF METERING |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | WAXAHACHIE OCF: REPLACE REVENUE METERS, PF METERIN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | TEXAS INSTRUMENTS SHERMAN: REPLACE REVENUE METERS, PF METERIN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-05 | 138 | 0 |  | 0
03TPIT0032 | Peters - Bellville ckt.1 | Upgraded limiting equipment at Peters to increase thermal ratings. |  |  | CNP, LCRA |  |  | 2003-11-30 | 2003-11-06 | 138 | 0 |  | 0 |  | AUSTIN | AUSTIN |  |  |  |  | 46220, 7270 | Y |  | Data shown includes only CNP portion of the line. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | VALLEY 345KV SWITCH: UPGRADE 345KV MAIN BUS TO 6IN SCH. 80 AL |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-07 | 345 | 0 |  | 0
No Project Number Will Be Developed | TEMPLE SWITCHING STATION: 138KV CB2560 RELAY MODIFICATIONS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-07 | 138 | 0 |  | 0
No Project Number Will Be Developed | NORWOOD (TPL) : INSTALL 2ND 345/138KV AUTO TRANSF( M045) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-14 | 345 | 0 |  | 0
No Project Number Will Be Developed | NORWOOD 345KV STATION: INSTALL 2ND 345/138 AUTO TRANSFORMER - |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-14 | 345 | 0 |  | 600
No Project Number Will Be Developed | NORWOOD 138KV STATION: MODIFY RELAYING |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-14 | 138 | 0 |  | 0
No Project Number Will Be Developed | VALLEY SES-ANNA SWITCHING STATION 345 KV: RECONDUCTOR (WA) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-15 | 345 | 26.5 |  | 0
No Project Number Will Be Developed | FOREST GROVE-CANTON SW. 138KV: TIE TO RAYBURN COUNTRY EXPLORE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | INDUSTRIAL SWITCHING STATION: UPGRADE STATION FOR SARGENT RD. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | WEST NETWORK: UPGRADE INDUSTRIAL TERMINAL EQUIPMENT (REF:467) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-18 | 138 | 0 |  | 0
No Project Number Will Be Developed | Wormser-Rio Bravo 138kV Reconductor | Reconductor and rebuild approximately 9.6 miles of existing 138kV transmission line from Rio Bravo Substation to Wormser Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conduc |  | AEP Group 000 | AEP/TCC |  | 22169830 | 2003-05-15 | 2003-11-19 | 138 | 9.6 |  | 0 |  | WEBB
No Project Number Will Be Developed | GREENVILLE AVENUE-BLACKWELL 138 KV LINE REBUILD (M436) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-20 | 138 | 3.8 |  | 0
No Project Number Will Be Developed | Crane Bus-Tie Extension | Extend 138kV line with single concrete pole construction, 795 ACSR drake conductors from AEP Texas North Crane Substation to LCRA Crane Switching Station |  | AEP Group 000 | AEP/TNC |  | 40289972 | 2003-11-21 | 2003-11-21 | 138 | 0.15 |  | 0 |  | Crane County
No Project Number Will Be Developed | Rio Pecos - Crane Line Extension | Extend the existing 138kV H-Frame line with single concrete or steel pole construction, double ckt. capable, 2-795 ACSR drake conductors into LCRA Crane Switching Station |  | AEP Group 000 | AEP/TNC |  | 40079205 | 2003-11-21 | 2003-11-21 | 138 | 0.5 |  | 0 |  | Crane County
No Project Number Will Be Developed | CUMBY TAP - CUMBY 138 KV (69 KV OPERATION) LINE REBUILD (R117 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-11-21 | 69 | 4.6 |  | 0
03TPIT0044 | Norwood 345/138 kV autotransformer | Install a (2nd) 345/138 kV autotransformer (600 MVA) at Norwood |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M045 | 2003-12-01 | 2003-12-01 | 345 | 0 |  | 600 |  | DALLAS | [5 empty] | 2406, 2423 | Y
03TPIT0043 | Odessa EHV tertiary reactors | Install two 75 Mvar tertiary reactors at Odessa EHV |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R372 | 2003-12-01 | 2003-12-01 | 345 | 0 |  | 0 | -150 | ECTOR | [5 empty] | 1027 | Y
03TPIT0041 | Morgan Creek tertiary reactors | Install 75 Mvar tertiary reactor at Morgan Creek |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R374 | 2003-12-01 | 2003-12-01 | 345 | 0 |  | 0 | -75 | MITCHELL | [5 empty] | 1032 | Y
03TPIT0052 | Handley - Richland 138 kV line | Upgrade Handley - Richland 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5051 | 2003-12-31 | 2003-12-01 | 138 | 9.9 |  | 0 |  | TARRANT | TARRANT |  |  |  |  | 1950, 2104, 2100, 2098 | Y |  | No XMFR Capacity added
03TPIT0045 | Payne - Sherman Line Material - Whitesboro Jordan 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R155 | 2003-12-01 | 2003-12-01 | 138 | 15.8 |  | 0 |  | GRAYSON | GRAYSON |  |  |  |  | 1758, 1704, 1724, 1705 | Y
03TPIT0042 | Cielo merchant plant project | Install 138 kV breaker at Sun |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  | 2003-12-01 | 2003-12-01 | 138 | 0 |  | 0 |  | SCURRY | [5 empty] | 1064, 1063 | Y
03TPIT0039 | Liggett - Norwood 138 kV line | Upgrade Liggett - Norwood 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5003 | 2003-12-01 | 2003-12-01 | 138 | 13 |  | 0 |  | DALLAS | DALLAS |  |  |  |  | 1922, 1924, 2408 | Y
03TPIT0038 | Eskota - S Abilene 138 kV line | Upgrade Eskota - S Abilene 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R226 | 2003-12-01 | 2003-12-01 | 138 | 5.61 |  | 0 |  | NOLAN | NOLAN |  |  |  |  | 1334, 1339, 6317, 6260 | Y
03TPIT0037 | Round Rock - Round Rock S 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R441 | 2003-12-01 | 2003-12-01 | 138 | 5 |  | 0 |  | TRAVIS | TRAVIS |  |  |  |  | 3668, 3672 | Y
03TPIT0034 | Primrose - Wedgwood 138 kV line | Upgrade Primrose - Wedgwood 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M046 | 2003-12-01 | 2003-12-01 | 138 | 2.15 |  | 0 |  | TARRANT | TARRANT |  |  |  |  | 2184, 2185, 2196, 2197 | Y
03TPIT0033 | Plano Tennyson 138 kV line | Construct Plano Tennyson 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M327 | 2003-12-01 | 2003-12-01 | 138 | 11.4 |  | 0 |  | DENTON | COLLIN |  |  |  |  | 2523, 2518, 2376, 2378, 2377 | Y
04TPIT0023 | West Yates SS to Mesa View, upgrade 69 kV line | Convert North McCamey to West Yates to Mesa View 69 kV line to 138 kV with 2x795 ACSR conductor and double circuit capable structures, add new switching station Mesa View tap, add switching station at West Yates tap, and move North McCamey 138/69 kV autot |  | AEP GROUP 237 | LCRA TSC / AEP |  | 857, LCRA#1003400 and #1003404 | 2003-12-19 | 2003-12-01 | 138 | 6 |  | 0 | 0 | PECOS | PECOS
05TPIT0001c | Braunig to Kennedy 138 kV Reconductor (Floresville - Stockdale Section) | Rebuild 138 kV line from Braunig to Elmendorf to Eagle Creek to Floresville to Stockdale to Kennedy. | Rebuild of entire line divided up to several projects, each rebuilding from one station to the next. |  | CPS | Gerald Ripps 210-353-2470 | T-0765 | 2003-12-01 | 2003-12-01 | 138 | 36 |  | 0 | 0 | BEXAR | WILSON |  |  |  |  | 5025,5135,5155,5412,5145,8186 | Y |  | There are no transformers associated with this project
03TPIT0047 | Lytle Capacitor Bank | Install new 138 kV - 14 MVAR capacitor bank at Lytle substation. |  |  | CPS | Martin Benavides 210-353-4624 | S-0070 | 2003-12-02 | 2003-12-01 | 138 | 0 |  | 0 | 14 | BEXAR | [5 empty] | 5290 | Y |  | There are no transformers or transmission lines associated with this project
03TPIT0051 | Himont - Bypark ckt.94 | Verified conductors clearance to increase thermal ratings. |  |  | CNP |  |  | 2003-12-30 | 2003-12-01 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 42790, 42900, 43356, 42220 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
03TPIT0050 | Capital - Himont ckt.94 | Verified conductors clearance to increase thermal ratings. |  |  | CNP |  |  | 2003-12-30 | 2003-12-01 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 42230, 42790 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
No Project Number Will Be Developed | Downtown area improvements project, upgraded circuits 91 Eastside to Polk and Eastside to University, and circuit 90 Polk to Midtown. |  |  |  | CNP |  |  |  | 2003-12-01 | 138 | 4.23 |  | 0 | [10 empty] | No transformer capacity added.
No Project Number Will Be Developed | Reconductored 138kV circuit 66 Humble to Kingwood and upgraded equipment at Humble and Kingwood. | Reconductored 138kV circuit 66 Humble to Kingwood and partially ckt.66 Kingwood to Atascocia. Upgraded equipment at Humble and Kingwood. |  |  | CNP |  |  |  | 2003-12-01 | 138 | 11.68 |  | 0 | [10 empty] | No transformer capacity added.
03TPIT0035 | Cumby Tap | Rebuild Cumby Tap |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R117 | 2003-12-01 | 2003-12-01 | 69 | 4.61 |  | 0 |  | HOPKINS | HOPKINS |  |  |  |  | 1812, 1813 | Y
04TPIT0002 | Industrial - E Levee 138 kV line | Upgrade Industrial - E Levee 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M467 | 2004-01-15 | 2003-12-03 | 138 | 3.03 |  | 0 |  | DALLAS | DALLAS |  |  |  |  | 2482, 2875, 2976 | Y |  | No XMFR Capacity added
03TPIT0049 | Zorn-McCarty Lane | Upgrade Zorn (7180)-McCarty Lane (7184) circuit 2 to 1433.6 ACSS/TW (493-MVA) (8.50 m) T-205 |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2003-12-03 | 2003-12-03 | 138 | 8.5 |  | 0 | 0 | GUADALUPE | HAYS | [5 empty] | Y | No XMFR Capacity added; No MVAR added
03TPIT0048 | Miller Creek-Dripping Springs | Convert Miller Creek (7479)-Dripping Springs (7512) to 138-kV 795 ACSR. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2003-12-03 | 2003-12-03 | 138 | 21.2 |  | 0 | 0 | BLANCO | HAYS | [5 empty] | Y | No XMFR Capacity added; No MVAR added
No Project Number Will Be Developed | ROUND ROCK SUBSTATION: MCNEIL LINE JUMPERS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | SUN SUBSTATION - KINDER-MORGAN TRANSFORMER #2 POI |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | CEDAR CREST: REPLACE OVERDUTIED CBS #CC-209 & #CC-255 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | CALMONT: REPLACE BREAKERS #620 AND # 630,CTS ON CB 920 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-05 | 138 | 0 |  | 0
No Project Number Will Be Developed | EAST LEVEE-INDUSTRIAL 138 KV: RECONDUCTOR |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-07 | 138 | 2.98 |  | 0
No Project Number Will Be Developed | BIG THREE ODESSA: REPLACE REVENUE METERS, PF METERING |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-12 | 138 | 0 |  | 0
No Project Number Will Be Developed | MIDKIFF: INSTALL TWO 138KV LINE TERMINALS - REF. R219 (08-01- |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-12 | 138 | 0 |  | 0
No Project Number Will Be Developed | Hidalgo - Southeast Edinburg 6.3 mile 138kv transmission line reconductor | Reconductor the approximately 6.3 miles of existing 138kv from Hidalgo to Southeast Edinburg. The old line is 795 ACSR conductor and the new line will be 795 ACSS conductor. Poles will remain the same. |  | AEP Group 000 | AEP/TCC |  | 40015548 | 2003-12-12 | 2003-12-12 | 138 | 6.3 |  | 0 |  | HIDALGO
No Project Number Will Be Developed | HANDLEY-HALTOM 138 KV CIRCUIT: RECONDUCTOR W/YUKON (ACSS/TW) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-14 | 138 | 9.9 |  | 0
No Project Number Will Be Developed | VALLEY 345KV SWITCHING STATION-PROVIDE INTERCONNECTION TO KIO |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-15 | 345 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | UPTON SUB: CONVERT TO 138 KV (R219) ITEM B |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-15 | 138 | 0 |  | 0
No Project Number Will Be Developed | MORGAN CREEK INSTALL 2-37.5 MVAR REACTORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-15 | 138 | 0 |  | 0 | -75
No Project Number Will Be Developed | DENTON DR - MORRISON (A) NORTH SECTION, (LOMBARDY-MORRISON) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-15 | 138 | 6.84 |  | 0
No Project Number Will Be Developed | SUN-CIELO 138 KV:CONSTRUCT 138 KV TIE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-16 | 138 | 0 |  | 0
No Project Number Will Be Developed | SUN SUBSTATION: MODIFICATION FOR BRAZOS WIND INTERCONNECT |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-16 | 138 | 0 |  | 0
No Project Number Will Be Developed | ESKOTA SW: UPGRADE 138KV SOUTH ABILENE LINE TERMINAL EQUIPMEN |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-19 | 138 | 0 |  | 0
No Project Number Will Be Developed | SHERMAN LINE MATERIAL-WHITESBORO JORDAN 138 KV UPGRADE (R155) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-19 | 138 | 11.5 |  | 0
No Project Number Will Be Developed | S. Abilene to Eskota | Reconductor and rebuild approximately 25.7 miles of existing 138kV transmission line. The old line is 40 ACRS on wood H-frame structures. The new line will be single pole structure with 795 ACSR conductor. |  | AEP Group 000 | LCRA TSC / AEP |  | 24914185 | 2004-03-01 | 2003-12-19 | 138 | 25.7 |  | 0 | 0 | TAYLOR | Nolan
No Project Number Will Be Developed | SHERMAN LINE MATERIAL: REMOVE CKT SWR 3013 & UPGRADE SWS 301 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-22 | 138 | 0 |  | 0
No Project Number Will Be Developed | DENTON DR - UPGRADE MORRISON SW. TERMINALS (#015 & #012) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-22 | 138 | 0 |  | 0
No Project Number Will Be Developed | CEDAR HILL-STERRETT 138KV:CONNECT BEPC SARDIS SWITCHING STATI |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-23 | 138 | 0 |  | 0
No Project Number Will Be Developed | BOWEN WEST TAP LINE, ADD LDS SWITCH ON H-FRAME |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-23 | 138 | 0 |  | 0
No Project Number Will Be Developed | WEDGWOOD-PRIMROSE 138 KV LINE - REBUILD (M046) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-23 | 138 | 4.3 |  | 0
No Project Number Will Be Developed | HANDLEY-EVERMAN (SW) 138 : REBUILD SW CKT. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-23 | 138 | 9 |  | 0
No Project Number Will Be Developed | HANDLEY-EVERMAN (NE) 138 : REBUILD NE CKT. |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-23 | 138 | 9 |  | 0
No Project Number Will Be Developed | OLEFIN (SHELL) : REPLACE REVENUE METERS, PF ME |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-26 | 138 | 0 |  | 0
No Project Number Will Be Developed | ENNIS SUBSTATION: REPLACE 138KV SWITCH #551 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-26 | 138 | 0 |  | 0
No Project Number Will Be Developed | SPRABERRY: UPGRADE SPRABERRY-MIDKIFF 138KV LINE TO 2000 AMPS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-26 | 138 | 23 |  | 0
No Project Number Will Be Developed | MULBERRY CREEK: REVISE CARRIER ON 345KV LINE FOR BITTER CREEK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-29 | 345 | 0 |  | 0
No Project Number Will Be Developed | MORGAN CREEK: REVISE CARRIER ON 345KV LINE FOR BITTER CREEK |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-29 | 345 | 0 |  | 0
No Project Number Will Be Developed | PLANO TENNYSON: ESTABLISH NEW 138KV LOOP LINE TERMINALS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-29 | 138 | 0 |  | 0
No Project Number Will Be Developed | PLANO TENNYSON 138 KV LOOP LINE REF NO M327 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-29 | 138 | 14.2 |  | 0
No Project Number Will Be Developed | TEXAS INSTRUMENTS: CAPACITOR POWER FACTOR METERING |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | EAST LEVEE - REBUILD INDUSTRIAL SWITCH LINE TERMINAL FOR 2390 |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | MORRISON LANE - UPGRADE LINE SWITCHES TO 3000A (SW# MR-014 & |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | ODESSA EHV: UPGRADE 138KV CRANE LINE TERMINAL (R218) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | LOMBARDY LANE: UPGRADE LINE TERMINALS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | RICHARDSON WOODHAVEN - UPGRADE E. RICHARDSON AND W. GARLAND T |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | MORRISON SW - UPGRADE DENTON DR. TERMINALS (#055 & #062) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | ENNIS SWITCH - ADD 138KV LINE TERMINAL TO ENNIS WEST (M279) |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-30 | 138 | 0 |  | 0
No Project Number Will Be Developed | ODESSA EHV INSTALL 4-37.5 MVAR REACTORS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-30 | 138 | 0 |  | 0 | -150
No Project Number Will Be Developed | CEDAR HILL SW : REP 345KV BRKRS, SW, LT, ADD 138KV CAPS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-31 | 345 | 0 |  | 0 | 55.2
No Project Number Will Be Developed | AEP SWITCH - TRANSFORMER REPLACEMENT AND EQUIPMENT FAILURE RE |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-31 | 138 | 0 |  | 0
No Project Number Will Be Developed | MORRISON SWITCHING STATION: ADD 220.4 MVAR CAP BANKS |  |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com |  |  | 2003-12-31 | 138 | 0 |  | 0 | 220.4
04TPIT0009 | Retrieve - West Columbia ckt.47 | Upgraded equipment at Retrieve. |  |  | CNP |  |  | 2004-02-28 | 2004-01-01 | 69 | 0 |  | 0 |  | BRAZORIA | BRAZORIA |  |  |  |  | 43140, 43390 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0011 | Velasco - Retrieve ckt.47 | Upgraded equipment at Retrieve. |  |  | CNP |  |  | 2004-02-28 | 2004-01-02 | 69 | 0 |  | 0 |  | BRAZORIA | BRAZORIA |  |  |  |  | 43370, 43140 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0001 | Zorn Auto | Replace the 478MVA Zorn Auto 2 with a 600MVA auto (7045-7180) |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2004-01-04 | 2004-01-04 | 345 | 0 |  | 600 | 0 | GUADALUPE | [6 empty] | Y | No XMFR Capacity added; No MVAR added
04TPIT0010 | Tomball - Pinehurst ckt.81 | Bundled 138 kV Tomball - Pinehurst ckt.81 and upgraded limiting equipment. |  |  | CNP |  |  | 2004-02-28 | 2004-01-10 | 138 | 7.34 |  | 0 |  | HARRIS | MONTGOMERY |  |  |  |  | 46510, 46520, 46240 | Y |  | No transformer capacity added.
04TPIT0008 | Chambers - King ckt. 97 | Upgraded limiting equipment at King to increase thermal ratings. |  |  | CNP |  |  | 2004-02-01 | 2004-02-01 | 345 | 0 |  | 0 |  | CHAMBERS | HARRIS |  |  |  |  | 40255, 40900 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0007 | Cedar Bayou - North Belt ckt.99 | Upgraded limiting equipment at Cedar Bayou to increase thermal ratings. |  |  | CNP |  |  | 2004-02-01 | 2004-02-01 | 345 | 0 |  | 0 |  | CHAMBERS | HARRIS |  |  |  |  | 40000, 46100 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0006 | Crane to McElroy, build 69kV line | Convert North McCamey to Crane 69 kV line to 138 kV double circuit with 2x795 ACSR conductor | In-Service | AEP GROUP 091 | AEP/TNC |  | 868 | 2004-02-01 | 2004-02-01 | 69 | 2 |  | 0 |  | CRANE | CRANE
03TPIT0046 | Everman - Handley 138 kV line | Rebuild Everman - Handley 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M576 | 2003-12-01 | 2004-02-10 | 138 | 8.94 |  | 0 |  | TARRANT | TARRANT |  |  |  |  | 1883, 1884, 1950, 1951 | Y
04TPIT0012 | Atascocita - Kingwood ckt.66 | Bundled 138 kV Atascocita - Kingwood ckt.66 and upgraded limiting equipment at Atascocita. |  |  | CNP |  |  | 2004-02-28 | 2004-02-28 | 138 | 5.11 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 40130, 40930 | Y |  | No transformer capacity added.
04TPIT0153 | Mesa View to Mesa View SS, rebuild 138 kV line | Convert North McCamey to West Yates to Mesa View 69 kV line to 138 kV with 2x795 ACSR conductor and double circuit capable structures, add new switching station Mesa View tap, add switching station at West Yates tap, and move North McCamey 138/69 kV autot |  | AEP GROUP 237 | LCRA TSC / AEP |  | 860, LCRA#1003405 | 2004-03-09 | 2004-03-01 | 138 | 4 |  | 0 | 0 | PECOS | PECOS
04TPIT0003 | Rio Pecos to Crane, upgrade 69 kV to 138 kV line | Convert Rio Pecos to Crane 69 kV line to 138 kV with 2x795 ACSR and double circuit capable structures |  | AEP GROUP 237 | LCRA TSC / AEP |  | 259, LCRA#1003413 | 2004-03-26 | 2004-03-01 | 138 | 24 |  | 56 | 0 | PECOS | CRANE | [6 empty] | No XMFR Capacity added
04TPIT0022 | Hill Country to Stonegate 138 kV line | Build new 138 kV line to Stonegate substation |  | S-0494, T-0493 | CPS | Mike Denning 210-353-2822 | T-0193 | 2004-03-04 | 2004-03-01 | 138 | 10 |  | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5210,5415 | Y |  | There are no transformers associated with this project
04TPIT0035 | Royse 345/138 kV autotransformer | Replace a 450 MVA 345/138 kV autotransformer at Royse with a 600 MVA autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M480 | 2004-05-01 | 2004-03-04 | 345 | 0 |  | 600 |  | ROCKWALL | [5 empty] | 2483, 2460 | Y
04TPIT0021 | Brownwood - Bangs 138 kV and 69 kV line | Rebuild existing Brownwood - Bangs 69 kV line as a DCKT 138 kV and 69 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R118 | 2004-03-01 | 2004-03-04 | 138 | 15.56 |  | 0 | 0 | BROWN | COLEMAN |  |  |  |  | 1662, 1669, 1671, 1661, 6355 | Y
04TPIT0076 | Whitney to Powell Rebuild | Rebuild the existing Whitney to Powell 69KV line |  |  | Brazos | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2004-06-01 | 2004-03-04 | 69 | 14.5 |  | 0 |  | Bosque | Bosque |  |  | 2003-03-01 | 2003-04-01 | 242327 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
04TPIT0062 | Copperas Cove - Copperas Cove LCRA 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R064 | 2004-06-01 | 2004-03-07 | 138 | 1.89 |  | 0 |  | CORYELL | CORYELL |  |  |  |  | 3630, 7061 | Y
03TPIT0040 | Sargent - Industrial 138 kV line | Upgrade Sargent - Industrial 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M466 | 2003-12-01 | 2004-03-18 | 138 | 0.6 |  | 0 |  | DALLAS | DALLAS |  |  |  |  | 2972, 2975 | Y
04TPIT0068 | Killeen Fort Hood Tap - Killeen W 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R014A | 2004-06-01 | 2004-03-26 | 138 | 1.9 |  | 0 |  | BELL | BELL |  |  |  |  | 3627, 3628, 3629 | Y
No Project Number Will Be Developed | Crane Line Extension | Extension of the Rio Pecos - Crane 69 kV rebuild into the new LCRA Transmission Services Corp. Crane Switching Station. |  | AEP Group 000 | AEP/TNC |  | 40079178a | 2004-01-16 | 2004-03-26 | 138 | 0.56 |  | 0 |  | Crane County
04TPIT0015 | North Belt - Inteq ckt.67 | Raised conductors and partially rebuilt ckt.67 to increase thermal ratings. |  |  | CNP |  |  | 2004-03-28 | 2004-03-28 | 138 | 1.88 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 46110, 45740, 45900 | Y |  | No transformer capacity added.
04TPIT0013 | Inteq - Intercontinental ckt.67 | Raised conductors and partially rebuilt ckt.67 to increase thermal ratings and upgrade in-series equipment. |  |  | CNP |  |  | 2004-03-28 | 2004-03-28 | 138 | 1.11 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 45900, 45910 | Y |  | Cost included in North Belt - Inteq ckt.67, Project #04TPIT0015. No transformer capacity added.
04TPIT0024 | T.H. Wharton - Kluge ckt.21 | Bundled 138 kV T.H. Wharton - Kluge ckt.21and upgraded equipment @T.H. Wharton . |  |  | CNP |  |  | 2004-03-30 | 2004-03-30 | 138 | 10.84 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 45515, 45951 | Y |  | No transformer capacity added.
05TPIT0001b | Braunig to Kennedy 138 kV Reconductor (Stockdale - Fall City section) | Rebuild 138 kV line from Braunig to Elmendorf to Eagle Creek to Floresville to Stockdale to Kennedy. | Rebuild of entire line divided up to several projects, each rebuilding from one station to the next. |  | CPS | Gerald Ripps 210-353-2470 | T-0763 | 2004-04-01 | 2004-04-01 | 138 | 36 |  | 0 | 0 | BEXAR | WILSON |  |  |  |  | 5025,5135,5155,5412,5145,8186 | Y |  | There are no transformers associated with this project
04TPIT0150 | Reconnect Foster 69 kV Substation | Radially connected to Flewellen 69 kV bus ckt.49 Flewellen to Rosenberg. |  |  | CNP |  |  | 2004-04-03 | 2004-04-03 | 69 | 0 |  | 0 |  | FORT BEND | FORT BEND |  |  |  |  | 44250 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0037 | Everman 345/138 kV autotransformer | Install (3rd) 345/138 kV autotransformer (600 MVA) at Everman |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5002 | 2004-05-01 | 2004-04-04 | 345 | 0 |  | 600 |  | TARRANT | [5 empty] | 1882, 1883 | Y
04TPIT0036 | Sargent Rd. 345/138 kV autotransformer | Install a 600 MVA 345/138 kv autotransformer at Sargent Rd. |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M458 | 2004-05-01 | 2004-04-04 | 345 | 0 |  | 600 |  | DALLAS | [5 empty] | 2946, 2947, 2948, 2949, 2950, 2940, 2941, 2951, 2969, 2972, 2973, 2398, 2427 | Y
04TPIT0072 | Hackberry - N Lake 138 kV line | Upgrade Hackberry - N Lake 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5036 | 2004-06-01 | 2004-04-04 | 138 | 4.2 |  | 0 |  | DALLAS | DALLAS |  |  |  |  | 2386, 2388, 2393 | Y
04TPIT0039 | Sargent - Parkdale 138 kV line | Upgrade Sargent - Parkdale 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M465 | 2004-05-01 | 2004-04-04 | 138 | 4.94 |  | 0 |  | DALLAS | DALLAS |  |  |  |  | 2445, 2969, 2950 | Y
04TPIT0057 | Garden Villas | Increased reactive capability to 93.3 MVAR |  |  | CNP |  |  | 2004-05-30 | 2004-04-04 | 138 | 0 |  | 0 | 33.3 | HARRIS | HARRIS |  |  |  |  | 42700 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0152 | Burleson to Sand Hill 138kV circuits | Take out two existing 138 kV circuits (Carson to AMD & Burleson to Met Center). Establish four new 138kV circuits (Burleson to AMD, Burleson to Carson Creek, Grove to MetCenter and Bergstrom to Kingsbery). Reconductor Bergstrom to Onion Creek to 3000 amp |  | CKT.982 #1-55940755 CKT.1010 #1-55940756 CKT.1017 #1-55940757 CKT.1020 #1-55940758 CKT.1021 #1-55940583 | Austin Energy | James Armke (512) 322-6705 james.armke@austinenergy.com | Budget # 4240, 2848,4242,4247,4848,4248 | 2004-04-04 | 2004-04-04 | 138 | 14.84 |  | 0 |  | TRAVIS | TRAVIS |  |  |  |  | 9120, 9151,9175,9251,9200,9164,9163,9123 | Y
04TPIT0045 | Greens Bayou - Humble ckt.94 | Rebuilt 2-397ACSR portion of Parkway - Humble ckt.94 to increase thermal ratings. |  |  | CNP |  |  | 2004-05-30 | 2004-04-12 | 138 | 3.5 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 41222, 40830 | Y |  | No transformer capacity added.
04TPIT0078 | Odessa EHV - Glenhaven 138 kv line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | W060B | 2004-06-01 | 2004-04-14 | 138 | 6.86 |  | 0 |  | ECTOR | ECTOR |  |  |  |  | 1027, 1128, 1127, 1121 | Y
04TPIT0019 | P.H. Robinson - Webster Tap ckt.92 | Raised conductors to increase thermal ratings |  |  | CNP |  |  | 2004-04-15 | 2004-04-15 | 138 | 0 |  | 0 |  | GALVESTON | HARRIS |  |  |  |  | 42010, 42842, 43502 | Y |  | Costs Included in PH Robinson-Webster - Ckt.93. Project #04TPIT0016. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0034 | Greens Bayou C - Lychem ckt.08 & Greens Bayou East - Explor ckt.03 | Swapped circuits at Greens Bayou |  |  | CNP |  |  | 2004-05-30 | 2004-04-29 | 138 | 0.07 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 40710, 40990 40716, 40560 | Y |  | No transformer capacity added.
04TPIT0054 | Blackland 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M360 | 2004-05-15 | 2004-04-30 | 138 | 0 |  | 0 | 55.2 | ROCKWALL | [5 empty] | 2713 | Y
04TPIT0033 | Bellaire - Garrot ckt.37 | Bundled 138 kV Bellaire - Garrot ckt.37 and upgraded in-series equipment @ Bellaire & Kirby. |  |  | CNP |  |  | 2004-04-30 | 2004-04-30 | 138 | 4.28 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 47015, 47016, 47320, 47660 | Y |  | No transformer capacity added.
04TPIT0031 | Addicks - Satsuma Tap ckt.21 | Bundled 138 kV Addicks - Satsuma Tap ckt.21 and upgraded equipment @Addicks. |  |  | CNP |  |  | 2004-04-30 | 2004-04-30 | 138 | 3.95 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 45610, 46302 | Y |  | No transformer capacity added.
04TPIT0030 | W.A. Parish - Dow ckt.99 | Raised conductors and upgrade Dow substation equipment to increase thermal ratings |  |  | CNP |  |  | 2004-05-30 | 2004-05-01 | 345 | 0 |  | 0 |  | FORT BEND | BRAZORIA |  |  |  |  | 44000 , 42500 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0046 | Veterans - Willow ckt.81 | Bundled 138 kV Veterans - Willow ckt.81 and upgrade limiting equipment at Willow. |  |  | CNP |  |  | 2004-05-30 | 2004-05-01 | 138 | 5.57 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 46552, 46660 | Y |  | No transformer capacity added.
04TPIT0053 | Allen Substation 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M317 | 2004-05-15 | 2004-05-02 | 138 | 0 |  | 0 | 73.6 | COLLIN | [5 empty] | 2531, 2549 | Y
No Project Number Will Be Developed | North Edinburg - Hidalgo 2.8 mile 138kv transmission line reconductor | Reconductor the approximately 2.8 miles of existing 138kv from North Edinburg to Hidalgo. The old line is 795 ACSR conductor and the new line will be 795 ACSS conductor. Existing single pole structures will be replace with new single pole structures as |  | AEP Group 000 | AEP/TCC |  | 4024695101 | 2004-05-02 | 2004-05-02 | 138 | 2.8 |  | 0 |  | HIDALGO
04TPIT0055 | Allen North Substation 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M3001 | 2004-05-15 | 2004-05-03 | 138 | 0 |  | 0 | 55.2 | COLLIN | [5 empty] | 2533, 2548 | Y
04TPIT0082 | Kirkland Park - TI 138 kV line | Upgrade Kirkland Park - TI 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M433A | 2004-06-01 | 2004-05-04 | 138 | 2.3 |  | 0 |  | DALLAS | DALLAS |  |  |  |  | 2456, 2637, 2457, 2636, 2640, 2638, 2639 | Y
04TPIT0073 | Allen Switch 345/138 kV autotransformer series reactor | Install three-ohm 138 kV series reactor on 450 MVA 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M313 | 2004-06-01 | 2004-05-04 | 138 | 0 |  | 0 |  | COLLIN | [5 empty] | 2513, 2511 | N
04TPIT0049 | Denton Dr - Morrison 138 kV line | Upgrade Denton Dr - Morrison 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M455 | 2004-05-15 | 2004-05-04 | 138 | 6.6 |  | 0 |  | DALLAS | DALLAS |  |  |  |  | 2487, 2488, 2786, 2784, 2780, 2794, 2787, 2785, 2781, 2795 | Y
04TPIT0087 | Hardy | Increased reactive capability to 93.3 MVAR |  |  | CNP |  |  | 2004-06-01 | 2004-05-04 | 138 | 0 |  | 0 | 33.3 | HARRIS | HARRIS |  |  |  |  | 45850 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0031 | North Texas to Cottondale Sw. | Rebuild existing North Texas to Cottondale Sw 69kv line with 138kv const. |  |  | Brazos | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2005-06-01 | 2004-05-04 | 138 | 26 |  | 0 |  | PARKER | WISE |  |  | 2003-05-01 | 2003-08-01 | 501,588,501 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
04TPIT0149 | Palo Alto 138-kV/13-kV Substation | Install a new 138/13 kV Substation |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2004-05-04 | 2004-05-04 | 138 | 0 |  | 28 | 4.8 | CAMERON | [5 empty] | 5965 | Y
04TPIT0151 | Barton to Patton Lane project | Relocate eight spans of circuit 928 (Barton to Patton) going into Patton Lane sub. Move 3 poles of Circuit 969 (Oak Hill to Patton Ln) for road widening. Reconductor part of Ckt 928 to bundled 795 ACSR Drake |  | N/A | Austin Energy | James Armke (512) 322-6705 james.armke@austinenergy.com | Budget # 4243 | 2004-05-04 | 2004-05-04 | 138 | 0.658 |  | 0 |  | TRAVIS | TRAVIS |  |  |  |  | 925392479158 | Y
04TPIT0070 | Forest Hill - Bryan Tap 69 kV line | Rebuild Forest Hill - Bryan Tap 69 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5066 | 2004-06-01 | 2004-05-04 | 69 | 3.75 |  | 0 |  | TARRANT | TARRANT |  |  |  |  | 1968, 2159 | Y
04TPIT0067 | Temple - N Temple 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R415 | 2004-06-01 | 2004-05-07 | 138 | 4.6 |  | 0 |  | BELL | BELL |  |  |  |  | 3607, 3608 | Y
04TPIT0032 | North Belt | Increased reactive capability to 110.8 MVAR |  |  | CNP |  |  | 2004-05-30 | 2004-05-11 | 138 | 0 |  | 0 | 100 | HARRIS | HARRIS |  |  |  |  | 46110 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0056 | Terrell Switch 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M374 | 2004-05-15 | 2004-05-12 | 138 | 0 |  | 0 | 55.2 | KAUFMAN | [5 empty] | 2721 | Y
04TPIT0028 | Jeanetta 345/138 kV autotransformer | Replaced failed 600 MVA autotransformer (A3) @Jeanetta |  |  | CNP |  |  | 2004-05-30 | 2004-05-13 | 345 | 0 |  | 600 |  | HARRIS | HARRIS |  |  |  |  | 47300 , 47310 | Y |  | No transmission circuits built, rebuilt or reconductored.
04TPIT0066 | Allen Switch - Ben Davis 138 kV line series reactor | Install seven-ohm 138 kV series reactor at Allen Switch on line to Ben Davis |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M357 | 2004-06-16 | 2004-05-16 | 138 | 0 |  | 0 |  | COLLIN | [5 empty] | 968, 2509, 2477 | N
04TPIT0074 | Benbrook - Wedgwood 138 kV line | Upgrade Benbrook - Wedgwood 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5037 | 2004-06-01 | 2004-05-17 | 138 | 5.65 |  | 0 |  | TARRANT | TARRANT |  |  |  |  | 1874, 1875, 2184, 2185 | Y
04TPIT0052 | Dallas North Network Substation 13.2 kV capacitors | Install 13.2 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M498A | 2004-05-04 | 2004-05-18 | 138 | 0 |  | 0 | 43.2 | DALLAS | [5 empty] | 2866 | Y
04TPIT0051 | Dallas West Network Substation 13.2 kV capacitors | Install 13.2 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M498B | 2004-05-15 | 2004-05-20 | 138 | 0 |  | 0 | 43.2 | DALLAS | [5 empty] | 2873 | Y
04TPIT0065 | Temple Switch 345/138 kV autotransformer series reactors | Install two-ohm 138 kV series reactor on autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R442 | 2004-06-15 | 2004-05-21 | 138 | 0 |  | 0 |  | BELL | [5 empty] | 3415, 3414 | N
04TPIT0077 | Shamburger - SE Tyler 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R337A | 2004-06-01 | 2004-05-24 | 138 | 2.01 |  | 0 |  | SMITH | SMITH |  |  |  |  | 3104, 3210 | Y
04TPIT0027 | Rio Pecos to N McCamey, rebuild 138 kV line | Re-build 138 kV Rio Pecos to North McCamey line as double circuit with 2-795 ACSR conductor |  | AEP GROUP 239 | LCRA TSC / AEP |  | 1245, LCRA#1003416 | 2004-05-27 | 2004-05-27 | 138 | 9.63 |  | 0 | 0 | UPTON | PECOS
04TPIT0061 | Rosehill-Lyons 138 kV line | Impedance change project |  |  | GARLAND |  |  | 2004-05-31 | 2004-05-31 | 138 | 1 |  | 0 |  | DALLAS | [5 empty] | 819817 | Y |  | Changes impedance for segments of the line
04TPIT0060 | Rosehill 138 kV new substation | New load serving |  |  | GARLAND |  |  | 2004-05-31 | 2004-05-31 | 138 | 0 |  | 0 |  | DALLAS | [5 empty] | 817 | Y |  | This project is related to 04TPIT0058 and 04TPIT0061 projects
04TPIT0058 | Wynn Joyce-Rosehill 138 kV line | Impedance change project |  |  | GARLAND |  |  | 2004-05-31 | 2004-05-31 | 138 | 1 |  | 0 |  | DALLAS | [5 empty] | 813817 | Y |  | Changes impedance for segments of the line
04TPIT0059 | Newman-Miller 69 kV line | Line upgrade |  |  | GARLAND |  |  | 2004-05-31 | 2004-05-31 | 69 | 2 |  | 0 |  | DALLAS | [5 empty] | 814824 | Y |  | Relieves overload and serves loads at Newman and Miller
04TPIT0081 | Hillsboro - Whitney 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R443 | 2004-06-01 | 2004-06-01 | 138 | 17.45 |  | 0 |  | HILL | BOSQUE |  |  |  |  | 3546, 3522 | Y
04TPIT0050 | Mansfield Substation 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M372 | 2004-06-01 | 2004-06-01 | 138 | 0 |  | 0 | 55.2 | TARRANT | [5 empty] | 2208 | Y
04TPIT0181 | Stonegate 138kV Substation | Build new 138 kV line to Stonegate substation |  | T-0493 | CPS | Ulrich Skerhut 210-353-2923 | S-0494 | 2004-06-01 | 2004-06-01 | 138 | 0.1 |  | 100 | 0 | BEXAR | BEXAR |  |  |  |  | 5415, 5180 | Y
08TPIT0072 | Ckt 982 Bergstrom to Met Center Reconductor | Reconductor the last span of the Ckt 982 terminating at Met Center with bundled 795 ACSR Drake conductors capable of carrying 2000 Amperes. |  | N/A | Austin Energy | James Armke (512) 322-6705 james.armke@austinenergy.com | Budget #26112 | 2006-06-01 | 2004-06-01 | 138 | 0.1 |  | 0 |  | TRAVIS | TRAVIS |  |  |  |  | Busses 9163, 9164 | Y
04TPIT0048 | W.A. Parish - Obrien ckt.99 | Raised conductors and upgrade substation equipment to increase thermal ratings |  |  | CNP |  |  | 2004-05-30 | 2004-06-04 | 345 | 0 |  | 0 |  | FORT BEND | FORT BEND |  |  |  |  | 44000 , 44500 | Y |  | Costs Included in WA Parish - Obrien ckt 98: 04TPIT0047. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0130 | Northaven - Alpha Rd 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M478 | 2004-06-04 | 2004-06-13 | 138 | 4.6 |  | 0 |  | DALLAS | DALLAS |  |  |  |  | 2596, 2657, 2597,2659 | Y
04TPIT0026b | Hockley - Macedonia ckt.1 | Install 138kV line equipment to build tie to LCRA. |  |  | LCRA TSC / CNP |  |  | 2004-05-30 | 2004-06-14 | 138 | 3.2 |  | 0 | 0 | HARRIS | WALLER |  |  |  |  | 45880, 7671 | Y
04TPIT0026a | Hockley - Macedonia | Construct a new 959 ACSS (392-MVA) 138-kV transmission line (approximately thirteen miles) between the Reliant / HL&P Hockley (45880) and the San Bernard Electric Cooperative (SBEC) Macedonia(7671) substations and add two 138-kV circuit breakers at the Prairie View substation. |  |  | LCRA TSC / CNP | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2004-05-30 | 2004-06-14 | 138 | 13 |  | 0 | 0 | HARRIS | WALLER |  |  |  |  | 45880, 7671 | Y | No XMFR Capacity added; No MVAR added
04TPIT0014 | P.H. Robinson - Telephone Tap ckt.91 | Raised conductors to increase thermal ratings to 90/90deg C. |  |  | CNP |  |  | 2004-05-30 | 2004-06-15 | 138 | 0 |  | 0 |  | GALVESTON | BRAZORIA |  |  |  |  | 42015, 42561, 42762, 42922 | Y |  | Costs Included in PH Robinson-Mary's Creek Ckt.06 Project #04TPIT0004. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0004 | P.H. Robinson -Telephone Tap ckt.06 | Raised conductors to increase thermal ratings to 90/90deg C. |  |  | CNP |  |  | 2004-05-30 | 2004-06-15 | 138 | 0 |  | 0 |  | GALVESTON | BRAZORIA |  |  |  |  | 42015, 43081, 42761, 42921 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0038 | Polaris - Genoa Tap ckt.95 | Partially reconductored and partially raised conductors to increase thermal ratings |  |  | CNP |  |  | 2004-05-30 | 2004-06-18 | 138 | 1.69 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 43101, 42291 | Y |  | No transformer capacity added.
04TPIT0085 | T.H. Wharton 345/138 kV autotransformer | Replaced 400 MVA autotransformer (A1) @T.H. Wharton with 800MVA auto |  |  | CNP |  |  | 2004-06-30 | 2004-06-21 | 345 | 0 |  | 800 |  | HARRIS | HARRIS |  |  |  |  | 45500 , 45510 | Y |  | No transmission circuits built, rebuilt or reconductored.
04TPIT0180 | Marion-Comal | Reconductor the following ckts with 959 mcm ACSS (392-MVA) conductor: Marion (7178) – Gpi (7159) 138-kV cicuit 1 (4.4 m), Gpi (7158) – Loop 337(7456) 138-kV circuit 1 (5.6 m), Comal (7176) – Loop 337(7456) 138-kV circuit 1 (2.1 m) |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2004-06-30 | 2004-06-30 | 138 | 12.1 |  | 0 | 0 | GUADALUPE | COMAL | [5 empty] | Y | No XMFR Capacity added; No MVAR added
04TPIT0178 | Kendall-Kerrville Stadium | Upgrade the 16.7-mile Kendall(7150)-Kerrville Stadium(7138) 336 ACSR 138-kV transmission line to 795 ACSR (220-MVA). |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2004-06-30 | 2004-06-30 | 138 | 16.7 |  | 0 | 0 | KENDALL | KERR | [5 empty] | Y | No XMFR Capacity added; No MVAR added
04TPIT0089 | Bellville South-Peters | Upgrade the 8.6-mile Bellville South(7270)-Peters(46220) 795 ACSR (220-MVA) 138-kV transmission line to 959 ACSS (392-MVA). |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2004-06-30 | 2004-06-30 | 138 | 8.6 |  | 0 | 0 | AUSTIN | [6 empty] | Y | No XMFR Capacity added; No MVAR added
04TPIT0086 | Comfort-Verde Creek | Increase the line-to-ground clearance on the 13.3-mile Comfort(7155)-Verde Creek(7146) 138-kV transmission line as necessary to upgrade the circuit from its existing design rating of 104-MVA to its full conductor rating of 128-MVA. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2004-06-30 | 2004-06-30 | 138 | 13.3 |  | 0 | 0 | KENDALL | KERR | [5 empty] | Y | No XMFR Capacity added; No MVAR added; No New Conductor
06TPIT0121 | Texas City, Amoco-Terminal 69kV line rebuild | Rebuild line from Amoco to Terminal substation in Texas City to double-circuit construction. Part of larger project to bring 138kV to Valero refinery. One circuit will become 138kV line from Amoco-Loop 197. |  |  | TNMP | Rex McDaniel, 409-948-8451, rmcdaniel@tnpe.com | GCEC24512 | 2004-07-01 | 2004-07-01 | 69 | 1 |  | 0 |  | GALVESTON | GALVESTON |  |  |  |  | 38650, 39070 | Y
04TPIT0084 | Salem-Bellville South | Construct a new four terminal substation (Highway 36) at the intersection of the Brenham(7292)-Brenham North(7294) and Salem(7289)-Bellville North(7287) transmission lines. Upgrade the 5.7-mile Salem(7289)-Brenham(7292)-Highway 36(7291) 795 ACSR (220-MVA) 138-kV transmission to 959 ACSS (392-MVA). Upgrade the 19.6-mile Salem(7289)-Highway 36(7291)-Bellville North(7287)-Bellville South(7270) 4/0 ACSR (47-MVA) 69-kV transmission line to 959 ACSS (392-MVA) 138-kV. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2004-06-30 | 2004-07-08 | 138 | 25.3 |  | 0 | 0 | WASHINGTON | AUSTIN | [5 empty] | Y | No XMFR Capacity added; No MVAR added
04TPIT0016 | P.H. Robinson - Webster ckt.93 | Bundled 138 kV P.H. Robinson - Webster ckt.93 and upgrade limiting equipment. |  |  | CNP |  |  | 2004-07-30 | 2004-07-25 | 138 | 11.93 |  | 0 |  | GALVESTON | HARRIS |  |  |  |  | 42015, 43500 | Y |  | No transformer capacity added.
05TPIT0033 | Bowie to St Jo | Rebuild existing Bowie to St Jo 138kv line |  |  | Brazos | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2005-06-01 | 2004-08-01 | 138 | 20 |  | 0 |  | MONTAGUE | MONTAGUE |  |  | 2003-05-01 | 2003-08-01 | 620,762,746 |  |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
04TPIT0123 | Everman - Forest Hill 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5039 | 2004-12-01 | 2004-08-04 | 138 | 1.88 |  | 0 |  | TARRANT | TARRANT |  |  |  |  | 1884, 1967 | Y
05TPIT0115 | Greens Bayou - Fidelity ckt.21 | Verified conductors clearance to increase thermal ratings |  |  | CNP |  |  | 2004-08-30 | 2004-08-30 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 40710, 40590 | N |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0173 | Fidelity - Davson ckt.21 | Verified conductors clearance to increase thermal ratings |  |  | CNP |  | 93/78 | 2004-08-30 | 2004-08-30 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 40590, 41712, 40420 | N |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0101 | Twin Buttes cut-in to SAPS, rebuild 138 kV line | Twin Buttes 345/138 kV substation cut-in to the Big Lake to SAPS 138 kV line and re-build of Twin Buttes to SAPS 138 kV line |  | AEP GROUP 081 | LCRA TSC / AEP |  | 1216, LCRA#1002909 | 2004-08-31 | 2004-08-31 | 138 | 7 |  | 0 | 0 | IRION | TOM GREEN
04TPIT0100 | SAPS to Big Lake, cut-in Twin Buttes with dble crct 138 kV line | Twin Buttes 345/138 kV substation cut-in to the Big Lake to SAPS 138 kV line and re-build of Twin Buttes to SAPS 138 kV line |  | AEP GROUP 081 | LCRA TSC / AEP |  | 642, LCRA#1002908 | 2004-08-31 | 2004-08-31 | 138 | 9.7 |  | 0 | 0 | IRION | TOM GREEN
04TPIT0147 | Rio Pecos to North McCamey, add second 138 kV circuit | Re-build 138 kV Rio Pecos to North McCamey line as double circuit with 2-795 ACSR conductor | Complete | AEP GROUP 239 | LCRA TSC / AEP |  | 262, LCRA#1004230 | 2004-09-03 | 2004-09-01 | 138 | 9.81 |  | 0 | 0 | UPTON | PECOS
04TPIT0119 | North McCamey to Crane, add second 138 kV circuit | Convert North McCamey to Crane 69 kV line to 138 kV double circuit with 2x795 ACSR conductor |  | AEP GROUP 091 | LCRA TSC / AEP |  | 1622, LCRA#10042298 | 2004-09-03 | 2004-09-03 | 138 | 23 |  | 0 | 0 | CRANE | UPTON
05TPIT0013 | NW Carrollton - Carrollton Frankford 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M316 | 2004-12-31 | 2004-09-04 | 138 | 0.93 |  | 0 |  | DALLAS | DALLAS |  |  |  |  | 2362, 2519 | Y
No Project Number Will Be Developed | Crane to McElroy Cut-In 69 kV | Construct 1.57 miles of 69 kV from Crane to the McElroy/N. McCamey Cut-In |  | AEP Group 000 | AEP/TNC |  | 24907967 | 2004-06-04 | 2004-09-14 | 69 | 1.57 |  | 0 |  | CRANE | UPTON
04TPIT0103 | Rio Pecos to Mesa View SS, rebuild 138 kV Line | Rebuild 138 kV Rio Pecos to Mesa View Switching Station line with 2x795 ACSR conductor and double circuit capable structures |  | AEP GROUP 239 | LCRA TSC / AEP |  | 263, LCRA#1003411 | 2004-09-15 | 2004-09-15 | 138 | 27 |  | 0 | 0 | PECOS | PECOS
04TPIT0170 | T.H.Wharton - Jewett ckt.1 | Raised conductors to increase thermal ratings |  |  | CNP, TXU |  |  | 2004-09-16 | 2004-09-16 | 345 | 0 |  | 0 |  | HARRIS | LEON |  |  |  |  | 45500, 3390 | N |  | Data shown includes only CNP portion of the line. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0168 | Gibbons Creek - Roans Prairie ckt.75 | Verified conductors clearance to increase thermal ratings. |  |  | CNP, TMPA |  |  | 2004-09-16 | 2004-09-16 | 345 | 0 |  | 0 |  | GRIMES | GRIMES |  |  |  |  | 967, 40600 | N |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
08TPIT0056 | Tomball - Jewett ckt.1 | Verified tie line from Tomball to TXU tie point conductor clearance to increase thermal ratings to 1450 MVA |  |  | CNP |  |  | 2008-12-31 | 2004-09-16 | 345 | 0 |  | 0 |  | HARRIS | LEON |  | 2004-03-08 |  |  | 46500, 3390 | N |  | Data shown includes only CNP portion of the line. Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored..
04TPIT0164 | Tomball - King ckt.74 | Verified conductors clearance to increase thermal ratings. |  |  | CNP |  |  | 2004-09-16 | 2004-09-16 | 345 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 46500, 45971, 40900 | N |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored..
04TPIT0162 | Roans Prairie - King ckt.75 | Verified conductors clearance to increase thermal ratings. |  |  | CNP |  |  | 2004-09-16 | 2004-09-16 | 345 | 0 |  | 0 |  | GRIMES | HARRIS |  |  |  |  | 40600, 45972, 40900 | N |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored..
04TPIT00163 | T.H.Wharton - Obrien ckt.98 | Verified conductors clearance to increase thermal ratings. |  |  | CNP |  |  | 2004-09-16 | 2004-09-16 | 345 | 0 |  | 0 |  | HARRIS | FORT BEND |  |  |  |  | 45500, 44500 | N |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored..
04TPIT0161 | DOW LaPort - Borden ckt.84 | Verified conductors clearance to increase thermal ratings. |  |  | CNP |  |  | 2004-09-21 | 2004-09-21 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 40490, 40210 | N |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored..
04TPIT0137 | Midessa - Midland W 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R290 | 2004-12-01 | 2004-10-01 | 138 | 3.81 |  | 0 |  | MIDLAND | MIDLAND |  |  |  |  | 1059, 1117 | Y
04TPIT0083 | Ben Hur to Perry and Ben Hur to Prairie Hill Rebuild | Rebuild existing Ben Hur to Perry and Ben Hur to Prairie Hill 69kv lines with 138kv construction and 795mcm conductor. Continue to operate at 69kv |  |  | Brazos | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2004-10-01 | 2004-10-01 | 138 | 23.57 |  | 0 |  | FALLS | LIMESTONE |  |  | 2003-03-01 | 2003-03-01 | 92,99,107 | Y |  | There is no reactive or transformer capability associated with this project
No Project Number Will Be Developed | N McAllen - W. McAllen 138kV at FM 2220 | Relocate 16 structures for road improvement |  | AEP Group 000 | AEP/TCC |  | 40389465 | 2004-10-01 | 2004-10-01 | 138 | 0.76 |  | 0 |  | HIDALGO
04TPIT0047 | W.A. Parish - Obrien ckt.98 | Raised conductors and upgraded substation equipment to increase thermal ratings |  |  | CNP |  |  | 2004-10-04 | 2004-10-04 | 345 | 0 |  | 0 |  | FORT BEND | FORT BEND |  |  |  |  | 44000 , 44500 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0069 | Mountain Creek - Westmoreland 138 kV line | Convert Mountain Creek - Westmoreland 69 kV line to 138 kV operation |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M4020 | 2004-09-01 | 2004-10-04 | 138 | 3.65 |  | 0 |  | DALLAS | DALLAS |  |  |  |  | 2411, 3042, 2416 | Y
04TPIT0096 | Twin Buttes, add SS with 345/138 kV autotransformer | Twin Buttes 345/138 kV substation cut-in to the Big Lake to SAPS 138 kV line and re-build of Twin Buttes to SAPS 138 kV line |  | AEP GROUP 081 | LCRA TSC / AEP |  | 216, LCRA#1002182 | 2004-10-12 | 2004-10-12 | 345 | 0 |  | 280 | 36
04TPIT0105 | W.A. Parish - Oasis ckt.99 | Bundled 345 kV W.A. Parish - Oasis Ckt.99. Partially rebuilt 69 kV ckt.53 from Karsten to Manvel Tap |  |  | CNP |  |  | 2004-10-15 | 2004-10-15 | 345 | 24.13 |  | 0 |  | FORT BEND | BRAZORIA |  | 2003-09-03 | 2003-11-21 |  | 44000 , 43035, 44440, 44400 | Y |  | No transformer capacity added.
04TPIT0109 | Hickory Forest-New Berlin | Construct a new 795 ACSR (220-MVA) 138-kV transmission line (approximately thirteen miles) between the Hickory Forest(7225) and New Berlin(7612) substations. The new transmission line will be operated at 69-kV initially. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2005-06-04 | 2004-10-22 | 138 | 13 |  | 0 | 0 | GUADALUPE | [6 empty] | Y | No XMFR Capacity added; No MVAR added
04TPIT0110 | Westwood - Jeanetta ckt.25 | Upgraded limiting equipment at Jeanetta to increase thermal ratings. |  |  | CNP |  |  | 2004-10-30 | 2004-10-30 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 47461, 47310 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0136 | Benbrook - Calmont 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5004 | 2004-12-01 | 2004-11-01 | 138 | 4.67 |  | 0 |  | TARRANT | TARRANT |  |  |  |  | 1874, 1875, 1955 | Y
04TPIT0064 | Forest Hill 138/69 kV autotransformer | Replace Forest Hill 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M176 | 2004-12-04 | 2004-11-01 | 138 | 0 |  | 150 |  | TARRANT | [5 empty] | 1967, 1968 | Y
04TPIT0079 | Tintop to Brock Reconductor | Rebuild existing Tintop to Brock 69kv line with 138kv construction and 795mcm conductor. Continue to operate at 69kv |  |  | Brazos | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2004-11-01 | 2004-11-01 | 138 | 8.76 |  | 0 |  | PARKER | PARKER |  |  | 2003-01-01 | 2003-01-01 | 494,489,487 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
04TPIT0063 | Spring to Jordan Conversion | Convert section of BEPC system north of Spring to 138KV operation.Construct 138/69KV switching station at Hawkins. System north and west of Hawkins remains operated at 69KV |  |  | Brazos | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2004-11-01 | 2004-11-01 | 138 | 0 |  | 60 |  | COOKE | COOKE |  |  | 2003-09-01 | 2003-12-04 | 1705,722,718,707,698,704,699,684 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
04TPIT0020 | Polk to Halls Acres, reconductor 138 kV line | Reconductor 138 kV MVEC Pharr to Hall Acres line from 336 to 795 ACSS conductor | In-Service | AEP GROUP 064 | AEP/TCC |  | 840 | 2004-11-01 | 2004-11-01 | 138 | 3 |  | 0 |  | HIDALGO | HIDALGO
04TPIT0117 | Jefferson - College ckt.06 | Upgraded in-series equipment at Jefferson to increase emergency ratings. |  |  | CNP |  |  | 2004-12-01 | 2004-11-02 | 138 | 0 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 41240, 42312 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0112 | Oasis Switching Station | Built Oasis 345 kV Substation and looped ckt.99 Dow-WAP and ckt.99 Dow-PHR into the new substation. |  |  | CNP |  |  | 2004-12-01 | 2004-11-09 | 345 | 0.5 |  | 0 |  | BRAZORIA | BRAZORIA |  | 2004-09-03 | 2003-11-21 |  | 43035 | Y |  | No transformer capacity added.
04TPIT0114 | Klein - Willow ckt.81 | Bundled 138 kV Klein - Willow ckt.81 and upgraded limiting equipment at Klein and Willow. |  |  | CNP |  |  | 2004-12-31 | 2004-11-12 | 138 | 2.37 |  | 0 |  | HARRIS | HARRIS |  |  |  |  | 45940, 46660 | Y |  | No transformer capacity added.
04TPIT0159 | North McCamey 138 kV Substation, add two breakers to split breaker and half busses | Add two 138 kV breakers to split the North McCamey breaker and half busses isolating generation from load | In-Service | AEP GROUP 238 | LCRA TSC / AEP |  | 1402, LCRA#1005940 | 2004-11-30 | 2004-11-30 | 138 | 0 |  | 0 | 2 | UPTON | [6 empty] | Y
04TPIT0128 | Mulberry Creek, add 36 MVar shunt reactor | The addition of 36 MVAr shunt reactor on the autotransformer tertiary at Mulberry Creek. | In-Service | AEP GROUP 287 | AEP/TNC |  | 1409 | 2004-12-01 | 2004-12-01 | 345 | 0 |  | 0 | 36 | TAYLOR | [6 empty] | Y
05TPIT0016 | Killeen Switch - Killeen Taft 138 kV line | Add second 138 kV circuit |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R411 | 2004-12-31 | 2004-12-01 | 138 | 5.2 |  | 0 |  | BELL | BELL |  |  |  |  | 3423, 3616, 3619 | Y
04TPIT0138 | Odessa EHV - TI Tap 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R293 | 2004-12-01 | 2004-12-01 | 138 | 8.91 |  | 0 |  | ECTOR | ECTOR |  |  |  |  | 1027, 1137 | Y
04TPIT0135 | Paris - Commerce 69 kV line | Convert 69 kV line to 138 kV operation |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R109B | 2004-11-01 | 2004-12-01 | 138 | 70.7 |  | 0 |  | LAMAR | HUNT |  |  |  |  | 1805, 1821, 1806, 1803, 1778, 1693, 1817, 1816 | Y
04TPIT0122 | Selden (BEC) - Walnut Springs 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R161 | 2004-12-01 | 2004-12-01 | 138 | 25.4 |  | 0 |  | ERATH | BOSQUE |  |  |  |  | 1644, 1645, 1646 | Y
04TPIT0144 | Rincon to Rockport, rebuild 138 kV line | Rebuild Rincon to Rockport 138 kV line from 4/0 to 795 ACSR conductor | In-Service | AEP GROUP 005 | LCRA TSC / AEP |  | 275, LCRA#1003452 | 2004-12-07 | 2004-12-01 | 138 | 15 |  | 0 | 0 | SAN PATRICIO | ARANSAS
04TPIT0146 | South Lane - Wharton ckt.60 | Raised conductors to increase thermal ratings and upgraded limiting equipment. |  |  | CNP |  |  | 2004-12-30 | 2004-12-01 | 138 | 0 |  | 0 |  | WHARTON | WHARTON |  |  |  |  | 43190, 43570 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0125 | Red Creek, add 100 MVar shunt reactor | The addition of 100 MVAR shunt reactor at the 345 KV Red Creek | In-Service | AEP GROUP 287 | AEP/TNC |  | 1411 | 2004-12-31 | 2004-12-31 | 345 | 0 |  | 0 | 100 | TOM GREEN | [6 empty] | Y
No Project Number Will Be Developed | Roma Tap Substation | Replace 3 switches with 3-breaker ring bus |  | AEP Group 000 | AEP/TCC |  | 40306673 | 2004-12-31 | 2004-12-31 | 138 | 0 |  | 0 |  | Starr
04TPIT0154 | Holly STATCOM | Install a 95 MVA Statcom with a dynamic range of -80 MVAR to +110 MVAR at the Pedernales 138 kV bus |  | #1-55948879 #1-55951973 | Austin Energy | James Armke (512) 322-6705 james.armke@austinenergy.com | Budget # 1423 | 2004-12-01 | 2005-01-01 | 138 | 0 | 0 | 220 | 93.6 | TRAVIS | TRAVIS |  |  |  |  | 91189025 | Y | (-80 Mvar,+110 Mvar) An additional three 31.2 Mvar of capacitor banks will be installed. | (-80 Mvar,+110 Mvar) An additional three 31.2 Mvar of capacitor banks will be installed.
05TPIT0018 | Collin - Colony 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M282 | 2004-12-31 | 2005-01-01 | 138 | 0 | 9.47 | 0 | 0 | COLLIN | DENTON |  |  |  |  | 2370, 2517, 2518 | Y
05TPIT0144 | Roma, upgrade 2 transformers & distribution equipment | Convert Bates to Rio Grande City 69 kV line to 138 kV with 795 ACSR conductor (rebuild 4/0 section between La Grulla to Rio Grande City) | In-Service | AEP GROUP 208 | AEP/TCC |  | 1190 | 2005-01-02 | 2005-01-02 | 138 | 0 | 0 | 25 | 0 | STARR
05TPIT0145 | TAMU to South Switch | Construct 138 kv underground/overhead line |  | 1-55951371 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 810 | 2005-02-01 | 2005-01-05 | 138 | 6.2 | 0 | 0 | 0 | BRAZOS | BRAZOS |  |  |  |  | 32799-32893 | Y |  | There were no new transformers added with this project.
04TPIT0132 | McColl to N McAllen, reconductor/upgrade double circuit 138 kV line | Reconductor North Edinburg to North McAllen 138/69 kV double circuit line with 795 ACSS conductor | In-Service | AEP GROUP 064 | AEP/TCC |  | 278 | 2005-01-05 | 2005-01-05 | 138 | 0 | 13.16 | 0 | 0 | HIDALGO | HIDALGO
05TPIT0129 | Norwood system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M434 | 2005-05-01 | 2005-01-05 | 138 | 0 | 0 | 0 | 110.4 | DALLAS | [5 empty] | 2408, 2409 | Y
05TPIT0116 | Hackberry system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5094 | 2005-05-01 | 2005-01-05 | 138 | 0 | 0 | 0 | 110.4 | DALLAS | [5 empty] | 2388 | Y
05TPIT0004 | Mesa View SS to Ft Lancaster, rebuild 138 kV Line | Rebuild 138 kV Mesa View SS to Fort Lancaster line with 2x795 ACSR conductor and double circuit capable structures | In-Service | AEP GROUP 239 | LCRA TSC / AEP |  | 264, LCRA#1003412 | 2005-01-07 | 2005-01-07 | 138 | 0 | 20 | 0 | 0 | PECOS | PECOS | [5 empty] | Y
04TPIT0017 | Bellaire - Brays ckt.09 | Bundled 138kV Bellaire - Brays ckt 09 |  |  | CNP |  |  | 2005-01-12 | 2005-01-12 | 138 | 0 | 3.21 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47015, 47050 | Y |  | No transformer capacity added.
04TPIT0108 | Jeanetta - Dunvale ckt.05 | Raised conductors to increase thermal ratings and upgraded in-series equipment at Jeanetta. |  |  | CNP |  |  | 2005-01-17 | 2005-01-17 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47310, 47071 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0018 | Dunvale - Sharps ckt.05 | Raised conductors to increase thermal ratings. |  |  | CNP |  |  | 2005-01-17 | 2005-01-17 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47071, 47192, 47411 | Y |  | Costs Included in Jeanetta Dunvale ckt.05 Project #04TPIT0108. No transformer capacity added and no transmission circuits built, rebuilt or reconductored..
04TPIT0142 | Obrien 345/138 kV autotransformer | Added third 345/138 kV, 400MVA autotransformer (A3) @Obrien |  |  | CNP |  |  | 2005-01-31 | 2005-01-27 | 345 | 0 | 0.1 | 400 | 0 | FORT BEND | FORT BEND |  |  |  |  | 44500 , 44510 | Y
05TPIT0192b | P.H. Robinson - Heights ckt.1 | Verified tie line from CNP tie point to Heights conductors clearance and upgrade limiting equipment to increase thermal ratings. |  |  | CNP, TNMP |  |  | 2005-01-30 | 2005-01-30 | 138 | 0 | 8.1 | 0 | 0 | GALVESTON | GALVESTON |  |  |  |  | 42015, 38740 | Y |  | Data shown includes only TNMP portion of the line. No transformer capacity added.
04TPIT0094 | Hamilton Wolfe 138 kV Substation | Install new 138 kV substation, loop into existing Medical Ctr. to Bandera 138 kV lines. |  | T-0009, S-0111 | CPS | Ulrich Skerhut 210-353-2923 | S-0059 | 2005-01-18 | 2005-02-01 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5187 | Y |  | This is substation work associated with project 05TPIT0283, transmission miles are not included.
05TPIT0283 | Hamilton Wolfe 138 kV Substation Loop | Install new 138 kV substation loop into existing Medical Ctr. to Bandera 138 kV lines. |  | S-0059 | CPS | Ramon Heard 210-353-4494 | T-0009 | 2005-01-18 | 2005-02-01 | 138 | 1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5187 | Y |  | This is the transmission line portion of this project, transformer capacity is not included
04TPIT0141 | Airline, re-terminate Davis 138 kV line | Reconfigure the Airline to Holly and the Barney Davis to Westside 138 kV transmission lines creating a Airline to Westside 138 kV transmission line and a Barney Davis to Holly 138 kV transmission line. | In-Service | AEP GROUP 041 | AEP/TCC |  | 1580 | 2005-02-01 | 2005-02-01 | 138 | 0 | 0 | 0 | 0 | NUECES | NUECES
04TPIT0139 | Airline, re-terminate Holly 138 kV line | Reconfigure the Airline to Holly and the Barney Davis to Westside 138 kV transmission lines creating Airline to Westside and Barney Davis to Holly 138 kV transmission lines | In-Service | AEP GROUP 041 | AEP/TCC |  | 1588 | 2005-02-01 | 2005-02-01 | 138 | 0 | 0 | 0 | 0 | NUECES | NUECES
04TPIT0120 | Sandow - Minerva - Robertson 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R099B | 2005-02-15 | 2005-02-05 | 138 | 0 | 44.9 | 0 | 0 | MILAM | ROBERTSON |  |  |  |  | 3430, 3678, 3679, 3683, 3682, 32 | Y
05TPIT0005 | Mulberry Creek, add 2-138 kV 10 Ohm series reactors | The addition of 2-138 kV series reactors at Mulberry Creek in the NW Abilene and Elm Creek 138 kV lines | In-Service | AEP GROUP 287 | AEP/TNC |  | 1412 | 2005-02-05 | 2005-02-05 | 138 | 0 | 0 | 275 | 43.2 | TAYLOR | [6 empty] | Y
05TPIT0017 | Watermill - Lancaster 138 kV line | Construct 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M295 | 2005-02-01 | 2005-02-05 | 138 | 3 | 0 | 0 | 0 | DALLAS | DALLAS |  |  | 2001-12-01 | 2002-01-01 | 2429, 3066 | Y
05TPIT0139 | W Levee system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M4035 | 2005-05-01 | 2005-02-05 | 138 | 0 | 0 | 0 | 55.2 | DALLAS | [5 empty] | 2399 | Y
05TPIT0113 | Flewellen - Katy Tap ckt.66 | Replaced limiting equipment at Flewellen to increase thermal ratings |  |  | CNP |  |  | 2005-03-01 | 2005-02-05 | 138 | 0 | 0 | 0 | 0 | FORT BEND | WALLER |  |  |  |  | 44230, 44422 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0196 | West Galveston 138/69kV autotransformer | Upgraded Autotransformer (A2) position to increase thermal ratings |  |  | CNP |  |  | 2005-03-01 | 2005-02-05 | 138 | 0 | 0 | 100 | 0 | GALVESTON | GALVESTON |  |  |  |  | 43400, 43410 | Y |  | No transmission circuits built, rebuilt or reconductored.
04TPIT0090 | Marion-Comal | Reconductor the following ckts with 959 mcm ACSS (392-MVA) conductor: Marion (7178) – Gpi (7159) 138-kV cicuit 1 (4.4 m), Gpi (7158) – Loop 337(7456) 138-kV circuit 1 (5.6 m), Comal (7176) – Loop 337(7456) 138-kV circuit 1 (2.1 m) |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2005-06-30 | 2005-02-10 | 138 | 0 | 12.1 | 0 | 0 | GUADALUPE | COMAL | [5 empty] | Y |  | No XMFR Capacity added; No MVAR added
05TPIT0194 | Flewellen 138/69kV autotransformer | Upgraded Autotransformer (A1) position to increase thermal ratings |  |  | CNP |  |  | 2005-02-28 | 2005-02-18 | 138 | 0 | 0 | 100 | 0 | HARRIS | HARRIS |  |  |  |  | 44230, 44240 | Y |  | No transmission circuits built, rebuilt or reconductored.
05TPIT0035R | Roma, add 138 kV SS | Convert Roma to Rio Grande City 69 kV line to 138 kV line with 795 ACSR conductor | In-Service | AEP GROUP 208 | AEP/TCC |  | 1195 | 2005-02-28 | 2005-02-28 | 138 | 0 | 0 | 0 | 0 | STARR
05TPIT0193 | Deepwater - Magnolia Park ckt.70 | Upgraded limiting equipment to increase thermal ratings. |  |  | CNP |  |  | 2005-02-28 | 2005-02-28 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40460, 40650, 47700 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0197 | White Oak 138/69kV autotransformer | Upgraded Autotransformer (A2) position to increase thermal ratings |  |  | CNP |  |  | 2005-03-30 | 2005-02-28 | 138 | 0 | 0 | 168 | 0 | HARRIS | HARRIS |  |  |  |  | 46615, 46620 | Y |  | No transmission circuits built, rebuilt or reconductored.
04TPIT0104 | Stonegate to Green Mountain 138 kV line | Build new 138 kV line to Stonegate substation |  | S-0494, T-0193 | CPS | LeeRoy Perez 210-353-4976 | T-0493 | 2005-07-01 | 2005-03-01 | 138 | 11 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5415, 5180 | Y |  | There are no transformers associated with this project
07TPIT0003 | Roanoke Switch 345/138 kV autotransformer | Install (2nd) 345/138 kV autotransformer (600 MVA) at Roanoke Switch |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5011 | 2005-05-15 | 2005-03-05 | 345 | 0 | 0 | 600 | 0 | DENTON |  |  |  | 2004-04-01 | 2004-05-01 | 640, 646, 661, 988, 1436, 1845, 1847, 1848, 1849, 1850, 1851, 1852, 1853, 1854, 1855, 1857, 2018, 2033 | Y
05TPIT0070 | Salem 345/138 kV autotransformer upgrade | Upgrade Salem 345/138 kV autotransformer capacity to 672 MVA |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1003810 | 2005-06-30 | 2005-03-05 | 345 | 0 | 0 | 672 | 0 | WASHINGTON | [5 empty] | 7058 | Y | No MVAR added
04TPIT0160 | Roanoke - Keller 138 kV line | Rebuild 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M545 | 2005-03-01 | 2005-03-05 | 138 | 0 | 7.42 | 0 | 0 | DENTON | TARRANT |  |  | 2004-04-01 | 2004-05-01 | 565, 1852, 1854, 1857 | Y
05TPIT0141 | Waco W system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R451 | 2005-05-01 | 2005-03-05 | 138 | 0 | 0 | 0 | 55.2 | MCLENNAN | [5 empty] | 3436 | Y
07TPIT0074 | Waxahachie 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M3006 | 2007-05-01 | 2005-03-05 | 138 | 0 | 0 | 0 | 36.8 | ELLIS | [5 empty] | 2321 | Y
05TPIT0127 | North Lake system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M4033 | 2005-05-01 | 2005-03-05 | 138 | 0 | 0 | 0 | 110.4 | DALLAS | [5 empty] | 2386, 2385 | Y
05TPIT0135 | Roanoke Switch system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5093 | 2005-05-01 | 2005-03-05 | 138 | 0 | 0 | 0 | 55.2 | DENTON | [5 empty] | 1854 | Y
05TPIT0282 | West Denton Sub - Upgrade Smit Auto Rating | Added additional cooling equipment to increase the rating from 400 to 600 MVA | On schedule |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T04008 | 2005-03-13 | 2005-03-13 | 345 | 0 | 0 | 600 | 0 |  | DENTON |  |  |  |  | 988, 986 | Y
06TPIT0006 | Watermill - Tricorner 345 kV line | Upgrade Watermill - Tricorner 345 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M464 | 2005-03-01 | 2005-03-16 | 345 | 0 | 11.44 | 0 | 0 | DALLAS | DALLAS |  |  | 2004-04-01 | 2004-05-01 | 2428, 2432 | Y
05TPIT0195 | Gable Street 138/69 kV autotransformer | Upgraded Autotransformer (A1) position to increase thermal ratings |  |  | CNP |  |  | 2005-03-01 | 2005-03-28 | 138 | 0 | 0 | 200 | 0 | HARRIS | HARRIS |  |  |  |  | 47630, 47640 | Y |  | No transmission circuits built, rebuilt or reconductored.
05TPIT0110 | Eastside | Increased reactive capability to 100 MVAR |  |  | CNP |  |  | 2005-03-30 | 2005-03-30 | 138 | 0 | 0 | 0 | 40 | HARRIS | HARRIS |  |  |  |  | 47610 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0165 | Ft. Lancaster, expand 138 kV to three position ring bus | Add of a Fort Lancaster to Friend Ranch 2x795 ACSR 138 kV line and double circuit capable structures | In-Service | AEP GROUP 240 | LCRA TSC / AEP |  | 217, LCRA#1005238 | 2005-06-01 | 2005-04-01 | 138 | 0 | 0 | 0 | 0 | PECOS | PECOS
05TPIT0243 | Construct Trinity Bay 138KV Substation | Looped substation into ckt.03 Cedar - Baytown |  |  | CNP |  |  | 2005-04-01 | 2005-04-01 | 138 | 0.12 | 0 | 0 | 0 | CHAMBERS | CHAMBERS |  |  |  |  | 41610 | Y |  | No transformer capacity added.
05TPIT0164 | Santa Rosa Distribution, upgrade 2 transformers & distribution equipment | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | In-Service | AEP GROUP 068 | AEP/TCC |  | 1283 | 2005-04-01 | 2005-04-01 | 138 | 0 | 0 | 25 | 0 | HIDALGO | HIDALGO
05TPIT0281 | Toyota 138 kV Substation loop | Install new 138 kV substation loop into existing Braunig to Howard line. |  | S-0092 | CPS | Adam Marin 210-353-2476 | T-0046 | 2005-04-01 | 2005-04-01 | 138 | 1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5428 | Y |  | This is the transmission line portion of this project, transformer capacity is not included
06TPIT0115 | North Pharr, add 138 kV SS with temporary 138/69 kV auto | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | In-Service | AEP GROUP 068 | AEP/TCC |  | 279 | 2005-04-01 | 2005-04-01 | 138 | 0 | 0 | 0 | 0 | HIDALGO
05TPIT0199 | Greens Bayou 138/69 kV autotransformer | Upgraded Autotransformer (A5) position to increase thermal ratings |  |  | CNP |  |  | 2005-04-01 | 2005-04-01 | 138 | 0 | 0 | 200 | 0 | HARRIS | HARRIS |  |  |  |  | 40716, 40720 | Y |  | No transmission circuits built, rebuilt or reconductored.
04TPIT0041 | Veterans - Gears ckt.67 | Verified conductors clearance to increase thermal ratings. |  |  | CNP |  |  | 2005-04-01 | 2005-04-01 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46551, 45781 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored..
05TPIT0279 | Relocate Tidal Generating Unit #2 | Relocated Gas Turbine Generating Unit #2 from Tidal to DIABOX. |  |  | CNP |  |  | 2005-04-01 | 2005-04-01 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 41580, 48902, 40480, 48614 | Y |  | Due to the robustness of the system in the relocation area no transmission improvements were required.
05TPIT0147 | Eagle Mountain 345 kV breakers | Install two 345 kV breakers |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5099 | 2005-05-01 | 2005-04-05 | 345 | 0 | 0 | 0 | 0 | TARRANT | [5 empty] | 1436, 1855, 1859, 1860 | Y
05TPIT0177 | Comfort-Cico | Upgrade all terminal equipment on the Comfort(7155)-Cico(7151) 138kV transmission line to upgrade rating of line to 220MVA. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1005370 | 2005-06-05 | 2005-04-06 | 138 | 0 | 17 | 0 | 0 | KENDALL | KENDALL | [5 empty] | Y |  | No XMFR Capacity added; No MVAR added; No New Conductor
05TPIT0277 | Disconnect Cooper 69kV Substation from the system | Disconnected substation and deenergized ckt.19 H.O. Clarke - Cooper |  |  | CNP |  |  | 2005-04-11 | 2005-04-11 | 69 | 0 | 1.29 | 0 | 0 | HARRIS | FORT BEND |  |  |  |  | 47160, 47060 | Y |  | No transformer capacity added and 1.29 miles of transmission circuit from H.O. Clarke to Cooper was removed.
05TPIT0211 | Baytown - EXXON ckt.66 | Raised conductors to increase thermal ratings |  |  | CNP |  |  | 2005-06-30 | 2005-04-13 | 138 | 0 | 1.91 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40170, 40570 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0284 | McColl Road to North McAllen, reconductor/upgrade double circuit 138 kV Line | Reconductor North Edinburg to North McAllen 138/69 kV double circuit line with 795 ACSS conductor | In-service | AEP GROUP 064 | AEP/TCC |  | 278 | 2005-06-15 | 2005-04-15 | 138 | 0 | 22.31 | 0 | 0 | HIDALGO | HIDALGO
04TPIT0043 | South Mission to Bentsen | Convert Bates to South Mission to South McAllen 69 kV line to 138 kV with 1590 ACSS conductor reconnected to Frontera, and conversion South McAllen and South Mission to 138 kV. Upgrade 69 kV line to 138 kV |  | 1145 | SU | Mark Caskey, (956) 687-5600 mcaskey@su-power.com | 275 | 2005-03-31 | 2005-04-15 | 138 | 3 | 3.6 | 0 | 0 | HIDALGO | [8 empty] | Bates to South McAllen 69 kV line lacks the capacity to add the Sharyland Bentsen Substation
04TPIT0044 | Bentsen to South McAllen | Convert Bates to South Mission to South McAllen 69 kV line to 138 kV with 1590 ACSS conductor reconnected to Frontera, and conversion South McAllen and South Mission to 138 kV. Upgrade 69 kV line to 138 kV |  | 1223 | SU | Mark Caskey, (956) 687-5600 mcaskey@su-power.com | 275 | 2005-03-31 | 2005-04-15 | 138 | 0 | 0 | 0 | 0 | HIDALGO | [8 empty] | Bates to South McAllen 69 kV line lacks the capacity to add the Sharyland Bentsen Substation
04TPIT0005 | MVEC Pharr to North Pharr, reconductor 138 kV line | Reconductor 138 kV MVEC Pharr to Hall Acres line from 336 to 795 ACSS conductor | In-Service | AEP GROUP 064 | AEP/TCC |  | 287 | 2005-04-18 | 2005-04-18 | 138 | 0 | 3.49 | 0 | 0 | HIDALGO | HIDALGO
04TPIT0111 | T.H. Wharton - Gears ckt.95 | Verified conductors clearance to increase thermal ratings and upgrade in-series equipment at T.H. Wharton. |  |  | CNP |  |  | 2005-04-19 | 2005-04-19 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 45510, 45512, 45782 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0161 | Monticello 345 kV breaker | Install one 345 kV bus tie breaker |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R116 | 2005-05-01 | 2005-04-29 | 345 | 0 | 0 | 0 | 0 | TITUS | [5 empty] | 1695 | Y
05TPIT0201 | Copperas Cove and Clear Creek 138 kV capacitors | Install two 138 kV capacitor banks |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R036C | 2005-05-01 | 2005-04-29 | 138 | 0 | 0 | 0 | 36.8 | CORYELL | BELL |  |  |  |  | 3628, 3630 | Y
06TPIT0048 | Paris Switch - Brookston 138 kV line | Upgrade 138 kV line |  | R109A | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R109C | 2005-05-15 | 2005-04-30 | 138 | 0 | 7 | 0 | 0 | LAMAR | LAMAR |  |  |  |  | 1693, 1776, 1775, 1833 | Y
05TPIT0003 | Toyota 138 kV Substation | Install new 138 kV substation, loop into existing Braunig to Howard line. |  | T-0046 | CPS | Adam Marin 210-353-2476 | S-0092 | 2005-04-01 | 2005-05-01 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5428 | Y |  | This is substation work associated with project 05TPIT0281, transmission miles are not included.
04TPIT0158 | Santa Anna to Bangs, build 138 kV line | Convert Santa Anna to Brownwood 69 kV line to 138 kV with 795 MCM ACSR conductor |  | AEP GROUP 209 | LCRA TSC / AEP |  | 592, LCRA#1003451 | 2005-05-01 | 2005-05-01 | 138 | 0 | 8.3 | 0 | 0 | COLEMAN | BROWN
05TPIT0120 | LCP - Pleasanton 138kV Reroute | Reroute part of the existing LCP-Pleasanton 138kV line |  | S-0092 | CPS | Adam Marin 210-353-2476 | T-0047 | 2005-05-01 | 2005-05-01 | 138 | 2.5 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5260, 8203 | Y |  | There are no transformers associated with this project
05TPIT0138 | South Abilene, add 2-28.8 MVAR cap | Add 6-28.8 MVAR 138 kV capacitor banks in Abilene area | In-service | AEP GROUP 287 | AEP/TNC |  | 1410 | 2005-05-28 | 2005-05-01 | 138 | 0 | 0 | 0 | 57.6 | TAYLOR | [5 empty] | 6260 | Y
05TPIT0198 | North McCamey, add 2x28.8 MVAR caps | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-service | AEP GROUP 250 | AEP/TNC |  | 1755 | 2005-05-15 | 2005-05-01 | 138 | 0 | 0 | 0 | 57.6 | UPTON | [5 empty] | 6595 | Y
05TPIT0020 | East Munday, add 28.8 MVAR cap | Add 6-28.8 MVAR 138 kV capacitor banks in Abilene area | In-service | AEP GROUP 287 | AEP/TNC |  | 1634 | 2005-05-30 | 2005-05-01 | 138 | 0 | 0 | 0 | 28.8 | CALLAHAN | [6 empty] | Y
05TPIT0246 | Disconnected Choate 138KV Substation from CenterPoint Energy's system. | Disconnected customer owned Choate substation from CNP's ckt.79 Bayou - Orion and reconnected it to Bayou. |  |  | CNP |  |  | 2005-05-01 | 2005-05-01 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 41205, 40310, 42160 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0203 | South Cross, add 3.6 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-service | AEP GROUP 250 | AEP/TNC |  | 1759 | 2005-05-01 | 2005-05-01 | 69 | 0 | 0 | 0 | 3.6 | CROCKET | [5 empty] | 6594, 6587 | Y
05TPIT0015 | Anna 345/138 kV autotransformer | Install a (2nd) 345/138 kV autotransformer (600 MVA) at Anna |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M286 | 2005-05-01 | 2005-05-03 | 345 | 0 | 0 | 600 | 0 | COLLIN | [5 empty] | 2373, 2374 | Y
05TPIT0160 | Martin Lake 345 kV breakers | Install two 345 kV bus tie breakers |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R366 | 2005-05-01 | 2005-05-05 | 345 | 0 | 0 | 0 | 0 | RUSK | [5 empty] | 3100 | Y
04TPIT0091b | P.H. Robinson - ISP -Greensbelt ckt.1 | Reconductored 2-636 ACSR tie line running from CNP tie point to ISP to Greenbelt to 2-636 ACSS conductor |  |  | CNP, TNMP |  |  | 2005-01-01 | 2005-05-05 | 138 | 0 | 8.1 | 0 | 0 | GALVESTON | GALVESTON |  |  |  |  | 42015, 38500, 38575 | Y |  | Data shown includes only TNMP portion of the line. No transformer capacity added.
04TPIT0107 | Bates to Frontera, reconductor 138 kV line | Reconductor Bates to Frontera 138 kV line from 1272 ACSR to 1272 ACSS | In-service | AEP GROUP 064 | AEP/TCC |  | 1293 | 2005-05-06 | 2005-05-05 | 138 | 0 | 0.19 | 0 | 0 | HIDALGO | HIDALGO
04TPIT0140 | Rockport to Fulton #2, rebuild 69 kV Line | Rebuild Rockport to Fulton #2 69 kV line from 4/0 to 795 ACSR |  | AEP GROUP 031 | LCRA TSC / AEP |  | 5, LCRA#1003450 | 2005-04-01 | 2005-05-05 | 69 | 0 | 7 | 0 | 0 | ARANSAS | ARANSAS
05TPIT0106 | Cedar Hill Switch system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M4032 | 2005-07-05 | 2005-05-06 | 138 | 0 | 0 | 0 | 55.2 | DALLAS | [5 empty] | 2421 | Y
04TPIT0091a | P.H. Robinson - ISP ckt.1 | Reconductored tie line from P.H. Robinson to TNMP tie point and upgraded limiting equipment at P.H. Robinson to increase thermal ratings. |  |  | CNP, TNMP |  |  | 2005-05-30 | 2005-05-10 | 138 | 0 | 0.39 | 0 | 0 | GALVESTON | GALVESTON |  |  |  |  | 42015, 38500 | Y |  | Data shown includes only CNP portion of the line. No transformer capacity added.
05TPIT0192a | P.H. Robinson - Heights ckt.1 | Verified tie line from P.H. Robinson to TNMP tie point conductors clearance and upgraded limiting equipment at P.H. Robinson to increase thermal ratings. |  |  | CNP, TNMP |  |  | 2005-05-30 | 2005-05-10 | 138 | 0 | 0 | 0 | 0 | GALVESTON | GALVESTON |  |  |  |  | 42015, 38740 | Y |  | Data shown includes only CNP portion of the line. No transformer capacity added.
06TPIT0004 | Frontera to Goodwin, upgrade 69 kV to 138 kV line | Convert Bates to Rio Grande City 69 kV line to 138 kV with 795 ACSR conductor (rebuild 4/0 section between La Grulla to Rio Grande City) | In-Service, operating temporarily at 69 kV - convert to 138 kV in Spring 2006 | AEP GROUP 208 | LCRA TSC / AEP |  | 591, LCRA#1004249 | 2006-04-28 | 2005-05-12 | 138 | 0 | 4 | 0 | 0 | HIDALGO | STARR
05TPIT0162 | Morrison 138 kV breakers | Install two 138 kV bus tie breakers |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M4036 | 2005-05-01 | 2005-05-12 | 138 | 0 | 0 | 0 | 0 | DALLAS | [5 empty] | 2780, 2781, 2782, 2783, 2794, 2795 | Y
05TPIT0030 | Collin - Renner 138 kV line | Rebuild Collin - Renner 138 kV line for DCKT operation |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M376 | 2005-06-01 | 2005-05-13 | 138 | 13.9 | 13.9 | 0 | 0 | COLLIN | COLLIN |  |  |  |  | 2370, 655, 2368, 2369, 2516, 2523, 2521, 2524, 2523, 2510, 2509, 2525, 2515, 2352, 2353, 2365, 2526 | Y
05TPIT0276 | Tomball | Increased reactive capability to 93.3MVAR |  |  | CNP |  |  | 2005-05-13 | 2005-05-13 | 138 | 0 | 0 | 0 | 33.3 | HARRIS | HARRIS |  |  |  |  | 46520 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0131 | Rockwall - E Richardson 138 kV line | Rebuild Rockwall - E Richardson 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M379 | 2005-05-05 | 2005-05-15 | 138 | 0 | 25.5 | 0 | 0 | ROCKWALL | DALLAS |  |  |  |  | 2702, 2701, 2700, 2699, 2609, 2698, 2690 | Y
05TPIT0158 | Handley 138/69 kV autotransformer | Install a 150 MVA 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5096 | 2005-05-01 | 2005-05-15 | 138 | 0 | 0 | 150 | 0 | TARRANT | [5 empty] | 1951, 1952 | Y
05TPIT0062 | Filter Plant 138-kV Substation | Convert Filter Plant Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-06 | 2005-05-15 | 138 | 0 | 0 | 56 | 9.6 | CAMERON | [5 empty] | 59420 | Y
05TPIT0059 | FM 802 138-kV Substation | Convert Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-03 | 2005-05-15 | 138 | 0 | 0 | 56 | 9.6 | CAMERON | [5 empty] | 59400 | Y
05TPIT0060 | Midtown 138-kV Substation | Convert Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-03 | 2005-05-15 | 138 | 0 | 0 | 56 | 9.6 | CAMERON | [5 empty] | 59490 | Y
04TPIT0118 | White Point, add 2 series 10 Ohm reactors on Nueces Bay 138 kV lines | Install series reactors on both Nueces Bay to Whitepoint 138 kV circuits | In-service | AEP GROUP 041 | AEP/TCC |  | 1492 | 2005-05-15 | 2005-05-15 | 138 | 0 | 0 | 275 | 43.2 | NUECES
05TPIT0063 | Airport 138-kV Substation | Relocate one 138/69-kV 60 MVA autotransformer from Loma Alta |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-07 | 2005-05-15 | 138 | 0 | 0 | 60 | 0 | CAMERON | [5 empty] | 59460 | Y
05TPIT0061 | Military Hwy 138-kV Substation | Facilitate the substation for a new 138-kV Circuit to Midtown substation |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-05 | 2005-05-15 | 138 | 0 | 0 | 0 | 0 | CAMERON | [5 empty] | 8339 | Y
00TPITno09 | Loma Alta 138-kV Substation | Facilitate the substation for a new 138-kV Circuit |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-03 | 2005-05-15 | 138 | 0 | 0 | 0 | 0 | CAMERON | [5 empty] | 5962 | Y
04TPIT0157 | South Mission, upgrade two 68 kV distributioin banks | Convert Bates to South Mission to South McAllen 69 kV line to 138 kV with 1590 ACSS reconnected to Frontera, and convert South McAllen and South Mission to 138 kV | In-service | AEP GROUP 265 | AEP/TCC |  | 1258 | 2005-05-01 | 2005-05-16 | 138 | 0 | 0 | 57.6 | 0 | HIDALGO
05TPIT0121 | Liggett system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5092 | 2005-05-01 | 2005-05-17 | 138 | 0 | 0 | 0 | 110.4 | DALLAS | [5 empty] | 1922, 1924 | Y
05TPIT0245 | Deepwater - South Channel ckt.16 | Raised conductors and upgraded limiting equipment at Deepwater to increase thermal ratings. |  |  | CNP |  |  | 2005-12-30 | 2005-05-17 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40470, 41061, 40051, 41380 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0275 | Deepwater - Simson ckt.23 | Raised conductors to increase thermal ratings. |  |  | CNP |  |  | 2005-12-30 | 2005-05-17 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40470, 41460 | Y |  | Cost included in Deepwater - South Channel ckt.16, Project #05TPIT0245. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0022 | Watermill - Cedar Hill (2nd) 345 kV circuit | Install Watermill - Cedar Hill (2nd) 345 kV circuit |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M294 | 2005-05-15 | 2005-05-20 | 345 | 17.3 | 0 | 0 | 0 | DALLAS | DALLAS |  |  | 2001-12-20 | 2002-01-01 | 2420, 2427, 2428 | Y
05TPIT0269 | Obrien | Increased reactive capability to 120MVAR |  |  | CNP |  |  | 2005-05-13 | 2005-05-20 | 138 | 0 | 0 | 0 | 20 | FORT BEND | FORT BEND |  |  |  |  | 44510 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0270 | T.H.Wharton East | Increased reactive capability to 120MVAR |  |  | CNP |  |  | 2005-05-13 | 2005-05-20 | 138 | 0 | 0 | 0 | 20 | HARRIS | HARRIS |  |  |  |  | 45510 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0271 | T.H.Wharton West | Increased reactive capability to 120MVAR |  |  | CNP |  |  | 2005-05-13 | 2005-05-20 | 138 | 0 | 0 | 0 | 20 | HARRIS | HARRIS |  |  |  |  | 45515 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0272 | North Belt | Increased reactive capability to 120MVAR |  |  | CNP |  |  | 2005-05-13 | 2005-05-20 | 138 | 0 | 0 | 0 | 20 | HARRIS | HARRIS |  |  |  |  | 46112 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0273 | Jeanetta | Increased reactive capability to 127.2MVAR |  |  | CNP |  |  | 2005-05-13 | 2005-05-20 | 138 | 0 | 0 | 0 | 20 | HARRIS | HARRIS |  |  |  |  | 47310 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0274 | Humble | Increased reactive capability to 14.4MVAR |  |  | CNP |  |  | 2005-05-13 | 2005-05-20 | 138 | 0 | 0 | 0 | 3.6 | HARRIS | HARRIS |  |  |  |  | 40830 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0263 | Crosby - Barhill ckt.86 | Verified conductors clearance to increase thermal ratings |  |  | CNP |  |  | 2005-05-30 | 2005-05-24 | 138 | 0 | 0 | 0 | 0 | HARRIS | CHAMBERS |  |  |  |  | 40390, 40150 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0264 | Barhill - Hacher ckt.86 | Verified conductors clearance to increase thermal ratings |  |  | CNP |  |  | 2005-05-30 | 2005-05-24 | 138 | 0 | 0 | 0 | 0 | CHAMBERS | CHAMBERS |  |  |  |  | 40150, 40770 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0265 | Hacher - Enprod ckt.86 | Verified conductors clearance to increase thermal ratings |  |  | CNP |  |  | 2005-05-30 | 2005-05-24 | 138 | 0 | 0 | 0 | 0 | CHAMBERS | CHAMBERS |  |  |  |  | 40770, 40510 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0266 | Enprod - Mont Belvieu ckt.86 | Verified conductors clearance to increase thermal ratings |  |  | CNP |  |  | 2005-05-30 | 2005-05-24 | 138 | 0 | 0 | 0 | 0 | CHAMBERS | CHAMBERS |  |  |  |  | 40510, 40340, 40220, 41111 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0267 | Bayou - Orion ckt.79 | Verified conductors clearance to increase thermal ratings |  |  | CNP |  |  | 2005-05-30 | 2005-05-24 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 42160, 41205 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0268 | Fondren - H.O. Clarke ckt.25 | Verified conductors clearance to increase thermal ratings |  |  | CNP |  |  | 2005-05-30 | 2005-05-24 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47100, 47412, 47150 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0262 | Brittmoore | Increased reactive capability to 127.2MVAR |  |  | CNP |  |  | 2005-05-13 | 2005-05-25 | 138 | 0 | 0 | 0 | 20 | HARRIS | HARRIS |  |  |  |  | 44120 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0116 | Santa Anna, add 138 kV SS | Convert Santa Anna to Brownwood 69 kV line to 138 kV with 795 MCM ACSR conductor | In-service | AEP GROUP 209 | AEP/TNC |  | 1175 | 2005-05-01 | 2005-05-27 | 138 | 0 | 0 | 0 | 0 | COLEMAN | [6 empty] | Y
04TPIT0115 | Santa Anna to Bangs, rebuild 69 kV circuit | Convert Santa Anna to Brownwood 69 kV line to 138 kV with 795 MCM ACSR conductor | In-service | AEP GROUP 209 | AEP/TNC |  | 1575 | 2005-05-15 | 2005-05-27 | 69 | 0 | 8 | 0 | 0 | COLEMAN | COLEMAN | [5 empty] | Y
05TPIT0012 | Benbrook - Mistletoe 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5033 | 2005-05-01 | 2005-05-28 | 138 | 0 | 9.8 | 0 | 0 | TARRANT | TARRANT |  |  |  |  | 1875, 2174, 2173 | Y
05TPIT0008 | Fair Oaks Ranch 138 kV Substation | Install new 138kV substation, loop into existing Boerne (LCRA) to Fair Oaks (LCRA) line. |  | T-0003 | CPS | Hector Torres 210-353-2404 | S-0096 | 2005-06-01 | 2005-06-01 | 138 | 0 | 0 | 0 | 100 | KENDALL | KENDALL |  |  |  |  | 5470 | Y |  | This is substation work associated with project 05TPIT0260, transmission miles are not included.
05TPIT0260 | Fair Oaks Ranch 138 kV Substation loop | Install new 138kV substation loop into existing Boerne (LCRA) to Fair Oaks (LCRA) line. |  | S-0096 | CPS | Ramon Heard 210-353-4494 | T-0003 | 2005-06-01 | 2005-06-01 | 138 | 4.59 | 0 | 0 | 0 | KENDALL | KENDALL |  |  |  |  | 5470 | Y |  | This is the transmission line portion of this project, transformer capacity is not included
05TPIT0001 | Braunig to Kennedy 138 kV Reconductor (Braunig - Elmendorf Section) | Rebuild 138 kV line from Braunig to Elmendorf to Eagle Creek to Floresville to Stockdale to Kennedy. | Rebuild of entire line divided up to several projects, each rebuilding from one station to the next. |  | CPS | Gerald Ripps 210-353-2470 | T-0760 | Jul-05 | 2005-06-01 | 138 | 0 | 5.8 | 0 | 0 | BEXAR | WILSON |  |  |  |  | 5025,5135,5155,5412,5145,8186 | Y |  | There are no transformers associated with this project
05TPIT0071 | Kendall-Miller Creek | Increase the line-to-ground clearance on the 40.4-mile Kendall(7152)-Miller Creek(7479) 138-kV transmission line as necessary to upgrade the circuit from its existing design rating of 82-MVA to its full conductor rating of 128-MVA. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1002925 | 2005-06-30 | 2005-06-01 | 138 | 0 | 40.4 | 0 | 0 | KENDALL | BLANCO | [5 empty] | Y |  | No MVAR added
05TPIT0045 | Loma Alta - Price Rd 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-01 | 2005-06-01 | 138 | 0 | 8.31 | 0 | 0 | CAMERON | [5 empty] | 5962, 59410 | Y
05TPIT0212 | Cedar Bayou - Baytown ckt.88 | Raised conductors and partially reconductored ckt.88 Cedar Bayou - Baytown, and upgraded limiting equipment @Cedar Bayou to increase thermal ratings. |  |  | CNP |  |  | 2005-05-30 | 2005-06-01 | 138 | 0 | 4.27 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40015, 40236,40235, 40170 | Y |  | No transformer capacity added.
05TPIT0052 | Midtown - Military Hwy 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-01 | 2005-06-01 | 138 | 0 | 3.17 | 0 | 0 | CAMERON | [5 empty] | 59490, 8339 | Y
05TPIT0293 | Friend Ranch Substation terminal addition | Add terminal at Friend Ranch for new LCRA Ft. Lancaster to Friend Ranch 138kV line |  | AEP Group 000 | LCRA TSC / AEP |  | 24908014 40288951 40288918 40288943 40288953 | 2005-06-01 | 2005-06-01 | 138 | 0 | 0 | 0 | 0 | Crockett County
05TPIT0055 | Filter Plant - Airport 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-01 | 2005-06-01 | 138 | 0 | 2.82 | 0 | 0 | CAMERON | [5 empty] | 59420, 59460 | Y
04TPIT0133 | Frontera to N McAllen, tap Palmhurst sub at 138 kV | Convert Moore Field and Palmhurst substations from 69 kV to 138 kV and connect to North Edinburg to Bates 138 kV line | In-Service | AEP GROUP 292 | AEP/TCC |  | 1291 | 2005-06-01 | 2005-06-01 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO
05TPIT0054 | Price Rd - FM 802 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-01 | 2005-06-01 | 138 | 0 | 2.08 | 0 | 0 | CAMERON | [5 empty] | 59410, 59400 | Y
05TPIT0053 | FM 802 - Midtown 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-01 | 2005-06-01 | 138 | 0 | 1.83 | 0 | 0 | CAMERON | [5 empty] | 59400, 59490 | Y
05TPIT0056 | Price Rd - Filter Plant 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-01 | 2005-06-01 | 138 | 0 | 1.48 | 0 | 0 | CAMERON | [5 empty] | 59410, 59420 | Y
05TPIT0261 | Ft. Lancaster to Friend Ranch, build 138 kV line | Addition of a Fort Lancaster to Friend Ranch 2x795 ACSR 138 kV line and double circuit capable structures |  | AEP Group 240 | LCRA TSC / AEP |  | 58 | 2005-06-01 | 2005-06-01 | 138 | 0 | 0 | 0 | 0
05TPIT0247 | Deepwater - South Houston ckt.13 | Upgraded limiting equipment at South Houston to increase thermal ratings. |  |  | CNP |  |  | 2005-06-01 | 2005-06-01 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40470, 43171, 43170 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0159 | Lake Creek second 345/138 kV autotransformer | Install a 600 MVA 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R453 | 2005-05-01 | 2005-06-02 | 345 | 0 | 0 | 600 | 0 | MCLENNAN | [5 empty] | 3409, 3410 | Y
05TPIT0058 | Price Rd 138-kV Substation | Convert Price Rd Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2005-06-02 | 2005-06-02 | 138 | 0 | 0 | 56 | 0 | CAMERON | [5 empty] | 59410 | Y
06TPIT0108 | Greens Bayou | Installed new 138kV 120 MVAR capacitor bank on 138kV ckt.70 to Lydell. |  |  | CNP |  |  | 2005-05-01 | 2005-06-02 | 138 | 0 | 0 | 0 | 120 | HARRIS | HARRIS |  |  |  |  | 40717 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0292 | Santa Anna-Bangs 138 kV line | Rebuild existing 69kV single wood pole line with double circuit 138/69 kV single steel pole construction, 2- 795 ACSR conductor |  | AEP Group 000 | LCRA TSC / AEP |  | 40424168 & 40474050 | 2005-06-07 | 2005-06-07 | 138 | 0 | 7.21 | 0 | 0 | Coleman County
05TPIT0014 | Iron Bridge 138/69 kV autotransformer | Install 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R357 | 2005-05-01 | 2005-06-10 | 138 | 0 | 0 | 25 | 0 | HUNT | [5 empty] | 3169, 3185 | Y
05TPIT0132 | Plano Tennyson system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M381 | 2005-05-01 | 2005-06-10 | 138 | 0 | 0 | 0 | 110.4 | COLLIN | [5 empty] | 2523 | Y
05TPIT0104 | Carrollton East system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M3013 | 2005-05-01 | 2005-06-10 | 138 | 0 | 0 | 0 | 110.4 | DALLAS | [5 empty] | 2578 | Y
05TPIT0146 | Construct Goodyear 138KV Substation | Looped into Deepwater - Magnolia Park ckt.70 |  |  | CNP |  |  | 2005-05-01 | 2005-06-15 | 138 | 0.28 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40650 | Y |  | No transformer capacity added.
05TPIT0010 | Liggett - Euless 138 kV line | Upgrade underground sections of 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5038 | 2005-05-01 | 2005-06-16 | 138 | 0 | 2.69 | 0 | 0 | DALLAS | TARRANT |  |  |  |  | 1922, 2006, 2009, 2016 | Y
05TPIT0114 | Garceno to Roma, upgrade 69 kV to 138 kV line | Convert Roma to Rio Grande City 69 kV line to 138 kV line with 795 ACSR conductor | In-Service | AEP GROUP 208 | LCRA TSC / AEP |  | 1286, LCRA#1003622 | 2005-09-05 | 2005-06-16 | 138 | 0 | 5.3 | 0 | 0 | STARR | STARR
05TPIT0214 | Flewellen - Obrien ckt.73 | Bundled 138kV Flewellen - Obrien ckt.73 and upgraded limiting equipment @Obrien and Flewellen substations to increase thermal ratings. |  |  | CNP |  |  | 2005-05-30 | 2005-06-17 | 138 | 0 | 6.65 | 0 | 0 | FORT BEND | FORT BEND |  |  |  |  | 44230, 44510 | Y |  | No transformer capacity added.
05TPIT0210 | Cedar Bayou 345/138 kV autotransformer | Added fourth 345/138 kV, 800MVA autotransformer (A1) @Cedar Bayou and reconnected third auto (A3) to the west bus, parallel to 2A & 2B |  |  | CNP |  |  | 2005-06-30 | 2005-06-20 | 345 | 0 | 4.27 | 800 | 0 | HARRIS | HARRIS |  |  |  |  | 40000 , 40010 | Y
06TPIT0105 | Crosby | Installed new 138kV 100 MVAR capacitor bank on 138kV ckt.66 to Atascocita. |  |  | CNP |  |  | 2005-06-15 | 2005-06-21 | 138 | 0 | 0 | 0 | 100 | HARRIS | HARRIS |  |  |  |  | 40391 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0102 | Allen Switch system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M389 | 2005-05-15 | 2005-06-29 | 138 | 0 | 0 | 0 | 110.4 | COLLIN | [5 empty] | 2509, 2510 | Y |  | No MVAR added
05TPIT0217 | Northwest Reliability Project, Phase 1 | Converted Kluge to a breaker substation. Looped Kluge into ckt.81 Klein - Pinehurst and ckt.21 Cameron - Addicks. Upgraded limiting equipment at Cameron and Kluge. Installed new 80 MVAR capacitor bank @ Kluge and 14.4 MVAR capacitor banks @Gertie and Cyfa |  |  | CNP |  |  | 2005-06-30 | 2005-06-30 | 138 | 0 | 15.4 | 0 | 108.8 | HARRIS | HARRIS |  |  |  |  | 45952, 45953, 45801,45711 | Y |  | No transformer capacity added.
05TPIT0064 | HiCross-Marshall Ford | Upgrade the 16.5-mile HiCross(7202)-Marshall Ford(7356) 336 ACSR (128-MVA) 138-kV transmission line to Bundled 795 ACSR (440-MVA) and 1433 ACSS (439-MVA). |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1002513 | 2005-06-30 | 2005-07-01 | 138 | 0 | 16.5 | 0 | 0 | TRAVIS | [5 empty] | SEE PROJECT DESCRIPTION | Y
05TPIT0032 | Reno to Cottondale Switch | Rebuild existing Reno to Cottondale Sw. 69kv line with 138kv const. |  |  | Brazos | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2005-06-01 | 2005-07-01 | 138 | 0 | 19.25 | 0 | 0 | WISE | PARKER |  |  | 2003-05-01 | 2003-08-01 | 541,595,596,561 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
05TPIT0034 | Jack County Plant to Cottondale Sw | Construct 3 138kv circuits from Jack County plant to vicinity of Cottondale Sw. |  |  | Brazos | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2005-07-01 | 2005-07-01 | 138 | 5 | 0 | 0 | 0 | JACK | WISE |  |  | 2003-05-01 | 2003-08-01 | 579,561 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
05TPIT0024 | Southwest Research (SWRI) loop 138 kV line | Build new 138 kV line to SWRI substation |  | S-0090 | CPS | Ramon Heard 210-353-4494 | T-0024 | 2005-07-01 | 2005-07-01 | 138 | 1.6 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5419, 5490 | Y |  | There are no transformers associated with this project
05TPIT0244 | Burleson Auto Relocation and Circuit 831 conversion | Relocate the existing 220MVA Burleson autotransformer to replace the failed Seaholm autotransformer and convert the 69kV Circuit 831 back to 138kV Circuit 1015. |  | #1-55952621 #1-55952619 | Austin Energy | James Armke (512) 322-6705 james.armke@austinenergy.com | N/A | 2005-05-01 | 2005-07-01 | 138 | 0 | 2.56 | 200 | 0 | TRAVIS | TRAVIS |  |  |  |  | 9118, 91232 | N
05TPIT0259 | White Oak North | Increased reactive capability to 120MVAR |  |  | CNP |  |  | 2005-07-01 | 2005-07-01 | 138 | 0 | 0 | 0 | 20 | HARRIS | HARRIS |  |  |  |  | 46610 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0191 | Central Austin : Build 69 kV Substation | Establish a new substation with (2) 30MVA transformers between Fiesta and Koenig Lane substations. New 69-kV transmission lines will be established. |  | #1-55952616 | Austin Energy | James Armke (512) 322-6705 james.armke@austinenergy.com | Budget #2838, 4246, 4838, 23119, 23219 | 2005-03-31 | 2005-07-01 | 69 | 2.51 | 0 | 60 | 0 | TRAVIS | TRAVIS |  |  |  |  | 9269 | Y
05TPIT0101 | Alamito Creek, add 7.2 MVAR capacitor | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 250 | AEP/TNC |  | 1763 | 2005-08-01 | 2005-07-01 | 69 | 0 | 0 | 0 | 7.2 | PRESIDIO | [6 empty] | Y
07TPIT0054 | Westfield | Installed new 138kV 80 MVAR capacitor bank on 138kV ckt.66 to Treaschwig. |  |  | CNP |  |  | 2005-07-30 | 2005-07-06 | 138 | 0 | 0 | 0 | 80 | HARRIS | HARRIS |  |  |  |  | 46571 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0140 | Waco E system reactive capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R439 | 2005-05-01 | 2005-07-08 | 138 | 0 | 0 | 0 | 110.4 | MCLENNAN | [5 empty] | 3438 | Y
05TPIT0163 | Sun 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R603 | 2005-05-01 | 2005-07-08 | 138 | 0 | 0 | 0 | 55.2 | SCURRY | [5 empty] | 1064 | Y
05TPIT0202 | Killeen Switch 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R459 | 2005-05-01 | 2005-07-08 | 138 | 0 | 0 | 0 | 110.4 | BELL | [5 empty] | 3423 | Y
05TPIT0216 | Parkway Tap - Glenwood ckt.95 | Raised conductors to increase thermal ratings |  |  | CNP |  |  | 2005-05-30 | 2005-07-14 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 41221, 40620 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0215 | Greens Bayou - Parkway Tap ckt.95 | Raised conductors to increase thermal ratings |  |  | CNP |  |  | 2005-05-30 | 2005-07-14 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40710, 41221 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0111 | EXXON - Bertron, S R Plant ckt.03 | Raised conductors to increase thermal ratings. |  |  | CNP |  |  | 2005-12-15 | 2005-07-19 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40570, 41405 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0220 | Frontera, 138/69 kV auto | Convert Bates to Rio Grande City 69 kV line to 138 kV with 795 ACSR conductor (rebuild 4/0 section between La Grulla to Rio Grande City) | In-Service | AEP GROUP 208 | AEP/TCC |  | 1188 | 2005-08-01 | 2005-07-29 | 69 | 0 | 0 | 56 | 0 | HIDALC\GO
05TPIT0073 | Kendall 345/138 kV autotransformer # 2 | Install a second 345/138 kV autotransformer at the Kendall substation |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1002926 | 2005-06-30 | 2005-08-01 | 345 | 0 | 0 | 478 | 0 | KENDALL | [5 empty] | 7046 | Y |  | No MVAR added; No New Conductor
05TPIT0288 | P.H. Robinson 345/138 kV autotransformer | Upgraded Autotransformer (A1) position to increase thermal ratings |  |  | CNP |  |  | 2005-08-05 | 2005-08-05 | 345 | 0 | 0 | 460 | 0 | GALVESTON | GALVESTON |  |  |  |  | 42000, 42015 | Y |  | No transmission circuits built, rebuilt or reconductored.
05TPIT0213 | Grant - Plaza ckt.08 | Raised conductors and partially rebuilt ckt.08 to increase thermal ratings |  |  | CNP |  |  | 2005-08-31 | 2005-08-31 | 138 | 0 | 0.96 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47110, 47350 | Y |  | No transformer capacity added.
05TPIT0105 | Cedar Bayou - Strang ckt.87 | Raised conductors to increase thermal ratings. |  |  | CNP |  |  | 2005-11-15 | 2005-08-31 | 138 | 0 | 0 | 0 | 0 | CHAMBERS | HARRIS |  |  |  |  | 40010, 41500 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0075 | Grandview to Happy Hill Switch Rebuild | Rebuild existing Grandview to Happy Hill Switch 138kv line with at least 1033mcm conductor, convert Conley load to 138kv |  |  | Brazos | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2005-09-01 | 2005-09-01 | 138 | 0 | 9.8 | 0 | 0 | JOHNSON | JOHNSON |  |  | 2001-09-01 | 2001-10-01 | 436,432,416 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
05TPIT0204 | McElroy, add 7.2 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 250 | AEP/TNC |  | 1758 | 2005-12-01 | 2005-09-01 | 69 | 0 | 0 | 0 | 7.2 | CRANE | [5 empty] | 6607 | Y
05TPIT0206 | Fort Davis, add 3.6 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 250 | AEP/TNC |  | 1760 | 2005-10-01 | 2005-09-01 | 69 | 0 | 0 | 0 | 3.6 | JEFF DAVIS | [5 empty] | 6676 | Y
05TPIT0051 | Presidio, add 3.6 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 250 | AEP/TNC |  | 1757 | 2005-09-01 | 2005-09-01 | 69 | 0 | 0 | 0 | 3.6 | PRESIDIO | [6 empty] | Y
05TPIT0039 | Bowie to Cottondale Sw. | Rebuild existing Bowie to Cottondale Sw 69kv line with 138kv const. |  |  | Brazos | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2005-09-01 | 2005-09-06 | 138 | 0 | 30 | 0 | 0 | MONTAGUE | WISE |  |  | 2003-05-01 | 2003-08-01 | 620,600,608,612,620 | Y |  | There is no reactive or transformer capability associated with this project
04TPIT0099 | Cedar Bayou D - Warvue ckt.84 | Verified conductor clearance to increase thermal ratings. |  |  | CNP |  |  | 2005-08-30 | 2005-09-06 | 138 | 0 | 0 | 0 | 0 | HARRIS | CHAMBERS |  |  |  |  | 40012, 41700 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0093 | Cedar Bayou W - Chevon ckt.86 | Verified conductor clearance to increase thermal ratings. |  |  | CNP |  |  | 2005-08-30 | 2005-09-06 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40015, 40300 | Y |  | Cost included in Cedar Bayou D - Warvue Ckt.84, Project #04TPIT0099. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0098 | Mont Belvieu - Warvue ckt.84 | Verified conductor clearance to increase thermal ratings. |  |  | CNP |  |  | 2005-08-30 | 2005-09-06 | 138 | 0 | 0 | 0 | 0 | HARRIS | CHAMBERS |  |  |  |  | 41111, 41700 | Y |  | Cost included in Cedar Bayou D - Warvue Ckt.84, Project #04TPIT0099. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0121 | Whitney - Walnut Springs 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R405-WAC | 2005-12-05 | 2005-09-23 | 138 | 0 | 17.4 | 0 | 0 | BOSQUE | BOSQUE |  |  |  |  | 1646, 3546 | Y
05TPIT0037 | Rio Grande City to Garceno, upgrade 69 kV to 138 kV line | Convert Roma to Rio Grande City 69 kV line to 138 kV line with 795 ACSR conductor | In-Service | AEP GROUP 208 | LCRA TSC / AEP |  | 1191, LCRA#1003622 | 2005-09-30 | 2005-09-30 | 138 | 0 | 7 | 0 | 0 | STARR | STARR | [5 empty] | Y
05TPIT0226 | Downtown 138/69kV autotransformer | Upgraded Autotransformer (A2) position to increase thermal ratings |  |  | CNP |  |  | 2005-09-30 | 2005-09-30 | 138 | 0 | 0 | 200 | 0 | HARRIS | HARRIS |  |  |  |  | 47500, 47510 | Y |  | No transmission circuits built, rebuilt or reconductored.
05TPIT0225 | Freeport | Installed new 7.2 MVAR capacitor bank. |  |  | CNP |  |  | 2005-09-30 | 2005-09-30 | 69 | 0 | 0 | 0 | 7.2 | BRAZORIA | BRAZORIA |  |  |  |  | 42640 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0133 | Putnam, add 28.8 MVAR cap | Add 6-28.8 MVAR 138 kV capacitor banks in Abilene area | In-Service | AEP GROUP 287 | AEP/TNC |  | 1633 | 2005-08-19 | 2005-10-01 | 138 | 0 | 0 | 0 | 28.8 | KNOX | [5 empty] | 6309 | Y
05TPIT0227 | West Columbia 138/69kV autotransformer | Upgraded Autotransformer (A2) position to increase thermal ratings |  |  | CNP |  |  | 2005-10-31 | 2005-10-01 | 138 | 0 | 0 | 100 | 0 | BRAZORIA | BRAZORIA |  |  |  |  | 43380, 43390 | Y |  | No transmission circuits built, rebuilt or reconductored.
05TPIT0231 | Obrien - Obrien Distribution Tap ckt.25 | Bundled 138 kV Obrien - Obrien Distribution Tap ckt.25 and upgraded limiting equipment at Obrien. |  |  | CNP |  |  | 2005-11-30 | 2005-10-10 | 138 | 0.05 | 0 | 0 | 0 | FORT BEND | FORT BEND |  |  |  |  | 44510, 44511 | Y |  | No transformer capacity added.
06TPIT0137 | Kendall-Comfort | Upgrade the 1.0-mile Kendall(7150)-Comfort(7155) 795 ACSR 138-kV transmission line to bundled 795 ACSR (440-MVA). |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1005356 | 2006-12-30 | 2005-10-13 | 138 | 0 | 1 | 0 | 0 | KENDALL | KENDALL |  |  |  |  | SEE PROJECT DESCRIPTION | Y
05TPIT0286 | T.H. Wharton 345/138 kV autotransformer | Upgraded Autotransformer (A1) position to increase thermal ratings |  |  | CNP |  |  | 2005-10-17 | 2005-10-17 | 345 | 0 | 0 | 914 | 0 | HARRIS | HARRIS |  |  |  |  | 45500, 45510 | Y | No transmission circuits built, rebuilt or reconductored.
05TPIT0287 | North Belt 345/138 kV autotransformer | Upgraded Autotransformer (A2) position to increase thermal ratings |  |  | CNP |  |  | 2005-10-17 | 2005-10-17 | 345 | 0 | 0 | 672 | 0 | HARRIS | HARRIS |  |  |  |  | 46100, 46110 | Y | No transmission circuits built, rebuilt or reconductored.
05TPIT0006 | North Pharr to Polk, reconductor 138 kV line | Reconductor 138 kV MVEC Pharr to Hall Acres line from 336 to 795 ACSS conductor | In-Service | AEP GROUP 064 | AEP/TCC |  | 1149 | 2005-10-01 | 2005-10-20 | 138 | 0 | 3.58 | 0 | 0 | HIDALGO
06TPIT0142 | Venus - Johnson Switch 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5102 | 2006-05-01 | 2005-10-31 | 345 | 0 | 24.11 | 0 | 0 | ELLIS | JOHNSON |  | 2005-03-17 | 2005-06-16 |  | 1902, 1907 | Y
05TPIT0219 | Key, add 138 kV switching station | Add Key Switching Station in the Frontera to North McAllen 138 kV terminating North Edinburg to MVEC Alton to Key 138 kV line | In-Service | AEP GROUP 292 | AEP/TCC |  | 819 | 2005-08-01 | 2005-11-01 | 138 | 0 | 0 | 0 | 0 | HIDALGO
05TPIT0221 | Construct King 138KV Substation | Serve substation by double tap configuration: tap to Deussen - Chamon ckt.94 and to Greens Bayou - Humble ckt.94 |  |  | CNP |  |  | 2005-11-01 | 2005-11-01 | 138 | 0.62 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40911, 40912 | Y | No transformer capacity added.
05TPIT0124 | Moore Field area, Construct 138 kV hairpin | Convert Moore Field and Palmhurst substations from 69 kV to 138 kV and connect to North Edinburg to Bates 138 kV line | In-Service | AEP GROUP 292 | AEP/TCC |  | 1290 | 2005-11-01 | 2005-11-01 | 138 | 0 | 0 | 0 | 0 | HIDALGO
05TPIT0180 | Moore Field, upgrade 2 transformers & distribution equipment | Convert Moore Field and Palmhurst substations from 69 kV to 138 kV and connect to North Edinburg to Bates 138 kV line | In-Service | AEP GROUP 292 | AEP/TCC |  | 291 | 2005-11-01 | 2005-11-01 | 138 | 0 | 0 | 25 | 0 | HIDALGO
05TPIT0232 | Obrien - Obrien Distribution Tap ckt.73 | Bundled 138 kV Obrien - Obrien Distribution Tap ckt.73 and upgraded limiting equipment at Obrien. |  |  | CNP |  |  | 2005-11-30 | 2005-11-01 | 138 | 0 | 0.1 | 0 | 0 | FORT BEND | FORT BEND |  |  |  |  | 44510, 44512 | Y | No transformer capacity added.
05TPIT0284b | Mason Switching Station, add 2 breakers | Addition of two 69 kV breakers at Mason Switching Station | In-Service | AEP GROUP 314 | AEP/TNC |  | 1685 | 2005-12-31 | 2005-11-01 | 69 | 0 | 0 | 0 | 0 | MASON
05TPIT0285 | McColl Road to North McAllen, reconductor/upgrade double circuit 138 kV Line | Reconductor North Edinburg to North McAllen 138/69 kV double circuit line with 795 ACSS conductor | In-Service | AEP GROUP 064 | AEP/TCC |  | 278 | 2005-04-15 | 2005-11-02 | 138 | 0 | 22.31 | 0 | 0 | HIDALGO
05TPIT0103 | Alton to AEP N. McAllen 138kV Tie Line & Palmhurst Switching Station | Construct 138kV line from MVEC Alton to the Frontera to AEP North McAllen 138kV line and add a 138kV switching station | A temporary 138kV tie between AEP North McAllen- AEP Palmhurst to MVEC Alton was completed April 30, 2005. The new AEP Switching Station expected Oct. 2005. | 04TPIT0025 & 05TPIT0250 | MVEC | Loretta C. Gallaga (956) 463-1584 lgallaga@magicvalley.coop | 801143 | 2005-11-05 | 2005-11-05 | 138 | 1.2 | 0 | 0 | 0 | HIDALGO | HIDALGO |  | 2003-04-03 | 2003-06-06
07TPIT0007 | Hackberry - Grapevine Ball St 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5006-WAC | 2005-12-05 | 2005-11-08 | 138 | 0 | 11.95 | 0 | 0 | DALLAS | TARRANT |  | 2004-04-01 | 2004-05-01 |  | 2017, 2021, 2022, 2388 | Y
06TPIT0007 | Temple Pecan Creek Switching Station | Establish Temple Pecan Creek Switching station and install a 600 MVA 345/138 kV autotransformer. |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | E097A | 2006-05-01 | 2005-11-16 | 345 | 10.2 | 0 | 600 | 0 | BELL | [5 empty] | 3412, 3420 | Y
06TPIT0171 | Temple Pecan Creek - Temple Elm Creek 138 kV line | Construct 138 kV line from Temple Pecan Creek to Temple Elm Creek. |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | E097A | 2006-05-01 | 2005-11-16 | 138 | 9.6 | 0 | 0 | 0 | BELL | BELL |  |  |  |  | 3420, 13662 | Y
05TPIT0291 | Strang - Chorin ckt.87 | Verified conductors clearance to increase thermal ratings |  |  | CNP |  |  | 2005-11-15 | 2005-11-16 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 41500, 40320 | Y | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0017 | Temple Elm Creek - Temple NW - Belton 138 kV line | Establish Temple Elm Creek Switching Station and upgrade 138 kV line to Belton |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | E097B | 2006-05-15 | 2005-11-25 | 138 | 0 | 19.2 | 0 | 0 | BELL | BELL |  |  |  |  | 3608, 3609, 3610, 13662 | Y
05TPIT0229 | Bellaire 345/138kV autotransformer | Upgrade Autotransformer (A1) position to increase thermal ratings |  |  | CNP |  | CNP | 2005-11-30 | 2005-11-30 | 345 | 0 | 0 | 600 | 0 | HARRIS | HARRIS |  |  |  |  | 47000, 47010 | Y | No transmission circuits built, rebuilt or reconductored.
04TPIT0102 | N Pharr to N Alamo, upgrade 69 kV line | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | In-Service | AEP GROUP 068 | LCRA TSC / AEP |  | 281, LCRA#1003359 | 2006-04-28 | 2005-11-30 | 138 | 0 | 4 | 0 | 0 | HIDALGO | HIDALGO
06TPIT0216 | Fayetteville-Frelsburg | Replace under-rated limiting line terminal equipment at Fayetteville(7286) to increase Fayetteville(7286)-Frelsburg(7263) to the conductor's rating. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2006-06-01 | 2005-11-30 | 138 | 0 | 0 | 0 | 0 | Fayette
05TPIT0126 | North Belt - Greens Road Tap ckt.90 | Raised conductors to increase thermal ratings and upgraded limiting equipment at North Belt |  |  | CNP |  |  | 2005-12-31 | 2005-11-30 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46110, 45822 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0125 | Newport - Hardy ckt.86 | Raised conductors to increase thermal ratings. |  |  | CNP |  |  | 2005-12-31 | 2005-11-30 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 41150, 46032, 46331, 45821, 45640, 46281, 45840 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0143 | Zorn Auto | Replace the 600MVA Zorn Auto 2 with a 478MVA auto (7045-7180) |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1005117 | 2005-10-01 | 2005-12-01 | 345 | 0 | 0 | 478 | 0 | GUADALUPE | [5 empty] | SEE PROJECT DESCRIPTION | Y
05TPIT0230 | Bellaire 345/138kV autotransformer | Upgraded Autotransformer (A4) position to increase thermal ratings |  |  | CNP |  |  | 2005-12-01 | 2005-12-01 | 345 | 0 | 0 | 600 | 0 | HARRIS | HARRIS |  |  |  |  | 47000, 47010 | Y |  | No transmission circuits built, rebuilt or reconductored.
05TPIT0096 | La Palma to Rio Hondo, rebuild 138 kV line | Rebuild La Palma to Rio Hondo 138 kV with 2-795 ACSS, double circuit capable and add 345/138 kV autotransformer at Rio Hondo | In-Service | AEP GROUP 293 | AEP/TCC |  | 1459 | 2005-12-31 | 2005-12-01 | 138 | 0 | 10.1 | 0 | 0 | CAMERON
06TPIT0032 | Royse - Ben Davis (TMPA) 138 kV line (Oncor Electric Delivery section) | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M309 | 2005-12-01 | 2005-12-01 | 138 | 0 | 17.47 | 0 | 0 | ROCKWALL | COLLIN |  |  | 2003-06-01 | 2003-07-01 | 2472, 2693, 2694, 2695, 2692, 2697, 2696, 968 | Y |  | Complete to change of ownership awaiting other complettion of work
05TPIT0112 | Falcon SS, add 138 kV SS | Build Falcon Switching Station at the double circuit tap in the Bates to Wormser 138 kV line | In-Service | AEP GROUP 280 | AEP/TCC |  | 1348 | 2005-10-01 | 2005-12-01 | 138 | 0 | 0 | 0 | 0 | STARR
07TPIT0064 | Ennis SE. 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M362-WAC | 2005-07-01 | 2005-12-01 | 138 | 0 | 0 | 0 | 110.4 | ELLIS | [5 empty] | 2326 | Y
05TPIT0235 | Construct Terminal 138KV Substation | Looped into Bayway - Hunter ckt.79 |  |  | CNP |  |  | 2005-12-01 | 2005-12-01 | 138 | 0.82 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 42955 | Y |  | No transformer capacity added.
05TPIT0236 | University 138/69kV autotransformer | Upgraded Autotransformer (A1) position to increase thermal ratings |  |  | CNP |  |  | 2005-12-31 | 2005-12-01 | 138 | 0 | 0 | 200 | 0 | HARRIS | HARRIS |  |  |  |  | 47750, 47752 | Y |  | No transmission circuits built, rebuilt or reconductored.
05TPIT0228 | Clodine - Barker ckt.78 | Raised conductors to increase thermal ratings |  |  | CNP |  |  | 2005-11-30 | 2005-12-01 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 44140, 44051 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0239 | Gable Street 69kV reconfiguration | Disconnected 69kV ckt.12 and 15 from Gable Street, and reconnected them to form 69kV ckt.12 University-General Foods-Brown & Root-Bringhurst-Clinton. |  |  | CNP |  |  | 2005-12-31 | 2005-12-01 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47641, 47550, 47640, 47670 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0240 | ckt.32 Gable Street to Downtown | Closed normally open 69kV ckt.32 Gable Street to Downtown. Upgraded 69kV substation equipment at Gable Street and Downtown to increase thermal rating of ckt.32 Gable Street to Downtown |  |  | CNP |  |  | 2005-12-31 | 2005-12-01 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47640, 47650, 47510, 47642 | Y |  | Cost included in Gable Street 69kV reconfiguration Project #05TPIT0239. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0145 | Dallas 800/900 - Greenville 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M447-WAC | 2005-10-30 | 2005-12-04 | 138 | 0 | 4.92 | 0 | 0 | DALLAS | DALLAS |  |  |  |  | 2859, 2883, 2860, 2882, 2864, 2868, 2865, 2869 | Y
06TPIT0145 | ckt.90 Midtown to Polk | Installed power flow control reactor in series with ckt.90 Midtown to Polk. |  |  | CNP |  |  | 2005-12-05 | 2005-12-05 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47705, 47706, 47730 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0119 | LaGrulla to Rio Grande City, upgrade 69 kV to 138 kV line | Convert Bates to Rio Grande City 69 kV line to 138 kV with 795 ACSR conductor (rebuild 4/0 section between La Grulla to Rio Grande City) | In-Service | AEP GROUP 208 | LCRA TSC / AEP |  | 1289, LCRA#1004249 | 2005-09-30 | 2005-12-05 | 138 | 0 | 13.1 | 0 | 0 | STARR | STARR
05TPIT0082 | Rio Grande City, add SS with 138/69 kV autotransformer | Convert Bates to Rio Grande City 69 kV line to 138 kV with 795 ACSR conductor (rebuild 4/0 section between La Grulla to Rio Grande City) | In-Service | AEP GROUP 208 | AEP/TCC |  | 1194 | 2005-10-30 | 2005-12-07 | 138 | 0 | 0 | 93 | 0 | STARR
05TPIT0183 | La Grulla, upgrade 2 transformers & distribution equipment | Convert Bates to Rio Grande City 69 kV line to 138 kV with 795 ACSR conductor (rebuild 4/0 section between La Grulla to Rio Grande City) | In-Service | AEP GROUP 208 | AEP/TCC |  | 1177 | 2005-10-15 | 2005-12-08 | 138 | 0 | 0 | 25 | 0 | STARR
05TPIT0242 | ckt.21 Greens Bayou - Gable St | Raised conductors to increase thermal ratings. |  |  | CNP |  |  | 2005-12-31 | 2005-12-16 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40710, 40962, 47712, 47630 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0241 | ckt.32 Dunlavy to Hydepark | Upgraded substation equipment at Dunlavy to increase thermal rating of ckt.32 Dunlavy to Hydepark |  |  | CNP |  |  | 2005-12-31 | 2005-12-16 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47580, 47690 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
08TPIT0054 | T.H.Wharton - Jewett ckt.1 | Upgraded tie lines from TH Wharton to TXU tie point to increase thermal ratings to 1450 MVA by raising conductors and upgraded limiting equipment at TH Wharton |  |  | CNP |  |  | 2005-12-30 | 2005-12-30 | 345 | 0 | 0 | 0 | 0 | HARRIS | LEON |  | 2004-09-10 | 2004-11-01 | 2005-03-15 | 45500, 3390 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0218 | Glenwood - Bertwood ckt.95 | Raised conductors to increase thermal ratings | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2005-12-30 | 2006-01-01 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40620, 40180 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0184 | Highway 9, replace 138/69 kV autotransformer | Cut-in the Nueces Bay to Morris Street 138 kV line into Highway 9 substation | IN-SERVICE | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1589 | 2006-01-01 | 2006-01-01 | 138 | 0 | 0 | 187 | 0 | NUECES | [6 empty] | Y
05TPIT0169 | TAMU to Atkins 138 reconductor | Reconductor an existing 138 to 795 ACSR - Currently 636 ACSR |  | 1-308098601 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 809 | 2006-06-06 | 2006-01-06 | 138 | 0 | 3.83 | 0 | 0 | BRAZOS | BRAZOS |  |  |  |  | 2007 32799-32862 2008 and beyond 32799-32006 32006-32862 | Y |  | There were no new transformers added with this project.
05TPIT0188 | Atkins Capacitor Addition | Install 54 MVAR Capacitors at 138 kV |  | 1-274266431 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 418 | 2006-01-06 | 2006-01-06 | 138 | 0 | 0 | 0 | 54 | BRAZOS | [5 empty] | 32862 | Y |  | There were no new transformers added with this project and/or this project was within an existing substation and there was no new transmission lines installed.
06TPIT0239 | Disconnect and remove Minimax 138KV Substation from CenterPoint Energy's system. | Disconnected and removed customer owned Minimax substation from CNP's ckt.73 White Oak - Wirt. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-01-21 | 2006-01-21 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46070 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0181 | Carbon 69 kV Switching Station | Establish switching station to provide interconnection for a generator. |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R607-WACF | 2006-01-31 | 2006-01-31 | 69 | 0 | 0 | 0 | 0 | HOWARD | [5 empty] | 1321 | Y
05TPIT0223 | Rio Pecos, add +/-25 MVAR DRCS | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | IN-SERVICE | AEP GROUP 250 | AEP/TNC |  | 250 | 2005-10-05 | 2006-01-31 | 69 | 0 | 0 | 0 | 50 | PECOS | [5 empty] | 6601 | Y
06TPIT0005 | Asherton to Conoco, rebuild 138 kV Line | Rebuild Asherton to Eagle Pass 138 kV line from 4/0 to 795 MCM ACSR |  | AEP GROUP 235 | LCRA TSC / AEP | Brian Johnson 918-599-2653 | 94, LCRA#1003626 | 2006-02-01 | 2006-02-01 | 138 | 0 | 33 | 0 | 0 | DIMMIT | MAVERICK | [5 empty] | Y
06TPIT0204 | Mont Belvieu 138/12kV transformer | Converted part of the 69 kV load at Mont Belvieu to 138kV. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-03-01 | 2006-02-09 | 138 | 0 | 0 | 50 | 0 | CHAMBERS | CHAMBERS |  |  |  |  | 41112, 41111 | Y |  | No transformer capacity added.
05TPIT0122 | Magnolia Park | Installed new 138kV 60 MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-02-15 | 2006-02-14 | 138 | 0.1 | 0 | 0 | 60 | HARRIS | HARRIS |  |  |  |  | 47700 | Y |  | No transformer capacity added.
06TPIT0186 | Webster | Installed new 138kV 100 MVAR capacitor bank on 138kV ckt.63 to La Marque. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-02-01 | 2006-02-14 | 138 | 0 | 0 | 0 | 100 | HARRIS | HARRIS |  |  |  |  | 43505 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0122 | Treaschwig to Westfield ckt.66 | Raised conductors to increase thermal ratings | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-02-06 | 2006-02-15 | 138 | 0 | 7.1 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46550, 46571, 46570 | Y
04TPIT0106 | Santa Rosa to N Mercedes, upgrade 69 kV line | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station |  | AEP GROUP 068 | LCRA TSC / AEP | Rich Haley 918-599-2653 | 1265, LCRA#1003359 | 2006-02-17 | 2006-02-17 | 138 | 0 | 5 | 0 | 0 | CAMERON | HIDALGO | [5 empty] | Y
04TPIT0129 | Santa Rosa to Harlingen SS, upgrade 69 kV line | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station |  | AEP GROUP 068 | LCRA TSC / AEP | Rich Haley 918-599-2653 | 42, LCRA#1003359 | 2006-02-17 | 2006-02-17 | 138 | 0 | 8 | 0 | 0 | CAMERON | CAMERON | [5 empty] | Y
06TPIT0153 | Constructed Franklin 138KV Substation, Phase 1. | Serve substation by looping into ckt.21 from Gable Street to Crockett | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-02-15 | 2006-02-17 | 138 | 0.06 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47620 | Y |  | No transformer capacity added.
05TPIT0128 | Northwest Abilene, add 28.8 MVAR cap | Add 6-28.8 MVAR 138 kV capacitor banks in Abilene area | IN-SERVICE | AEP GROUP 287 | AEP/TNC | Ashley Beasley 918-599-2653 | 1631 | 2006-02-28 | 2006-02-28 | 138 | 0 | 0 | 0 | 28.8 | TAYLOR | [6 empty] | Y
05TPIT0109 | Fort Phantom, add 28.8 MVAR cap | Add 6-28.8 MVAR 138 kV capacitor banks in Abilene area | IN-SERVICE | AEP GROUP 287 | AEP/TNC | Ashley Beasley 918-599-2653 | 1632 | 2006-02-28 | 2006-02-28 | 138 | 0 | 0 | 0 | 28.8 | TAYLOR | [6 empty] | Y
06TPIT0183 | Crosby | Increased reactive capability to 106.7MVAR | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-04-01 | 2006-03-01 | 138 | 0 | 0 | 0 | 6.7 | HARRIS | HARRIS |  |  |  |  | 40391 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0200 | Friend Ranch, add 28.8 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | IN-SERVICE | AEP GROUP 213 | AEP/TNC | Ashley Beasley 918-599-2653 | 1754 | 2006-03-31 | 2006-03-01 | 138 | 0 | 0 | 0 | 28.8 | CROCKET | [5 empty] | 6562 | Y
06TPIT0066 | Spring to St Jo Rebuild | Rebuild existing 138kv Spring to St Jo line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-04-01 | 2006-03-01 | 138 | 0 | 23.4 | 0 | 0 | COOKE | COOKE |  |  |  |  | 684691695746 | Y |  | There is no reactive or transformer capability associated with this project
07TPIT0029 | Hilltop Lakes to Hilltop Lakes Switch Upgrade or Rebuild | Rebuild or uprate the existing Hilltop Lakes to Hilltop Lakes Switch 69KV line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-05-01 | 2006-03-01 | 69 | 0 | 17.2 | 0 | 0 | LEON | ROBERTSON |  |  |  |  | 48,43 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0194 | Bellaire | Increased reactive capability to 120MVAR. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-03-01 | 2006-03-02 | 138 | 0 | 0 | 0 | 20 | HARRIS | HARRIS |  |  |  |  | 47010 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0208 | Rio Pecos, upgrade 57.6 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | IN-SERVICE | AEP GROUP 213 | AEP/TNC | Brett Madison 918-599-2653 | 250 | 2006-12-31 | 2006-03-03 | 138 | 0 | 0 | 0 | 57.6 | PECOS | [5 empty] | 6601 | Y
04TPIT0124 | Westside, add 2-28.8 MVAR capacitors | Install capacitor banks at various locations in the Corpus Chrisi area | IN-SERVICE | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1608 | 2006-04-01 | 2006-03-06 | 138 | 0 | 0 | 0 | 57.6 | NUECES | [6 empty] | Y
06TPIT0103 | Clear Springs | Add a new 345/138 kV 478 MVA auto-transformer at the Clear Springs substation(7050). The existing 345 kV bus at the Clear Springs will be converted from a ring bus configuration to a double-bus double-breaker configuration. Upgrade the 7.2-mile Clear Springs(7680)-Geronimo(7604)-Seguin(7228) 138 kV transmission line (T-264) from 336 ACSR to single 1433.6 ACSS (492 MVA), double circuit capable. Upgrade the 7.2-mile Clear Springs(7680)-Freiheit(7462)-Hortontown(7175)-Comal(7176) 138 kV transmission line (T-264, T-394, and T-119) from 336 ACSR to Bundled 959 ACSS (784 MVA) single circuit. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1005349 | 2006-06-30 | 2006-03-14 | 345 | 0 | 0 | 478 | 0 | GUADALUPE |  |  | 2005-04-01 | 2005-06-01 | Endorsed | SEE PROJECT DESCRIPTION | Y | Reviewing proejct scope for Harris Branch auto-transformer. Considering the Gilleland site.
05TPIT0224 | Crane, add +/-25 MVAR DRCS | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | IN-SERVICE | AEP GROUP 213 | AEP/TNC | Brett Madison 918-599-2653 | 1753 | 2006-03-15 | 2006-03-15 | 69 | 0 | 0 | 0 | 50 | CRANE | [5 empty] | 6615 | Y
05TPIT0094 | Venus - Cedar Hill Substation 138 kV line | Construct 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M346-WACF | 2006-05-15 | 2006-03-16 | 138 | 6.9 | 0 | 0 | 0 | DALLAS | DALLAS |  |  |  |  | 1915, 2311, 1908, 2300, 2313, 2314, 3054, 3056, 3055, 3053 | Y
08TPIT0070 | Liggett - Shady Grove 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5063-WACF | 2006-12-15 | 2006-03-20 | 138 | 0 | 2.5 | 0 | 0 | DALLAS | TARRANT |  |  |  |  | 1922, 2270, 2271 | Y
05TPIT0248 | Constructed Booster 138KV Substation | Serve substation by looping into ckt.02 Velasco - Seaway | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-03-15 | 2006-03-20 | 138 | 0.18 | 0 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  |  | 43360, 42195, 43220 | Y |  | No transformer capacity added.
06TPIT0251 | Velasco to Seaway Switch ckt.02 | Raised conductors to increase thermal ratings | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-03-20 | 2006-03-21 | 138 | 0 | 0 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  |  | 43360, 42195, 43220 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0021 | Brand 138 kV substation upgrade | Substation upgrade |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2006-03-22 | 2006-03-22 | 138 | 0 | 0 | 0 | 0 | DALLAS | [5 empty] | 827 | Y
06TPIT0189 | White Oak South | Increased reactive capability to 100MVAR | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-04-01 | 2006-03-23 | 138 | 0 | 0 | 0 | 6.7 | HARRIS | HARRIS |  |  |  |  | 46615 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0187 | North Belt | Increased reactive capability to 14.4MVAR | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-04-01 | 2006-03-23 | 138 | 0 | 0 | 0 | 3.6 | HARRIS | HARRIS |  |  |  |  | 46111 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0188 | Satsuma | Increased reactive capability to 14.4MVAR | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-04-01 | 2006-03-24 | 138 | 0 | 0 | 0 | 3.6 | HARRIS | HARRIS |  |  |  |  | 46300 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0056 | Barney Davis, add 2-28.8 MVAR capacitors | Install capacitor banks at various locations in the Corpus Chrisi area | IN-SERVICE | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1591 | 2006-04-10 | 2006-03-31 | 138 | 0 | 0 | 0 | 57.6 | NUECES | [6 empty] | Y
05TPIT0207 | Sonora, add 2x14.4 MVAR caps | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | IN-SERVICE | AEP GROUP 213 | AEP/TNC | Ashley Beasley 918-599-2653 | 1756 | 2006-03-31 | 2006-03-31 | 138 | 0 | 0 | 0 | 28.8 | SUTTON | [5 empty] | 6515, 6513 | Y
05TPIT0222 | Friend Ranch, add +/-25 MVAR DRCS | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | IN-SERVICE | AEP GROUP 213 | AEP/TNC | Ashley Beasley 918-599-2653 | 1754 | 2006-03-31 | 2006-03-31 | 69 | 0 | 0 | 0 | 50 | CROCKET | [5 empty] | 6562 | Y
05TPIT0250 | MVEC W. Edinburg- MVEC Alton | Rebuild 138kV line from W. Edinburg to Alton |  | 04TPIT0025 & 05TPIT0103 | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org | 801147 | 2006-03-01 | 2006-04-01 | 138 | 0 | 6.8 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
01TPIT0001 | AEPTC Weslaco Switch to MVEC | Built a tie line between the AEPTC Weslaco Switch and the MVEC cross valley 138 kV line |  |  | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org |  | 2006-03-01 | 2006-04-01 | 138 | 6.8 | 0 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
05TPIT0249 | FM 106 138kV Line Relocation | Relocate 1.8 Miles of 138kV Line between MVEC Central and MVEC East Rio Hondo due to TXDOT Road Widening Project |  |  | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org | 711622 | 2006-04-01 | 2006-04-01 | 138 | 0 | 1.8 | 0 | 0 | CAMERON | CAMERON | [5 empty] | N |  | This has not yet been reflected in the SSWG Base Case but will need to be added.
00TPIT0001 | AEPTC Rio Hondo to MVEC 138 lines | Built two lines to tie between the AEPTC Rio Hondo 345 to 138 kV Substation and MVEC's 138 kV lines |  |  | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org |  | 2006-04-01 | 2006-04-01 | 138 | 1.8 | 0 | 0 | 0 | CAMERON | CAMERON | [5 empty] | Y
08TPIT0055 | Jewett - TH Wharton 345 kV line upgrade | Upgrade tie lines from Jewett to TXU Electric Delivery tie point to increase thermal ratings to 1450 MVA or above. |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R465-WACF | 2006-05-01 | 2006-04-03 | 345 | 0 | 32.04 | 0 | 0 | LEON | LEON |  | 2004-09-10 |  | 2005-03-01 | 45500, 3390 | Y
05TPIT0255 | Capacitor Bank Addition at Greens Prairie Substation | Adding two 27 Mvar zero sequence closing transmission capacitor banks at Greens Prairie Substation |  |  | COCS | Garry Lange 979 764 3682 glange@cstx.gov |  | 2006-02-06 | 2006-04-06 | 138 | 0 | 0 | 0 | 54 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | Y |  | Adding two 27 Mvar zero sequence closing transmission capacitor banks at Greens Prairie Substation
05TPIT0076 | N Weslaco to Weslaco SS, upgrade 69 kV line | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station |  | AEP GROUP 068 | LCRA TSC / AEP | Rich Haley 918-599-2653 | 1267, LCRA#1003359 | 2006-04-07 | 2006-04-07 | 138 | 0 | 1 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
06TPIT0107 | Goodwin to LaGrulla, upgrade 69 kV to 138 kV line | Convert Bates to Rio Grande City 69 kV line to 138 kV with 795 ACSR conductor (rebuild 4/0 section between La Grulla to Rio Grande City) | Schedule Update | AEP GROUP 208 | LCRA TSC / AEP | Georger Carpenter 918-599-2653 | 1288, LCRA#1004249 | 2006-05-06 | 2006-04-07 | 138 | 0 | 14.1 | 0 | 0 | STARR | STARR | [5 empty] | Y
06TPIT0205 | Ben Davis- McCree 138 line Re-route for Crisrt Rd Sub | Provide source for new Garland Sub | On schedule | 05TPIT0100 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org |  | 2006-04-07 | 2006-04-07 | 138 | 0 | 0 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 850 | Y
06TPIT0094 | Stryker Creek - Troup 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R363-WACF | 2006-05-15 | 2006-04-10 | 138 | 0 | 15.53 | 0 | 0 | CHEROKEE | CHEROKEE |  |  |  |  | 3110, 3147 | Y
06TPIT0033 | Anna Switch - Allen Switch 138 kV line | Upgrade 138 existing kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M292-WACF | 2006-05-01 | 2006-04-12 | 138 | 0 | 42 | 0 | 0 | COLLIN | COLLIN |  |  |  |  | 2374, 2529, 2532, 2553, 2530, 2533, 2531, 2509, 2510, 2549, 2548, 2547, 2546, 2544, 2560, 2561 | Y
06TPIT0139 | Pueblo to Eagle Pass Escondido, rebuild 138 kV line | Rebuild Asherton to Eagle Pass 138 kV line from 4/0 to 795 MCM ACSR | IN-SERVICE | AEP GROUP 235 | LCRA TSC / AEP | Brian Johnson 918-599-2653 | 1715, LCRA#1003626 | 2006-05-31 | 2006-04-15 | 138 | 0 | 7.22 | 0 | 0 | MAVERICK | MAVERICK | [5 empty] | Y
05TPIT0233 | Northwest Austin 138 kV Substation | Establish a new 138 kV substation with one 30 MVA transformer and cut the new substation in between Jollyville and Williamson substation. |  | #1-322406631 | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | Budget #2794, 4794, 2835, 7010,7011 | 2006-02-15 | 2006-04-19 | 138 | 0.2 | 0 | 30 | 0 | TRAVIS | TRAVIS |  |  |  |  | Bus 9245 | Y
05TPIT0007 | North McAllen to West McAllen, reconductor 138 kV line | Reconductor 138 kV North McAllen to West McAllen with 795 ACSS conductor | IN-SERVICE | AEP GROUP 064 | AEP/TCC | Rich Haley 918-599-2653 | 283 | 2006-04-20 | 2006-04-20 | 138 | 0 | 4.71 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
06TPIT0209 | Benbrook 345 kV circuit breaker | Install a 345 kV circuit breaker |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5097-WACF | 2006-05-15 | 2006-04-21 | 345 | 0 | 0 | 0 | 0 | TARRANT |  |  | 2004-04-02 | 2005-06-16 |  | 1870, 1935 | Y
06TPIT0161 | Valley 345/138 kV autotransformer | Replace existing 450 MVA 345/138 kV autotransformer with a 600 MVA autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R500-WACF | 2006-05-01 | 2006-04-23 | 345 | 0 | 0 | 600 | 0 | FANNIN | [5 empty] | 1690, 1691 | Y
06TPIT0093 | Tyler SE - Tyler GE 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R336-WACF | 2006-05-01 | 2006-04-27 | 138 | 0 | 1.03 | 0 | 0 | SMITH | SMITH |  |  |  |  | 3143, 3213 | Y
06TPIT0196 | Bellaire 345/138 kV autotransformer. | Added 800MVA autotransformer (A2) at Bellaire, swap ckt.05 to Jeanetta and ckt.09 to Brays at Bellaire and upgrade fault duty rating of Bellaire North 138kV bus to at least 63kA. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-30 | 2006-04-27 | 345 | 0 | 0 | 800 | 0 | HARRIS | HARRIS |  |  |  |  | 47000, 47010 | Y |  | No transmission circuits built, rebuilt or reconductored.
06TPIT0208 | Alvarado 138/69 kV autotransformer | Replace existing autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M367-WACF | 2006-05-15 | 2006-04-29 | 138 | 0 | 0 | 50 | 0 | JOHNSON | [5 empty] | 2298, 2297 | Y
06TPIT0210 | Collin series reactor | Install 2-ohm 138 kV series reactor on the 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M323-WACF | 2006-05-15 | 2006-04-29 | 138 | 0 | 0 | 0 | 0 | COLLIN | [5 empty] | 2370, 2372 | N
06TPIT0019 | Sterrett - Waxahachie Pump 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M281-WACF | 2006-05-15 | 2006-04-30 | 138 | 0 | 0.64 | 0 | 0 | ELLIS | ELLIS |  |  |  |  | 2316, 2317, 2319 | Y
06TPIT0141 | Chico Gifford Hill - BEC Wise County Switch - Decatur 138 kV line | Loop Chico Gifford Hill - Decatur 138 kV line into BEC's Wise County Switch |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R176-WACF | 2006-05-01 | 2006-04-30 | 138 | 0 | 0.5 | 0 | 0 | WISE | WISE |  |  |  |  | 1565, 1564 | Y
06TPIT0200 | Airline 138 kV, Install -40/+50 Mvar SVC | South Texas area 180 MVAR of dynamic reactive support | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Michael Glueck 918-599-2653 | 2042 | 2006-05-01 | 2006-04-30 | 69 | 0 | 0 | 0 | 90 | NUECES | [6 empty] | Y
06TPIT0106 | Eagle Pass Escondido, add 138 kV SS and 1-28.8 cap bank | Rebuild Asherton to Eagle Pass 138 kV line from 4/0 to 795 MCM ACSR | IN-SERVICE | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1656 | 2006-05-31 | 2006-05-01 | 138 | 0 | 0 | 0 | 28.8 | MAVERICK | [6 empty] | Y
05TPIT0057 | Uvalde, add 1-14.4 138 kV MVAr caps | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | IN-SERVICE | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1448 | 2006-05-01 | 2006-05-01 | 138 | 0 | 0 | 0 | 14.4 | UVALDE |  |  | 2006-01-10 | 2006-02-14 | 2006-07-18 |  | Y
06TPIT0123 | Uvalde, add 14.4 69 kV MVAr caps | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | IN-SERVICE | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 884 | 2006-05-01 | 2006-05-01 | 69 | 0 | 0 | 0 | 14.4 | UVALDE |  |  | 2006-01-10 | 2006-02-14 | 2006-07-18 |  | Y
05TPIT0166 | Hearne to Hearne Southwest Rebuild | Rebuild existing Hearne - Hearne Southwest with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-04-01 | 2006-05-01 | 69 | 0 | 2.62 | 0 | 0 | ROBERTSON | ROBERTSON |  |  |  |  | 36,31 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0052 | Tomball | Increased cap bank size to 14.4 MVAR | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-30 | 2006-05-04 | 138 | 0 | 0 | 0 | 3.6 | HARRIS | HARRIS |  |  |  |  | 46511 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0255 | Garden Villas | Increased reactive capability to 100.03 MVAR | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-04 | 2006-05-04 | 138 | 0 | 0 | 0 | 6.7 | BRAZORIA | BRAZORIA |  |  |  |  | 42700 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0218 | Howard Lane-McNeil | Replace under-rated limiting line terminal equipment at Howard Lane(7335) and McNeil(7334) to increase Howard Lane(7335)-McNeil(7334) to the conductor's rating. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2006-06-01 | 2006-05-05 | 138 | 0 | 0 | 0 | 0 | Travis | [6 empty] | Y
05TPIT0038 | Leon Creek to Pleasanton, rebuild 138 kV line | Reconductor Leon to Pleasanton 138kV line from 336 to 795 ACSR. | IN-SERVICE | AEP GROUP 044 | AEP/TCC | Brian Johnson 918-599-2653 | 1398 | 2006-05-31 | 2006-05-05 | 138 | 0 | 15.4 | 0 | 0 | ATASCOSA | BEXAR | [5 empty] | Y
05TPIT0258 | North Denton Sub; Additition for DME Transformer | Install 25MVA, 138kV to 13.2 kV substation transformer served from TMPA 138kV bus | On schedule | None | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | 600569 | 2006-05-01 | 2006-05-06 | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  | 985 | Y
05TPIT0001 | Braunig to Kennedy 138 kV Reconductor (Elmendorf - Floresville Section) | Rebuild 138 kV line from Braunig to Elmendorf to Eagle Creek to Floresville to Stockdale to Kennedy. | Rebuild of entire line divided up to several projects, each rebuilding from one station to the next. | T-0762 | CPS | Gerald Ripps 210-353-2470 | T-0762 | Jun-06 | 2006-05-06 | 138 | 0 | 14 | 0 | 0 | BEXAR | WILSON |  |  |  |  | 5025 5132 5135 5155 5412 | Y |  | There are no transformers associated with this project
06TPIT0126 | Goodwin, upgrade 2 transformers & distribution equipment | Convert Bates to Rio Grande City 69 kV line to 138 kV with 795 ACSR conductor (rebuild 4/0 section between La Grulla to Rio Grande City) | IN-SERVICE | AEP GROUP 208 | AEP/TCC | George Carpenter 918-599-2653 | 1189 | 2006-04-30 | 2006-05-08 | 138 | 0 | 0 | 40 | 0 | HIDALGO | [6 empty] | Y
06TPIT0212 | Lott 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R468-WACF | 2006-05-15 | 2006-05-11 | 69 | 0 | 0 | 0 | 9.2 | FALLS | [5 empty] | 3642 | Y
06TPIT0076 | Comfort-Raymond Barker | Upgrade the 9.8-mile Comfort(7155)-Raymond Barker Tap (7157) 336 ACSR (64-MVA) 69-kV transmission line to 795 ACSR (220-MVA) 138-kV. Upgrade the 2-mile Raymond Barker Tap (7157)-Verde Creek (7146) 336 ACSR (128-MVA) 138-kV transmission line to 795 ACSR (220-MVA). Relocate the 138-69-kV 45-MVA auto-transformer from Comfort to Raymond Barker Tap. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1003053 | 2006-06-30 | 2006-05-15 | 138 | 0 | 11.8 | 45 | 0 | KENDALL | KERR |  |  |  |  | SEE PROJECT DESCRIPTION | Y
06TPIT0178 | North Denton Sub: Add 2 138 terminals for BEPC line and auto | Expand 138 kV bus for BEPC's Spring line and autotransformer | On schedule | 05TPIT0043 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05004 | 2006-05-15 | 2006-05-15 | 138 | 0 | 0 | 0 | 0 | DENTON |  | Tier 4 |  |  |  | 985 | Y
06TPIT0184 | South Channel | Installed new 138kV 120 MVAR capacitor bank on 138kV ckt.06 to Jefferson. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-15 | 2006-05-15 | 138 | 0 | 0 | 0 | 120 | HARRIS | HARRIS |  |  |  |  | 41371 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0185 | P.H. Robinson | Installed new 138kV 106.7 MVAR capacitor bank on 138kV ckt.92 to Garden Villas. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-15 | 2006-05-15 | 138 | 0.1 | 0 | 0 | 106.7 | GALVESTON | GALVESTON |  |  |  |  | 42011 | Y |  | No transformer capacity added.
06TPIT0215 | Construct Cavern 138KV Substation | Looped into Biport - Riwood ckt.82 | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-30 | 2006-05-15 | 138 | 0.27 | 0 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  |  | 43300 | Y |  | No transformer capacity added.
05TPIT0137 | Silber Dip to White Oak ckt.81 | Raised conductors to increase thermal ratings | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-30 | 2006-05-15 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 44656, 46615 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0097 | Raymondville, upgrade 138/69 kV auto | Upgrade Raymondville 138/69 kV autotransformer to 93 MVA | IN-SERVICE | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1560 | 2006-06-01 | 2006-05-15 | 138 | 0 | 0 | 93 | 0 | CAMERON | [6 empty] | Y
05TPIT0134 | Kleberg add 28.8 MVAR capacitor | Install capacitor banks at various locations in the East Valley area | IN-SERVICE | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1665 | 2006-07-31 | 2006-05-15 | 138 | 0 | 0 | 0 | 28.8 | CAMERON | [6 empty] | Y
07TPIT0051 | Humble | Installed new 138kV 60 MVAR capacitor bank on 138kV ckt.94 to Duessen. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-15 | 2006-05-17 | 138 | 0 | 0 | 0 | 60 | HARRIS | HARRIS |  |  |  |  | 40831 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0108 | Decker to Techridge 138kV circuit | Establish a new 138kV circuit from Decker to Techridge subs. Rebuild part of LCRA's T146 to establish a second Dessau to McNeil 138 kV circuit with 3000A capacity. Reconductor existing Ckt 904 (Dessau to McNeil) to 3000 A capacity. |  | CKT 975 #1-320527853 CKT 904 #1-320527859 CKT 909 #1-320527862 | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | Budget #1436, 1437, 4244, 24126 | 2006-05-31 | 2006-05-17 | 138 | 23.17 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  |  | Busses 9187,9190,9193,9079 | Y
05TPIT0085 | Rio Grande City, add 28.8 MVar caps | Install Capacitor Banks at Bates, Falcon, Garza, and Rio Grande City. | IN-SERVICE | AEP GROUP 292 | AEP/TCC | Tim Stelljes 918-599-2653 | 1533 | 2006-06-16 | 2006-05-19 | 138 | 0 | 0 | 0 | 28.8 | STARR | [6 empty] | Y
06TPIT0150 | Dilley SS, Install -40/+50 Mvar SVC | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dean Meeks 918-599-2653 | 1776 | 2006-05-01 | 2006-05-24 | 69 | 0 | 0 | 0 | 90 | FRIO | [6 empty] | Y
05TPIT0043 | North Denton Conversion and Rebuild North Denton to Spring | Convert existing 138/69kv tie between Bepc and Tmpa buses at North Denton to 138kv, Rebuild North Denton to Spring line with 1033 conductor |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-03-06 | 2006-05-24 | 138 | 0 | 17.9 | 0 | 0 | DENTON | DENTON |  |  |  |  | 684680672682 | Y | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0211 | Lamar Blossum 138/69 kV autotransformer | Replace existing 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R502-WACF | 2006-05-15 | 2006-05-26 | 138 | 0 | 0 | 100 | 0 | LAMAR | [5 empty] | 1771, 1772 | Y
06TPIT0074 | Fayetteville-Pisek-Welcome-Salem | Convert the 24.1-mile Fayetteville(7286)-Pisek(7296)-Welcome(7577)-Salem(7289) 795 ACSR transmission line from 69-kV to 138-kV operation. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1006413 | 2006-06-30 | 2006-05-26 | 69 | 0 | 24.1 | 0 | 0 | FAYETTE | WASHINGTON |  |  |  |  | SEE PROJECT DESCRIPTION | Y
06TPIT0220 | Freeport area 69kV system upgrade, Phase 1. | Converted all 69 kV load at Velasco to 138 kV and rearrange connections to remove common mode outage of Velasco 69 kV autotransformers | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-06-30 | 2006-05-26 | 138 | 0 | 0.02 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  |  | 43360, 43370 | Y |  | No transformer capacity added.
05TPIT0090 | Nelson Sharpe, add 345/138 kV autotransformer | Construct Nelson Sharpe 345/138 kV substation in the Lon Hill to Rio Hondo 345 kV line and add a phase-shifting transformer at Nelson Sharpe in Davis 138 kV line | IN-SERVICE | AEP GROUP 294 | AEP/TCC | Tommy Antill 918-599-2653 | 1471 | 2006-05-31 | 2006-05-27 | 345 | 0 | 0 | 675 | 0 | KLEBERG | [6 empty] | Y
06TPIT0055 | W McAllen to S McAllen, reconductor 138 kV line | Reconductor West McAllen to South McAllen 138 kV with 795 ACSS. | IN-SERVICE | AEP GROUP 292 | AEP/TCC | Rich Haley 918-599-2653 | 1454 | 2006-05-28 | 2006-05-28 | 138 | 0 | 3.28 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
06TPIT0130 | North Alamo Distribution, upgrade 2 transformers & distribution equipment | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | IN-SERVICE | AEP GROUP 068 | AEP/TCC | Rich Haley 918-599-2653 | 1280 | 2006-04-28 | 2006-05-30 | 138 | 0 | 0 | 57.6 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
05TPIT0028 | Marquis 138 kV new substation and new 138 kV/69 kV autotransformer (100MVA) | New load serving and install a new 138 kV/69 kV autotransformer (100MVA) at Marquis substation |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2006-06-01 | 2006-06-01 | 138 | 0 | 0 | 100 | 0 | DALLAS | [5 empty] | 848, 852 | Y
05TPIT0029 | Marquis-Shiloh 138 kV line | Line upgrade |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2006-06-01 | 2006-06-01 | 138 | 0 | 0.67 | 0 | 0 | DALLAS | [5 empty] | 848, 830 | Y
05TPIT0027 | Fairdale/Kraft-Marquis 138 kV line | Line upgrade |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2006-06-01 | 2006-06-01 | 138 | 0 | 1 | 0 | 0 | DALLAS | [5 empty] | 805/836, 848 | Y
05TPIT0046 | Weil Tract SS, add 138 kV SS | Cut-in the Citgo North Oak Park to Lon Hill 138 kV transmission line into Weil Tract substation | IN-SERVICE | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1579 | 2006-06-01 | 2006-06-01 | 138 | 0 | 0 | 0 | 0 | NUECES | [6 empty] | Y
06TPIT0045 | Tennessee Colony 138 kV capacitor | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R327-WACF | 2006-05-15 | 2006-06-05 | 138 | 0 | 0 | 0 | 36.8 | ANDERSON | [5 empty] | 3281 | Y
06TPIT0254 | Karsten | Increased reactive capability to 106.7 MVAR | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-06-05 | 2006-06-05 | 138 | 0 | 0 | 0 | 6.7 | BRAZORIA | BRAZORIA |  |  |  |  | 44410 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0219a | Construct West Bay 138KV Mobil Substation, Phase 1. | Served substation by re-energizing ckt.48 from Stewart to West Bay mobil substation. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-07-01 | 2006-06-06 | 138 | 0 | 0 | 0 | 0 | GALVESTON | GALVESTON |  |  |  |  | 43520 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0190 | Nall Capacitor Addition | Install 27 MVAR Capacitors at 69 kV |  | 1-328303301 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 809 | 2006-06-06 | 2006-06-06 | 69 | 0 | 0 | 0 | 27 | BRAZOS | [5 empty] | 32872 | Y | There were no new transformers added with this project and/or this project was within an existing substation and there was no new transmission lines installed.
05TPIT0189 | East Capacitor Addition | Install 54 MVAR Capacitors at 69 kV |  | 1-328303321 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 418 | 2006-06-06 | 2006-06-06 | 69 | 0 | 0 | 0 | 54 | BRAZOS | [5 empty] | 32896 | Y | There were no new transformers added with this project and/or this project was within an existing substation and there was no new transmission lines installed.
05TPIT0036 | Highway 9, cut-in Nueces Bay to Morris 138 kV line | Cut-in the Nueces Bay to Morris Street 138 kV line into Highway 9 substation | IN-SERVICE | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1577 | 2006-06-01 | 2006-06-06 | 138 | 0 | 0 | 0 | 0 | NUECES | NUECES | [5 empty] | Y
04TPIT0127 | Weil Tract, bypass/cut-in Citgo NOP to Lon Hill 138kV line | Cut-in the Citgo North Oak Park to Lon Hill 138 kV transmission line into Weil Tract substation |  | AEP GROUP 041 | LCRA TSC / AEP | Michael Glueck 918-599-2653 | 1578, LCRA#1005717 | 2006-06-01 | 2006-06-08 | 138 | 0 | 0 | 0 | 0 | NUECES | [6 empty] | Y
07TPIT0100 | N Mercedes to N Weslaco, upgrade 69 kV to 138 kV Line | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station |  | AEP GROUP 068 | LCRA TSC / AEP | Rich Haley 918-599-2653 | 1266 | 2006-07-01 | 2006-06-08 | 69 | 0 | 5 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
06TPIT0214 | Canyon-San Marcos | Tap the Canyon(7200)-Camp Gary(7196) 69kV transmission line with the San Marcos substation 3 miles from Canyon. The Canyon-San Marcos line will terminate at the 138kV San Marcos bus (7192) and the Camp Gary-San Marcos line will terminate at the 69kV San Marcos bus (7199). Upgrade the Canyon(7200)-San Marcos(7192) 4/0-ACSR 69-kV transmission line to bundled 795-ACSR 138-kV. Relocate one of the 138/69-kV 45-MVA auto-transformers from Canyon (7200) to San Marcos(7192). |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1002336 | 2006-06-01 | 2006-06-09 | 138 | 0 | 3 | 45 | 0 | HAYS | [5 empty] | SEE PROJECT DESCRIPTION | Y
07TPIT0063 | E. Levee - Reagan St. 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M4039-WACF | 2006-05-15 | 2006-06-11 | 138 | 0 | 1.6 | 0 | 0 | DALLAS | DALLAS |  | 2004-04-02 | 2005-06-16 |  | 2482, 2819 | Y
06TPIT0192 | Franz | Installed new 138kV 43.2MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-24 | 2006-06-12 | 138 | 0 | 0 | 0 | 43.2 | HARRIS | HARRIS |  |  |  |  | 44261, 44262 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0002 | Harmony Hills to Castle Hills to Med. Center 138kV Reconductor | Reconductor existing 138 kV line with 2-795 ACSR & 2-1272 ACSR. |  |  | CPS | Gerald Ripps 210-353-2470 | T-0020 | Jun-06 | 2006-06-13 | 138 | 0 | 6.3 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5195 5080 5455 | Y |  | There are no transformers associated with this project
06TPIT0240 | Freeport | Increased reactive capability to 21.6MVAR | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-01 | 2006-06-13 | 69 | 0 | 0 | 0 | 14.4 | BRAZORIA | BRAZORIA |  |  |  |  | 42640 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0066 | Coronado-Graphite Mine-Lampasas | Upgrade the 27.5-mile Coronado(7086)-Graphite Mine(7084)-Lampasas(7064) 336 ACSR 138-kV transmission line to 795 ACSR. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1004373 | 2006-06-30 | 2006-06-15 | 138 | 27.5 | 0 | 0 | 0 | BURNET | LAMPASAS |  |  |  |  | SEE PROJECT DESCRIPTION | Y
06TPIT0193 | Needville | Installed new 69kV 7.2MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-15 | 2006-06-15 | 69 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  |  | 43000 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0260 | Obrien - Mason ckt.25 | Verified in-series equipment at Obrien and at Mason to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2006-06-25 | 138 | 0 | 0 | 0 | 0 | FORT BEND | HARRIS |  |  |  |  | 44510, 44450 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0259 | Spencer - Pasadena ckt.06 | Verified in-series equipment at Pasadena to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2006-06-26 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 43271, 43040 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0258 | Greens Bayou - Oates tap ckt.38 | Verified in-series equipment at Greens Bayou to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2006-06-26 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40720, 41192 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0136 | Santa Rosa, add 28.8 MVAR capacitor | Install capacitor banks at various locations in the East Valley area | IN-SERVICE | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1647 | 2006-06-01 | 2006-06-26 | 138 | 0 | 0 | 0 | 28.8 | CAMERON | [6 empty] | Y
06TPIT0073 | Andice-Glasscock | Construct a new 795 ACSR (220-MVA) 138-kV transmission line (approximately eleven miles) between the Andice(7522) and Glasscock(7523) substations and add two 138-kV circuit breakers at the Glasscock(7523) substation. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 241201 | 2006-06-30 | 2006-06-28 | 138 | 11 | 0 | 0 | 0 | WILLIAMSON |  |  | 2001-10-01 | 2001-11-01 | Endorsed | SEE PROJECT DESCRIPTION | Y
05TPIT0107 | Coffee Port, add 1-28.8 MVAR capacitor | Install capacitor banks at various locations in the East Valley area | IN-SERVICE | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1649 | 2006-07-01 | 2006-06-29 | 138 | 0 | 0 | 0 | 28.8 | CAMERON | [6 empty] | Y
06TPIT0078 | Sandy Creek | Construct a new 795 ACSR 69-kV transmission line (approximately three miles) between a new Sandy Creek(7127) substation and the Sunrise Beach(7400) substation. Add a 138/69-kV 45-MVA auto-transformer at the new Sandy Creek substation which is to be cut into the Ferguson(7126)-Pitsburg(7120) 138-kV transmission line. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1001623 | 2006-06-30 | 2006-06-30 | 69 | 2.6 | 0 | 45 | 0 | LLANO |  |  | 2003-09-01 | 2003-10-01 |  | SEE PROJECT DESCRIPTION | Y
08TPIT0058B | Tomball two 345/138 kV autotransformers. | Replaced two 600MVA Autotransformers (A1) and (A2) at Tomball with two 800MVA autos. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-06-30 | 2006-06-30 | 345 | 0 | 0 | 1600 | 0 | HARRIS | HARRIS |  | 2004-09-10 |  |  | 46500, 46510 | Y |  | Part of Houston area constraint mitigation project. No transmission circuits built, rebuilt or reconductored.
06TPIT0206 | Convert 69kV Ellington substation to a 138kV double tap substation. | Converted 69kV Ellington substation to a 138kV double tap substation. Tap Ellington into ckt.07 Webster-Garden Villas and ckt.91 P.H. Robinson-Cougar. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-30 | 2006-06-30 | 138 | 0.2 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 42581, 42582 | Y |  | No transformer capacity added.
05TPIT0095 | Rio Hondo, add 345/138 kV auto | Rebuild La Palma to Rio Hondo 138 kV with 2-795 ACSS, double circuit capable and add 345/138 kV autotransformer at Rio Hondo | IN-SERVICE | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1462 | 2006-05-31 | 2006-06-30 | 345 | 0 | 0 | 675 | 0 | CAMERON | [6 empty] | Y
06TPIT0114 | Nelson Sharpe, add 150 MVA PST in Davis line and 2-43.2 MVAR caps | Construct Nelson Sharpe 345/138 kV substation in the Lon Hill to Rio Hondo 345 kV line and add a phase-shifting transformer at Nelson Sharpe in Davis 138 kV line | IN-SERVICE | AEP GROUP 294 | AEP/TCC | Tommy Antill 918-599-2653 | 1628 | 2006-06-01 | 2006-06-30 | 138 | 0 | 0 | 150 | 86.4 | KLEBERG | [6 empty] | Y
05TPIT0083 | Frontera, add 2-57.6 MVAR caps | Install Capacitor Banks at Bates, Falcon, Garza, and Rio Grande City. | IN-SERVICE | AEP GROUP 292 | AEP/TCC | Rich Haley 918-599-2653 | 1534 | 2006-09-30 | 2006-06-30 | 138 | 0 | 0 | 0 | 115.2 | STARR | [6 empty] | Y
05TPIT0048 | Airline, add 1-57.6 MVAR caps | Install capacitor banks at various locations in the Corpus Chrisi area | IN-SERVICE | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1607 | 2006-06-01 | 2006-06-30 | 138 | 0 | 0 | 0 | 57.6 | NUECES | [6 empty] | Y
06TPIT0221 | Bluff Creek, Expand Bluff Creek to 345/138 kV Station with first 345/138 kV Auto | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | IN-SERVICE | AEP GROUP 341 | AEP/TNC | Ashley Beasley 918-599-2653 | 2072 | 2006-07-31 | 2006-06-30 | 345 | 0 | 0 | 675 | 0 | TAYLOR | [6 empty] | Y
06TPIT0213 | Bluff Creek, cut-in Red Creek to Mulberry Creek, 345 kV Termination | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | IN-SERVICE | AEP GROUP 341 | AEP/TNC | Ashley Beasley 918-599-2653 | 2011 | 2006-05-30 | 2006-06-30 | 345 | 0 | 0 | 0 | 0 | TAYLOR | [5 empty] | 6444, 6230 | Y
07TPIT0058 | Jewett to Watson Chapel Rebuild,Hilltop Lakes - Iola Conversion | Rebuild existing Jewett to Watson Chapel line with 1033,convert Hilltop lakes to Iola to 138KV operation |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-07-01 | 2006-07-01 | 138 | 0 | 21 | 0 | 0 | LEON | ROBERTSON |  |  |  |  | 333392 | Y |  | There is no reactive or transformer capability associated with this project
06TPIT0190 | Katy | Installled new 138kV 14.4MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-06 | 2006-07-05 | 138 | 0 | 0 | 0 | 14.4 | WALLER | WALLER |  |  |  |  | 44421 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
09TPIT0057 | Fayetteville-Willow Springs | Replace under-rated limiting line terminal equipment to increase Fayetteville (7286)-Willow Springs (7273) to the conductor's rating. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2009-06-30 | 2006-07-11 | 138 | 0 | 0 | 0 | 0 | FAYETTE | FAYETTE | [5 empty] | Y |  | This project is included with theMcNeil-Gilleland and Jollyville-Avery Ranch projects.
09TPIT0058 | Jollyville-Avery Ranch | Replace under-rated limiting line terminal equipment to increase Jollyville (9223)-Avery Ranch (7534) to the conductor's rating. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2009-06-30 | 2006-07-11 | 138 | 0 | 0 | 0 | 0 | WILLIAMSON | WILLIAMSON | [5 empty] | Y |  | This project is included with the McNeil-Gilleland and Fayetteville-Willow Springs projects.
06TPIT0217 | Flatonia-Plum | Replace under-rated limiting line terminal equipment at Flatonia (7248) to increase Flatonia (7248)-Plum (7274) to the conductor's rating. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2006-06-01 | 2006-07-11 | 138 | 0 | 0 | 0 | 0 | FAYETTE | FAYETTE | [5 empty] | Y
06TPIT0182 | Baytown | Installed new 138kV 120 MVAR capacitor bank on 138kV ckt.88 to Cedar Bayou. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-15 | 2006-07-14 | 138 | 0 | 0 | 0 | 120 | HARRIS | HARRIS |  |  |  |  | 40171 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0067 | Canyon-San Marcos | Upgrade the 3.0-mile section of the Canyon(7200)-Camp Gary(7196) 4/0-ACSR 69-kV transmission line between Canyon(7200) and San Marcos(7192) to bundled 795-ACSR 138-kV. Terminate the Camp Gary(7196) 69-kV transmission line at San Marcos(7199). Relocate one of the 138/69-kV 45-MVA auto-transformers from Canyon(7200) to San Marcos(7192). Retire one of the 138/69-kV 45-MVA auto-transformers at Canyon(7200). | The original Buda-San Marcos project was split into two separate projects: San Marcos-Canyon (LCRA TSC) and Buda-Canyon (see PEC TPIT) |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1002336 | 2007-07-30 | 2006-07-18 | 138 | 0 | 15 | 45 | 0 | HAYS | [5 empty] | SEE PROJECT DESCRIPTION | Y
05TPIT0080 | North Laredo SS, add 150 MVA PST on Asherton 138 kV line | Install a 150 MVA PST at North Laredo substation with capacitors at Asherton and North Laredo. | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Brian Johnson 918-599-2653 | 1440 | 2006-11-10 | 2006-07-28 | 138 | 0 | 0 | 150 | 0 | WEBB | [6 empty] | Y |  | Includes costs for 05TPIT00500 and 06TPIT0134
06TPIT0128 | Laredo BtB to Laredo Power Plant, Milo 138 kV cut-in | Construct 100 MW asynchronous interconnection with CFE, with a new 138 kV switching station. | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Don Kendall 918-599-2653 | 1711 | 2006-10-01 | 2006-07-28 | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB | [5 empty] | Y
05TPIT0050 | North Laredo SS, add 28.8 MVAR cap on source side of PST | Install a 150 MVA PST at North Laredo substation with capacitors at Asherton and North Laredo. | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Brian Johnson 918-599-2653 | 1452 | 2006-11-30 | 2006-07-28 | 138 | 0 | 0 | 0 | 28.8 | WEBB | [6 empty] | Y |  | Cost included in 05TPIT0080
06TPIT0134 | North Laredo SS, add 28.8 MVAR cap on load side of PST | Install a 150 MVA PST at North Laredo substation with capacitors at Asherton and North Laredo. | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Brian Johnson 918-599-2653 | 1689 | 2006-11-30 | 2006-07-28 | 138 | 0 | 0 | 0 | 28.8 | WEBB | [6 empty] | Y |  | Cost included in 05TPIT0080
07TPIT0053 | Weslaco SS to N Alamo, upgrade 69 kV line | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | Schedule Update | AEP GROUP 068 | LCRA TSC / AEP | Rich Haley 918-599-2653 | 282, LCRA#1003359 | 2006-07-30 | 2006-07-30 | 138 | 0 | 6 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
05TPIT0100 | Crist Road 138 kV new substation | New load serving |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2006-07-01 | 2006-07-31 | 138 | 0 | 0 | 0 | 0 | DALLAS | [5 empty] | 850 | Y
05TPIT0098 | Ben Davis-Crist Road 138 kV line | Line upgrade |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2006-07-01 | 2006-07-31 | 138 | 0 | 1.5 | 0 | 0 | DALLAS | [5 empty] | 968, 850 | Y
05TPIT0099 | Crist Road-McCree 138 kV line | Line upgrade |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2006-07-01 | 2006-07-31 | 138 | 0 | 5.5 | 0 | 0 | DALLAS | [5 empty] | 850, 835 | Y
05TPIT0049 | Big Foot, add 14.4 MVAR 138 kV capacitor | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | IN-SERVICE | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1450 | 2006-11-30 | 2006-07-31 | 138 | 0 | 0 | 0 | 14.4 | UVALDE | [6 empty] | Y |  | Includes costs for 06TPIT0201
06TPIT0201 | Big Foot, add 7.2 MVAR 69 kV capacitor | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | IN-SERVICE | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 2069 | 2006-11-30 | 2006-07-31 | 69 | 0 | 0 | 0 | 7.2 | UVALDE | [6 empty] | Y |  | Cost included in 05TPIT0049
06TPIT0157 | Jack County to Wise County Switch | Line from Jack County Plant to new station vicinity of Bridgeport | Construction/ROW delays |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-08-15 | 2006-08-01 | 138 | 16 | 0 | 0 | 0 | JACK | WISE |  |  | 2003-05-01 | 2003-08-01 | 579570 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0002 | Krum Switching Station | Install 138/69kv switching station at existing Krum 138kv station, route existing Decatur to Krum 69kv line into station |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-08-01 | 2006-08-01 | 138 | 0 | 0 | 60 | 0 | DENTON | [5 empty] | 1989670673 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0058C | Addicks 345/138 kV autotransformer. | Added second 600MVA Autotransformer (A2) at Addicks. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-15 | 2006-08-02 | 345 | 0 | 0 | 600 | 0 | HARRIS | HARRIS |  | 2004-09-10 |  |  | 45600, 45610 | Y |  | Part of Houston area constraint mitigation project. No transmission circuits built, rebuilt or reconductored.
08TPIT0031 | Channelview | Installed new 138kV 80 MVAR capacitor bank on 138kV ckt.84 to Jacintoport. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-15 | 2006-08-09 | 138 | 0 | 0 | 0 | 80 | HARRIS | HARRIS |  |  |  |  | 40282 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0174 | Gibbons Creek - Keith Switch 138 line: Reconductor | Reconductor 2 miles of line to increase capacity and provide alternate path of power into Bryan/College Station area | On schedule | 06TPIT0157 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T04011 | 2006-10-06 | 2006-08-26 | 138 | 0 | 2 | 0 | 0 | GRIMES | GRIMES | Tier 3 |  | 2004-04-20 |  | 2, 964 | Y
06TPIT0244 | Looped new 138/35kV substation near Magnolia Park into ckt.08 Magnolia Park to Ninth | Serve substation by looping into ckt.08 Magnolia Park - Ninth | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-09-01 | 2006-08-31 | 138 | 0.08 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47701 | Y |  | No transformer capacity added.
06TPIT0180 | Cap Rock: New 138 sub with ring bus and route Olinger - Greenvile line into sub | Construct a new 138 kV switching station to provide a source for Cap Rock Energy | On schedule |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05009 | 2006-08-06 | 2006-09-01 | 138 | 0 | 0 | 0 | 0 | HUNT |  | Tier 4 |  |  |  | 971 | Y
06TPIT0169 | Gibbons Creek to College Station Switch | Rebuild Iola to Booneville 69kv line with 795 or 1433 ACSS conductor and 138kv construction Route line into College Station Switch, establish Keith switch station near existing Keith 69kv station Route existing Gibbons Creek to Steep Hollow line into station |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-08-01 | 2006-09-01 | 138 | 0 | 26 | 0 | 0 | GRIMES | BRAZOS |  |  |  |  | 964,1,2,13,17,3200 | Y |  | There is no reactive or transformer capability associated with this project
07TPIT0146 | North Belt - Drilco ckt.67 | Verified in-series equipment rating at North Belt and Drilco to increase emergency rating. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-05-31 | 2006-09-12 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46110, 45740 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0147 | Drilco - Inteq ckt.67 | Verified in-series equipment at Drilco and Inteq to increase emergency rating. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-05-31 | 2006-09-12 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 45740, 45900 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0148 | Inteq- Intercontinental ckt.67 | Verified equipment at Inteq and Intercontinental to increase emergency rating. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-05-31 | 2006-09-12 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 45900, 45910 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0063 | Powell to Meridian | Rebuild exisiting Powell to Meridian 69kv line with 138kv const. |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-12-01 | 2006-10-01 | 69 | 0 | 9.7 | 0 | 0 | BOSQUE | BOSQUE |  |  |  |  | 327319 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0223 | Long Creek Switch | Construct 345 kV switching station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R620-WACF | 2006-11-01 | 2006-10-06 | 345 | 0 | 0.2 | 0 | 0 | SHACKELFORD | [5 empty] | 1437 | Y
05TPIT0181 | Big Lake Substation, reconfigure to five position ring bus | Reconfigure Big Lake 138 kV to ring bus | IN-SERVICE | AEP GROUP 238 | AEP/TNC | Brett Madison 918-599-2653 | 261 | 2006-11-10 | 2006-10-13 | 138 | 0 | 0 | 0 | 0 | REAGAN | [6 empty] | Y
06TPIT0117 | Sauer Dip to Silber Dip ckt.73 | Reconfigured Wirt, Echo and Sauer substations. Replaced overhead lines with underground | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-31 | 2006-10-19 | 138 | 0 | 6.2 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 44120, 44627, 44621, 44625, 44623, 44211, 44210, 44214, 44791, 44790, 44793, 44657, 46070 | Y |  | No transformer capacity added.
06TPIT0118 | Sauer Dip to Silber Dip ckt.81 | Reconfigured Wirt, Echo and Sauer substations. Replaced overhead lines with underground | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-31 | 2006-10-19 | 138 | 0 | 6 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 44120, 44626, 44622, 44620, 44624, 44212, 44215, 44213, 44792, 44795, 44794, 44656 | Y |  | Cost included in Sauer Dip to Silber Dip ckt.73 Project #06TPIT0117. No transformer capacity added.
08TPIT0058A | Greens Bayou 345/138 kV autotransformer. | Replaced 400MVA Autotransformer (A1) at Greens Bayou with 800MVA and swapped autotransformer (A1) and (A2) 138kV leads. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-11-01 | 2006-10-22 | 345 | 0 | 0 | 800 | 0 | HARRIS | HARRIS |  | 2004-09-10 |  |  | 40700, 40710 | Y |  | Part of Houston area constraint mitigation project. No transmission circuits built, rebuilt or reconductored.
06TPIT0253 | Disconnected Scott138KV Substation from CenterPoint Energy's system. | Disconnected customer owned Scott substation from CNP's ckt.60 Fort Bend - Orchard. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-10-22 | 2006-10-22 | 138 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND |  |  |  |  | 44630 | Y |  | Bus #44630 removed from the base cases. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0238 | White Oak - Heights ckt.34 | Raised conductors and partially reconductered ckt.34, and upgraded limiting equipment at Heights to increase thermal ratings | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-31 | 2006-10-25 | 69 | 0 | 4.4 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46620, 47680 | Y |  | No transformer capacity added.
05TPIT0081 | Hamilton Road 138 kV, add 150 MVA-PST on Sonora 138 kV line | Addition of a 150 MVA PST in the Hamilton Road to Sonora 138 kV line | IN-SERVICE | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1446 | 2007-05-31 | 2006-10-28 | 138 | 0 | 0 | 150 | 0 | VAL VERDE | [6 empty] | Y |  | Includes costs for 05TPIT0089
05TPIT0089 | Hamilton Road, add 2-14.4 MVar caps on source side of PST | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | IN-SERVICE | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1444 | 2007-05-31 | 2006-10-28 | 138 | 0 | 0 | 0 | 28.8 | VAL VERDE | [6 empty] | Y |  | Cost included in 05TPIT0081
07TPIT0080 | Zapata SS, add +/-25 MVAR DRCS | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dean Meeks 918-599-2653 | 1488 | 2006-09-30 | 2006-10-31 | 138 | 0 | 0 | 0 | 50 | ZAPATA | [6 empty] | Y
06TPIT0207 | Zapata SS, 6 BKR Ring Bus - 14.4 Cap Bank | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dean Meeks 918-599-2653 | 1488 | 2006-09-30 | 2006-10-31 | 138 | 0 | 0 | 0 | 28.8 | ZAPATA | [6 empty] | Y
06TPIT0163 | Odessa EHV 345/138 kV 300 MVA autotransformer replacement | Replace existing 300 MVA 345/138 kV autotransformer with a 450 MVA autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R291-WACF | 2007-05-07 | 2006-11-01 | 345 | 0 | 0 | 450 | 0 | ECTOR |  |  | 2006-06-26 | 2006-08-15 | N/A | 1026, 1027 | Y
07TPIT0183 | Stepehenville to Carlton Switch | Rebuild Stephenville to Carlton Switch 69KV line with 138kv const. And 795 conductor |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-11-01 | 2006-11-05 | 69 | 0 | 4.25 | 0 | 0 | ERATH | ERATH |  |  |  |  | 299297 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0086 | Paris Switch - Anna Switch 345 kV line and Valley S. Switching Station | Construct Paris Switch - Valley S. - Anna Switch 345 kV line and Valley S. Switching Station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R109A-WACF | 2006-11-06 | 2006-11-06 | 345 | 88.7 | 0 | 0 | 0 | LAMAR | COLLIN |  | 2002-05-01 | 2002-06-01 | 2001-09-01 | 1729, 1692, 1690, 2373 | Y
05TPIT0205 | Chinati, add 3.6 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | IN-SERVICE | AEP GROUP 213 | AEP/TNC | Brett Madison 918-599-2653 | 1767 | 2006-12-31 | 2006-11-09 | 69 | 0 | 0 | 0 | 3.6 | PRESIDIO | [5 empty] | 6682 | Y
05TPIT0041 | Falfurrias, add 28.8 MVAR caps | Addition 2x25 MVAR capacitor banks at Dilley and Falfurrias | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Dean Meeks 918-599-2653 | 1246 | 2006-11-10 | 2006-11-10 | 138 | 0 | 0 | 0 | 28.8 | FRIO | [6 empty] | Y
06TPIT0151 | Falurrias SS, add +/-25 MVAR DRCS | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dean Meeks 918-599-2653 | 1775 | 2006-11-10 | 2006-11-10 | 69 | 0 | 0 | 0 | 50 | BROOKS | [6 empty] | Y
07TPIT0010 | Centerville Switch - Parkdale 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M468-WACF | 2006-12-01 | 2006-11-14 | 138 | 0 | 16.8 | 0 | 0 | DALLAS | DALLAS |  | 2004-04-02 | 2005-06-16 |  | 2439, 2445, 2450, 2443, 2401, 2402, 2913, 2914, 2915, 2916 | Y
07TPIT0163 | Flewellen – Fort Bend ckt.09 | Verified conductors rating to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-12-15 | 2006-11-15 | 138 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND |  |  |  |  | 44231, 44100, 44280 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0176 | Ben Davis Sub: Add 345 terminal and install a 2nd 345-138 autotransformer | Expand 345 ring bus and add a 2nd 345-138 kV autotransformer | Problems scheduling clearences in the Garland area have contributed to the delay of the project. |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05008 | 2006-11-10 | 2006-11-26 | 345 | 0 | 0 | 600 | 0 | DALLAS | [5 empty] | 970, 968 | Y
06TPIT0173 | Ben Davis - Royse/Allen 138 line: Reconductor/Rebuild | Reconductor/Rebuild the 4 miles of this double circuit line which belongs to TMPA to increase rating on each circuit | Problems scheduling clearences in the Garland area have contributed to the delay of the project. | 06TPIT0032 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T04009 | 2006-11-10 | 2006-11-26 | 138 | 0 | 3.8 | 0 | 0 | DALLAS | COLLIN | Tier 4 |  | 2003-08-15 |  | 968, 2462 and 968, 2467 | Y
06TPIT0127 | Laredo BtB to Laredo Power Plant, Falfurrias 138 kV cut-in | Construct 100 MW asynchronous interconnection with CFE, with a new 138 kV switching station. | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Don Kendall 918-599-2653 | 1481 | 2006-12-31 | 2006-12-01 | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB | [5 empty] | Y
05TPIT0209 | Crane, add 57.6 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | IN-SERVICE | AEP GROUP 213 | AEP/TNC | Brett Madison 918-599-2653 | 1753 | 2007-03-31 | 2006-12-05 | 138 | 0 | 0 | 0 | 28.8 | CRANE | [5 empty] | 6615 | Y
07TPIT0194 | TH Wharton tap - Gears tap ckt.95 | Raised conductors to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-01-01 | 2006-12-07 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 45512, 45782 | Y |  | Part of Northwest Reliability Project, Phase 2, TPIT Project #05TPIT0237. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0033 | Power Plant 138-kV Substation | Relocate two 138/69-kV 60 MVA autotransformer from Militar Hwy |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2006-11-30 | 2006-12-07 | 138 | 0 | 0 | 120 | 0 | CAMERON | [5 empty] | 59300 | Y
07TPIT0030 | Military Hwy - Power Plant 138-kV Line | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2006-11-30 | 2006-12-07 | 138 | 0 | 2.29 | 0 | 0 | CAMERON | [5 empty] | 8339, 59300 | Y
07TPIT0032 | Military Hwy 138-kV Substation | Facilitate the substation for a new 138-kV Circuit to Power Plant substation |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2006-11-30 | 2006-12-07 | 138 | 0 | 0 | 0 | 0 | CAMERON | [5 empty] | 8339 | Y
06TPIT0248 | McDonald Road Switching Station | Construct 138 kV switching station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R625-WACF | 2006-12-31 | 2006-12-09 | 138 | 0 | 0.15 | 0 | 0 | GLASSCOCK | [5 empty] | 1135, 1354, 1032, 1360 | Y
06TPIT0012 | Venus - Liggett 345 kV line | Construct Venus - Liggett 345 kV line |  | M346 | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M571-WACF | 2006-12-15 | 2006-12-11 | 345 | 43.4 | 0 | 0 | 0 | ELLIS | DALLAS |  |  |  | 2001-08-01 | 1907, 1916 | Y
06TPIT0162 | Sandow Switch 345/138 kV autotransformer and 138 kV bus | Install 345/138 kV autotransformer and 138 kV bus |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R460-WACF | 2006-12-01 | 2006-12-12 | 345 | 0 | 0 | 600 | 0 | MILAM |  |  | 2006-03-15 | 2006-03-17 | 2006-10-17 | 3429, 3430 | Y
06TPIT0222 | Jefferson - South Channel ckt.06 | Upgraded in-series equipment at Jefferson and South Channel to increase emergency rating. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-12-31 | 2006-12-14 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 41240, 41370 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0229 | Bluff Creek, Expand Bluff Creek to 345/138 kV Station with second 345/138 kV Auto | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | IN-SERVICE | AEP GROUP 341 | AEP/TNC | Ashley Beasley 918-599-2653 | 2112 | 2006-12-15 | 2006-12-17 | 345 | 0 | 0 | 675 | 0 | TAYLOR | [6 empty] | Y
06TPIT0011 | Jacksboro Switch - W. Denton 345 kV line (Oncor Delivery portion) | Construct Jacksboro Switch - W. Denton 345 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R111-WACF | 2006-12-01 | 2006-12-20 | 345 | 72 | 0 | 0 | 0 | JACK | DENTON |  | 2003-08-25 | 2004-02-01 | 2004-04-01 | 1429, 988 | Y
05TPIT0237 | Northwest Reliability Project, Phase 2 | Converted Bammel to a sectionalized substation. Loop Bammel into ckt.67 TH Wharton - North Belt. Upgrade limiting equipment at TH Wharton East bus. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-12-30 | 2006-12-21 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 45651 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0256 | Bammel - Vetran tap ckt.67 | Raised conductors to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-12-21 | 2006-12-21 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 45651, 46551 | Y |  | Project cost included in Northwest Area Phase 2, Project #05TPIT0237. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0113 | Robstown tap to City of Robstown, rebuild 69 kV line | Rebuild the 69 kV line section from City of Robstown to Robstown tap with 336 ACSS | IN-SERVICE | AEP GROUP 027 | AEP/TCC | Michael Glueck 918-599-2653 | 84 | 2007-02-15 | 2006-12-21 | 69 | 0 | 0.74 | 0 | 0 | NUECES | NUECES | [5 empty] | Y
05TPIT0234 | Sandow - Rogers - Temple Switch 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R438-WACF | 2006-12-15 | 2006-12-28 | 138 | 0 | 38.7 | 0 | 0 | MILAM | BELL |  |  |  |  | 3675, 3430, 3415 | Y
06TPIT0236 | Flat Creek 138 kV Switch | Establish 138 kV switching station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R504-WACF | 2006-12-23 | 2006-12-28 | 138 | 0 | 0 | 0 | 0 | ERATH | [5 empty] | 1642, 1643 | Y
05TPIT0142 | Weil Tract SS, add 2-28.8 MVAR capacitors | Install capacitor banks at various locations in the Corpus Chrisi area | IN-SERVICE | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1666 | 2006-12-30 | 2006-12-30 | 138 | 0 | 0 | 0 | 57.6 | NUECES | [6 empty] | Y
06TPIT0202 | Crane, replace existing DRCS with +50/-40 MVAR DRCS | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | IN-SERVICE | AEP GROUP 213 | AEP/TNC | Brett Madison 918-599-2653 | 1788 | 2006-12-31 | 2007-01-01 | 69 | 0 | 0 | 0 | +50, -40 | CRANE | [5 empty] | 6615 | Y
07TPIT0056 | Hearne to Branchville Rebuild | Rebuild existing Hearne to Branchville with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-06-01 | 2007-01-05 | 69 | 0 | 9.6 | 0 | 0 | ROBERTSON | MILAM |  |  |  |  | 36,61 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0090 | Flatonia-Harwood | Increase the line-to-ground clearance on the Flatonia (7247) - Waelder (7232) - Thompsonville (7231) - Harwood (7230) 69 kV transmission line as necessary to increase the capacity of this circuit to its full conductor rating of 42 MVA. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2008-06-30 | 2007-01-18 | 69 | 0 | 24 | 0 | 0 | FAYETTE | GONZALES |  |  |  |  | SEE PROJECT DESCRIPTION | Y
06TPIT0237 | Bluff Creek, 138 kV Termination for Buffalo Gap | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | IN-SERVICE | AEP GROUP 341 | AEP/TNC | Ashley Beasley 918-599-2653 | 2013 | 2007-01-31 | 2007-01-31 | 138 | 0 | 0 | 0 | 0 | TAYLOR | TAYLOR | [5 empty] | Y
06TPIT0226 | W.A. Parish - Oasis ckt.99 | Expanded W. A. Parish and Oasis substations to separate parallel bundled 345 kV W.A. Parish - Oasis Ckt.99 into two separate circuits. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-02-05 | 2007-01-31 | 345 | 0.18 | 0 | 0 | 0 | FORT BEND | BRAZORIA |  |  |  |  | 44000 , 43035 | Y |  | No transformer capacity added.
07TPIT0111 | Bluff Creek, Add 90 MVAR SVC on Bluff Creek Auto tertiary | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | IN-SERVICE | AEP GROUP 341 | AEP/TNC | Ashley Beasley 918-599-2653 | 2075 | 2007-01-30 | 2007-01-31 | 345 | 0 | 0 | 0 | +50, -40 | TAYLOR | [6 empty] | Y
06TPIT0079 | Kendall-CPS Cagnon 345-kV line | Construct a 345 kV bundled 1590 ACSR line (approximately 45 miles) between Kendall (7046) and Cagnon (5056) | NOT AFFILIATED WITH AEP PROJECTS |  | LCRA TSC / CPS | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org / CPS Energy Don Stanton (210) 353-3125 DRStanton@cpsenergy.com | T-0026 | 2007-01-01 | 2007-01-31 | 345 | 45 | 0 | 0 | 0 | BEXAR | KENDALL |  | 2001-12-01 | 2001-12-01 | 2002-02-02 | 70465056 | Y
08TPIT0001 | Uvalde to Asphalt Mines, rebuild 138 kV line | Rebuild Uvalde to Hamilton Road 138 kV line from 4/0 to 795 ACSS |  | AEP GROUP 235 | LCRA TSC / AEP | Brian Johnson 918-599-2653 | 95, LCRA#1003627 | 2007-02-28 | 2007-02-01 | 138 | 0 | 14.39 | 0 | 0 | UVALDE | UVALDE | [5 empty] | Y
07TPIT0150 | Add new 69/12kV substation at Harrisburg. | Served substation by connecting to the 69kV bus @Harrisburg substation switchyard. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-02-28 | 2007-02-06 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40800 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0246 | Red Bluff 138 kV Substation | Construct Red Bluff Substation in the Vanderbilt to Danevang 138 kV line. Sub to have one 12/16/20 MVA 138/12 kV transformer and motor operated switches. | IN-SERVICE |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2007-02-07 | 2007-02-07 | 138 | 0 | 0 | 0 | 0 | JACKSON |  |  | N/A |  |  | 5588 | Y
08TPIT0037 | Asphalt Mines to Brackettville, rebuild 138 kV line | Rebuild Uvalde to Hamilton Road 138 kV line from 4/0 to 795 ACSS | Schedule Update | AEP GROUP 235 | LCRA TSC / AEP | Brian Johnson 918-599-2653 | 1716, LCRA#1003627 | 2007-02-28 | 2007-02-07 | 138 | 0 | 38.6 | 0 | 0 | KINNEY | UVALDE | [5 empty] | Y
07TPIT0209 | South Plant Substation 138-kV Substation - Will be in service at 69kV until south loop is converted to 138kV | New 138-kV Substation |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2007-02-21 | 2007-02-21 | 138 | 0 | 0 | 28 | 4.8 | CAMERON | [5 empty] | 59500 | Y | Substation will operate at 69-kV until upgrade is complete
05TPIT0047 | Dilley SS, add 2-57.6 MVAR caps | Addition 2x57.6 MVAR capacitor banks at Dilley and Falfurrias | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Dean Meeks 918-599-2653 | 1247 | 2007-02-27 | 2007-02-27 | 138 | 0 | 0 | 0 | 115.2 | BROOKS | [6 empty] | Y
07TPIT0208 | Obrien 345 kV sub. | Upgraded fault duty rating of Obrien 345 kV to at least 63kA | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-03-01 | 2007-03-01 | 345 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND |  |  |  |  | 44500 | N |  | Change is not applicable for the SSWG base cases.
06TPIT0040 | Denison North - Denison Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R138-WACF | 2007-05-15 | 2007-03-03 | 138 | 0 | 2.05 | 0 | 0 | GRAYSON | GRAYSON |  |  |  |  | 1739, 1743 | Y
06TPIT0013 | Cedar Hill Substation - DeSoto 138 kV line | Rebuild existing line for double-circuit operation |  | M269 | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M351-WACF | 2007-05-15 | 2007-03-05 | 138 | 6.2 | 6.2 | 0 | 0 | DALLAS | DALLAS |  |  |  |  | 2424, 2425, 3057, 3053 | Y
07TPIT0220 | Temple Switch 69 kV terminal equipment | Upgrade 69 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R482-WACF | 2007-05-01 | 2007-03-11 | 69 | 0 | 0 | 0 | 0 | BELL | [5 empty] | 3643 | Y |  | INCLUDED W/ R408B
07TPIT0125 | Temple Pecan Creek - Temple Switch 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R408B-WACF | 2007-05-15 | 2007-03-11 | 138 | 0 | 4.4 | 0 | 0 | BELL | BELL |  |  |  |  | 3415, 3420 | Y
06TPIT0124 | Anna Street, upgrade two transformers & distribution equipment | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Zacate Creek to 138 kV, convert Zacate Creek to 138 kV and transfer/convert Anna to 138 kV line | IN-SERVICE | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 1706 | 2007-03-14 | 2007-03-14 | 138 | 0 | 0 | 57.6 | 0 | WEBB | [6 empty] | Y
05TPIT0088 | Laredo to Anna Street, upgrade 69 kV Inner Loop to 138 kV ine | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Zacate Creek to 138 kV, convert Zacate Creek to 138 kV and transfer/convert Anna to 138 kV line | IN-SERVICE | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 51 | 2007-02-28 | 2007-03-14 | 138 | 0 | 3.17 | 0 | 0 | WEBB | WEBB | [5 empty] | Y
07TPIT0185 | WA Parish - Crabb River ckt.09 | Upgraded in-series equipment at Crabb River to increased thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-03-01 | 2007-03-19 | 138 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND |  |  |  |  | 44010, 44170 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0148 | STP - Dow ckt.18 and ckt.27 | Replaced 2000 Amp equipment on both circuits from STP to DOW. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-03-15 | 2007-03-20 | 345 | 0 | 0 | 0 | 0 | MATAGORDA | BRAZORIA |  | 2004-09-10 |  |  | 5915, 42500 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0009 | Pleasant Valley - Iowa Park Tap 69 kV line | Construct 69 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R126D-WACF | 2007-05-01 | 2007-03-23 | 69 | 12.2 | 0 | 0 | 0 | WICHITA | WICHITA |  |  |  |  | 1451, 1516, 1517, 1518 | Y
06TPIT0021 | Belton - Nolanville 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R029-WACF | 2007-05-06 | 2007-03-23 | 138 | 0 | 5.1 | 0 | 0 | BELL | BELL |  |  |  |  | 3610, 3617 | Y
07TPIT0217 | Roanoke Switch 138 kV terminal equipment | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5124A-WACF M5124B-WACF M5124C-WACF M5124D-WACF | 2007-05-01 | 2007-03-25 | 138 | 0 | 0 | 0 | 0 | DENTON | [5 empty] | 1850, 1852 | Y
07TPIT0255 | Hayes | Increased cap bank size to 14.4 MVAR | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-03-28 | 138 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  |  | 44312 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0143 | Colorado Bend Energy Center generating facility interconnection project, Phase I and Phase II. Built new 138kV Dyann substation. | Built a new 138 kV Dyann substation. Looped ckt.60 Wharton - South Lane into the new substation. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-04-30 | 2007-03-29 | 138 | 1.82 | 0 | 0 | 0 | WHARTON | WHARTON |  | 2006-03-29 |  |  | 42985, 48731, 48732, 48733, 48734, 48735, 48736 | Y |  | No transformer capacity added.
06TPIT0065 | Prairie Hill to Purdon Rebuild | Rebuild Prairie Hill to Purdon with 795 and 138KV construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-05-31 | 2007-04-01 | 69 | 0 | 24.24 | 0 | 0 | LIMESTONE | NAVARRO |  |  |  |  | 107194 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0101 | Bergstrom to Kingsbery Reconductor | Reconductor the existing circuit 1021 (Bergstrom to Kingsbery) with bundled 795 ACSR Drake conductors to increase the circuit capacity to 2000 Amperes. |  | N/A | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | 3230_117_4271 | 2007-04-01 | 2007-04-01 | 138 | 0 | 4 | 0 | 0 | TRAVIS | TRAVIS |  |  |  |  | Busses 9163,9123 | Y
07TPIT0081 | Pearson 69/138 kV Switching Station | Construct new Pearson 69/138 kV switching station with 83 MVA auto in the Quhi-Castroville 69 kV line where it crosses the CPS Hondo-Lytle 138 kV line | IN-SERVICE |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2007-04-01 | 2007-04-01 | 138 | 18.5 | 18.51 | 83 | 0 | MEDINA |  |  | N/A | N/A |  | 5805,5807,5290,5390 | Y
07TPIT0159 | Quail Switching Station | Construct 345 kV switching station. |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R626-WACF | 2007-04-16 | 2007-04-01 | 345 | 0 | 0.7 | 0 | 0 | ECTOR | [5 empty] | 1020, 1016,1030 | Y
06TPIT0219 | Construct West Bay 138KV Substation, Phase 2. | Served substation by extending ckt.48 and built a second circuit from Stewart to West Bay. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-03-31 | 2007-04-02 | 138 | 28 | 0 | 0 | 0 | GALVESTON | GALVESTON |  |  |  |  | 43520 | Y |  | No transformer capacity added.
06TPIT0140 | Elm Creek Switching Station | Install new 345 kV switching station at the intersection of the existing 345kV lines from STP-Skyline, STP-Hill Country, and both lines from Marion to San Miguel. | Project Delayed Due to Site Acquisition | T-0073 | CPS | Ulrich Skerhut 210-353-2923 | S-0188 | 2007-04-01 | 2007-04-02 | 345 | 0 | 0 | 0 | 0 | GUADALUPE | GUADALUPE |  |  |  |  | 5133 | Y |  | This is the substation work associated with project 06TPIT0172, transmission line miles are not included here
06TPIT0172 | Elm Creek Transmission Reroute | Reroute 345kV lines (STP- Skyline, STP- Hill Country, Marion, San Miguel) to connect with future Elm Creek Switchyard | Reroute dependent on Substation Construction | S-0188 | CPS | Ulrich Skerhut 210-353-2923 | T-0073 | 2007-04-01 | 2007-04-02 | 345 | 1 | 0 | 0 | 0 | GUADALUPE | GUADALUPE |  |  |  |  | 5133 | Y |  | There are no transformers associated with this project
06TPIT0230 | DeCordova - Everman 345 kV line upgrade | Upgrade existing 345 kV line to operate at an elevated conductor temperature |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5106-WACF | 2007-05-15 | 2007-04-04 | 345 | 0 | 34.4 | 0 | 0 | HOOD | TARRANT |  | 2005-03-01 | 2005-06-16 |  | 1888, 1887 | Y
07TPIT0219 | Temple 69 kV terminal equipment | Upgrade 69 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R486-WACF | 2007-05-01 | 2007-04-07 | 69 | 0 | 0 | 0 | 0 | BELL | [5 empty] | 3644 | Y
07TPIT0160 | Texas City, Freeway Park-Dickinson Transmission Upgrade | Reconductor 2-636 ACSR line running from Freeway Park to Dickinson to 2-636 ACSS conductor |  |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | GCEC26510 | 2007-03-01 | 2007-04-07 | 138 | 0 | 5.6 | 0 | 0 | GALVESTON | GALVESTON |  |  |  |  | 38820, 38850 | Y
07TPIT0221 | W. Waco 138 kV terminal equipment | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R481-WACF | 2007-05-01 | 2007-04-07 | 138 | 0 | 0 | 0 | 0 | MCLENNAN | [5 empty] | 3436 | Y
09TPIT0014 | Brackettville to Hamilton Road, rebuild 138 kV line | Rebuild Uvalde to Hamilton Road 138 kV line from 4/0 to 795 ACSS |  | AEP GROUP 235 | LCRA TSC / AEP | Brian Johnson 918-599-2653 | 1717, LCRA#1003627 | 2007-04-15 | 2007-04-07 | 138 | 0 | 29 | 0 | 0 | VAL VERDE | KINNEY | [5 empty] | Y
05TPIT0170 | Dansby to Atkins 138 reconductor | Reconductor an existing 138 to 1033 ACSR - Currently 477 and 636 ACSR |  |  | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 808 | 2007-05-01 | 2007-04-07 | 138 | 0 | 9 | 0 | 0 | BRAZOS | BRAZOS |  |  |  |  | 32862, 32897 | Y |  | There were no new transformers added with this project.
06TPIT0003 | Skyline - Replace 345kV Autotransformer #2 & #4 | Replace the two 480 MVA autotransformers(#2 & #4) with one 600 MVA autotransformer. | Project Delayed Due To Manufacturing Delays. |  | CPS | Darrell Clifton 210-353-4386 | S-0118 | 2007-04-07 | 2007-04-08 | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR |  |  |  |  | 5371 5369 5370 | Y |  | There is no transmission line additions associated with this project
07TPIT0206 | Fort Bend | Reduced cap bank size to 60MVAR. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-04-09 | 138 | 0 | 0 | 0 | -33.3 | FORT BEND | FORT BEND |  |  |  |  | 44300 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0102 | Camp Wood,add 69 kV SS & 2-3.6MVAR caps | Add 69 kV Capacitor at Camp Wood Substation with two 69 kV breakers for line terminations | IN-SERVICE | AEP GROUP 281 | AEP/TCC | Steve Guinty 918-599-2653 | 1395 | 2007-04-12 | 2007-04-12 | 69 | 0 | 0 | 0 | 7.2 | EDWARDS | [6 empty] | Y
06TPIT0008 | Venus - Sherry 345 kV line | Construct Venus - Sherry 345 kV line |  | M571 | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5032-WACF | 2007-05-15 | 2007-04-14 | 345 | 1.4 | 0 | 0 | 0 | ELLIS | TARRANT |  | 2006-05-25 | 2006-07-06 | 2006-10-17 | 1907, 1911, 1917 | Y
07TPIT0205 | Addicks | Increased cap bank size to 120MVAR | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-04-16 | 138 | 0 | 0 | 0 | 20 | HARRIS | HARRIS |  |  |  |  | 45620 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0203 | Laredo BTB Station, Rebuild and convert line to CFE to 230 kV. | Construct 100 MW asynchronous interconnection with CFE, with a new 138 kV switching station. | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Don Kendall 918-599-2653 | 1482 | 2007-04-16 | 2007-04-16 | 230 | 0 | 0.4 | 0 | 0 | WEBB | WEBB | [5 empty] | Y
07TPIT0164 | Golden 138 kV Switching Station | Establish new 138 kV switching station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R627-WACF | 2007-05-18 | 2007-04-18 | 138 | 0 | 0.22 | 0 | 0 | SCURRY | [5 empty] | 1064, 1067, 1315, 1068 | Y
08TPIT0052 | STP - Hillje ckt. | Built new 345 kV line from STP to Hillje. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-30 | 2007-04-18 | 345 | 19.4 | 0 | 0 | 0 | MATAGORDA | WHARTON |  | 2004-09-10 | 2004-11-01 | 2005-03-15 | 5915, 44330 | Y |  | No transformer capacity added.
06TPIT0049 | Centerville 69 kV to 138 kV voltage conversion, and its new 138 kV connections to McCree and Oates | Converts voltage for the substation and new 138 kV lines to McCree and Oates |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2007-04-19 | 2007-04-19 | 138 | 0 | 4.7 | 0 | 0 | DALLAS | [5 empty] | 810, 834, 831 | Y
07TPIT0189 | Tomball - Tomball tap ckt.66 | Verified conductors clearance to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-04-20 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46510, 46511 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0202 | Britmoore | Increased reactive capability to 134.4MVAR | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-04-26 | 138 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  |  | 44120 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
04TPIT0042 | Watermill - W. Levee (2nd) 345 kV circuit | Install Watermill - W. Levee (2nd) 345 kV circuit |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M462-WACF | 2007-05-01 | 2007-04-26 | 345 | 9 | 0 | 0 | 0 | DALLAS | DALLAS |  |  |  |  | 2398, 2997, 2427, 2428 | Y
07TPIT0177 | Weslaco SS bypass while upgrading North Weslaco Distribution | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | IN-SERVICE | AEP GROUP 068 | AEP/TCC | Rich Haley 918-599-2653 | 2208 | 2007-04-30 | 2007-04-30 | 138 | 0 | 0 | 0 | 0 | HIDALGO | [6 empty] | Y | Will be in-service temp for around 12 months and this is a bypass of Weslaco Switching Station between North Alamo to North Weslaco while work is being done to Weslaco.
06TPIT0085 | Royse - Terrell Switch 138/69 kV line | Rebuild existing 69 kV line for double-circuit with 69 kV and 138 kV circuits |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M359-WACF | 2007-05-15 | 2007-05-01 | 138 | 18.5 | 18.51 | 0 | 0 | ROCKWALL | KAUFMAN |  | 2004-04-02 | 2005-06-16 |  | 2471, 2721, 2722, 2729, 2463 | Y
07TPIT0184 | Hillje substation-related construction | For relocating the terminations at the STP corridor to accommodate the new Hillje substation. |  | 08TPIT0051 | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | 3230_117_4273 | 2007-06-01 | 2007-05-01 | 345 | 0 | 0 | 0 | 0 | BASTROP | BASTROP |  | 2004-09-01 | 2004-11-01 | 2005-03-01 | Busses 9073, 44200 | Y
06TPIT0035 | DeSoto 345/138 kV autotransformer | Install a 600 MVA 345/138 kV autotransformer at DeSoto |  | M351 | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M269-WACF | 2007-06-01 | 2007-05-01 | 345 | 0 | 0 | 600 | 0 | DALLAS | [5 empty] | 2431, 2424 | Y
07TPIT0004 | Plano Tennyson 345/138 kV autotransformer | Install a 600 MVA 345/138 kV autotransformer at Plano Tennyson |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M366-WACF | 2007-05-01 | 2007-05-01 | 345 | 0 | 0 | 600 | 0 | COLLIN |  |  | 2004-04-02 | 2005-06-16 |  | 2522, 2523 | Y
07TPIT0199 | West Chase | Installed new 138kV 14.4 MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-02 | 138 | 0 | 0 | 0 | 14.4 | HARRIS | HARRIS |  |  |  |  | 44760 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
06TPIT0249 | S.R. Bertron - Diabox ckt.22 | Verify conductors clearance and upgrade limiting equipment to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-05-01 | 2007-05-02 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 41405, 40480 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0204 | Seally | Installed new 138kV 10.8 MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-04 | 138 | 0 | 0 | 0 | 10.8 | AUSTIN | AUSTIN |  |  |  |  | 44640 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0142 | Built Quintana 69KV Substation | Serve substation by looping into ckt.47 Freeport - Surfsi | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-07 | 69 | 0 | 7.8 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  |  | 43135 | Y |  | No transformer capacity added.
07TPIT0193 | North Belt - Hidden tap ckt.95 | Upgraded limiting equipment at North Belt to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-05-30 | 2007-05-07 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46110, 45862 | Y |  | 1)_Part of Northwest Reliability Project, Phase 2 TPIT Project #05TPIT0237. 2)_No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0112 | Gibbons Creek Sub: Install breakers for autotransformers | Install breakers on the high side of T3 and low side of each autotransformer and reconfigure relaying | On schedule |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T06011 | 2007-05-15 | 2007-05-07 | 345 | 0 | 0 | 0 | 0 | GRIMES |  |  | 2005-09-01 | 2005-11-01 | 2006-01-01 | 967 & 964 | Y
07TPIT0196 | H.O. Clarke | Installed new 138kV 100 MVAR capacitor bank on 138kV ckt.90 to Garrott. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-09 | 138 | 0 | 0 | 0 | 100 | HARRIS | HARRIS |  |  |  |  | 47155 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0200 | Hockley | Installed new 138kV 26.7 MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-09 | 138 | 0 | 0 | 0 | 26.7 | HARRIS | HARRIS |  |  |  |  | 45880 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0192 | Galena - Crown - Jefferson ckt.94 | Upgraded in-series equipment at Crown and at Jefferson to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-10 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40612, 40400, 41240 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0169 | Barton 138 kV Switching Station | Establish new 138 kV switching station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R505A-WACF | 2007-05-25 | 2007-05-11 | 138 | 0 | 0 | 0 | 0 | JACK | [5 empty] | 1599, 1600 | Y
07TPIT0223 | Commerce Switch - Wolfe City 138 kV line | Rebuild existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R509-WACF | 2007-05-15 | 2007-05-14 | 138 | 0 | 12.7 | 0 | 0 | HUNT | HUNT |  |  |  |  | 1809, 1816 | Y
06TPIT0058 | Laredo BtB, build 100 MW CFE tie | Construct 100 MW asynchronous interconnection with CFE, with a new 138 kV switching station. | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Don Kendall 918-599-2653 | 1475 | 2007-05-13 | 2007-05-15 | 138 | 0 | 0 | 100 | 0 | WEBB | [6 empty] | Y |  | The scope of this project includes the ring bus, line cut-ins and connections to the Laredo Plant Station.
06TPIT0131 | North Mercedes Distribution, upgrade 2 transformers & distribution equipment | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | IN-SERVICE | AEP GROUP 068 | AEP/TCC | Rich Haley 918-599-2653 | 1282 | 2007-06-30 | 2007-05-15 | 138 | 0 | 0 | 25 | 0 | HIDALGO | [6 empty] | Y
06TPIT0147 | Smithers 345 kV sub. | Upgrade fault duty rating of Smithers 345 kV to at least 63kA | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-15 | 345 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND |  | 2004-09-10 |  |  | 44650 | N |  | 1)_Change is not applicable for the SSWG base cases. 2)_No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0146 | WAP 345 kV sub. | Upgrade fault duty rating of WAP 345 kV to at least 63kA | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-15 | 345 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND |  | 2004-09-10 |  |  | 44000 | N |  | 1)_Change is not applicable for the SSWG base cases. 2)_No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0212 | Graham 345 kV terminal equipment | Upgrade 345 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R633-F, R636-F | 2007-05-01 | 2007-05-17 | 345 | 0 | 0 | 0 | 0 | YOUNG | [5 empty] | 1430 | Y
07TPIT0216 | N. Wichita Falls 69 kV terminal equipment | Upgrade 69 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R508-WACF | 2007-05-01 | 2007-05-21 | 69 | 0 | 0 | 0 | 0 | WICHITA | [5 empty] | 1503 | Y
08TPIT0012 | Naaman-Apollo 69 kV line | Line upgrade |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2007-05-24 | 2007-05-24 | 69 | 0 | 5.66 | 0 | 0 | DALLAS | [5 empty] | 825, 800 | Y
06TPIT0044 | Temple - Troy 69 kV line | Upgrade 69 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R089-WACF | 2007-05-15 | 2007-05-24 | 69 | 0 | 6.1 | 0 | 0 | BELL | BELL |  |  |  |  | 3581, 3644 | Y
07TPIT0207 | Industrial | Installed new 138kV 7.2 MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-24 | 138 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  |  | 40841 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
06TPIT0020 | Stryker Creek - Jacksonville 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R362-WACF | 2007-06-01 | 2007-05-25 | 138 | 0 | 16.4 | 0 | 0 | CHEROKEE | CHEROKEE |  |  |  |  | 3110, 3112, 3253 | Y
07TPIT0226 | Graham Switching Station | Add circuit breakers |  | R505A | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R505B-WACF | 2007-05-15 | 2007-05-29 | 138 | 0 | 0 | 0 | 0 | YOUNG | [5 empty] | 1596 | Y
07TPIT0031 | Poage to Leon Junction Rebuild | Rebuild the existing Poage to Leon Junction 69KV line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-06-01 | 2007-06-01 | 69 | 0 | 24 | 0 | 0 | BELL | CORYELL |  |  |  |  | 126145 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0149 | Intercontinental- Westfield ckt.67 | Raise conductors and upgrade in-series equipment at Intercontinental and Westfield to increase emergency rating. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-06-01 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 45910, 46570 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0059 | North Weslaco Distribution, upgrade 2 transformers & distribution equipment | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | IN-SERVICE | AEP GROUP 068 | AEP/TCC | Rich Haley 918-599-2653 | 1281 | 2007-06-30 | 2007-06-01 | 138 | 0 | 0 | 12.5 | 0 | HIDALGO | [6 empty] | Y
07TPIT0243 | Abilene South to Bluff Creek, Reconductor 138 kV Line | Reconductor Abilene South to Bluff Creek 138 kV with with 1020 ACCC | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Ashley Beasley 918-599-2653 | 2198 | 2007-06-30 | 2007-06-01 | 138 | 0 | 18.5 | 0 | 0 | TAYLOR | TAYLOR | [5 empty] | Y
07TPIT0035 | New Berlin-Hickory Forest-Capote-Seguin | Convert the 21.4-mile New Berlin(7612)-Hickory Forest(7225)-Capote(7598) transmission line for 138-kV operation and disconnect the line from Capote. Convert the Capote-Seguin 69 kV line to a double-circuit transmission line by adding a new 5.6-mile 795 A |  |  | GVEC | David Tomczyszyn (830) 857-1110 dtomczyszyn@GVEC.org | Not yet assigned | 2008-06-30 | 2007-06-01 | 138 | 0 | 31.7 | 45 | 0 | GUADALUPE | GUADALUPE |  |  |  |  | SEE PROJECT DESCRIPTION | Y | SEE PROJECT DESCRIPTION
07TPIT0023 | Upgrade Seaton Autotransformer | Install second or larger auto at Seaton |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-10-01 | 2007-06-01 | 138 | 0 | 0 | 60 | 0 | BELL | [5 empty] | 130131 | Y |  | There is no right of way, circuit miles,conductor type,structure type,reactive capability or circuit breakers associated with this project
07TPIT0201 | South Houston | Installed new 69kV 7.2 MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-06-04 | 69 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  |  | 43170 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0222 | Wichita Falls 69 kV terminal equipment | Upgrade 69 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R507-WACF | 2007-05-01 | 2007-06-07 | 69 | 0 | 0 | 0 | 0 | WICHITA | [5 empty] | 1449 | Y |  | INCLUDED W/ R168A
08TPIT0063 | Branchville to Silver City Rebuild | Rebuild existing Branchville to Silver City 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2007-06-07 | 69 | 0 | 9.9 | 0 | 0 | MILAM | MILAM |  |  |  |  | 65,61 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0170 | Wells Branch 138kV substation | Establish a new 138kV Wells Branch substation with (2) 30MVA transformers. The substation will cut into existing LCRA's T-387 (Howard Ln - Round Rock S) and T-136 (McNeil - Round Rock). |  |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | 3240_117_4879 3230_117_2879 | 2007-06-01 | 2007-06-07 | 138 | 0.1 | 0 | 60 | 0 | TRAVIS | TRAVIS |  |  |  |  | Bus 9288 | Y
07TPIT0191 | Bayou - Bigbay ckt.79 | Verifed conductors clearance to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-02 | 2007-06-07 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 42160, 42180 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
06TPIT0175 | McCree Sub: Install 138 kV, 30 MVAR Cap Bank | Install new 30 MVAR, 138 kV capacitor bank | Larger projects were priorotized resulting in the delay of this project. |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T04002 | 2007-06-07 | 2007-06-07 | 138 | 0 | 0 | 0 | 30 | DALLAS |  | Tier 4 |  |  |  | 835 | Y
07TPIT0089 | Ben Davis - Royse 345 line: Reconductor | Reconductor 17 miles of line to increase capacity | Delivery of materials are contributing to delays on thi projects. |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05010 | 2007-06-07 | 2007-06-07 | 345 | 0 | 17 | 0 | 0 | DALLAS | ROCKWALL |  |  | 2005-06-16 |  | 970, 2461 | Y
07TPIT0061 | Verde Creek-Kerrville Stadium | Upgrade the 14.1-mile Verde Creek(7146)-Kerrville Stadium(7138) 336 ACSR 138-kV transmission line to 795 ACSR. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org | 1005354 | 2007-06-30 | 2007-06-08 | 138 | 0 | 14.01 | 0 | 0 | KERR | KERR |  |  |  |  | SEE PROJECT DESCRIPTION | Y
07TPIT0203 | Harrisburg | Installed new 69kV 7.2 MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-06-11 | 69 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  |  | 40800 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
06TPIT0091 | Forney - East Mesquite 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M285-WACF | 2007-05-01 | 2007-06-11 | 138 | 0 | 10.6 | 0 | 0 | KAUFMAN | DALLAS |  |  |  |  | 2438, 2756, 2769 | Y
07TPIT0198 | Alief | Installed new 138kV 7.2 MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-06-12 | 138 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  |  | 44020 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0197 | Crabb River | Installed new 138kV 14.4 MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-06-15 | 138 | 0 | 0 | 0 | 14.4 | FORT BEND | FORT BEND |  |  |  |  | 44170 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
06TPIT0156 | Laredo Heights to Anna Street, upgrade 69 kV inner loop to 138kV | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Heights to 138 kV, convert Heights to 138 kV and transfer/convert Anna to 138 kV line | IN-SERVICE | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 2001 | 2007-06-15 | 2007-06-15 | 138 | 0 | 1.96 | 80 | 0 | WEBB | WEBB | [5 empty] | Y
06TPIT0246 | Bluff Creek, Install 2 - 20 Mvar Reactors | Expand the Bluff Creek 345/138 kV station | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Ashley Beasley 918-599-2653 | 2133 | 2007-05-15 | 2007-06-15 | 138 | 0 | 0 | 0 | -40 | TAYLOR | [6 empty] | Y
08TPIT0051 | Hillje Switching Station | Built a new 345 kV Hillje substation. Loop ckt.1 STP-Holman into the new substation. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-30 | 2007-06-15 | 345 | 0 | 0.5 | 0 | 0 | WHARTON | WHARTON |  | 2004-09-10 | 2004-11-01 | 2005-03-15 | 44330 | Y |  | No transformer capacity added.
11TPIT0006 | Liggett 138 kV series reactors | Install 5-ohm 138 kV series reactors at Liggett in both circuits to Hackberry |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5119-WACF | 2007-06-15 | 2007-06-20 | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  | 2004-04-02 | 2005-06-16 |  | 1922, 1996, 1924, 2002 | N
06TPIT0061 | Weslaco Unit, add 1-28.8 Mvar cap | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substatio | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1322 | 2007-06-01 | 2007-06-27 | 138 | 0 | 0 | 0 | 28.8 | HIDALGO | [6 empty] | Y
06TPIT0177 | West Denton Sub: Construct 345 bus, add 2 line terminals and add a 2nd 345 auto | Expand 345 kV breaker and a half substation with line terminals for the Jacksboro line and N.W. Carrollton line. Add a 2nd 345-138 kV autotransformer | On schedule | 06TPIT0011 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T04010 | 2007-04-07 | 2007-06-28 | 345 | 0 | 0 | 600 | 0 | DENTON |  |  |  | 2004-01-21 |  | 988, 986 | Y
04TPIT0134 | Bates to Palmview, tap Palmhurst and upgrade 69 kV to 138 kV line | Convert Moore Field and Palmhurst substations from 69 kV to 138 kV and connect to North Edinburg to Bates 138 kV line | IN-SERVICE | AEP GROUP 292 | AEP/TCC | Bill Eakin 918-599-2653 | 1484 | 2007-07-15 | 2007-06-29 | 138 | 0 | 2 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
07TPIT0166 | Mountain Creek 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M4052-WACF | 2007-06-15 | 2007-06-29 | 138 | 0 | 0 | 0 | 110.4 | DALLAS | [5 empty] | 2411, 2412 | Y
06TPIT0152 | Menger Creek substation addition | Construct a new bundled 795 ACSR 138 kV transmission line approximately 4 miles in length from a tap point (7663) on the Boerne Cico (7151) -to- CPS Helotes (5200) transmission line to the proposed Menger Creek Substation (7665). | Not Affiliated With AEP Projects |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org | 1005925 | 2007-06-30 | 2007-06-29 | 138 | 4 | 0 | 0 | 0 | KENDALL |  |  | 2004-04-01 | 2004-04-01 | Endorsed | SEE PROJECT DESCRIPTION | Y
05TPIT0078 | Mustang Island to Port Aransas, rebuild 69 kV line | Rebuild North Padre to Port Aransas 69 kV transmission line from 4/0 ACSR to 795 ACSS |  | AEP GROUP 029 | LCRA TSC / AEP | Brad Woods (512) 369-4104 brad.woods@lcra.org | 1285, LCRA#1003910 | 2007-06-30 | 2007-06-30 | 69 | 0 | 8.3 | 0 | 0 | NUECES | NUECES | [5 empty] | Y |  | $ included in AEP project #140, LCRA project #1003910
06TPIT0159 | Peoria to Forreston Uprating | Rebuild the existing Peoria to Forreston 69kv line for a 100 deg C. operating temp. |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-06-01 | 2007-06-30 | 69 | 0 | 31 | 0 | 0 | HILL | HILL |  |  |  |  | 228224225 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0129 | Marion Circuit Breaker Replacement | Replace under-rated (IC) 345 kV circuit breakers at Marion (7044) |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2007-06-30 | 2007-06-30 | 345 | 0 | 0 | 0 | 0 | GUADALUPE |  |  | 2004-10-01 | 2004-10-01 | 2004-11-01 | SEE PROJECT DESCRIPTION | Y
07TPIT0176 | Port Lavaca 69 kV, add 1-7.2 MVAR Cap Banks | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2038 | 2007-07-01 | 2007-07-01 | 69 | 0 | 0 | 0 | 14.4 | Val VERDE | Val VERDE | [5 empty] | Y
05TPIT0084 | Falcon SS, add 14.4 MVAR capacitor | Install Capacitor Banks at Bates, Falcon, Garza, and Rio Grande City. | IN-SERVICE | AEP GROUP 292 | AEP/TCC | Bill Eakin 918-599-2653 | 1532 | 2007-06-15 | 2007-07-01 | 138 | 0 | 0 | 0 | 14.4 | STARR | [6 empty] | Y
06TPIT0224 | Lehigh | Construct a new 138 kV substation, Lehigh, near the existing Centex(7508) substation. Install a 138/69 kV 45 MVA auto-transformer at the Lehigh substation. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2007-06-30 | 2007-07-01 | 138 | 0 | 0 | 45 | 0 | HAYS | [5 empty] | SEE PROJECT DESCRIPTION | Y | The name of Kohler's Crossing Substaion has been changed to Lehigh Substation
07TPIT0181 | Navo Capacitor Bank | Install 35mvar 138kv capacitors at Navo | No room at Panther Creek to add cap bank |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-06-01 | 2007-07-01 | 138 | 0 | 0 | 0 | 37.5 | DENTON | [5 empty] | 662649 | Y |  | There are no circuit breakers, transmission line or transformer capacity associated with this project
05TPIT0167 | Palmhurst, upgrade second 69 kV distribution banks | Convert Moore Field and Palmhurst substations from 69 kV to 138 kV and connect to North Edinburg to Bates 138 kV line | IN-SERVICE | AEP GROUP 292 | AEP/TCC | Bill Eakin 918-599-2653 | 845 | 2007-07-15 | 2007-07-02 | 138 | 0 | 0 | 90 | 0 | HIDALGO | [6 empty] | Y
07TPIT0190 | Magnolia Park - University ckt.70 | Upgrade limiting equipment at Magnolia Park and at University to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-09-01 | 2007-07-03 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47700, 47751, 47750 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
07TPIT0187 | Galena - Gypsum tap ckt.20 | Verifed conductors clearance to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-07-03 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40611, 40751 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
04TPIT0025 | N. Edinburg to W. Edinburg, rebuild 138 kV line | Rebuild 138kV line from AEP N. Edinburg to MVEC W. Edinburg |  | 05TPIT0103 & 05TPIT0250 | STEC | Doug Evans 361-485-6459 devans@stec.org | 801145 | 2007-06-07 | 2007-07-05 | 138 | 0 | 4.6 | 0 | 0 | HIDALGO | HIDALGO |  | 2003-04-03 | 2003-06-06 |  |  | Y
06TPIT0149 | Beeville, add 2-14.4 Cap Banks | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 1773 | 2007-10-01 | 2007-07-23 | 69 | 0 | 0 | 0 | 40 | Val VERDE | [6 empty] | Y
07TPIT0171 | Sinton 69 kV, add 1-14.4 MVARCap Bank | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2033 | 2007-06-01 | 2007-07-28 | 69 | 0 | 0 | 0 | 14.4 | Val VERDE | Val VERDE | [5 empty] | Y
07TPIT0173 | Three Rivers 138 kV, add 1-28.8 MVAR Cap Bank | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2041 | 2007-07-01 | 2007-07-31 | 138 | 0 | 0 | 0 | 28.8 | Val VERDE | Val VERDE | [5 empty] | Y
08TPIT0053 | WAP - Hillje ckt. | Built new 345 kV double circuit line from WA Parish to Hillje. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-07-31 | 2007-07-31 | 345 | 97.84 | 0 | 0 | 0 | FORT BEND | WHARTON |  | 2004-09-10 | 2004-11-01 | 2005-03-15 | 44000, 44330 | Y |  | No transformer capacity added.
08TPIT0019 | Leon Junction to Santa Fe Sw. Rebuild | Rebuild existing Leon Junction to Santa Fe Sw. with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-06-01 | 2007-08-01 | 69 | 0 | 4.1 | 0 | 0 | CORYELL | CORYELL |  |  |  |  | 149145142 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0164 | Laredo Heights, upgrade two transformers & distribution equipment | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Heights to 138 kV, convert Heights to 138 kV and transfer/convert Anna to 138 kV line | IN-SERVICE | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 1996 | 2007-07-15 | 2007-08-01 | 138 | 0 | 0 | 80 | 0 | WEBB | [6 empty] | Y
05TPIT0186 | Zacate Creek, upgrade one transformer & distribution equipment | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Zacate Creek to 138 kV, convert Zacate Creek to 138 kV and transfer/convert Anna to 138 kV line | IN-SERVICE | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 1704 | 2007-08-10 | 2007-08-01 | 138 | 0 | 0 | 40 | 0 | WEBB | [6 empty] | Y
05TPIT0087 | Laredo to Zacate Creek, upgrade 69 kV to 138 kV line | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Zacate Creek to 138 kV, convert Zacate Creek to 138 kV and transfer/convert Anna to 138 kV line | IN-SERVICE | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 1302 | 2007-07-15 | 2007-08-01 | 138 | 0 | 2.61 | 0 | 0 | WEBB | WEBB | [5 empty] | Y |  | Scope of this project includes 50% of the Laredo Plant Station costs for the new 138kV line terminals
06TPIT0125 | Zacate Creek to Laredo Heights, upgrade 69 kV inner loop to 138kV | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Zacate Creek to 138 kV, convert Zacate Creek to 138 kV and transfer/convert Anna to 138 kV line | IN-SERVICE | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 1301 | 2007-07-15 | 2007-08-01 | 138 | 0 | 1.8 | 0 | 0 | WEBB | WEBB | [5 empty] | Y
07TPIT0128 | Bastrop West Capacitor Bank Addition | Install 138 kV, 31.2 MVAR shunt capacitor bank at Bastrop West(7555) |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2007-06-30 | 2007-08-02 | 138 | 0 | 0 | 0 | 31.2 | BASTROP | [5 empty] | SEE PROJECT DESCRIPTION | Y
07TPIT0079 | Hamilton, add +/-10 MVAR DRCS | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Brian Johnson 918-599-2653 | 1774 | 2007-08-01 | 2007-08-07 | 69 | 0 | 0 | 0 | 40 | UVALDE | [6 empty] | Y
06TPIT0053 | Rio Rico, add 10.8 Mvar cap | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1323 | 2007-08-31 | 2007-08-09 | 69 | 0 | 0 | 0 | 10.8 | HIDALGO | [6 empty] | Y
07TPIT0186 | Lamarque - West Galveston ckt.13 | Verifed conductors clearance to increase emergency rating to 72 MVA | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-08-15 | 2007-08-14 | 69 | 0 | 0 | 0 | 0 | GALVESTON | GALVESTON |  |  |  |  | 42860, 43410 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
06TPIT0241 | Velasco to Freeport ckt.47 | Raised conductors and partially rebuilt ckt.47 to increase thermal ratings | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-08-15 | 2007-08-15 | 69 | 0 | 4.32 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  |  | 43370, 42640 | Y |  | No transformer capacity to be added.
06TPIT0242 | Velasco to Surfsi ckt.10 | Raised conductors and partially rebuilt ckt.10 to increase thermal ratings | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-08-15 | 2007-08-15 | 69 | 0 | 2.46 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  |  | 43370, 43310 | Y |  | No transformer capacity to be added.
06TPIT0243 | Freeport to Surfsi ckt.47 | Raised conductors and partially rebuilt ckt.47 to increase thermal ratings | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-08-15 | 2007-08-15 | 69 | 0 | 1.79 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  |  | 42640, 43310 | Y |  | 1)_Project cost included in Project # 07TPIT0142, Service to Freeport LNG. 2)_No transformer capacity to be added.
06TPIT0129 | Laredo, add 2-57.6 MVAr caps | Construct 100 MW asynchronous interconnection with CFE, with a new 138 kV switching station. | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Don Kendall 918-599-2653 | 1220 | 2007-05-01 | 2007-08-28 | 138 | 0 | 0 | 0 | 115.2 | WEBB | [6 empty] | Y
05TPIT0123 | Military Highway, add 2-57.6 MVAR capacitors | Install capacitor banks at various locations in the East Valley area | IN-SERVICE | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1646 | 2007-10-31 | 2007-08-29 | 138 | 0 | 0 | 0 | 115.2 | CAMERON | [6 empty] | Y
07TPIT0218 | Spraberry Switch 138 kV terminal equipment | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R637-WAF | 2007-05-01 | 2007-09-27 | 138 | 0 | 0 | 0 | 0 | MIDLAND | [5 empty] | 1329 | Y
05TPIT0131 | Oak Hill 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Oak Hill substation. | Delay-Capacitor Contract Delay. |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | 3230_117_1443 | 2007-08-01 | 2007-10-01 | 138 | 0 | 0 | 0 | 31.2 | TRAVIS | TRAVIS |  |  |  |  | 9247 | Y
05TPIT0257 | College Station Spring Creek Substation | Build new distibution substation in the College Station Switch Station to Greens Prairie Substation line | Weather delays |  | COCS | Garry Lange 979 764 3682 glange@cstx.gov |  | 2007-09-07 | 2007-10-07 | 138 | 2 | 0 | 50 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | Y
07TPIT0088 | Sharyland HVDC Interconnect | Construct a 138 kV Transmission Line to implement a 150 MW High Voltage Direct Current Interconnection with Comision Federal De Electricidad. |  |  | SU | Mark E. Caskey, PE (956) 687-5600 mcaskey@su-power.com | PR.04.05067.CAP | 2007-09-22 | 2007-10-07 | 138 | 0.8 | 0 | 150 | 0 | HIDALGO | HIDALGO | Tier 2 |  |  |  | 8824, 8825 | Y | PUCT Approved CCN Docket 28834
07TPIT0211 | Dollarhide 138 kV terminal equipment | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R639-WAF | 2007-05-01 | 2007-10-16 | 138 | 0 | 0 | 0 | 0 | WINKLER | [5 empty] | 1149 | Y
07TPIT0254 | Matador: Install Breaker | Install Breaker/Upgrade Termination at Matador 69 kV station for IPP | IN-SERVICE | AEP GROUP 360 | AEP/TNC | Brett Madison 918-599-2653 | 2172 | 2007-09-30 | 2007-10-24 | 69 | 0 | 0 | 0 | 0 | MOTLEY | [6 empty] | Y
06TPIT0233 | North Emory (Formerly Liberty) 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R383-WAF | 2007-12-15 | 2007-10-26 | 138 | 0 | 0 | 0 | 18.4 | DELTA | [5 empty] | 3171 | Y
06TPIT0227 | Lamesa 138 kV capacitor | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R274B-WAF | 2007-12-15 | 2007-10-26 | 138 | 0 | 0 | 0 | 18.4 | DAWSON | [5 empty] | 1163 | Y
06TPIT0067 | Whitney to Covington Rebuild | Rebuild Whitney toCovington |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-11-01 | 2007-11-01 | 138 | 0 | 27.9 | 0 | 0 | BOSQUE | JOHNSON |  |  | 2003-12-01 | 2004-01-01 | 241444 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0057 | Hood - Spunky 138 Uprate or Rebuild | Uprate or rebuild with larger conductor the existing Hood to Spunky 138KV line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-12-01 | 2007-11-01 | 138 | 0 | 8.8 | 0 | 0 | HOOD | HOOD |  |  |  |  | 363356 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
09TPIT0026 | Upgrade Hasse 138/69 Autotransformer | Upgrade 40MVA 138/69KV auto at Hasse to 60 MVA |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2007-11-01 | 138 | 0 | 0 | 40 | 0 | COMANCHE | [5 empty] | 277, 1649 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
06TPIT0135 | Euless - Keller 138 kV line | Upgrade existing 138 kV line |  | M545 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M547-WACF | 2007-12-15 | 2007-11-02 | 138 | 0 | 28.8 | 0 | 0 | TARRANT | TARRANT |  |  |  |  | 565, 1957, 2016, 2026, 2027, 2029, 2034, 2035, 2037, 2038, 2050, 2051 | Y
07TPIT0109 | Midessa - Midland Airport 138 kV line upgrade | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R207-WACF | 2007-12-01 | 2007-11-02 | 138 | 0 | 7.2 | 0 | 0 | MIDLAND | MIDLAND |  |  |  |  | 1059, 1120 | Y
06TPIT0069 | Picacho, add 138 kV SS with 1-28.8 MVAR capacitor bank | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | IN-SERVICE | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1550 | 2008-08-31 | 2007-11-10 | 138 | 0 | 0 | 0 | 28.8 | VAL VERDE | [6 empty] | Y
07TPIT0237 | DeCordova - DeCordova Dam - Hood (BEC) 138 kV line (Oncor Electric Delivery section) | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5130-WACF | 2007-11-15 | 2007-11-11 | 138 | 0 | 3.3 | 0 | 0 | HOOD | HOOD |  |  |  |  | 2277, 1891 | Y
07TPIT0227 | Flat Creek - Lingleville - Stephenville 138 kV line | Rebuild existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R520B-WACF | 2007-12-07 | 2007-11-13 | 138 | 0 | 14.4 | 0 | 0 | ERATH | ERATH |  |  |  |  | 1640, 1641 | Y
07TPIT0103 | Six Street 138-kV Substation | Convert Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2007-11-16 | 2007-11-16 | 138 | 0 | 0 | 56 | 9.6 | CAMERON | [5 empty] | 59480 | Y
07TPIT0106 | Power Plant - Sixth Street 138-kV Line | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2007-11-16 | 2007-11-16 | 138 | 0 | 2.63 | 0 | 0 | CAMERON | [5 empty] | 59300, 59480 | Y
08TPIT0008 | Belton - South Harker Heights 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R449-WACF | 2007-12-15 | 2007-11-20 | 138 | 0 | 11.9 | 0 | 0 | BELL | BELL |  |  |  |  | 3610, 3633 | Y
07TPIT0235 | Nylon Tap - Olefin - General Tire 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R674-WACF | 2007-12-15 | 2007-11-20 | 138 | 0 | 1.4 | 0 | 0 | ECTOR | ECTOR |  |  |  |  | 1055, 1054, 1053 | Y
09TPIT0079 | Sixth St - South Plant 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2007-11-16 | 2007-11-28 | 138 | 0 | 2.7 | 0 | 0 | CAMERON | [5 empty] | 59480, 59500 | Y
09TPIT0080 | South Plant - Airport 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2007-12-03 | 2007-11-29 | 138 | 0 | 2.88 | 0 | 0 | CAMERON | [5 empty] | 59500, 59460 | Y
07TPIT0263 | Bellaire - Brays ckt.09 | Upgraded limiting equipment at Brays to increase thermal ratings. | IN-SERVICE | 08TPIT0156 | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-11-30 | 2007-11-30 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 47015, 47050 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. Cost included in Project #08TPIT0156, Increase thermal rating of ckt.09 HOC to Brays.
08TPIT0038 | Granbury to Stephenville Rebuild | Rebuild existing Granbury to Stephenville 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-12-01 | 2007-12-01 | 69 | 0 | 26.2 | 0 | 0 | ERATH | HOOD |  | 2006-10-25 | 2006-11-16 | N/A | 299303304305307 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0244 | Vega 138 kV substation | Establish a new 138kV substation by cutting into the existing Ckt 928 (Barton - Patton Lane) | Comments- The substation was energized in December as planned. |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | N/A | 2007-12-01 | 2007-12-01 | 138 | 0.1 | 0 | 50 | 0 | TRAVIS | TRAVIS |  |  |  |  | 9285 | Y
06TPIT0071 | Second Hawkins Auto | Install second auto at Hawkins for backup |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-12-01 | 2007-12-01 | 138 | 0 | 0 | 40 | 0 | COOKE | [5 empty] | 705707 | Y |  | There is no right of way, circuit miles,conductor type,structure type,reactive capability or circuit breakers associated with this project
07TPIT0165 | Lavon Switch 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3046-WA | 2007-11-15 | 2007-12-07 | 138 | 0 | 0 | 0 | 110.4 | COLLIN | [5 empty] | 2694 | Y
07TPIT0229 | Shamburger 345/138 kV autotransformer replacement | Replace existing 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R392-WAF | 2007-12-15 | 2007-12-07 | 345 | 0 | 0 | 724 | 0 | SMITH |  |  | 2007-04-10 | 2007-05-02 | N/A | 3103, 3104 | Y
07TPIT0245 | Convert Caney to a double tap substation | Converted Caney substation to a double tap configuration to improve reliability of the service provided to the customer and alleviated need for substation upgrade. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-12-31 | 2007-12-11 | 138 | 0.5 | 0 | 0 | 0 | WHARTON | WHARTON |  |  |  |  | 44130, 44131 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added.
07TPIT0228 | Odessa EHV - Odessa 2 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R208-WACF | 2007-12-15 | 2007-12-11 | 138 | 0 | 2.3 | 0 | 0 | ECTOR | ECTOR |  |  |  |  | 1027, 1126 | Y
07TPIT0240 | Stanton East 138 kV Switching Station | Construct 138 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R675-WAF | 2007-12-01 | 2007-12-14 | 138 | 0 | 0 | 0 | 0 | MARTIN | [5 empty] | 1326, 1023, 1324 | Y
07TPIT0062 | Cleburne W. 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M338-WAF | 2007-12-15 | 2007-12-17 | 138 | 0 | 0 | 0 | 18.4 | JOHNSON | [5 empty] | 2291 | Y
07TPIT0214 | Morgan Creek 345 kV terminal equipment | Upgrade 345 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R630-WAF, R631-WAF, R632-WAF | 2007-12-01 | 2007-12-17 | 345 | 0 | 0 | 0 | 0 | MITCHELL | [5 empty] | 1030 | Y
06TPIT0039 | DeLeon 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R107-WAF | 2007-12-15 | 2007-12-18 | 69 | 0 | 0 | 0 | 9.2 | COMANCHE | [5 empty] | 1633 | Y
07TPIT0066 | Itasca 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R452-WAF | 2007-12-15 | 2007-12-18 | 69 | 0 | 0 | 0 | 9.2 | HILL | [5 empty] | 3532 | Y
06TPIT0234 | Oak Creek 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R283-WAF | 2007-12-15 | 2007-12-18 | 69 | 0 | 0 | 0 | 9.2 | NOLAN | [5 empty] | 1406 | Y
06TPIT0088 | North Herty - Lufkin East 138 kV line | Upgrade existing 138 kV line to operate at an elevated conductor temperature |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R338-WACF | 2008-05-01 | 2007-12-19 | 138 | 0 | 9.47 | 0 | 0 | ANGELINA | ANGELINA |  |  |  |  | 3319, 3326 | Y
09TPIT0113 | Beeville, add +/-10 MVAR DRCS | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 1773 | 2007-12-10 | 2007-12-20 | 69 | 0 | 0 | 0 | 40 | BEE | [6 empty] | Y
06TPIT0231 | Ferris 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3028-WAF | 2007-12-15 | 2007-12-20 | 69 | 0 | 0 | 0 | 18.4 | ELLIS | [5 empty] | 2342 | Y
06TPIT0072 | McQueeney-New Berlin | Upgrade the 8.2-mile McQueeney(7606)-New Berlin(7612) 4/0 ACSR 69-kV transmission line to 795 ACSR 138-kV. |  |  | GVEC | David Tomczyszyn (830) 857-1110 dtomczyszyn@GVEC.org |  | 2007-11-30 | 2007-12-20 | 138 | 0 | 8.2 | 70 | 0 | GUADALUPE | [5 empty] | SEE PROJECT DESCRIPTION | Y | SEE PROJECT DESCRIPTION
07TPIT0145 | Wharton - Caney - East Bernard ckt.60 | Reconductored 138kV ckt.60 Wharton to East Bernard and upgraded limiting equipment at East Bernard to increase thermal ratings. Caney loop upgrade was excluded from this project. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-12-31 | 2007-12-21 | 138 | 0 | 14.9 | 0 | 0 | WHARTON | WHARTON |  |  |  |  | 43570, 44130, 44190 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project. 2)_No transformer capacity to be added.
07TPIT0167 | Mexia 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R479-WAF | 2007-12-15 | 2007-12-21 | 138 | 0 | 0 | 0 | 18.4 | LIMESTONE | [5 empty] | 3631, 3632 | Y
07TPIT0239 | Tonkawa 345 kV Switching Station | Construct 345 kV switching station |  | R677B | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R677-WAF | 2007-12-01 | 2007-12-21 | 345 | 0 | 0 | 0 | 0 | SCURRY | [5 empty] | 1030, 1430, 1048, 1049, 1057 | Y
08TPIT0091 | Lon Hill 138 kV, add 2-57.6 MVAR Cap Banks | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2039 | 2007-12-01 | 2007-12-27 | 138 | 0 | 0 | 0 | 115.2 | Val VERDE | Val VERDE | [5 empty] | Y
07TPIT0144 | Wharton - South Lane ckt.60 | Reconductored 138kV ckt.60 Wharton to South Lane and upgraded limiting equipment at South Lane. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-12-31 | 2007-12-28 | 138 | 0 | 10.88 | 0 | 0 | WHARTON | WHARTON |  |  |  |  | 43570, 44131, 42985, 43190 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project. 2)_No transformer capacity to be added.
07TPIT0264 | County Road 101, Install tap structures with switches | Interconnect Enterprise's Load to AEP's Permian Basin to Barrilla 138 kV line | IN-SERVICE | AEP GROUP 393 | AEP/TNMP | Brett Madison 918-599-2653 | 2270 | 2007-12-31 | 2007-12-31 | 138 | 0 | 0 | 0 | 0 | REEVES | [6 empty] | Y
07TPIT0168 | Burleson 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3044-WAF | 2007-12-15 | 2007-12-31 | 138 | 0 | 0 | 0 | 55.2 | TARRANT | [5 empty] | 2209 | Y
07TPIT0215 | Mulberry Creek 345 kV terminal equipment | Upgrade 345 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R634-WAF, R635-WAF | 2007-05-01 | 2007-12-31 | 345 | 0 | 0 | 0 | 0 | TAYLOR | [5 empty] | 6230, 6235 | Y
08TPIT0190 | New Berlin(7612)-Olmos(7613) (Wilson Tap) | Rebuild New Berlin(7612)-Olmos (Wilson Tap)(7613) 4/0 ACSR 69-kV transmission line to 795 ACSR and convert to 138-kV. Construct Olmos 69/138 kV switching station. Relocate the New Berlin Autotransformer to Olmos switching station. |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2008-12-01 | 2008-12-31 | 138 | 0 | 6.1 | 0 | 0 | WILSON | [5 empty] | See Project Title | Y
06TPIT0232 | Forney - Lake Hubbard 138 kV line | Upgrade existing 138 kV line to operate at an elevated conductor temperature |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4040-WA | 2008-12-15 | 2008-12-31 | 138 | 0 | 7.58 | 0 | 0 | KAUFMAN | DALLAS |  |  |  |  | 2438, 2934, 2402 | Y |  | Temporary upgrade completed in 2007 will be made permanent in 2008.
07TPIT0123 | Seagoville Switch - Lawson Rd. 138 kV line | Upgrade existing 138 kV line |  | M4038 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4042-WACF | 2008-12-01 | 2008-12-31 | 138 | 0 | 2.5 | 0 | 0 | DALLAS | DALLAS |  |  |  |  | 2434, 2779 | Y
08TPIT0173 | Lavon Switch second 138 kV capacitor installation | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3069-WACF | 2008-12-01 | 2008-12-31 | 138 | 0 | 0 | 0 | 36.8 | COLLIN | [5 empty] | 2694 | Y
06TPIT0235 | Rice 69 kV capacitor | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3025-WACF | 2008-12-01 | 2008-12-29 | 69 | 0 | 0 | 0 | 18.4 | NAVARRO | [5 empty] | 2347 | Y
08TPIT0106 | Gorman 69 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R514-WACF | 2008-12-01 | 2008-12-29 | 69 | 0 | 0 | 0 | 9.2 | EASTLAND | [5 empty] | 1630 | Y
08TPIT0112 | Tonkawa 345 kV Switching Station shunt reactor | Install 345 kV shunt reactor |  | R677 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R673B-WACF | 2008-12-01 | 2008-12-29 | 345 | 0 | 0 | 0 | -100 | SCURRY | [5 empty] | 1048 | Y
08TPIT0140 | Brownwood Switch - Goldthwaite 138 kV line | Reconductor existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R540-WACF | 2008-12-01 | 2008-12-22 | 138 | 0 | 29.54 | 0 | 0 | BROWN | MILLS |  |  |  |  | 1655, 7070 | Y
08TPIT0171 | No Trees 138 kV Switching Station | Construct new switching station to connect a new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R822-WACF | 2008-12-01 | 2008-12-22 | 138 | 0 | 0 | 0 | 0 | WINKLER | [5 empty] | 1146 | Y
09TPIT0111 | Bluff Creek to Oak Creek, Rebuild line | Rebuild the Bluff Creek to Oak Creek with 2X795 ACSS | IN-SERVICE | AEP GROUP 391 | AEP/TNC | Ashley Beasley 918-599-2653 | 2259 | 2009-01-31 | 2008-12-19 | 138 | 0 | 20.8 | 0 | 0 | TAYLOR | COKE | [5 empty] | Y
08TPIT0102 | Crandall 138 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3045-WACF | 2008-12-01 | 2008-12-19 | 138 | 0 | 0 | 0 | 55.2 | KAUFMAN | [5 empty] | 2727 | Y
07TPIT0124 | Seagoville Switch 345/138 kV autotransformer | Replace the existing 345/138 kV autotransformer |  | M4042 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4038-WACF | 2008-12-01 | 2008-12-19 | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 | 2006-09-27 | 2006-10-19 | N/A | 2433, 2434 | Y
08TPIT0142 | Elm Grove 138 kV new substation and load serving (load belongs to Oncor), and its 138 kV connections to Olinger and to Ben Davis | Elm Grove 138 kV new substation and load serving (load belongs to Oncor) |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-12-15 | 2008-12-17 | 138 | 0 | 20.1 | 0 | 0 | DALLAS | [5 empty] | 818, 2705, 968 | Y
08TPIT0103 | Eastland 69 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R512-WACF | 2008-12-01 | 2008-12-16 | 69 | 0 | 0 | 0 | 9.2 | EASTLAND | [5 empty] | 1622 | Y
09TPIT0041 | Collin - Custer (BEC) 138 kV line (Oncor Electric Delivery section) | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3029-WACF | 2015-05-15 | 2008-12-16 | 138 | 0 | 3.5 | 0 | 0 | COLLIN | COLLIN |  |  |  |  | 2370, 655 | N
08TPIT0176 | Custer (BEC) 138 kV loop line reconfigure | Convert 138 kV loop line into two radial lines |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3029-WA | 2008-12-01 | 2008-12-16 | 138 | 0 | 0 | 0 | 0 | COLLIN | [5 empty] | 2566, 2567 | Y
08TPIT0084 | Ballinger, Add distribution transformer and cap | Ballinger, Add 138/13.02 kV transformer, 14.4 Mvar 69 kV cap | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2149 | 2008-12-31 | 2008-12-15 | 138 | 0 | 0 | 0 | 14.4 | RUNNELS | [6 empty] | Y
08TPIT0175 | Comanche Peak capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R547-WACF | 2008-12-01 | 2008-12-11 | 138 | 0 | 0 | 0 | 18.4 | SOMERVELL | [5 empty] | 2278 | Y
09TPIT0169 | Tradinghouse terminal equipment | Replace terminal equipment on circuit to Lake Creek. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R716-WACF | 2008-12-01 | 2008-12-06 | 345 | 0 | 0 | 0 | 0 | MCLENNAN | [5 empty] | 3405 | Y
11TPIT0007 | Cibolo Creek - New 138kV Substation | Loop new 138kV substation into the existing 138kV Stonegate to Green Mountain line | Design/Build contract has been awarded | T-0110 | CPS | S: Bill Wards PM Ulrich Skerhut | S-0271 | 2008-12-01 | 2008-12-04 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5093 | Y |  | There are no transformers associated with this project
09TPIT0150 | Graham terminal equipment | Replace terminal equipment on circuit to Paint Creek. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R848-E | 2009-05-01 | 2008-12-01 | 138 | 0 | 0 | 0 | 0 | YOUNG | [5 empty] | 1431, 1371 | Y
08TPIT0184 | Lamesa Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment on lines to Holt Switch and Bluff Creek Switch. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R691-WACF - R694-WACF, R696-WACF & R697-WACF | 2008-11-15 | 2008-12-01 | 138 | 0 | 0 | 0 | 0 | DAWSON | [5 empty] | 1163 | Y
08TPIT0147 | Ajo to IPP, build 345 kV line | Build 345 kV switching station in the Nelson Sharpe to Rio Hondo 345 kV line and 345kV line from Ajo to IPP's | IN-SERVICE | AEP GROUP 343 | AEP/TCC | John Pulay 918-599-2653 | 2223 | 2008-11-30 | 2008-11-30 | 345 | 21.6 | 0 | 0 | 0 | KENEDY | KENEDY | [5 empty] | Y
08TPIT0205 | Longshore 345 kV Switching Station | Expand 345 kV switching station to connect additional wind farms |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R682B-WACF | 2008-11-21 | 2008-11-24 | 345 | 0 | 0 | 0 | 0 | HOWARD | [5 empty] | 1058 | Y
08TPIT0209 | Victoria: Generation Interconnect | Interconnect new generation at the Victoria substation, install a phase shifting transformer at Thomaston substation, and rebuild Magruder to North Victoria 69 kV Line | IN-SERVICE | AEP GROUP 402 | AEP/TCC | Dave Goetz 918-599-2653 | 3111 | 2008-11-15 | 2008-11-15 | 138 | 0 | 0 | 0 | 0 | VICTORIA |  | Tier 4 |  |  |  |  | Y |  | As of November, 2008, AEP transmission interconnection facilities are in-service. As of mid-January, 2009, the generating units at Victoria Plant are not yet commercially available.
08TPIT0083 | Clyde to Putnam, Rebuild 69 kV line | Rebuild the Clyde to Putnam 69 kV line | IN-SERVICE | AEP GROUP 354 | AEP/TNC | John Pulay 918-599-2653 | 2143 | 2008-11-30 | 2008-11-13 | 69 | 0 | 19.08 | 0 | 0 | CALLAHAN | CALLAHAN | [5 empty] | Y
06TPIT0081 | Airline to Laguna, rebuild 69 kV line | Rebuild Airline (8487) to Laguna (8494) 69 kV transmission line from 477 ACSR to 795 ACSR. |  | AEP GROUP 029 | LCRA TSC / AEP | Brad Woods (512) 369-4104 brad.woods@lcra.org | 4, LCRA#1003908 | 2008-11-11 | 2008-11-12 | 69 | 0 | 6.4 | 0 | 0 | NUECES | NUECES | Tier 4 |  |  |  |  | Y
08TPIT0179 | DeCordova terminal equipment upgrade | Upgrade 138 kV terminal equipment on 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5142-WACF | 2008-12-15 | 2008-11-10 | 138 | 0 | 0 | 0 | 0 | HOOD | [6 empty] | Y
08TPIT0174 | Tonkawa 345 kV Switching Station | Install 345 kV breakers to connect new wind farms |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R821-WACF | 2008-11-01 | 2008-11-05 | 345 | 0 | 0 | 0 | 0 | SCURRY | [5 empty] | 1048 | Y
08TPIT0137 | North Padre: Add 1-14.4 MVAR Cap Bank | North Padre: Add 1-14.4 MVAR 69KV Cap Bank and Termination Upgrades | IN-SERVICE | AEP GROUP 029 | AEP/TCC | Michael Glueck 918-599-2653 | 205 | 2008-11-03 | 2008-11-03 | 69 | 0 | 0 | 0 | 14.4 | ARANSAS |  | Tier 4 |  |  |  |  | Y
09TPIT0142 | Spur: Add 138 kV Terminal, upgrade relaying | Interconnect McAdoo Wind Farm at Spur substation, add 138 kV terminal, upgrade relaying, at Aspermont and Spur. | IN-SERVICE | AEP GROUP 395 | AEP/TNC | Dave Goetz 918-599-2653 | 3086 | 2008-11-30 | 2008-10-31 | 138 | 0 | 0 | 0 | 0 | DICKENS | [6 empty] | Y
08TPIT0154 | Cook Field Road 345 kV Switching Station | Construct new switching station to connect a new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R817-WACF | 2008-10-31 | 2008-10-31 | 345 | 0 | 0 | 0 | 0 | SHACKELFORD | [6 empty] | Y
07TPIT0233 | Anna Switch - Collin Switch 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3060-WACF | 2008-12-01 | 2008-10-30 | 345 | 0 | 13.2 | 0 | 0 | COLLIN | COLLIN | Tier 4 | 2006-10-10 | 2007-02-01 | 2007-04-01 | 2373, 2372 | Y
09TPIT0090 | Williamson County Capacitor Bank Additions | Add one 138 kV 31.2 MVAR capacitor bank at Avery Ranch(7534) and add one 138 kV 31.2 MVAR capacitor bank at Buttercup (7531). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-06-30 | 2008-10-22 | 138 | 0 | 0 | 0 | 62.4 | WILLIAMSON | [5 empty] | SEE PROJECT DESCRIPTION | Y
08TPIT0149 | Willow Valley 138 kV Switching Station | Construct new switching station to connect a new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R813-WACF | 2008-10-01 | 2008-10-03 | 138 | 0 | 0.23 | 0 | 0 | SCURRY | [5 empty] | 1048 | Y
09TPIT0168 | Temple Switch terminal equipment | Replace terminal equipment on circuit to Temple Pecan Creek. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R723-E | 2009-05-01 | 2008-10-01 | 138 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 3415 | Y
09TPIT0184b | La Marque to West Galveston Ckt. 13 removed and distribution load converted to be served from 138kV. | Disconnected both 138/69kV autotransfomers at West Galveston and Ckt.13 from La Marque to West Galveston. Converted distribution load from 69kV to 138kV. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-09-30 | 2008-09-30 | 138 | 0 | 0 | -183 | 0 | GALVESTON | GALVESTON |  |  |  |  | 43400, 43410, 42860 | Y |  | 1) Part of the Post-Ike Galveston area recovery plan. 2) Distribution load moved from bus 43410 to bus 43400. 3) Transformer capacity to be removed and no transmission circuits to be built, rebuilt or reconductored. 4) West Galveston 138kV ring bus to be rebuilt by May 2009 to reflect the pre-storm configuration @West Galveston.
08TPIT0134 | Ajo, Build 345 KV SS | Build 345 kV switching station with shunt reactors in the Nelson Sharpe to Rio Hondo 345 kV line and 345kV line from Ajo to IPP's | IN-SERVICE | AEP GROUP 343 | AEP/TCC | John Pulay 918-599-2653 | 2052 | 2008-09-30 | 2008-09-30 | 345 | 0 | 0 | 0 | -200 | KENEDY | [6 empty] | Y
09TPIT0091 | Giddings Capacitor Bank Addition | Add a 138 kV 31.2 MVAR capacitor bank at the Giddings (7302). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-06-30 | 2008-09-26 | 138 | 0 | 0 | 0 | 31.2 | LEE | [5 empty] | SEE PROJECT DESCRIPTION | Y
08TPIT0203 | Uprate White Baker to Rio Pecos | Rebuild existing 69kV line from White Baker to Rio Pecos to accommodate 300MW generation for 138kV interconnection at White Baker substation. Work will include changing out poles for clearance, and reconductoring from White Baker to Rio Pecos with 795 ACSS conductor. Building a new entrance to AEP Rio Pecos Plant to the 138kV bay. |  |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com | NTE 07207 | 2008-09-08 | 2008-09-08 | 69 | 0 | 14 | 0 | 0 | PECOS | CROCKETT |  |  |  |  | 38430, 6601 | Y
08TPIT0204 | White Baker Substation - Sherbino | Build new 138kV station at White Baker. The station will have 138kV ringbus section to serve Orion (BP) Sherbino Mesa Project and 69kV section to serve Northern Natural to White Baker. |  |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com | NTE 07207 | 2008-09-08 | 2008-09-08 | 138 | 0 | 0 | 70 | 0 | PECOS | PECOS |  |  |  |  | 38430, 38420 | Y
08TPIT0123 | Long Creek Switching Station circuit breakers | Install 345 kV circuit breakers |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R620B-WACF | 2008-08-01 | 2008-09-08 | 345 | 0 | 0 | 0 | 0 | SHACKELFORD | [5 empty] | 6230, 1435, 1437, 1430 | Y
08TPIT0207 | TXDOT Hwy 511 | Relocate 138kV line from Central Ave to East Rio Hondo Substation |  | 08TPIT0208 | STEC | Doug Evans 361-485-6459 devans@stec.org | 975628 | 2008-08-08 | 2008-08-31 | 138 | 0.75 | 0.19 | 0 | 0 | CAMERON | CAMERON | [5 empty] | Y |  | TXDOT Project to relocate line due to road widening
09TPIT0036 | Castroville - New 138kV Substation | Loop new 138kV substation into the existing 138kV TX Research to Lytle line | Design/Build contract has been awarded | T-0072 | CPS | PM: Ulrich Skerhut | S-0185 | 2008-09-01 | 2008-08-29 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5083 | Y |  | There are no transformers associated with this project
07TPIT0130 | Buda-Centex-Lehigh-Kyle-Canyon | Upgrade the 3.5-mile Lehigh-Buda(7498) 4/0-ACSR 69-kV transmission line to a 69/138 kV double circuit transmission line. One circuit will be 795 ACSR 69 KV and the other circuit will be bundled 795 ACSR 138 kV. The 69 kV circuit will terminate at Buda(7 |  | 06TPIT0224 | PEC | Randy Buchanan (830) 868-6058 |  | 2008-10-29 | 2008-08-08 | 138 | 3.5 | 12.2 | 0 | 0 | HAYS | [5 empty] | SEE PROJECT DESCRIPTION | Y | The name of Kohler's Crossing Substaion has been changed to Lehigh Substation
07TPIT0090 | Greenville: Construct new Shelby sub with 138-69 auto and re-route Royse line into new sub | Construct a new substation with a 138-69 kV autotransformer and route Royse line into sub | Construction Delays |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05012 | 2008-08-08 | 2008-08-08 | 138 | 4 | 0 | 150 | 0 | HUNT | HUNT |  |  |  |  | 960, 961 | Y
08TPIT0177 | Keller Wall Price 138 kV Capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5126-WACF | 2008-08-01 | 2008-08-04 | 138 | 0 | 0 | 0 | 110.4 | TARRANT | [6 empty] | Y
08TPIT0089 | Mill Creek - Gay Hill | Increase the line-to-ground clearance on the Mill Creek (7565) - Gay Hill (7572) 138 kV transmission line as necessary to increase the capacity of this circuit to its full conductor rating of 128 MVA. |  |  | BBEC | Eric Kocian (979) 542-4150 eric.kocian@bluebonnet.coop |  | 2008-08-02 | 2008-08-02 | 138 | 0 | 9.1 | 0 | 0 | WASHINGTON | WASHINGTON |  |  |  |  | SEE PROJECT DESCRIPTION | Y | SEE PROJECT DESCRIPTION
06TPIT0018 | Maypearl 69 kV capacitor | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R423-WACF | 2008-08-15 | 2008-08-01 | 69 | 0 | 0 | 0 | 27.6 | ELLIS | [5 empty] | 3536 | Y
08TPIT0114 | Plastipak 138 kV new substation | New load serving |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-07-31 | 2008-07-31 | 138 | 0 | 0 | 0 | 0 | DALLAS | [5 empty] | 808 | Y
08TPIT0115 | Plastipak-Fairdale 138 kV line | Line upgrade |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-07-31 | 2008-07-31 | 138 | 0 | 1.5 | 0 | 0 | DALLAS | [5 empty] | 808, 805 | Y
08TPIT0160 | Greens Bayou - Normandy Tap ckt.77 | Verified conductors clearance to increase thermal ratings. | IN-SERVICE |  | CNP | Danh Huynh; Dhuynh@garlandpower-light.org |  | 2008-07-30 | 2008-07-30 | 138 | 0 | 8.95 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40716, 41171 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
07TPIT0195 | Texas Gulf-New Gulf tap ckt.04 | Verified conductors clearance to increase thermal ratings. | IN-SERVICE |  | CNP | Danh Huynh; Dhuynh@garlandpower-light.org |  | 2008-12-01 | 2008-07-15 | 138 | 0 | 0 | 0 | 0 | WHARTON | WHARTON |  |  |  |  | 43340, 43011 | Y |  | 1) No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. 2) IDEV reflects change in project in-service date.
08TPIT0118 | South Lane City - New Gulf tap - Texas Gulf ckt.60 | Raised conductors to increase thermal ratings to 90/120deg C. | IN-SERVICE |  | CNP | Danh Huynh; Dhuynh@garlandpower-light.org |  | 2008-07-30 | 2008-07-15 | 138 | 0 | 10.56 | 0 | 0 | WHARTON | WHARTON |  |  |  |  | 43190, 43012, 43340 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
08TPIT0166 | Texas City 69F Reroute | Reroute 1.4 miles of 69 kV transmission line to outside of BP's Texas City Refinery | Construction has started for this project |  | TNMP | Danh Huynh; Dhuynh@garlandpower-light.org |  | 2008-07-08 | 2008-07-08 | 69 | 0 | 1.4 | 0 | 0 | GALVESTON | GALVESTON | [5 empty] | Y
06TPIT0165 | MVEC W. Edinburg-MVEC Palmhurst | Rebuild 138kV line from W. Edinburg to Palmhurst Substations | Material Issues | 04TPTI0025 | STEC | Doug Evans 361-485-6459 devans@stec.org | 791294 | 2008-12-08 | 2008-07-08 | 138 | 0 | 3.5 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
08TPIT0208 | TXDOT FM88 | Relocate 138kV line from MVEC Weslaco to AEP Weslaco Switch |  | 08TPIT0207 | STEC | Doug Evans 361-485-6459 devans@stec.org | 1189902 | 2008-09-08 | 2008-07-08 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | N |  | TXDOT Project to relocate line due to road widening. The line did not change.
07TPIT0065 | Gainesville - Muenster 69 kV line and Muenster 69 kV capacitors | Upgrade existing 69 kV line and install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R186-WACF | 2008-08-15 | 2008-07-01 | 69 | 0 | 13.84 | 0 | 18.4 | COOKE | MONTAGUE |  |  |  |  | 1709, 1712, 1716 | Y
05TPIT0044 | Asherton, add 14.4 MVAR cap on 138kV & 1-14.4 MVAR Cap on 69 kV | Install a 150 MVA PST at North Laredo substation with capacitors at Asherton and North Laredo. | IN-SERVICE | AEP GROUP 290 | AEP/TCC | Danh Huynh; Dhuynh@garlandpower-light.org | 1451 | 2008-05-08 | 2008-06-30 | 138 | 0 | 0 | 0 | 28.8 | DIMMIT | [6 empty] | Y
06TPIT0015 | Airline to Naval Base, rebuild 69 kV Line | Rebuild Airline to Naval Base 69 kV transmission line from 477 MCM to 795 ACSR |  | AEP GROUP 029 | LCRA TSC / AEP | Danh Huynh; Dhuynh@garlandpower-light.org | 3, LCRA#1003909 | 2008-06-15 | 2008-06-27 | 69 | 0 | 8 | 0 | 0 | NUECES | NUECES | [5 empty] | Y
08TPIT0119 | East Bernard - Orchard - Fort Bend ckt.60 | Reconductored 138kV ckt.60 East Bernard to Fort Bend and upgraded substations limiting equipment to increase thermal ratings. | IN-SERVICE |  | CNP | Danh Huynh; Dhuynh@garlandpower-light.org |  | 2008-06-30 | 2008-06-24 | 138 | 0 | 18.33 | 0 | 0 | WHARTON | FORT BEND |  |  |  |  | 44190, 44540, 44300 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added.
08TPIT0195 | Bandera - Add 69kV Breaker | Add 69kV Breaker to Bandera 69kV Bus |  |  | Bandera Electric | Brian Bartos | 115770 | 2008-06-08 | 2008-06-11 | 69 | 0 | 0 | 0 | 0 | BANDERA | BANDERA | [5 empty] | Y
09TPIT0078 | Loma Alta 138-kV Substation | Facilitate substation for a new 138/12.5-kV transformer | The Load has been installed instead on the 69-kV Bus. The substation upgrade to 138kV portion was part of another project. |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-06-02 | 2008-06-09 | 138 | 0 | 0 | 28 | 0 | CAMERON | [5 empty] | 5943 | Y
08TPIT0198 | Praxair Texas City #2 Station- TNMP 69-A Tap | TNMP will tap its existing 69kV line along SH146 to provide service to Praxair Texas City #2 Station | Line construction has been completed. Working on SCADA and Meter install. |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com |  | 2008-05-08 | 2008-06-08 | 69 | 0 | 0 | 60 | 0 | GALVESTON | GALVESTON |  |  |  |  | 39345, 39346 | Y
07TPIT0261 | County Rd 101 | Build 1.23 miles of 138 kV for retail service | Customer will be ready to take power on Oct-08 |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com |  | 2008-10-01 | 2008-06-08 | 138 | 1.23 | 0 | 0 | 0 | REEVES | REEVES |  |  |  |  | 6657, 38375 | Y
07TPIT0135 | Abilene Elm Creek to Abilene Shelton Street, Rebuild 69 kV line | Re-build 2.62 miles Abilene Elm Creek to Shelton 69 kV line @ 795 ACSS | IN-SERVICE | AEP GROUP 341 | AEP/TNC | John Pulay 918-599-2653 | 1989 | 2008-06-30 | 2008-06-02 | 69 | 0 | 2.62 | 0 | 0 | TAYLOR | TAYLOR | [5 empty] | Y
05TPIT0021 | Copperas Cove - Ding Dong (BEC) 138 kV line (Oncor Electric Delivery portion) | Construct 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R036A-WAC | 2008-07-01 | 2008-06-01 | 138 | 15.7 | 0 | 0 | 0 | CORYELL | BELL |  |  |  |  | 3630, 115, 3628, 3630 | Y
08TPIT0148 | Eskota Switching Station | Install 138 kV breaker to connect new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R806-WACF | 2008-07-01 | 2008-06-01 | 138 | 0 | 0 | 0 | 0 | HOWARD | [5 empty] | 1030, 1058, 1029 | Y
07TPIT0247 | Hillje 69 kV Substation | Construct Hillje Substation in the 69 kV line between Round Mott Switch and Louise. | IN-SERVICE |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2008-05-31 | 2008-05-31 | 69 | 0 | 0 | 0 | 0 | WHARTON |  |  | N/A |  |  | 5532 | Y
06TPIT0097 | Walnut 69 kV to 138 kV voltage conversion | Converts voltage for the substation |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-05-31 | 2008-05-31 | 138 | 0 | 0 | 0 | 0 | DALLAS | [5 empty] | 823 | Y
06TPIT0024 | Seaton - Poage 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R045-WACF | 2008-05-15 | 2008-05-30 | 69 | 0 | 11.9 | 0 | 0 | BELL | BELL |  |  |  |  | 131, 3635 | Y
05TPIT0143 | Weslaco SS, add 2-43.2 MVAR capacitor, cut-in Pharr to Harlingen SS 138 kV Line | Install capacitor banks at various locations in the East Valley area | IN-SERVICE | AEP GROUP 293 | AEP/TCC | Rich Haley 918-599-2653 | 1648 | 2008-09-30 | 2008-05-30 | 138 | 0 | 0 | 0 | 86.4 | CAMERON | [6 empty] | Y
08TPIT0191 | Olmito, Construct 138 kV Distribution Substation | Olmito: Construct a new substation with cut-in, between Military Highway and Palo Alto 138kV line | IN-SERVICE | AEP GROUP 255 | AEP/TCC | Rich Haley 918-599-2653 |  | 2008-08-29 | 2008-05-30 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
08TPIT0192 | Military Highway to Palo Alto 138kV line, cut-in Olmito at 138kV | Olmito: Construct a new substation with cut-in, between Military Highway and Palo Alto 138kV line | IN-SERVICE | AEP GROUP 255 | AEP/TCC | Rich Haley 918-599-2653 |  | 2008-08-29 | 2008-05-30 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
07TPIT0162 | S.R. Bertron - Fairmont ckt.06 | Raised conductors and partially reconductored ckt.06 to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-05-31 | 2008-05-30 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 41400, 41310, 41631, 42610 | Y |  | No transformer capacity to be added.
06TPIT0095 | Walnut-Fairdale line 69 kV to 138 kV voltage conversion | Converts voltage for the line |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-05-30 | 2008-05-30 | 138 | 0 | 1.92 | 0 | 0 | DALLAS | [5 empty] | 823, 803 | Y
07TPIT0075 | Add dynamic reactive device Phase 2 | Added dynamic reactive device at Crosby 138 kV bus | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-06-30 | 2008-05-23 | 138 | 0 | 0 | 0 | 140 | HARRIS | HARRIS |  | 2006-03-08 | 2006-07-12 | 2006-08-30 | 40392 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. IDEV reflects addition of the SVC model.
08TPIT0182 | Graham Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R542-WACF | 2008-05-01 | 2008-05-21 | 138 | 0 | 0 | 0 | 0 | YOUNG | [6 empty] | Y
06TPIT0245 | Bluff Creek, Install 1 - 57.6 Mvar Cap Bank | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Ashley Beasley 918-599-2653 | 2125 | 2008-05-15 | 2008-05-20 | 138 | 0 | 0 | 0 | 57.6 | TAYLOR | [6 empty] | Y
08TPIT0188 | Paul Davis Tap terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R695-WACF & R800-WACF | 2008-05-01 | 2008-05-20 | 138 | 0 | 0 | 0 | 0 | DAWSON | [6 empty] | Y
06TPIT0050 | Cagnon to Lytle - New 138 kV line | Build new 138 kV line from Cagnon to Lytle. This project has been broken out into 3 phases. Phase 1: Cagnon - TX Research (Dec07) Phase 2: TX Research - Lytle (May08) | 12 Step Public Review Caused Delay of Start | T-0072 | CPS | PM: Ulrich Skerhut 210-353-2923 | T-0011 | 2008-05-15 | 2008-05-16 | 138 | 21.7 | 0 | 0 | 0 | BEXAR | MEDINA |  |  |  |  | 5055 5083 5290 | Y |  | There are no transformers associated with this project
08TPIT0186 | Mustang Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R699-WACF | 2008-05-01 | 2008-05-16 | 138 | 0 | 0 | 0 | 0 | ANDREWS | [6 empty] | Y
07TPIT0174 | Morris 138 kV, add 1-28.8 MVAR Cap Bank | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2040 | 2008-05-15 | 2008-05-15 | 138 | 0 | 0 | 0 | 28.8 | Val VERDE | Val VERDE | [5 empty] | Y
06TPIT0228 | Athens load conversion and second 138 kV line | Convert load to 138 kV service and add second 138 kV source |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R369-WAC | 2008-05-01 | 2008-05-15 | 138 | 2 | 0 | 0 | 0 | HENDERSON | HENDERSON |  |  |  |  | 3239, 3238 | Y
08TPIT0139 | Longshore 345 kV Switching Station | Construct 345 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R682-WACF | 2008-05-15 | 2008-05-14 | 345 | 0 | 0.22 | 0 | 0 | HOWARD | [5 empty] | 1030, 1058, 1029 | Y
09TPIT0028 | Goldthwaite | Upgrade the 138-69 kV 25 MVA auto-transformer (T1) at the Goldthwaite substation(7070) to 45 MVA. |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org | Not yet assigned | 2008-06-29 | 2008-05-13 | 138 | 0 | 0 | 45 | 0 | MILLS | [5 empty] | SEE PROJECT DESCRIPTION | Y
06TPIT0144 | Add dynamic reactive device Phase 1 | Added dynamic reactive device at Bellaire South 138 kV bus | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-06-30 | 2008-05-12 | 138 | 0 | 0 | 0 | 140 | HARRIS | HARRIS |  | 2006-03-08 | 2006-07-12 | 2006-08-30 | 47016 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. IDEV reflects addition of the SVC model.
06TPIT0054 | Rangerville, add 7.2 Mvar cap | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1324 | 2008-05-08 | 2008-05-08 | 69 | 0 | 0 | 0 | 7.2 | CAMERON | [6 empty] | Y
08TPIT0017 | Olney to Shannon Rebuild | Rebuild the existing Olney to Shannon 69KV line with 795 138KV construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-05-01 | 69 | 0 | 28.5 | 0 | 0 | YOUNG | CLAY |  |  |  |  | 788776772 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0185 | Leon Switch terminal equipment upgrade | Upgrade 69 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R541-E | 2008-05-01 | 2008-05-01 | 69 | 0 | 0 | 0 | 0 | EASTLAND | [6 empty] | Y
07TPIT0139 | Temple Pecan Creek - Lake Creek 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R408A-WACF | 2008-06-01 | 2008-05-01 | 138 | 0 | 28.5 | 0 | 0 | BELL | MCLENNAN |  | 2007-04-23 | 2007-05-21 | N/A | 3410, 3420 | Y
07TPIT0241 | Drumright 138 kV Switching Station | Construct 138 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R671-WACF | 2008-05-31 | 2008-05-01 | 138 | 0 | 0 | 0 | 0 | GLASSCOCK | [5 empty] | 1335, 1336, 1331, 1328 | Y
08TPIT0178 | China Grove Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R687-WACF to R690-WACF | 2008-05-01 | 2008-05-01 | 138 | 0 | 0 | 0 | 0 | MITCHELL | [6 empty] | Y
08TPIT0141 | Manvel | Installed new 69kV 7.2 MVAR capacitor bank. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-05-31 | 2008-04-30 | 69 | 0 | 0 | 0 | 7.2 | BRAZORIA | BRAZORIA |  |  |  |  | 44440 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
04TPIT0148 | Walnut-Fairdale 69 kV line | Line upgrade |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-04-30 | 2008-04-30 | 69 | 0 | 2 | 0 | 0 | DALLAS | [5 empty] | 823, 803 | Y
06TPIT0099 | Fairdale load 69 kV to 138 kV voltage conversion | Converts voltage for its load |  |  | GARLAND | David Grubbs;Dgrubbs@garlandpower-light.org; |  | 2008-04-30 | 2008-04-30 | 138 | 0 | 0 | 0 | 0 | DALLAS | [5 empty] | 803 | Y
06TPIT0110 | Hidalgo to S McAllen, upgrade 69 kV line | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substatio | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1315 | 2008-06-30 | 2008-04-18 | 138 | 0 | 3.7 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
06TPIT0132 | Hidalgo, upgrade 2 transformers & distribution equipment | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1707 | 2008-05-31 | 2008-04-18 | 138 | 0 | 0 | 0 | 0 | HIDALGO | [6 empty] | Y
08TPIT0143 | Lampasas-Adamsville-Evant | Upgrade the Lampasas(7064)-Adamsville(7066)-Evant(7068) 138 kV transmission line (T-128) from 4/0 ACSR (84 MVA) to 795 ACSR (220 MVA |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2008-06-30 | 2008-04-15 | 138 | 0 | 26 | 0 | 0 | LAMPASAS | CORYELL |  | 2007-02-19 | 2007-03-12 | N/A | SEE PROJECT DESCRIPTION | Y
08TPIT0046 | Nolanville - Harker Heights 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R050-WACF | 2008-05-15 | 2008-04-15 | 138 | 0 | 7 | 0 | 0 | BELL | BELL |  |  |  |  | 3617, 3618 | Y
07TPIT0154 | Putnam, Replace existing 69/138 kV Autotransformer | Putnam, replace 69/138 kV Autotransformer with 90 MVA | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Dave Goetz 918-599-2653 | 2147 | 2008-04-30 | 2008-04-11 | 138 | 0 | 0 | 90 | 0 | CALLAHAN | [6 empty] | Y
09TPIT0089 | Waterport - Loma Alta 138-kV Circuit | Add a new 138-kV circuit to Loma Alta Substation |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-04-11 | 2008-04-11 | 138 | 0 | 4.29 | 0 | 0 | CAMERON | [5 empty] | 59450, 5962 | Y
08TPIT0100 | Twin Oak circuit breakers | Install 345 kV circuit breakers to connect a new power plant |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R498-WACF | 2008-06-01 | 2008-04-08 | 345 | 0 | 0 | 0 | 0 | ROBERTSON | [5 empty] | 3400, 13691, 13692 | Y
08TPIT0189 | Benbrook Switch terminal equipment upgrade | Upgrade 345 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5120-WACF | 2008-05-01 | 2008-04-07 | 345 | 0 | 0 | 0 | 0 | TARRANT | [6 empty] | Y
08TPIT0183 | Key Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R698-WACF & R805-WACF | 2008-05-01 | 2008-04-05 | 138 | 0 | 0 | 0 | 0 | DAWSON | [6 empty] | Y
08TPIT0197 | Reconfigure ckt.03 EXXON - S.R. Bertron and ckt.88 Baytown - Rohmas substation. | Reconfigured ckt.03 EXXON - S.R. Bertron and ckt.88 Baytown - Rohmas substation to create two new circuits ckt.03 EXXON - Baytown and ckt.88 S.R. Bertron - Rohmas to ensure reliable service to the customers in the Baytown area. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-04-10 | 2008-04-03 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40570, 40170, 41405, 41350 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0017 | Pancake to Gatesville Rebuild | Rebuild existing Pancake to Gatesville with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-06-01 | 2008-04-01 | 69 | 0 | 4 | 0 | 0 | CORYELL | CORYELL |  |  |  |  | 157158 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0039 | Hasse to Downing Upgrade/Rebuild | Rebuild or Upgrade existing Hasse to Downing line with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-04-01 | 69 | 0 | 7.3 | 0 | 0 | COMANCHE | COMANCHE |  |  |  |  | 277281 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
10TPIT0014 | Olney Auto | Increase 138/69 autotransformer capacity at Olney |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 | 2008-04-01 | 138 | 0 | 0 | 0 | 0 | YOUNT | [5 empty] | 788787 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
09TPIT0034 | Bunker to Hood Rebuild | Rebuild existing Bunker to Hood 138kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-06-01 | 2008-04-01 | 138 | 0 | 9.1 | 0 | 0 | HOOD | HOOD |  |  |  |  | 363352306 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0199 | Capote Substation (7598)- Convert to 138 kV Operation | 138 kV conversion involves switching, relocation of jumpers and other minor work. |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2008-04-01 | 2008-04-01 | 138 | 0 | 0 | 0 | 0 | GUADALUPE | [5 empty] | See Project Title | Y
08TPIT0180 | Exxon Sharon Ridge Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R802-WA & R803-WA | 2008-05-01 | 2008-04-01 | 138 | 0 | 0 | 0 | 0 | SCURRY | [6 empty] | Y
07TPIT0121 | Morgan Creek 345/138 kV autotransformer | Install third 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R608-WACF | 2007-12-01 | 2008-04-01 | 345 | 0 | 0 | 300 | 0 | MITCHELL |  |  | 2006-09-20 | 2006-10-18 | N/A | 1030, 1032 | Y
07TPIT0085 | Hi-Line to Hidalgo, upgrade 69 kV line to 138 kV | Add Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Stewart Road 69 kV to 138 kV and convert Hidalgo and Dyer substations to 138 kV | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1792 | 2008-03-31 | 2008-03-31 | 69 | 0 | 2 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
08TPIT0113 | Flatonia Autotransformer Addition | Add a new 138-69 kV 45 MVA autotransformer at the Flatonia substation (7248). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2008-06-30 | 2008-03-31 | 138 | 0 | 0 | 30 | 0 | FAYETTE | [5 empty] | SEE PROJECT DESCRIPTION | Y
09TPIT0040 | Jack Creek Sub: new 345 sub near Kurten | New 345 KV sub with one 600 MVA 345-138 autotransformer | On Schedule |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T06012 | 2008-05-07 | 2008-03-31 | 345 | 0 | 0 | 600 | 0 | BRAZOS |  |  | 2005-09-01 | 2005-11-01 | 2006-01-01 | ? | Y
08TPIT0181 | Gail Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R801-WACF & R804-WACF | 2008-05-01 | 2008-03-29 | 138 | 0 | 0 | 0 | 0 | BORDEN | [6 empty] | Y
08TPIT0159 | Satsuma - Gertie ckt.76 | Verified conductors clearance to increase thermal ratings. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2008-05-31 | 2008-03-26 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46302, 45802 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
07TPIT0117 | Seaway Teague - W. Fairfield 138 kV line | Upgrade existing 138 kV line |  | R478 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R478A-WACF | 2008-05-15 | 2008-03-25 | 138 | 0 | 13 | 0 | 0 | FREESTONE | FREESTONE |  | 2007-02-13 | 2007-03-06 | N/A | 3392, 3501, 3503 | Y
08TPIT0194 | Lane City: Upgrade Series Reactor to 2000 Amps | Upgrade Lane City substation bus and series reactors | IN-SERVICE | AEP GROUP 387 | AEP/TCC | Dave Goetz 918-599-2653 | 2234 | 2008-03-08 | 2008-03-24 | 138 | 0 | 0 | 0 | 0 | WHARTON | [6 empty] | Y
08TPIT0201 | Disconnect and remove Simson 69kV Substation from CenterPoint Energy's system. | Disconnected and removed customer owned Simson substation from CNP's ckt.23 Deepwater - S.R. Bertron. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-03-15 | 2008-03-18 | 69 | 0.02 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 40470, 41460,41415 | Y |  | 1)_No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. 2)_PSS/E bus #41460 will be removed from the base cases.
08TPIT0099 | Sandow Switch circuit breaker installation | Install 138 kV circuit breakers and terminate existing 138 kV lines |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R701-WACF | 2008-11-01 | 2008-03-17 | 138 | 0 | 0 | 0 | 0 | MILAM | [5 empty] | 13431, 13432, 13430, 13429 | Y
07TPIT0114 | E. Mesquite - W. Mesquite 138 kV line | Upgrade existing 138 kV line |  | M4038 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4041-WACF | 2008-04-30 | 2008-03-14 | 138 | 0 | 2.7 | 0 | 0 | DALLAS | DALLAS |  |  |  |  | 2754, 2756 | Y
00TPITno00 | Airport - Waterport 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-03-09 | 2008-03-09 | 138 | 0 | 8.8 | 0 | 0 | CAMERON | [5 empty] | 59460, 59450 | Y
00TPITno18 | Waterport 138-kV Substation | Convert Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-03-09 | 2008-03-09 | 138 | 0 | 0 | 28 | 0 | CAMERON | [5 empty] | 59450 | Y |  | `
07TPIT0105 | Airport Substation138-kV Substation | Convert Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-03-09 | 2008-03-09 | 138 | 0 | 0 | 28 | 0 | CAMERON | [5 empty] | 59460 | Y |  | The existing 138/69-kV and a 69/12.5-kV transformers will remain.
08TPIT0036 | Austrop to Decker Reconductor Last Three Spans of the circuit. | Reconductor the remaining three spans of Circuit 921 (Austrop to Decker) coming into the Decker Plant switchyard with triple bundle 795 ACSR Drake conductors. | Comments: The three spans have been replaced but the rerating will not be done until the breakers are changed out before Summer 2009. |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | PLAN_117_P003 | 2008-03-01 | 2008-03-08 | 138 | 0 | 0.58 | 0 | 0 | TRAVIS | TRAVIS |  |  |  |  | 9187, 7328 | Y
08TPIT0187 | Olefin Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R684-WACF - R686-WACF | 2008-05-01 | 2008-03-05 | 138 | 0 | 0 | 0 | 0 | ECTOR | [6 empty] | Y
06TPIT0104 | Convert Circuit 822 (Burleson to Cardinal Lane) and 824 (Cardinal Lane to Seaholm) from 69kV to 138kV. | Convert the 69kV circuit 822 (Burleson to Cardinal Lane) and Circuit 824 (Cardinal Lane to Seaholm) to 138kV capable of carrying at least 3000 Amps. | The reconductoring of both Circuit 822 and 824 is now complete. They will still operate at the 69kV level and switch to 138kV after the new Cardinal Lane substation completion in June 2008. |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | 3230_117_4268 3230_117_4269 3230_117_4274 3230_117_4275 | 2008-02-08 | 2008-03-01 | 138 | 0 | 5.7 | 0 | 0 | TRAVIS | TRAVIS |  |  |  |  | 9120,9179,9299, 9132 | Y
08TPIT0016 | Covington to Grandview Upgrade or Rebuild | Rebuild Covington to Grandview |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-03-01 | 138 | 0 | 9.9 | 0 | 0 | JOHNSON | JOHNSON |  |  |  |  | 444443436 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0155 | Putnam, Add 138 kV phase shift transformer | Putnam, Add 138 kV phase shift transformer on the Abilene South to Putnam 138 kV line | IN-SERVICE | AEP GROUP 354 | AEP/TNC | Dave Goetz 918-599-2653 | 2148 | 2008-03-10 | 2008-02-28 | 138 | 0 | 0 | 150 | 0 | CALLAHAN | [6 empty] | Y
05TPIT0077 | North Padre to Mustang Island, rebuild 69 kV line | Rebuild North Padre (8856) to Port Aransas (8436) 69 kV transmission line from 4/0 ACSR to 795 ACSS |  | AEP GROUP 029 | LCRA TSC / AEP | Brad Woods (512) 369-4104 brad.woods@lcra.org | 140, LCRA#1003910 | 2008-02-25 | 2008-02-25 | 69 | 0 | 6.7 | 0 | 0 | NUECES | NUECES |  |  |  |  | SEE PROJECT DESCRIPTION | Y
08TPIT0161 | Tomball - Tomball Distribution Tap ckt.81 | Verified equipment rating at Tomball to increase emergency rating. | IN-SERVICE |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2008-05-31 | 2008-02-15 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  |  | 46510, 46512 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
06TPIT0170 | College Station Post Oak Substation to Southwood Valley Substation Line Reconducter | Reconducter College Station Post Oak substation to Southwood Valley Substation with 1033 ACSS | Material Deliveries |  | COCS | Garry Lange 979 764 3682 glange@cstx.gov |  | 2008-02-08 | 2008-02-08 | 138 | 0 | 3 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | Y |  | Transmission Rebuilt on Line
05TPIT0256 | College Station Switch Station to Post Oak Substation Line Reconducter | Reconductor College Station Switch Station to Post Oak Station with 1033 ACSS | Material Deliveries |  | COCS | Garry Lange 979 764 3682 glange@cstx.gov |  | 2008-02-07 | 2008-02-08 | 138 | 0 | 1.7 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | Y |  | Transmission Rebuilt on Line
07TPIT0127 | Bandera to Hamilton Wolfe to Med. Center - Reconductor | Reconductor existing 138 kV line with 1-1272 ACSR. Phase 1: Med. Center to Hamilton Wolfe (Dec 07) Phase 2: Bandera to Hamilton Wolfe (Feb 08) | Distribution Conflicts & Budget Delays | T-0084 | CPS | PM: Ulrich Skerhut 210-353-2923 | T-0084 | 2008-02-08 | 2008-02-08 | 138 | 0 | 1.7 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5020 5300 5187 | Y |  | There are no transformers associated with this project
07TPIT0101 | Hi-Line to Stewart Rd tap, upgrade 69 kV line to 138 kV | Add Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Stewart Road 69 kV to 138 kV and convert Hidalgo and Dyer substations to 138 kV | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1791 | 2008-05-01 | 2008-01-25 | 69 | 0 | 3 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
05TPIT0075 | San Diego, add 69 kV breakers and 1 - 7.2 MVAR 69 kV cap | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2043 | 2007-11-30 | 2008-01-25 | 69 | 0 | 0 | 0 | 7.2 | JIM WELLS | [6 empty] | Y
06TPIT0059 | Stewart Road, build 138/69 kV SS with 2-28.8 MVar caps | Construct a new Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1318 | 2008-01-25 | 2008-01-25 | 138 | 0 | 0 | 93 | 57.6 | HIDALGO | [6 empty] | Y
06TPIT0120 | Stewart Rd to Hi-Line , build 138/69 kV double circuit line | Construct a new Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | IN-SERVICE | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1319 | 2008-01-25 | 2008-01-25 | 138 | 3 | 0 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | Y
08TPIT0144 | Glasscock Capacitor Bank Addition | Add a 138 kV 31.2 MVAR capacitor bank at Glasscock (7523). |  |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2008-06-30 | 2008-01-24 | 138 | 0 | 0 | 0 | 31.2 | WILLIAMSON | [5 empty] | SEE PROJECT DESCRIPTION | Y
07TPIT0179 | Paducah: Add a 20 MVAR 138 KV Shunt Reactor | Replace 69/138 kV auto at Paducah with an 90 MVA 69/138 kV with LTC and add 20 MVAR 138 kV shunt reactor | IN-SERVICE | AEP GROUP 289 | AEP/TNC | Brett Madison 918-599-2653 | 1994 | 2008-01-18 | 2008-01-18 | 138 | 0 | 0 | 0 | -20 | COTTLE | [6 empty] | Y
08TPIT0170 | Jewett - Seaway Teague 138 kV line | Upgrade existing 138 kV line |  | R478A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R478-WACF | 2008-05-01 | 2008-01-16 | 138 | 0 | 10.75 | 0 | 0 | LEON | FREESTONE |  | 2007-02-13 | 2007-03-06 | N/A |  | Y
12TPIT0001 | Texas Research Park - New Substation | Install new 138kV substation. May be part of T-0049 or T-0072. |  | S-0225 | CPS | PM: Janna Junkin 210-353-2524 | T-0072 | 2007-12-14 | 2008-01-09 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  |  | 5430 | Y |  | There are no transformers associated with this project
09TPIT0033 | Gatesville to Fort Gates Switch Rebuild | Rebuild existiing Gatesville to Fort Gates Switch 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-06-01 | 2008-01-01 | 69 | 0 | 7.5 | 0 | 0 | CORYELL | CORYELL |  |  |  |  | 157250 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0182 | Hilltop Lakes to Petteway Rebuild | Rebuild the existing Hilltop Lakes Switch to Petteway 69KV line with 795 and 138KV construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-01-01 | 2008-01-01 | 69 | 0 | 8.28 | 0 | 0 | ROBERTSON | ROBERTSON |  |  |  |  | 43,93 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0256 | Bethel Capacitor Bank | Install 7.2 mvar of capacitors at Bethel |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-12-01 | 2008-01-01 | 69 | 0 | 0 | 0 | 7.2 | ELLIS | [5 empty] | 204 | Y |  | There are no circuit breakers, transmission line or transformer capacity associated with this project
08TPIT0064 | Hood to Decordova Rebuild | Rebuild existing Hood to Decordova 138kv line | Brazos to rebuild TXUED portion of line |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-01-01 | 138 | 0 | 2.2 | 0 | 0 | HOOD | HOOD |  |  |  |  | 2277363 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project

## ERCOTTPIT5YearPlanProjects
Project Number | Project Name | Proposed in-service year | Status of Project | Associated TPIT ERCOT Project Number(s) | Notes
2007-R1 | Rothwood 345/138-kV switch station | 2010 | In Service | 09TPIT0086 | See the future construction projects tab for details (CNP) | Planning Stage
2007-R2 | Add a second 345/138-kV autotransformer at Forney | 2012 | Planning Stage |  | (ONCOR) | In RPG Process
2007-R3 | Roanoke Switch 345/138-kV autotransformer #1 upgrade | 2010 | In Service |  | (ONCOR) Scheduled for installation in 2009. | Canceled
2007-R4 | Roanoke Switch-Southlake 138-kV line upgrade | 2009 | Design Stage |  | (ONCOR) Scheduled for installation in 2011. | In Construction
2007-R5 | Liggett 345/138-kV autotransformer upgrade | 2012 | Planning Stage |  | (ONCOR) | Design Stage
2007-R6 | McCree-Shiloh 138-kV line upgrade | 2010 | Design Stage | 09TPIT0077 | This project will be delayed one year (GARLAND) | CCN
2007-R7 | Fairdale-Brand 138-kV line upgrade | 2012 | Design Stage | 10TPIT0038 | This project will be associated with the College-Brand 138-kV line upgrade project (GARLAND) and will be dalayed two years | In Service
2007-R8 | Lake Creek-Robinson 138-kV line upgrade | 2012 | Planning Stage |  | (ONCOR) Scheduled for installation in 2014.
2007-R9 | Coppell Tap-McKamy Tap 138-kV line upgrade | 2012 | Planning Stage |  | (ONCOR) Scheduled for installation in 2013.
2007-R10 | Construct a second McNeil-Summit 138-kV line | 2012 | Planning Stage | 08TPIT0034 | New proposal calls for reconductoring of the original circuit to 3000A and delayed to 2013..
2007-R11 | Cross Timbers-Roanoke 138-kV line upgrade | 2011 | Planning Stage |  | (BRAZOS)
2007-R12 | Add a second 345/138-kV autotransformer at Lewisville | 2012 | Planning Stage |  | (BRAZOS)
2007-R13 | Temple North-Temple Elm Creek 138-kV circuit reconfigure | 2009 | In Service |  | (ONCOR) Scheduled for installation in 2010.
2007-R14 | West Denton-Fort Worth-Teasley 138-kV upgrade | 2012 | Planning Stage |  | (TMPA)
2007-R15 | Anderson-Westover Hills 138-kV line upgrade | 2010 | Planning Stage | 11TPIT0025 | (CPS)
2007-E1 | East Bernard-Orchard-Fort Bend 138-kV line upgrade | 2009 | In Service | 08TPIT0119 | See the completed projects tab for details (CNP)
2007-E2 | Add a second 345/138-kV autotransformer at Concord | 2009 | In Service |  | (BRAZOS)
2007-E3 | Add a second 345/138-kV autotransformer at Whitney | 2010 | In Service |  | (BRAZOS)
2007-E4 | Nacogdoches Southeast-Lufkin Switch 345-kV line | 2012 | Planning Stage |  | (ONCOR)
2007-E5 | Moss-Odessa Southwest 138-kV line terminal equipment upgrade | 2009 | In Service |  | (ONCOR)
2007-E6 | South McAllen-Las Milpas 138-kV line upgrade | 2012 | Planning Stage | NA | This project may be impacted by potential IPP interconnection (AEP)
2007- E7a | Clear Crossing 345-kV Switch Station | 2009 | Planning Stage | 08TPIT0136 | (AEP)
2007- E7b | Lamesa area upgrades | 2010 | In RPG Process |  | (ONCOR)
2007- E7c | Paint Creek-Murray-Graham 138-kV line upgrade | 2011 | In Service |  | ONCOR completed terminal equipment upgrade at Graham in 2008.
2007- E7d | Barton-Oran 138-kV line series reactor | 2011 | Planning Stage |  | (ONCOR)
2007- E7e | Oklaunion-Bowman 345-kV line | 2012 | CCN | 11TPIT0061 | (ONCOR) CREZ Riley to Bowman project
2007-E7f | Red Creek-Killeen Switch 345-kV line | 2012 | CCN |  | (ONCOR & LCRA) Replaced by CREZ Twin Buttes - Brown and Brown - Killeen Switch 345 kV lines
2009-R1 | Moss-Westover 138-kV line upgrade | 2011 | Planning Stage |  |  | Planning Stage
2009-R2 | Crane 69-kV bus tie upgrade | 2011 | Design Stage | 11TPIT0120 | Pegasus 138 kV Tap and Point of Interconnection project replaces this project. | In RPG Process
2009-R3 | Ackerly-Lamesa upgrades | 2011 | In RPG Process | 11TPIT0060 |  | Canceled
2009-R4 | Odessa North-North Cowden 69-kV line upgrade | 2011 | Planning Stage | 14TPIT0009 |  | In Construction
2009-R5 | Holt-Emma Tap 69-kV line upgrade | 2011 | Planning Stage | 14TPIT0008 |  | Design Stage
2009-R6 | Odessa EHV third 345/138-kV autotransformer addition | 2011 | In Construction | 10TPIT0113 |  | CCN
2009-R7 | Close San Angelo Power Station 138-kV bus tie | 2010 |  |  |  | In Service
2009-R8 | Abilene South-Ballinger upgrades | 2010
2009-R9 | Montague-Johnson Switch-Bowie 69-kV line upgrade | 2011 | Planning Stage
2009-R10 | Olney-Rice Switch 138-kV line upgrade | 2011 | Planning Stage | 10TPIT0141
2009-R11 | Denton area 138-kV line upgrades | 2011
2009-R12 | Payne-M&M POI 138-kV line upgrades | 2012 | Planning Stage | 08TPIT0109
2009-R13 | Add a second Carrollton Northwest-Collin Switch 138-kV line project | 2013 | Planning Stage | 11TPIT0032
2009-R14 | Frisco-Collin Switch 138-kV line upgrade | 2012 | Design Stage | 08TPIT0068
2009-R15 | Collin Switch second 345/138-kV autotransformer addition | 2013 | Planning Stage | 09TPIT0042
2009-R16 | Austin Ranch #1-Colony 138-kV line upgrade | 2010 | Planning Stage | 10TPIT0018
2009-R17 | Lewisville second 345/138-kV autotransformer addition | 2012 | Planning Stage | 07TPIT0042
2009-R18 | Highland TNP-West TNP 138-kV line uprate | 2013
2009-R19 | Mesquite West-Mesquite Western Electric-Prairie Creek 138-kV line upgrade | 2012 | Planning Stage | 14TPIT0016
2009-R20 | Garland area 138-kV line upgrades | 2011
2009-R21 | West Levee 138-kV bus split | 2011 | Planning Stage
2009-R22 | Sargent Road-St. Augustine 138-kV line upgrade | 2011 | Planning Stage
2009-R23 | Industrial East-Compton-Cedar Crest East 138-kV line upgrade | 2011 | Planning Stage | 13TPIT0059
2009-R24 | Cedar Crest-South Oak Cliff 138-kV line upgrade | 2012 | Planning Stage
2009-R25 | Mayfield-Cedar Hill 138-kV line upgrade | 2011 | Planning Stage
2009-R26 | Cedar Hill second 345/138-kV autotransformer addition | 2011 | Planning Stage | 13TPIT0062 | Addition of a second autotransformer has been deferred because the existing autotransformer failed and was replaced by a larger autotransformer.
2009-R27 | Randol Mill-Hemphill 138-kV line terminal equipment upgrade | 2011 | Planning Stage
2009-R28 | Hicks 345/138-kV autotransformer and 138-kV line project | 2013 | Planning Stage
2009-R29 | Downing-Mountary 69-kV line upgrade | 2014 | Planning Stage
2009-R30 | Robinson-Robinson Northwest 138-kV line upgrade | 2012 | Planning Stage
2009-R31 | Belton-Belton Southwest 138-kV line upgrade | 2011 | Planning Stage
2009-R32 | Killeen Switch-Killeen South-Killeen Fort Hood Tap 138-kV line upgrade | 2011 | Planning Stage |  | Killeen Switch - Killeen South 138 kV line upgrade is planned for 2011. The Killeen South - Killeen Fort Hood Tap 138 kV line upgrade is under study.
2009-R33 | Hutto Switch second 345/138-kV autotransformer addition | 2013 | Planning Stage
2009-R34 | Gilleland Creek 138-kV bus tie upgrade | 2014
2009-R35 | Whitestone-Buttercup 138-kV line upgrade | 2013
2009-R36 | McNeil-Summit-Williamson 138-kV line upgrade | 2013 | Planning Stage | 08TPIT0034 | McNeil to Summit upgrade is scheduled for May 2012
2009-R37 | Elkton-Tyler Bullard-Tyler Loop 138-kV line terminal equipment upgrade | 2014 | Planning Stage | 09TPIT0170
2009-R38 | PH Robinson-Alta Loma 138-kV line upgrade | 2012 | Design Stage | 10TPIT0126
2009-R39 | Alvin area 138-kV line reliability upgrades | 2013
2009-R40 | Galveston area 138-kV line upgrades | 2011 | Design Stage | 11TPIT0074
2009-R41 | Texas City Water-Intercity-Lamarque 69-kV line upgrade | 2011
2009-E1 | Scurry County upgrades | 2014
2009-E2 | Midland East-Stanton West 138-kV line upgrade | 2014 | Planning Stage
2009-E3 | Close Sonora Atlantic-Sonora 69-kV line | 2010
2009-E4 | Seagoville-Kleburg Tap 138-kV line upgrade | 2014 | Planning Stage
2009-E5 | Tyler Bullard-Tyler Loop 138-kV line upgrade | 2010 | Design Stage | 09TPIT0170
2009-E6 | Shamburger-Tyler Northwest 138-kV line upgrade | 2014 | Planning Stage | 09TPIT0122
2009-E7 | Alvin area 138-kV line economic upgrades | 2010
2009-E8 | Oasis-Meadow 345-kV line upgrade | 2011 | Design Stage | 11TPIT0113
2009-E9 | Kenedy Switch Station #1-Kenedy Substation second 69-kV line addition | 2014
2009-E10 | HEC-Aderhold Substation 138-kV line upgrade | 2014
2009-E11 | South McAllen-Las Milpas 138-kV line series upgrade | 2014