## ImprovementCostSummary03012013
PRIVILEGED AND CONFIDENTIAL, DO NOT release outside of ERCOT Staff or Transmission Providers organization. Contains critical cost information that can affect bids for projects.
| Project Cost | [5 empty] | Circuit Miles |  |  |  |  | XFMR MVA
| Project Cost | [5 empty] | XFMR MVA
| 345 | 138 | 69 | total |  |  | 345 | 138 | 69 | total
2011 | 648929545 | 325895515 | 204249547 | 1179074607 |  | 2011 | 4822 | 983 | 0 | 5805
2012 | 555678900 | 465991803 | 239442495 | 1261113198 |  | 2012 | 2600 | 734 | 0 | 3334 |  | For ROS and BOD reports
2013 | 5427532661 | 478324617 | 148514006 | 6054371284 | 8494559089 | 2013 | 2078 | 168 | 0 | 2246 | 11385
2014 | 152850700 | 477489482 | 155322031 | 785662213 |  | 2014 | 2000 | 480 | 150 | 2630 |  | ·All Projects (in engineering, routing, licensing and construction) (sum of F13, E16) |  |  |  | 9679419930
2015 | 312235462 | 465246232 | 71789000 | 849270694 |  | 2015 | 32000 | 380 | 0 | 32380
2016 | 610884000 | 406237557 | 11800000 | 1028921557 |  | 2016 | 1050 | 0 | 0 | 1050 |  | ·Transmission Projects Energized in 2013 (E15) |  |  |  | 38587021
2017 | 116793325 | 86845000 | 4100000 | 207738325 |  | 2017 | 0 | 40 | 0 | 40
2018 | 111996244 | 110293850 | 0 | 222290094 |  | 2018 | 700 | 0 | 0 | 700
2019+ | 222823294 | 274307847 | 72621643 | 569752784 | 3663635667 | 2019+ | 4300 | 470 | 60 | 4830 | 41630
2013COM | 0 | 37677896 | 909125 | 38587021 |  | 2013COM | 0 | 93 | 0 | 93
2013PLAN | 5427532661 | 440646721 | 147604881 | 6015784263 |  | 2013PLAN | 2078 | 75 | 0 | 2153
2011-2019+ | 8159724131 | 3090631903 | 907838722 | 12158194756 |  | 2011-2019+ | 49550 | 3255 | 210 | 53015
2011-2013 | 6632141106 | 1270211935 | 592206048 | 8494559089 |  | 2011-2013 | 9500 | 1885 | 0 | 11385
2014-2019+ | 1527583025 | 1820419968 | 315632674 | 3663635667 |  | 2014-2019+ | 40050 | 1370 | 210 | 41630
| Circuit Miles New | [5 empty] | Circuit Miles Rebuilt, Reconductored or Upgraded |  |  |  |  | TOTAL
| 345 | 138 | 69 | total |  |  | 345 | 138 | 69 | total |  | 345 | 138 | 69 | total
2011 | 624.3 | 61.2 | 3.6 | 689.1 |  | 2011 | 12.9 | 313.1 | 284.7 | 610.7 |  | 637.2 | 374.3 | 288.3 | 1299.8
2012 | 473.8 | 107.8 | 60 | 641.6 |  | 2012 | 16.4 | 352.2 | 217.9 | 586.5 |  | 490.2 | 460 | 277.9 | 1228.1
2013 | 3903.1 | 107 | 0 | 4010.1 | 5340.8 | 2013 | 92.7 | 333.3 | 165.5 | 591.5 | 1788.7 | 3995.8 | 440.3 | 165.5 | 4601.6
2014 | 7.3 | 140.3 | 0 | 147.6 |  | 2014 | 70.4 | 336.6 | 167.1 | 574.1 |  | 77.7 | 476.9 | 167.1 | 721.7
2015 | 131 | 128.3 | 0 | 259.3 |  | 2015 | 143.8 | 407 | 76.4 | 627.2 |  | 274.8 | 535.3 | 76.4 | 886.5
2016 | 288.5 | 189.7 | 0 | 478.2 |  | 2016 | 52 | 177.5 | 12.9 | 242.4 |  | 340.5 | 367.2 | 12.9 | 720.6
2017 | 13.5 | 12.3 | 0 | 25.8 |  | 2017 | 0 | 48.8 | 4.6 | 53.4 |  | 13.5 | 61.1 | 4.6 | 79.2
2018 | 16.5 | 67.1 | 0 | 83.6 |  | 2018 | 0 | 7.2 | 0 | 7.2 |  | 16.5 | 74.3 | 0 | 90.8
2019+ | 55.8 | 121.3 | 20 | 197.1 | 1191.6 | 2019+ | 70.6 | 200.7 | 69.2 | 340.5 | 1844.8 | 126.4 | 322 | 89.2 | 537.6
2013COM | 0 | 4.1 | 0 | 4.1 |  | 2013COM | 0 | 23.9 | 0 | 23.9 |  | 0 | 28 | 0 | 28
2013PLAN | 3903.1 | 102.9 | 0 | 4006 |  | 2013PLAN | 92.7 | 309.4 | 165.5 | 567.6 |  | 3995.8 | 412.3 | 165.5 | 4573.6
2011-2019+ | 5513.8 | 935 | 83.6 | 6532.4 |  | 2011-2019+ | 458.8 | 2176.4 | 998.3 | 3633.5 |  | 5972.6 | 3111.4 | 1081.9 | 10165.9
2011-2013 | 5001.2 | 276 | 63.6 | 5340.8 |  | 2011-2013 | 122 | 998.6 | 668.1 | 1788.7 |  | 5123.2 | 1274.6 | 731.7 | 7129.5
2014-2019+ | 512.6 | 659 | 20 | 1191.6 |  | 2014-2019+ | 336.8 | 1177.8 | 330.2 | 1844.8 |  | 849.4 | 1836.8 | 350.2 | 3036.4

## FutureTPIT03012013NoCost
MARCH BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS As Of 03/01/2013
Projects (New/Old) | Service Date Changes | ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional)
Old Project | Change in Service Date. Changed from 2/1/2013 to 3/1/2013 | 13TPIT0144 | Central Dawson 69 kV POI/South Lamesa Sub | Tap the 69 kV Lamesa/Ackerly Line where the line intersects Dawson Co. Road 22 and construct a 10 MVA substation to replace a distribution metering point |  |  |  | Under Construction |  | Golden Spread/Lyntegar EC | Chris Koenig 806-349-5201 ckoenig@gsec.coop |  | 2013-03-01 |  | 69 | 0 | 0 | 0.0 | 0 | DAWSON | DAWSON | Tier 4 |  |  |  | 9413 | Y | N
Old Project | No Change | 11TPIT0110b | Valverde-AEP Weslaco Switch | Rebuild 4.5 Miles of 138kV line from Alberta Switch to Valverde Substation to AEP Weslaco Switch | Original clearance was shortened due to a higher priority clearance. Second clearance is required to complete work. | Weslaco Switch | Valverde | Planned | 07TPIT7777 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-03-01 |  | 138 | 0 | 4.5 | 0.0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8759-8769-8354 | Y | N |  | Divided Project into two projects. Associated with Alberta Switch to Valverde
Old Project | No Change | 12TPIT0097 | Cross substation | Construct new 138 kV load serving substation in San Miguel to Pearsall line. |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-03-01 |  | 138 | 0 | 0 | 0.0 | 0 | ATASCOSA |  | Tier 4 |  |  |  | 5707 | Y | N
Old Project | No Change | 12TPIT0196 | 0274 Gardendale Substation | Transfer 0274 Gardendale Substation into ERCOT | New | Oncor Moss 138 KV | Oncor Midland East 138 KV | Planned |  | SU | Dwight Yarbrough (956) 279-6902 dyarbrough@sharyland.com |  | 2013-03-01 |  | 138 | 0 | 0 | 0 | 0 | MIDLAND |  | Tier 4 |  |  | N/A |  | N | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 3/1/2013 | 13TPIT0134 | Cumby Switch | Upgrade existing 138/69 kV autotransformer | Autotransformer cooling upgrade was implemented instead of replacement of existing autotransformer |  |  | Planned |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R908-WAC | 2013-03-01 |  | 138 | 0 | 0 | 50.0 | 0 | DELTA |  | Tier 4 |  |  |  | 1815, 1812 | Y | N
Old Project | Change in Service Date. Changed from 2/1/2013 to 3/1/2013 | 13TPIT0165 | 1775 Driver Substation | Constuct new 2-30 MVA substation with ring bus to feed new and existing load | New | 1881 Skywest Breaker Yard | 0566 Midkiff Substation | Under Construction |  | SU | Dwight Yarbrough (956) 279-6902 dyarbrough@sharyland.com |  | 2013-03-01 |  | 138 | 0 | 0 | 0 | 0 | MIDLAND |  | Tier 4 | 2012-08-17 | on-going | N/A |  | N | N
Old Project | Change in Service Date. Changed from 2/1/2013 to 3/1/2013 | 13TPIT0166 | 1881 Skywest Breaker Yard | Construct new 1881 Skywest Breaker Station in conjuction with LCRA for new and existiong load moving to ERCOT, 1775 Driver Substation, 0566 Midkiff Substation, and 2058 Pembrook Substation | New | 1956 Substation | 1775 Driver Substation | Under Construction |  | SU | Dwight Yarbrough (956) 279-6902 dyarbrough@sharyland.com |  | 2013-03-01 |  | 138 | 0 | 0 | 0 | 0 | MIDLAND | UPTON | Tier 4 | 2012-08-17 | on-going | N/A |  | N | N
Old Project | Change in Service Date. Changed from 2/1/2013 to 3/1/2013 | 13TPIT0167 | Skywest Breaker Yard to Driver Substation 8175 Transmission Line | Construct 4 miles of new 138 Kv transmission line in an existing transmission line for 1775 Driver Substation | New | 1881 Skywest Breaker Yard | 1775 Driver Substation | Planned |  | SU | Dwight Yarbrough (956) 279-6902 dyarbrough@sharyland.com |  | 2013-03-01 |  | 138 | 4 | 0 | 0 | 0 | MIDLAND | MIDLAND | Tier 4 | 2012-08-17 | on-going | N/A |  | N | N
Old Project | Change in Service Date. Changed from 2/1/2013 to 3/1/2013 | 13TPIT0168 | Driver Substation to Midkiff Substation 7566 Transmission Line | Construct 4 miles of new 138 Kv transmission line in an existing transmission line for 1775 Driver Substation | New | 1775 Driver Substation | 0566 Midkiff Substation | Planned |  | SU | Dwight Yarbrough (956) 279-6902 dyarbrough@sharyland.com |  | 2013-03-01 |  | 138 | 4 | 0 | 0 | 0 | MIDLAND | MIDLAND | Tier 4 | 2012-08-17 | on-going | N/A |  | N | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 3/1/2013 | 13TPIT0200 | Lakepointe - Jones St 138 kV line (Oncor section) | Increase rating of line | Change in construction schedule | Lewisville Switch | Jones St | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2013-03-01 |  | 138 | 0 | 5 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  | 37010, 1972 | Y | N
Old Project | Change in Service Date. Changed from 3/1/2013 to 3/6/2013 | 13TPIT0048 | Scurry County (Central A) - West Shackelford (Central C) | CREZ Assigned Project to build West Shackelford (Central C) substation in Shackelford county and double ckt 345 kV lines from Scurry County sub (Oncor Central A facility) to West Shackelford substation utilizing 2-1590 ACSS/TW "Falcon" conductor; Approximate route distance is 103 miles. Two 100 MVAR (2 x -100) shunt reactors will be placed on the line terminals to Sam Switch and Navarro at West Shackelford (one on each circuit). |  | Scurry County South | West Shackelford | under construction |  | Lone Star Transmission, LLC | Matthew Gomes 512-236-3133 matthew.gomes@lonestar-transmission.com |  | 2013-03-06 |  | 345 | 206.2 | 0 | 0.0 | -200 | SCURRY | SHACKELFORD | CREZ | N/A | N/A | N/A | West Shackelford 68000 | Y | N
Old Project | Change in Service Date. Changed from 2/21/2013 to 3/8/2013 | 15TPIT0012 | Petteway to Ben Hur | Rebuild Petteway to Ben Hur 69 kV line with 795 ACSR |  | Petteway | Ben Hur | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10046 | 2013-03-08 |  | 69 | 0 | 23.59 | 0.0 | 0 | ROBERTSON | LIMESTONE | Tier 4 |  |  |  | 93, 85, 99 | Y | N
Old Project | No Change | 07TPIT0250 | Lone Tree: Install 1-14.4 MVAR 69 kV Cap Banks | Add capacitors in Victoria area at the McGruder Victoria plant and Lone Tree | Changed Status | Lone Tree |  | Under Construction | 389 - 0667 | AEP/TCC | Dave Goetz 918-599-2664 | 2047 | 2013-03-13 |  | 69 | 0 | 0 | 0 | 14.4 | VICTORIA |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 11TPIT0076 | Cottonwood 345 kV Station and Cotttonwood to Dermott 345 kV line | Establish new 345 kV Cottonwood station and construct a new double circuit 345 kV transmission line WETT new Cottonwood and Oncor's Dermott 345 kV stations. Includes 2x50 MVAR shunt reactor banks at Cottonwood. |  | Cottonwood | Dermott | Planned |  | Wind Energy Transmission Texas (WETT) | Julius Horvath (512) 279-7377 julius.horvath@windenergyoftexas.com |  | 2013-03-13 |  | 345 | 74.2 | 0 | 0.0 | 2 x -50 | DICKENS | SCURRY | CREZ |  |  |  | 59904 | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | Change in Service Date. Changed from 2/1/2013 to 3/19/2013 | 13TPIT0143 | El Campo - Ricebird - Nada Transmission Line Upgrade and Substation Addition | Construct a new 138 kV Ricebird Substation (78104) and terminate the 138 kV transmission lines from El Campo (8102) and Nada (78103) at the Ricebird Substation. Install a new 60MVA 138/69kV autotransformer at the Nada substation. |  | El Campo Substation | Nada Substation | Planned | 13TPIT0120 (STEC) | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-03-19 |  | 138 | 0 | 17.5 | 60.0 | 0 | COLORADO | WHARTON | Tier 3 | 2011-10-14 | 2011-11-09 | N/A | SEE PROJECT DESCRIPTION | Y | N |  | Coordinate this project with STEC
Old Project | No Change | 13TPIT0140 | Smiley Substation Addition | Replace existing station, add 138x69kV-13.09x26.18 dual kV, 12/16/20 MVA PWT w/associated structures, bus, panels, etc |  | Smiley |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2013-03-28 |  | 69 | 0 | 0 | 0.0 | 0 | GONZALES |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | Change in Service Date. Changed from 2/25/2013 to 3/29/2013 | 13TPIT0117 | Sunniland 69 kV substation: STEC Interconnect | Sunniland 69 kV STEC Interconnection: Construct 69 kV Substation Including Motor Operated Switches with Interconnection on Pleasanton - Three Rivers 69kV line. | Changed inservice date and reformated project number to match other numbers | Sunniland |  | Under Construction | 556 - 0716 | AEP/TCC | Kenneth Haley 918-599-2664 | 3431 | 2013-03-29 |  | 69 | 0 | 0 | 0 | 0 | LIVE OAK |  | Tier 4 |  |  |  | 8406 | Y | N
Old Project | Change in Service Date. Changed from 3/13/2013 to 3/31/2013 | 10TPIT0070 | Magruder to North Victoria: Rebuild 69 kV Line | Reconductor Magruder to North Victoria 69 kV line to 795 ACSS. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. | Date Change | Magruder | North Victoria | Under Construction | 389 - 0567 | AEP/TCC | Dave Goetz 918-599-2664 | 3261 | 2013-03-31 |  | 69 | 0 | 3.7 | 0 | 0 | VICTORIA | VICTORIA | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/20/2013 to 3/31/2013 | 13TPIT0205 | Barilla Draw 69 kV Tap | This project will tap TNMP's IH20 to Flattop 69kV line to serve the Barilla Draw Field customer load and Install a 15 MVAR 69 kV Cap Bank at Barilla Draw Station |  | IH20 | Barilla Draw Tap | Under Construction |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2013-03-31 |  | 69 | 0 | 0 | 0 | 15 | REEVES | REEVES | Tier 4 |  |  |  | 38060, 38065 | Y | N |  | Barilla Draw Tap will be Approximately 11.57 Miles from IH20
Old Project | Change in Service Date. Changed from 2/20/2013 to 3/31/2013 | 13TPIT0206 | Bone Springs 69 kV Tap | This project will tap TNMP's Wink to Cochise 69kV line to serve the Bone Springs customer load. |  | Wink | Bone Springs Tap | Under Construction |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2013-03-31 |  | 69 | 0 | 0 | 0 | 0 | WARD | WARD | Tier 4 |  |  |  | 38170, 38175 | Y | N |  | Bone Springs Tap will be Approximately 3.48 Miles from Cochise.
Old Project | Change in Service Date. Changed from 1/31/2013 to 3/31/2013 | 13TPIT0207 | Texas City Main Cap Bank | Install a New 25 MVAR 69 kV Cap Bank at Texas City Main Station and Retire the 14.4 MVAR Cap Bank at Amoco 69kV Bus |  | Texas City Main |  | Under Construction |  | TNMP | Tony Hudson, 281-581-4712, Anthony.Hudson@tnmp.com | STE08512 | 2013-03-31 |  | 69 | 0 | 0 | 0 | 25 | GALVESTON |  | Tier 4 |  |  |  | 38650, 39140 | Y | N |  | 14.4 MVAR 69kV Cap Bank at Amoco Station to be retired.
Old Project | Change in Service Date. Changed from 12/31/2012 to 3/31/2013 | 12TPIT0171 | HO Clarke - Knight Ckt. 08 | Upgrade 138kV Ckt.08 HO Clarke to Knight to increase thermal ratings. | Delay in project schedule | HO Clarke | Knight | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-03-31 |  | 138 | 0 | 3.94 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47150, 47331 | Y | N
Old Project | Change in Service Date. Changed from 6/30/2013 to 3/31/2013 | 11TPIT0077 | Riley, Add two 130.9 MVar capacitors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Riley |  | Under Construction | 467 - 0668 | AEP/ETT | Glen Reed 918-599-2664 | 2379 | 2013-03-31 |  | 345 | 0 | 0 | 0 | +261.8 | WILBARGER |  | CREZ Modified |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 6/1/2013 to 3/31/2013 | 11TPIT0078 | Riley, add four 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Riley |  | Planned | 467 - 0668 | AEP/ETT | Glen Reed 918-599-2664 | 2380 | 2013-03-31 |  | 345 | 0 | 0 | 0 | -200 | WILBARGER |  | CREZ Modified |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 6/1/2013 to 3/31/2013 | 11TPIT0079 | Riley, Expand 345 kV switch station for the additon of the West Krum to Riley 345 kV double circuit | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 | Schedule Update | Riley |  | Planned | 467 - 0668 | AEP/ETT | Glen Reed 918-599-2664 | 2435 | 2013-03-31 |  | 345 | 0 | 0 | 0 | 0 | WILBARGER |  | CREZ Modified |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/1/2013 to 3/31/2013 | 13TPIT0049 | West Shackelford (Central C) - Sam Switch/Navarro | CREZ Assigned Project to build double ckt 345 kV lines from S West Shackelford -Romney-Kopperl-Sam Switch and Shackelford -Romney-Kopperl-Navarro transmission lines utilizing 2-1590 ACSS/TW "Falcon" conductor; Approximate route distance is 190 miles between West Shackleford and Sam Switch and 225 miles between West Shackleford and Navarro stations. Series compensators will be installed at Romney and Kopperl substations, in addition to 4 - 4x50 MVAr reactor banks at Romney substation. |  | West Shackelford | Circuit 1 - Sam Switch Circuit 2 - Navarro | under construction |  | Lone Star Transmission, LLC | Matthew Gomes 512-236-3133 matthew.gomes@lonestar-transmission.com |  | 2013-03-31 |  | 345 | 414.1 | 0 | 0.0 | -200 | SHACKELFORD | HILL / NAVARRO | CREZ | N/A | N/A | N/A | Romney 1 W 68010 Romney 2 W 68050 Romney 1 E 68020 Romney 2 E 68060 Kopperl 1 W 68030 Kopperl 2 W 68070 Kopperl 1 E 68040 Kopperl 2 E 68080 Sam Switch 68090 Navarro 68091 Sam Reactr 68005 Nav Reactr 68006 | Y | N | Revised as of 12/1/2012 - LST successfully cut-in and energized Navarro and Sam Switch and Navarro switchyards (only) on existing Oncor lines according to the following schedule: • Navarro (first set of lines) - October 1 - 15, 2012 (Navarro energized on October 12, 2012 as scheduled) • Navarro (second set of lines) - October 16 - November 2, 2012 (Navarro fully operational on October 31, 2012) • Sam Switch - November 3 - 17, 2012 (Sam Switch energized on November 17, 2012 as scheduled) | Project scope also include two series capacitor bank stations (Kopperl, Romney) equally spaced between West Shackelford and Sam Switch consisting of two series capacitor banks rated at 683 MVAR and 817 MVAR, with associated switches and line terminals and associated components at both Sam Switch and Navarro substations. There will be 4 x 50 MVAR shunt reactor banks at Romney, 2 x 50 MVAR on the east side of the series capacitors and 2 x 50 MVAR on the west side.
Old Project | Change in Service Date. Changed from 1/1/2013 to 4/1/2013 | 11TPIT0162 | Cordele 69 kV Substation | Construct new 69 kV load serving substation in the line between Edna and Ganado Switch |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-04-01 |  | 69 | 0 | 0 | 0.0 | 0 | JACKSON |  | Tier 4 |  |  |  | 5524 | Y | N
Old Project | No Change | 13TPIT0183 | Coy City Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-04-01 |  | 69 | 0 | 0 | 0.0 | 9.6 | KARNES |  | Tier 2 | 2011-12-16 | 2012-04-25 | N/A | 5720 | Y | N |  | This location was chosen for 9.6 MVAR instead of having all 19.2 MVAR at Kenedy.
Old Project | No Change | 13TPIT0197 | Pleasanton Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-04-01 |  | 69 | 0 | 0 | 0.0 | 9.6 | ATASCOSA |  | Tier 2 | 2011-12-16 | 2012-04-25 | N/A | 5714 | Y | N
Old Project | Change in Service Date. Changed from 3/1/2013 to 4/1/2013 | 12TPIT0172 | Western Dawson 138 kV POI/Patricia Sub | Tap the 138 kV Andrews/Lamesa Line where the line intersects FM 829. Build 7.5 miles of 138 kV transmission south to new Patricia Sub, which will be loaded approximately 5 MVA when energized. |  |  |  | Under Construction |  | Golden Spread/Lyntegar EC | Chris Koenig 806-349-5201 ckoenig@gsec.coop |  | 2013-04-01 |  | 138 | 7.5 | 0 | 0.0 | 0 | DAWSON | DAWSON | Tier 4 |  |  |  | 9418 | Y | N
Old Project | No Change | 12TPIT0049 | LS04 Silverton to Cottonwood | Construct a new 345kV double circuit line from Silverton switching station to WETT's Cottonwod switching station | New | Cottonwood | Silverton | Under Construction | 12TPIT0050 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharyland.com |  | 2013-04-07 |  | 345 | 64.5 | 0 | 0.0 | 0 | BRISCOE | DICKENS | CREZ |  |  |  | 99103-99104 | Y | N
Old Project | No Change | 12TPIT0050 | Silverton Collection Station | Construct the new 345 kV Silverton switching station.Initial build is 14 element folded breaker and one half bus arrangement. | New |  |  | Under Construction | 12TPIT0049 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharyland.com |  | 2013-04-07 |  | 345 | 0 | 0 | 0.0 | +50, -150 | BRISCOE |  | CREZ |  |  |  | 99103 | Y | N
Old Project | Change in Service Date. Changed from 1/13/2013 to 4/13/2013 | 12TPIT0175 | Switch Station Entergy Tie | Build a tranmission tie between COCS Switch Station and Entergy Switch Station for emergency tie per a PUCT order. |  | 138 kV Switch S1617ETI | 138 kV Switch 26421 | Planned |  | COCS | Tony Michalsky 979- 764-3438 tmichalsky@cstx.gov |  | 2013-04-13 |  | 138 | 0 | 0 | 0.0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32000 | N | N
Old Project | Change in Service Date. Changed from 1/14/2013 to 4/16/2013 | 10TPIT0082 | Carlton Switch to Mountary Rebuild | Rebuild Carlton Switch to Mountary with 959ACSS |  | Carlton | Mountary | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 08051 | 2013-04-16 |  | 69 | 0 | 9.6 | 0.0 | 0 | ERATH | COMANCHE | Tier 4 |  |  |  | 297, 294 | Y | N
Old Project | No Change | 12TPIT0128 | WA Parish - Sienna Ckt. 02 | Upgrade 138 kV Ckt. 02 WA Parish to Sienna to increase thermal ratings. |  | WA Parish | Sienna | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-04-30 |  | 138 | 0 | 4.2 | 0.0 | 0 | FORT BEND | FORT BEND | Tier 4 |  |  |  | 44651, 44010 | Y | N
Old Project | No Change | 12TPIT0204 | Construct: Catarina 138 kV station | Contruct new Catarina station on Asherton to North Laredo 138 kV line | Reformated project number to match other numbers | Catarina |  | Under Construction | 590 - 0760 | AEP/TCC | Frank Pritzlaff (AEP) 918-599-2664 | 3455 | 2013-04-30 |  | 138 | 0 | 0 | 0 | 0 | DIMMIT |  | Tier 4 |  |  |  | 8970 | Y | N
Old Project | Change in Service Date. Changed from 12/31/2012 to 4/30/2013 | 12TPIT0205 | McCampbell: New substation Cut In | Customer construct 138kV substation. 138kV Cut-In on substation. | Changed inservice date, Contact and reformated project number to match other numbers | Dupont SS | Whitepoint SS | Planned | 561 - 0729 | AEP/TCC | Terry Weeks 918-599-2664 | 3435 | 2013-04-30 |  | 138 | 0 | 0 | 0 | 0 | SAN PATRICIO | 0 | Tier 4 | 0 | 0 | 0 | 0 | Y | N | 0 | 0
Old Project | No Change | 13TPIT0141 | NORTON 138kV Substation | Construct service to new 138kV NORTON customer-owned substation. Loop through Ckt. 86 HACHER - ENPROD. |  | NORTON | HACHER/ ENPROD | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-04-30 |  | 138 | 1.98 | 0 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 4 |  |  |  | 40770, 40760, 40510 | Y | N
Old Project | Change in Service Date. Changed from 6/30/2013 to 4/30/2013 | 13TPIT0189 | Brazos Valley to Fort Bend Ckt.09 | Upgrade 138kV Ckt. 09 Brazos Valley to Fort Bend to increase thermal ratings. | Accelerated project schedule | Brazos Valley | Fort Bend | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-04-30 |  | 138 | 0 | 5.62 | 0.0 | 0 | FORT BEND | FORT BEND | Tier 4 |  |  |  | 44100, 44280 | Y | N |  | Part of Fort Bend Area Upgrades.
Old Project | No Change | 13TPIT0196 | MILLER 138kV Substation | Construct service to new 138kV MILLER customer-owned substation. Loop through Ckt.88 BARNES to SR Bertron. |  | MILLER | BARNES/ SR Bertron | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-04-30 |  | 138 | 0.2 | 0.3 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 41355, 41420, 41405 | Y | N
Old Project | Change in Service Date. Changed from 4/1/2013 to 5/1/2013 | 12TPIT0149 | Cordele Capacitor | Add 19.2 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-05-01 |  | 69 | 0 | 0 | 0 | 19.2 | JACKSON |  | Tier 4 | 2011-12-16 | 2012-04-25 | N/A | 5524 | Y | N
Old Project | Change in Service Date. Changed from 4/1/2013 to 5/1/2013 | 12TPIT0157 | West Sinton Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-05-01 |  | 69 | 0 | 0 | 0.0 | 9.6 | SAN PATRICIO |  | Tier 4 |  |  |  | 5622 | Y | N
Old Project | Change in Service Date. Changed from 3/29/2013 to 5/1/2013 | 12TPIT0200 | Hico cap bank | Install 6.6 MVAR, 69kV cap bank at Hico Substation |  | Hico |  | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE03212 | 2013-05-01 |  | 69 | 0 | 0 | 0.0 | 6.6 | Hamilton |  | Tier 4 |  |  |  | 37750 | Y | N
Old Project | Change in Service Date. Changed from 4/1/2013 to 5/1/2013 | 13TPIT0184 | Poteet Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-05-01 |  | 69 | 0 | 0 | 0.0 | 9.6 | ATASCOSA |  | Tier 2 | 2011-12-16 | 2012-04-25 | N/A | 5710 | Y | N |  | This location was chosen for a capcitor bank because there is not room for a capacitor bank at Pleasanton unless more land is purchased.
Old Project | No Change | 13TPIT0211 | Edna Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-05-01 |  | 69 | 0 | 0 | 0.0 | 9.6 | JACKSON |  | Tier 4 |  |  |  | 5522 | Y | N
New Project | New Project | 13TPIT0234 | Fullerton - Exxon Fullerton 69 kV Line | Upgrade existing 69 kV line |  | Fullerton | Exxon Fullerton | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8160-E | 2013-05-01 |  | 69 | 0 | 0.1 | 0 | 0 | ANDREWS | ANDREWS | Tier 4 |  |  |  | 12751274 | Y | N
Old Project | No Change | 11TPIT0024 | TCC - 138kV Line Reroutes | The following 138kV lines will be rerouted: Cagnon - AMDTP - AMD becomes Cagnon - AMD Cagnon - AMDTP - Pinn becomes Cagnon - Pinn Pinn - SWRI becomes Pinn - Westside Construct a new 138kV line from TCC - SWRI Cagnon - AMD line upgrade to 1590AAC |  | Cagnon Cagnon Pinn Rd TCC | AMD Pinn Rd Westside SWRI | Planned | S-0384 | CPS | T: Kevin Phillips | T-0106 | 2013-05-01 |  | 138 | 5.8 | 0 | 0.0 | 0 | BEXAR | BEXAR | Tier 4 | 2012-08-07 | 2012-12-03 | N/A | 5423 5419 5345 5002 5004 5490 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 12TPIT0160 | Clear Creek Substation terminal equipment | Upgrade terminal equipment at Clear Creek Substation in the Killeen Switch - Lampasas 138 kV line |  |  |  | Planned |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R760A, B & C-WAC | 2013-05-01 |  | 138 | 0 | 0 | 0.0 | 0 | BELL |  | Tier 4 |  |  |  | 3628 | Y | N
Old Project | No Change | 12TPIT0217 | Moss - Holt Switch 138 kV line | Increase line rating by raising operating temperature of conductor |  | Moss | Holt Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2013-05-01 |  | 138 | 0 | 18.1 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1141, 1019 | Y | N
Old Project | No Change | 13TPIT0046 | Flatonia-Yoakum Gartner Road | Upgrade and convert the 27.7 mile Flatonia (7248)-Moulton (7236)-Henkhaus (7237)-Shiner (7238)-Yoakum Gartner Road (7242) 2/0 ACSR 69 kV transmission line to 795 ACSR 138 kV. |  | Flatonia | Yoakum Gartner Road | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-05-01 |  | 138 | 0 | 27.7 | 0.0 | 0 | FAYETTE | DEWITT | Tier 3 |  | 2009-03-01 |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 13TPIT0066 | E C Mornhinweg | Construct a new 138 kV 959 ACSS transmission line between the GPI switching station (7459) and the new E C Mornhinweg substation (7463). |  | GPI | EC Mornhinweg | Planned |  | NBU | Greg Baumbach (830) 629-8441 gbaumbach@nbutexas.com |  | 2013-05-01 |  | 138 | 2.7 | 0 | 0.0 | 0 | COMAL | COMAL | Tier 2 | 2009-02-06 | 2009-06-01 | N/A | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 13TPIT0163 | Payne Switch | Upgrade 138 kV switching station |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4106-WAC | 2013-05-01 |  | 138 | 0.25 | 0 | 0.0 | 0 | GRAYSON |  | Tier 4 |  |  |  | 1758 | Y | N
Old Project | No Change | 13TPIT0170 | 2570 East Stiles Substation | Construct new 2570 East Stiles Substaion, 30MVA | New | 2372 St. Lawerence Substation | 2168 Stiles Substation | Planned |  | SU | Dwight Yarbrough (956) 279-6902 dyarbrough@sharyland.com |  | 2013-05-01 |  | 138 | 2 | 0 | 0 | 0 | REAGAN |  | Tier 4 |  |  | N/A |  | N | N |  | 130
Old Project | No Change | 13TPIT0218 | Sulphur Springs Switch tertiary shunt reactors | Install shunt tertiary reactors |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R923-E | 2013-05-01 |  | 138 | 0 | 0 | 0 | -37.5 | HOPKINS |  | Tier 4 |  |  |  | 1698 | Y | N
Old Project | No Change | 13TPIT0219 | Paris Switch tertiary shunt reactors | Install shunt tertiary reactors |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R922-WAC | 2013-05-01 |  | 138 | 0 | 0 | 0 | -37.5 | LAMAR |  | Tier 4 |  |  |  | 1693 | Y | N
Old Project | No Change | 13TPIT0220 | Permian Basin - Wink 138 kV line | Upgrade terminal equipment at Wink |  | Permian Basin | Wink | Conceptual | R8066 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2013-05-01 |  | 138 | 0 | 0 | 0 | 0 | WARD | WINKLER | Tier 4 |  |  |  | 1010, 1074 | Y | N |  | Switches at Wink will be replaced as part of the Wink Switch - Loving - El Mar - Mason 138 kV line reconstruction project (13TPIT0152).
Old Project | No Change | 13TPIT0091 | Big Hill Reactive Devices | Install two each 50 MVAR Reactor Banks and two each 72 MVAR Capacitor Banks at the Big Hill station (76003). |  | Big Hill |  | Planned | 13TPIT0029 (AEP) 13TPIT0084 (AEP) 13TPIT0086 (AEP) 13TPIT0087 (AEP) | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-05-01 |  | 345 | 0 | 0 | 0.0 | -100, 144 | SCHLEICHER |  | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | Cost is included in the 12TPIT0028 project
Old Project | No Change | 13TPIT0077 | Kendall to Miller Creek to Paleface | Upgrade existing Kendall (7150) to Miller Creek (7479)line to 1433 ACSS/TW (Merrimack) and Miller Creek (7479) Creek to Paleface (7476) line to 795 ACSR (Drake). |  | Kendall | Paleface | Planned | 13TPIT0210 (PEC) | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-05-02 |  | 138 | 0 | 56.88 | 0.0 | 0 | KENDALL | BURNET | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 11TPIT0038 | CSU Northgate Substation | Install (3) Breaker ring to include (2) 138 lines and tap to College Station Utilities | Name changed back to Northgate (from Finfeather) at CSU's request | CSU Northgate | CSU Northgate | planned |  | BTU/CSU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-05-06 |  | 138 | 0 | 0 | 0.0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 2/12/2013 to 5/13/2013 | 12TPIT0093 | Switch Station Transformer Addition | Add 40 MVA Power Transformer. |  | 138 kV Switch S10009A | 138 kV Switch S12009A | Planned |  | COCS | Tony Michalsky 979- 764-3438 tmichalsky@cstx.gov |  | 2013-05-13 |  | 138 | 0 | 0 | 0.0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32000 | Y | N
Old Project | No Change | 12TPIT0183 | Gonzales: Add terminal position and rebuild 2.43 mile 69 kV line to Acacia Solar Farm | Interconnect Acacia Solar Farm into the Gonzales 69 kV station, rebuild 69 kV line with 477 ACSR | Project Title Update | Gonzales |  | Under Construction | 513 - 0710 | AEP/ETT | Frank Pritzlaff 918-599-2664 | 2568 | 2013-05-31 |  | 69 | 0 | 2.2 | 0 | 0 | PRESIDIO | PRESIDIO | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0115 | Barnhart SWTEC: Add 3.6 Mvar capacitor bank | Add 3.6 Mvar capacitor bank at Barnhart SWTEC and add 10 MVA DRCS with 7.2 Mvar capacitor bank at Yucca |  | Barnhart |  | Planned | 558 - 0721 | AEP/TNC | Michael Tallon 918-599-2664 | 2560 | 2013-05-31 |  | 69 | 0 | 0 | 0 | +3.6 | IRION |  | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2013 to 5/31/2013 | 13TPIT0120 | Ricebird Station and autotransformer. | Construct 69 kV Ricebird station, install 150 MVA autotransformer, tie into El Campo to Round Mott Switch 69 kV line and connect 69 kV line from Nada at Ricebird. |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-05-31 |  | 69 | 0 | 0 | 150.0 | 0 | WHARTON |  | Tier 3 | 2011-10-14 | 2011-11-09 | N/A | 5535, 78104 | Y | N |  | Coordinated project with LCRA
Old Project | No Change | 13TPIT0191 | Southwyck Cap Bank | Install 28.8MVAR capacitor bank at Southwyck substation. |  | Southwyck |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-05-31 |  | 138 | 0 | 0 | 0 | 28.8 | BRAZORIA |  | Tier 4 |  |  |  | 43260 | Y | N
Old Project | No Change | 13TPIT0192 | Lockwood Cap Bank | Install 14.4MVAR capacitor bank at Lockwood substation. |  | Lockwood |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-05-31 |  | 138 | 0 | 0 | 0 | 14.4 | HARRIS |  | Tier 4 |  |  |  | 46032 | Y | N
Old Project | Change in Service Date. Changed from 7/31/2013 to 5/31/2013 | 13TPIT0215 | TANKER 138kV Substation | Construct service to new 138kV TANKER customer-owned substation. Loop through Ckt.94 Galena Park - Crown. | Accelerated project schedule | TANKER | Galena Park/ CROWN | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-05-31 |  | 138 | 0.1 | 0 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 40612, 40630, 40400 | N | N
Old Project | No Change | 13TPIT0222 | Greenville Line Reroute | Reroute an existing line segment to accommodate a proposed construction project |  | Olinger | Greenville Interchange | Planned |  | TMPA | Tom Chambers 936-873-1125 tchambers@texasmpa.org | T13007 | 2013-05-31 |  | 138 | 0 | 0.7 | 0 | 0 | Hunt |  | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 13TPIT0225 | Bobwhite: Build new 138 kV Box Bay Switch Structure | Construct new Bobwhite station along the East Munday to Lake Pauline 138 kV line | Contact Update | Bobwhite |  | Planned | 586 - 0767 | AEP/TNC | Eric Scott 918-599-2664 | 2803 | 2013-05-31 |  | 138 | 0 | 0 | 0 | 0 | FOARD |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 14TPIT0058k | Mont Belvieu Area Upgrades | Upgrade 138kV Ckt. 86 Bender to Duncan to increase thermal ratings. |  | BENDER | DUNCAN | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-05-31 |  | 138 | 0 | 1.91 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 4 | 2012-02-03 | 2012-03-05 | N/A | 40155, 40360 | Y | N |  | Cost included in main project
Old Project | No Change | 14TPIT0058l | Mont Belvieu Area Upgrades | Upgrade 138kV Ckt. 86 Crosby to Bender to increase thermal ratings. (Thermal uprate) |  | CROSBY | BENDER | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-05-31 |  | 138 | 0 | 7.89 | 0.0 | 0 | HARRIS | CHAMBERS | Tier 4 | 2012-02-03 | 2012-03-05 | N/A | 40390, 40155 | Y | N |  | Cost included in main project. This TPIT entry includes the thermal uprate of the circuit segment, which is scheduled to be complete in May 2013
Old Project | Change in Service Date. Changed from 3/14/2013 to 5/31/2013 | 12TPIT0056 | Grelton 345 kV Station and Grelton to Long Draw 345 kV line | Establish new 345 kV Grelton station and construct a new single circuit, double circuit capable 345 kV transmission line between new Grelton and new Long Draw 345 kV stations. Includes 1x50 MVAR shunt capacitor bank at Grelton. |  | Grelton | Long Draw | Planned |  | Wind Energy Transmission Texas (WETT) | Julius Horvath (512) 279-7377 julius.horvath@windenergyoftexas.com |  | 2013-05-31 |  | 345 | 55.4 | 0 | 0.0 | 50 | MARTIN | BORDEN | CREZ |  |  |  | 59901 | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | Change in Service Date. Changed from 3/15/2013 to 5/31/2013 | 12TPIT0057 | Grelton to Odessa 345 kV line | Construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Grelton and Oncor's existing Odessa 345 kV stations. |  | Grelton | Odessa | Planned |  | Wind Energy Transmission Texas (WETT) | Julius Horvath (512) 279-7377 julius.horvath@windenergyoftexas.com |  | 2013-05-31 |  | 345 | 49.9 | 0 | 0.0 | 0 | MARTIN | SCURRY | CREZ |  |  |  |  | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | Change in Service Date. Changed from 3/16/2013 to 5/31/2013 | 12TPIT0058 | Long Draw 345 kV Station and Long Draw to Scurry County South 345 kV line | Establish new 345 kV Long Draw station and construct a new double circuit 345 kV transmission line between WETT's new Long Draw and Oncor's Scurry County South 345 kV stations. |  | Long Draw | Scurry | Planned |  | Wind Energy Transmission Texas (WETT) | Julius Horvath (512) 279-7377 julius.horvath@windenergyoftexas.com |  | 2013-05-31 |  | 345 | 50.7 | 0 | 0.0 | 0 | BORDEN | SCURRY | CREZ |  |  |  | 59900 | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | No Change | 13TPIT0102 | Greens Bayou Autotransformer Upgrade | Replace existing 400MVA Greens Bayou autotransformer A2 with 800MVA autotransformer. |  |  |  | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-05-31 |  | 345 | 0 | 0 | 400.0 | 0 | HARRIS |  | Tier 4 |  |  |  | 40700, 40716, 49019 | Y | N
Old Project | No Change | 13TPIT0103 | Obrien Autotransformer Upgrade | Replace existing 400MVA Obrien autotransformer A3 with 800MVA autotransformer. |  |  |  | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-05-31 |  | 345 | 0 | 0 | 400.0 | 0 | FORT BEND |  | Tier 4 |  |  |  | 44500, 44510, 49063 | Y | N
Old Project | Change in Service Date. Changed from 3/29/2013 to 6/1/2013 | 13TPIT0202 | Barstow Tap cap bank | Install 10 MVAR, 69kV cap bank at Barstow Tap Substation |  | Barstow Tap |  | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2013-06-01 |  | 69 | 0 | 0 | 0.0 | 10 | REEVES |  | Tier 4 |  |  |  | 38150 | Y | N
Old Project | No Change | 11TPIT0085 | Doedyns-Sioux 138kV Line | Build New 138kV Line from Doedyns-Sioux Substations | Delays due to Right of Way process | Doedyns | Sioux | Planned | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org | 789640 | 2013-06-01 |  | 138 | 5.5 | 0 | 0.0 | 0 | HIDALGO | HIDALGO | Tier 2 | 2005-02-01 | 2005-04-20 |  | 8753-8792 | Y | N
Old Project | No Change | 13TPIT0069 | Panther Springs - New 138kV Substation | Loop new 138kV substation into existing 138kV Hill Country to Stonegate circuit #1 line |  | Panther Springs | Hill Country/Stonegate | Planned | T-0172 | CPS | PM: Cathleen Ballard | S-0616 | 2013-06-01 |  | 138 | 0.1 | 0 | 0.0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5331 5210 5415 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 13TPIT0092 | Killeen Switch - Killeen Elms Road - Harker Heights 138 kV line | Upgrade existing 138 kV line |  | Killeen Switch | Harker Heights | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R777-WAC | 2013-06-01 |  | 138 | 0 | 14.8 | 0.0 | 0 | BELL | BELL | CREZ |  |  |  | 3423, 3633 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0135 | Holt Switch - Goldsmith - Goldsmith South 138 kV line | Rebuild existing 69 kV line to create a double-circuit line with 69 kV and 138 kV circuits and convert Goldsmith South to 138 kV. |  | Holt Switch | Goldsmith South Substation | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8050A-E | 2013-06-01 |  | 138 | 9 | 0 | 0.0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1141, 11256, 11250 | Y | N |  | Goldsmith - Goldsmith South section completed in 3/2013
Old Project | No Change | 13TPIT0139 | Greenville 138kV Line Rebuild Olinger to Interchange to Shelby Tap (Segment 1) | Replace wooden transmission structures and install new conductor on approximately 20 miles of line | Split project in two line segments to facilitate outage coordination | Olinger | Greenville Interchange | Under Construction |  | TMPA | Tom Chambers 936-873-1125 tchambers@texasmpa.org | T13005 | 2013-06-01 |  | 138 | 0 | 20 | 0.0 | 0 | Hunt |  | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 4/15/2013 to 6/1/2013 | 13TPIT0182 | Comanche cap bank | Install a 30 MVAR, 138 kV capacitor bank at Comanche Switching Station. |  | Comanche |  | Planned |  | TNMP | Tony Hudson, 281-581-4712, Anthony.Hudson@tnmp.com |  | 2013-06-01 |  | 138 | 0 | 0 | 0.0 | 30 | Galveston |  | Tier 4 |  |  |  | 38560 | Y | N
Old Project | No Change | 13TPIT0201 | Goldsmith South - Goldsmith Junction 138 kV line | Rebuild existing 69 kV line to create a double-circuit line with 69 kV and 138 kV circuits and connect the 138 kV circuit to an existing Moss - Ector County North 138 kV line. |  | Goldsmith South Substation | Goldsmith Junction | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8120-E | 2013-06-01 |  | 138 | 5.54 | 5.5 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 11250 | Y | N
Old Project | No Change | 15TPIT0006 | Bandera to Broadview - 138kV substation equipment upgrade | Upgrade substation equipment at Broadview to remove existing MLSE on the Bandera to Broadview 138kV line |  | Bandera | Broadview | Planned |  | CPS | PM: Ulrich Skerhut | S-0395 | 2013-06-01 |  | 138 | 0 | 0 | 0.0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5020 5040 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 10TPIT0031 | Dunlap 138/345kV Autotransformer Project | Install a 138/345 672 MVA autoxfmr at Dunlap, configuring a Dunlap to Lost Pines 345 kV circuit, add a new 345kV line from Dunlap to Austrop and merge 138kv Dunlap to Decker and Decker to Techridge into one single circuit bypassing Decker. Re-terminate the WebberSolar Tap into the vacant Austrop 138kV position. | As part of the project, the existing Webber Solar Tap will be removed and the solar plant will be connected to the existing vacant position at Austrop substation. | Dunlap Substation | Dunlap Substation | Under Construction |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P132 | 2013-06-01 |  | 345 | 0 | 0 | 672.0 | 0 | TRAVIS | TRAVIS | Tier 3 | 2010-04-01 | 2010-06-01 | N/A | 9044, 9045 | Y | N
Old Project | No Change | 13TPIT0036 | Krum West - Riley (Oklaunion) 345 kV line (Oncor Electric Delivery portion) | Construct double-circuit 345 kV line |  | Krum West | Riley | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C050-E | 2013-06-01 |  | 345 | 326.2 | 0 | 0.0 | 0 | DENTON | WILBARGER | CREZ |  |  |  | 1730, 6101 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0037 | Krum West Switch | Construct 345 kV switching station |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C017-E | 2013-06-01 |  | 345 | 0 | 0 | 0.0 | 0 | DENTON |  | CREZ |  |  |  | 1730 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0038 | Hicks Switch | Construct 345 kV switching station |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C030-E | 2013-06-01 |  | 345 | 0 | 0 | 0.0 | 0 | TARRANT |  | CREZ |  |  |  | 2081 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0039 | Willow Creek - Hicks Switch 345 kV line | Construct double-circuit 345 kV line |  | Hicks Switch | Willow Creek | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C061-E | 2013-06-01 |  | 345 | 80.4 | 0 | 0.0 | 0 | TARRANT | WISE | CREZ |  |  |  | 2081, 1421 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0040 | Willow Creek Switch circuit breakers | Install 345 kV circuit breakers. |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C012B-E | 2013-06-01 |  | 345 | 0 | 0 | 0.0 | 0 | WISE |  | CREZ |  |  |  | 1421 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | Change in Service Date. Changed from 12/1/2013 to 6/1/2013 | 13TPIT0074 | Willow Creek Switch | Install shunt reactors. |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C054B-E | 2013-06-01 |  | 345 | 0 | 0 | 0.0 | -100 | WISE |  | CREZ |  |  |  | 1421 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0093 | Willow Valley Switch | Install 345/138 kV autotransformer |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8029-E | 2013-06-01 |  | 345 | 0 | 0 | 600.0 | 0 | BORDEN |  | Tier 2 | 2011-03-01 | 2011-04-01 |  | 1301 | Y | N
Old Project | No Change | 13TPIT0096 | Krum West Switch reactors | Install shunt reactors |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C085R-E | 2013-06-01 |  | 345 | 0 | 0 | 0.0 | -100 | DENTON |  | CREZ |  |  |  | 2373 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0181 | Gilleland Creek Autotransformer Replacement | Replace failed autotransformer at the Gilleland Creek substation | No autotransformer will be in service at Gilleland Creek until the replacement is installed |  |  | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-06-01 |  | 345 | 0 | 0 | 672.0 | 0 | TRAVIS |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | Cost will be determined during the September TPIT.
Old Project | Change in Service Date. Changed from 3/29/2013 to 6/3/2013 | 12TPIT0126 | Pyote cap bank | Install 10 MVAR, 69kV cap bank at Pyote Substation |  | Pyote |  | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE03912 | 2013-06-03 |  | 69 | 0 | 0 | 0.0 | 10 | Ward |  | Tier 4 |  |  |  | 38000 | Y | N
Old Project | Change in Service Date. Changed from 4/11/2013 to 6/13/2013 | 11TPIT0134 | Dye Mound Capacitor Bank | Install 25 MVAR at Dye Mound substation |  | Dye Mound |  | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10026 | 2013-06-13 |  | 138 | 0 | 0 | 0 | 25 | MONTAGUE |  | Tier 4 |  |  |  | 741 | Y | N
Old Project | Change in Service Date. Changed from 4/19/2013 to 6/13/2013 | 12TPIT0135 | Spring to Bridgeport Switch | Rebuild 30.3 miles of line with 959 ACSS |  | Spring | Bridgeport Switch | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11008 | 2013-06-13 |  | 138 | 0 | 33.3 | 0.0 | 0 | COOKE | WISE | Tier 4 |  |  |  | 684, 587, 634, 992 | Y | N
Old Project | No Change | 12TPIT0051 | LS01 Silverton to Nazareth | Construct a new 345kV single circuit line from Silverton switching station to Nazareth switching station. | New | Silverton | Nazareth | Under Construction | 12TPIT0053 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharyland.com |  | 2013-06-20 |  | 345 | 46 | 0 | 0.0 | 0 | BRISCOE | CASTRO | CREZ |  |  |  | 99103-99101 | Y | N
Old Project | No Change | 12TPIT0053 | Nazareth Collection Station | Construct the new 345 kV Nazareth switching station.Initial build is 7 element ring bus arrangement. | New |  |  | Under Construction | 12TPIT0051 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharyland.com |  | 2013-06-20 |  | 345 | 0 | 0 | 0.0 | -50 | CASTRO |  | CREZ |  |  |  | 99101 | Y | N
Old Project | No Change | 13TPIT0012 | Zorn Autotransformer Addition | Add a new 345-138 kV 478 MVA autotransformer at the Zorn substation (7042). |  | Big Hill |  | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-06-27 |  | 345 | 0 | 0 | 478 | 0 | GUADALUPE |  | Tier 3 | 2008-01-30 | 2008-06-10 | N/A | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 11TPIT0174 | Nall to Briarcrest Upgrade | Upgrade 0.82 miles of conductor from 2/0 ACSR to 795 ACSR and replace transmission poles as needed. |  | Nall Lane Substation | Briarcrest Substation | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-06-30 |  | 69 | 0 | 0.82 | 0.0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 13TPIT0175 | Wormser Road: Install DRCS | Relocate DRCS from Hamilton Road to Wormser Road. | Reformated project number to match other numbers | Wormser |  | Planned | 563 - 0731 | AEP/TCC/ETT | Glen Reed 918-599-2664 | 3441 | 2013-06-30 |  | 69 | 0 | 0 | 0 | 0 | VAL VERDE | 0 | Tier 4 | 0 | 0 | 0 | 0 | N | N | 0 | 0
Old Project | Change in Service Date. Changed from 4/30/2013 to 6/30/2013 | 13TPIT0122 | Choate Station and Autotransformer | Build new Choate substation where Pawnee to Four Corners 138 kV and Kenedy to Charco 69 kV lines cross and add a 150 MVA 139/69 kV autotransformer |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-06-30 |  | 138 | 0 | 0 | 150.0 | 0 | KARNES |  | Tier 2 | 2011-12-16 | 2012-04-25 | N/A | 5728, 5729 | Y | N
Old Project | No Change | 13TPIT0213 | Mont Belvieu Area Upgrades | Install second 73.3MVAR capacitor bank at Mont Belvieu substation. |  | Mont Belvieu |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-06-30 |  | 138 | 0 | 0 | 0.0 | 73.3 | CHAMBERS |  | Tier 4 |  |  |  | 41111 | Y | N
Old Project | Change in Service Date. Changed from 9/30/2013 to 6/30/2013 | 13TPIT0214 | RALYND 138kV Substation | Construct service to new 138kV RALYND customer-owned substation. Loop through ENPROD - NORTON and rename circuits to 59. | Accelerated project schedule | RALYND | ENPROD/ NORTON | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-06-30 |  | 138 | 0.3 | 0 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 4 |  |  |  | 40762 | N | N
Old Project | No Change | 13TPIT0223 | Bryan East Carrier Replacement | Upgrade line protection and communications by replacing wavetrap equipment with OPGW and modern relays |  | Bryan East | Gibbons Creek | Planned |  | TMPA | Tom Chambers 936-873-1125 tchambers@texasmpa.org | T13003 | 2013-06-30 |  | 138 | 0 | 0 | 0 | 0 | Brazos |  | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 13TPIT0098 | Faraday Switch | Establish new 345 kV Faraday station in WETT's Long Draw-S. Scurry 345 kV line. |  |  |  | Planned |  | Wind Energy Transmission Texas (WETT) | Julius Horvath (512) 279-7377 julius.horvath@windenergyoftexas.com |  | 2013-06-30 |  | 345 | 0 | 0 | 0.0 | 0 | BORDEN |  | Tier 2 | 2011-03-18 | 2011-04-18 | N/A | 59905 | Y | N |  | Project is shown in the DSB 2013 and later (2014, 2015, etc) cases
Old Project | Change in Service Date. Changed from 6/1/2013 to 7/1/2013 | 13TPIT0164 | Big Oak 69 kV Substation | Build new load serving station in the 69 kV line between Beeville and Goliad Switch. |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-07-01 |  | 69 | 0 | 0 | 0.0 | 0 | GOLIAD |  | Tier 4 | 2012-08-31 | on-going | N/A | 5675 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 7/1/2013 | 13TPIT0127 | Tilden 138 kV Substation | Convert Tilden from 69 kV to 138 kV and connect to new 138 kV line from Tilden to George West. |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-07-01 |  | 138 | 0 | 0 | 0.0 | 0 | MCMULLEN |  | Tier 4 |  |  |  | 5701 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 7/1/2013 | 13TPIT0129 | George West to Tilden Rebuild | Rebuild 4/0 ACSR 69 kV to double circuit 138 kV capable 795 ACSR. One circuit will be operated at 69 kV from George West to Choke Canyon Prison Sub. The other will be 138 kV from George West to Tilden |  | George West | Tilden | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-07-01 |  | 138 | 20.6 | 8.4 | 0.0 | 0 | MCMULLEN | LIVE OAK | Tier 4 |  |  |  | 5688, 5701 | Y | N
Old Project | No Change | 05TPIT0072 | Mountain Top-Blanco-Devil's Hill | Close the 69-kV switch (SW 458) at the Blanco substation(7482) to loop the load located at the Blanco substation. Upgrade the capacity of the 138-69-kV auto-transformer (T2) at the Devil’s Hill substation(7493) from 20-MVA to 45-MVA. | Devil's Hill Auto Installed. Construction for Blanco bus to close Loop not scheduled to complete until July 2013. | Mountain Top | Devil's Hill | Under Construction |  | PEC | Tony Perez (830) 868-5158 | 1005443 | 2013-07-13 |  | 138 | 0 | 0 | 45.0 | 0 | BLANCO | COMAL | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 13TPIT0146 | Central Avenue Sub- 138kV Breaker Addition | Install 138kV Breakers |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-07-13 |  | 138 | 0 | 0 | 0.0 | 0 | CAMERON |  | Tier 4 |  |  |  | 8766 | Y | N
Old Project | Change in Service Date. Changed from 6/10/2013 to 7/15/2013 | 11TPIT0133 | Bowie to Montague Rebuild | Rebuild Bowie to Montague 69kV line with 959 ACSS |  | Bowie | Montague | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10015 | 2013-07-15 |  | 69 | 0 | 11 | 0.0 | 0 | MONTAGUE | MONTAGUE | Tier 4 |  |  |  | 621, 632, 633 | Y | N
Old Project | No Change | 12TPIT0022 | North McCamey Autotransformer Addition | Add two new 345-138 kV 800 MVA autotransformer at the North McCamey substation (76595). |  | North McCamey |  | Planned | 12TPIT0026 (STEC) 12TPIT0027 (STEC) | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-07-17 |  | 345 | 0 | 0 | 1600 | 0 | UPTON |  | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | CREZ Default project assigned to LCRA TSC
Old Project | No Change | 12TPIT0048 | Hereford Collection Station | Construct the new 345 kV Hereford switching station.Initial build is 7 element folded breaker and one half bus arrangement | New |  |  | Under Construction | 13TPIT0042, 13TPIT0043 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharyland.com |  | 2013-07-20 |  | 345 | 0 | 0 | 0.0 | -200 | DEAF SMITH |  | CREZ |  |  |  | 99102 | Y | N
Old Project | No Change | 12TPIT0052 | LS02 Nazareth to Hereford | Construct a new 345kV single circuit line from Nazareth Switching to Hereford switching station | New | Nazareth | Hereford | Under Construction |  | SU | Mark Caskey, (214) 978-8243, mcaskey@sharyland.com |  | 2013-07-20 |  | 345 | 25.5 | 0 | 0.0 | 0 | CASTRO | DEAF SMITH | CREZ |  |  |  | 99101-99102 | Y | N
Old Project | No Change | 13TPIT0216 | Reveille substation 138kV: STEC Interconnect | Reveille substation 138kV: STEC Interconnect | Changed Status and Associated project number format | Reveille |  | Under Construction | 564 - 0732 | AEP/TCC | Mike Tallon 918-599-2664 | 3442 | 2013-07-22 |  | 138 | 0 | 0 | 0 | 0 | LA SALLE |  | Tier 4 |  |  |  | 8612 | Y | N
Old Project | Change in Service Date. Changed from 6/30/2013 to 7/30/2013 | 13TPIT0051 | Gray to Tesla, build double circuit 345 kV line | Build new Gray Substation (Panhandle B-B) including 150 to 200 MVAR of reactive compensation and 345 kV double circuit line from Gray to Tesla | The transmission line is still scheduled to be completed March, 2013 but CTT expects the in-service date will be dependent on the in-service date of downstream facilities. | Gray | Tesla | Under Construction |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-07-30 |  | 345 | 218 | 0 | 0.0 | 0 | GRAY | CHILDRESS | CREZ |  |  |  | 79000-60501, CKT 1 & 79000-60501, CKT 2 | Y | N
Old Project | Change in Service Date. Changed from 6/30/2013 to 7/30/2013 | 13TPIT0052 | Gray Substation (Panhandle B-B), build new collector substation | Build new Gray Substation (Panhandle B-B) including 150 to 200 MVAR of reactive compensation and 345 kV double circuit line from Gray to Tesla | The Gray Substation is still scheduled to be completed March, 2013 but CTT expects the in-service date will be dependent on the in-service date of downstream facilities. | - | - | Under Construction |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-07-30 |  | 345 | 0 | 0 | 0.0 | 0 | GRAY | - | CREZ |  |  |  | 79000 | Y | N
Old Project | Change in Service Date. Changed from 6/30/2013 to 7/30/2013 | 13TPIT0053 | Gray Substation (Panhandle B-B), build 150 to 200 MVAR of Reactive Compensation | Build new Gray Substation (Panhandle B-B) including 150 to 200 MVAR of reactive compensation and 345 kV double circuit line from Gray to Tesla | The installation of the reactors are still scheduled to be completed March, 2013 but CTT expects the in-service date will be dependent on the in-service date of downstream facilities. | - | - | Under Construction |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-07-30 |  | 345 | 0 | 0 | 0.0 | -200 | GRAY | - | CREZ |  |  |  | 79000 | Y | N
Old Project | Change in Service Date. Changed from 5/31/2013 to 7/31/2013 | 12TPIT0059 | Sand Bluff 345 kV Station and Sand Bluff to Divide 345 kV line | Establish new 345 kV Sand Bluff station and construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Sand Bluff and LCRA TSC's Divide 345 kV stations. |  | Sand Bluff | Divide | Planned |  | Wind Energy Transmission Texas (WETT) | Julius Horvath (512) 279-7377 julius.horvath@windenergyoftexas.com |  | 2013-07-31 |  | 345 | 37 | 0 | 0.0 | 0 | GLASSCOCK | COKE | CREZ |  |  |  | 59902 | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | Change in Service Date. Changed from 5/31/2013 to 7/31/2013 | 12TPIT0060 | Bearkat 345 kV Station and Bearkat to Sand Bluff 345 kV line | Establish new 345 kV Bearkat station and construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Sand Bluff and new Bearkat 345 kV stations. |  | Bearkat | Sandbluff | Planned |  | Wind Energy Transmission Texas (WETT) | Julius Horvath (512) 279-7377 julius.horvath@windenergyoftexas.com |  | 2013-07-31 |  | 345 | 28.9 | 0 | 0.0 | 0 | GLASSCOCK | STERLING | CREZ |  |  |  | 59903 | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | Change in Service Date. Changed from 5/31/2013 to 7/31/2013 | 12TPIT0061 | Sand Bluff to Long Draw 345 kV line | Construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Sand Bluff and new Long Draw 345 kV stations. |  | Sand Bluff | Long Draw | Planned |  | Wind Energy Transmission Texas (WETT) | Julius Horvath (512) 279-7377 julius.horvath@windenergyoftexas.com |  | 2013-07-31 |  | 345 | 77.4 | 0 | 0.0 | 0 | GLASSCOCK | BORDEN | CREZ |  |  |  |  | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | Change in Service Date. Changed from 6/30/2013 to 7/31/2013 | 13TPIT0019 | Riley to Edith Clarke double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | Schedule Update | Riley | Edith Clarke | Under Construction | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2381 | 2013-07-31 |  | 345 | 86.6 | 0 | 0 | 0 | WILBARGER | COTTLE | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 6/30/2013 to 7/31/2013 | 13TPIT0020 | Tesla to Edith Clarke double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | Schedule Update | Tesla | Edith Clarke | Under Construction | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2382 | 2013-07-31 |  | 345 | 110.4 | 0 | 0 | 0 | COTTLE | COTTLE | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 6/1/2013 to 7/31/2013 | 13TPIT0022 | Gray to Oklaunion double circuit 345kV line (Tesla to Riley portion) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | Schedule Update | Tesla | Riley | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2384 | 2013-07-31 |  | 345 | 131.2 | 0 | 0 | 0 | GRAY | WILBARGER | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/25/2013 to 7/31/2013 | 13TPIT0023 | Edith Clarke 345kV station | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | Schedule Update | Edith Clarke |  | Under Construction | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2387 | 2013-07-31 |  | 345 | 0 | 0 | 0 | 0 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2013 to 7/31/2013 | 13TPIT0024 | Edith Clarke, add two 130.9 MVar capacitors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Edith Clarke |  | Under Construction | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2389 | 2013-07-31 |  | 345 | 0 | 0 | 0 | +261.8 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2013 to 7/31/2013 | 13TPIT0025 | Edith Clarke, add four 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Edith Clarke |  | Under Construction | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2390 | 2013-07-31 |  | 345 | 0 | 0 | 0 | -200 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2013 to 7/31/2013 | 13TPIT0026 | Tesla 345kv Switching Station | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis **Complete but Not in Service** | Schedule Update | Tesla |  | Under Construction | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2393 | 2013-07-31 |  | 345 | 0 | 0 | 0 | 0 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2013 to 7/31/2013 | 13TPIT0027 | Tesla, add two 130.9 MVar capacitors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Tesla |  | Under Construction | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2394 | 2013-07-31 |  | 345 | 0 | 0 | 0 | +261.8 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2013 to 7/31/2013 | 13TPIT0028 | Tesla, add four 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis **Complete but Not in Service** | Schedule Update | Tesla |  | Under Construction | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2395 | 2013-07-31 |  | 345 | 0 | 0 | 0 | -200 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 4/1/2013 to 8/1/2013 | 13TPIT0132 | Freer Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-08-01 |  | 69 | 0 | 0 | 0.0 | 9.6 | WEBB |  | Tier 4 |  |  |  | 5880 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 8/1/2013 | 13TPIT0147 | Carrizo Springs Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-08-01 |  | 69 | 0 | 0 | 0.0 | 9.6 | DIMMIT |  | Tier 1 | 2012-04-16 | 2012-08-30 | 2012-09-18 | 5872 | Y | N
Old Project | No Change | 12TPIT0029 | Big Hill to Kendall | Construct a new double circuit 345 kV transmission line (approximately 137 miles) between the new Big Hill (76003) and the existing Kendall station (7046). The new transmission lines will consist of Cumberland conductor to provide a thermal rating of 2988 MVA each. |  | Big Hill | Kendall | Planned | 13TPIT0018 (STEC) 13TPIT0029 (AEP) 13TPIT0084 (AEP) 13TPIT0086 (AEP) 13TPIT0087 (AEP) | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-08-01 |  | 345 | 274 | 0 | 0.0 | 0 | SCHLEICHER | KENDALL | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 13TPIT0018 | McCamey C to McCamey D (Bakersfield to Big Hill) | Construct new 113 miles 1590 ACSR 345 kV line from Bakersfiled to Big Hill (McCamey C to McCamey D). |  | Bakersfield | Big Hill | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-08-01 |  | 345 | 112 | 0 | 0.0 | 0 | PECOS | SCHLEICHER | CREZ |  |  |  | 76002-76003 | Y | N
Old Project | No Change | 13TPIT0042 | LS03 White Deer to Hereford | Construct a new 345kV single circuit line from White Deer switching station to Hereford switching station | New | White Deer | Hereford | Under Construction | 12TPIT0048, 13TPIT0043 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharyland.com |  | 2013-08-30 |  | 345 | 91.2 | 0 | 0.0 | 0 | CARSON | DEAF SMITH | CREZ |  |  |  | 99201-99102 | Y | N
Old Project | No Change | 13TPIT0043 | White Deer Collection Station | Construct the new 345 kV White Deer switching station.Initial build is 10 element folded breaker and one half bus arrangement. | New |  |  | Under Construction | 12TPIT0048, 13TPIT0042 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharyland.com |  | 2013-08-30 |  | 345 | 0 | 0 | 0.0 | -100 | CARSON |  | CREZ |  |  |  | 99201 | Y | N
Old Project | Change in Service Date. Changed from 12/31/2012 to 8/31/2013 | 12TPIT0194 | Castroville Switch to Quihi | Rebuild the existing Castroville Switch to Quihi Sw 69 kV line with 795 ACSR at the same time AEP is constructing Uvalde to CPS Castroville 138 kV line with 2x795 ACSR. Utilizes open circuit for existing 69kV circuits in same ROW. Also removes the pole mounted switches that are Quihi Switch. |  | Castroville Switch | Quihi | Planned | 08TPIT0018 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-08-31 |  | 69 | 0 | 7.38 | 0 | 0 | MEDINA | MEDINA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 5805, 5807, 5821 | Y | N |  | The cost for this project appears low, but the cost of the towers is in the associated separate project.
Old Project | Change in Service Date. Changed from 12/31/2013 to 8/31/2013 | 13TPIT0086 | Edison, add two 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Edison |  | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2487 | 2013-08-31 |  | 345 | 0 | 0 | 0 | -100 | KENDALL |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 12/31/2013 to 8/31/2013 | 13TPIT0087 | Orsted, add two 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Orsted |  | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2488 | 2013-08-31 |  | 345 | 0 | 0 | 0 | -100 | KENDALL |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 5/31/2013 to 9/1/2013 | 12TPIT0081 | 36th St - New 138kV Substation | Loop new 138kV substation into existing 138kV Merida to Medina Base line and replace exiting Kelly Field #3 138kV substation | Delayed due to Budget Constraints | Merida | Medina Base | Planned | T-0161 | CPS | PM: Hector Torres | S-0578 | 2013-09-01 |  | 138 | 0.1 | 0 | 0.0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5427 5245 5305 5310 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 13TPIT0151 | Gibbons Creek Reactive Support | Install transmission reactors and associated switching devices and replace existing T1 autotransformer |  | Gibbons Creek | Gibbons Creek | Planned |  | TMPA | Tom Chambers 936-873-1125 tchambers@texasmpa.org | T13003 | 2013-09-01 |  | 345 | 0 | 0 | 600.0 | -135 | Grimes |  | Tier 3 | 2012-09-24 | 2012-10-29 | N/A |  | N | N
Old Project | No Change | 13TPIT0055 | Tule Canyon to Tesla, build double circuit 345 kV line | Build 345 kV double circuit line from Tule Canyon to Tesla | Updated station names. | Tule Canyon | Tesla | Under Construction |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-09-12 |  | 345 | 172 | 0 | 0.0 | 0 | BRISCOE | CHILDRESS | CREZ |  |  |  | 79503-79001, 79002-60501 & 79503-79003, 79004-60501 | Y | N
Old Project | No Change | 13TPIT0056 | Tule Canyon to Tesla, build series compensation | Add series compenstion to both circuit of the 345 kV double circuit line from Tule Canyon to Tesla | Updated station names. | - | - | Under Construction |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-09-12 |  | 345 | 0 | 0 | 0.0 | 0 | Hall | - | CREZ |  |  |  | 79001-79002 & 79003-79004 | Y | N
New Project | New Project | 13TPIT0232 | West Lamesa 138 kV Sub | Tap the Western Dawson (Jim Payne Breaker Station) and build 4.5 miles of 138 kV transmission north to the new West Lamesa Sub, which will be loaded to 4 MVA when energized. |  |  |  | Planned |  | Golden Spread/Lyntegar EC | Chris Koenig 806-349-5201 ckoenig@gsec.coop |  | 2013-09-13 |  | 138 | 4.5 | 0 | 0 | 0 | DAWSON | DAWSON | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 11TPIT0108 | Penascal Wind Phases 3 Generation Interconnect | Penascal Wind Phases 2 and 3 (Added Terminal From) |  | Penascal |  | Under Construction | 489 - 0690 | AEP/ETT/TCC | John Pulay 918-599-2664 | 3370 | 2013-09-21 |  | 345 | 0 | 0 | 0 | 0 | KENNEDY |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0176 | Wormser Road: Install Capacitor Bank | Install one (1) - 14.4 MVAR Capacitor Bank at Wormser Road substation. | Reformated project number to match other numbers | Wormser |  | Planned | 563 - 0731 | AEP/TCC | Glen Reed 918-599-2664 | 3457 | 2013-09-30 |  | 69 | 0 | 0 | 0 | 0 | VAL VERDE | 0 | Tier 4 | 0 | 0 | 0 | 0 | N | N | 0 | 0
Old Project | No Change | 10TPIT0048 | Koppe Bridge Substation | Install (4) Breaker ring to include (2) 138 lines and (1) 138/12.5 transformer |  | Koppe Bridge | Koppe Bridge | under construction | 10TPIT0049 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-09-30 |  | 138 | 0 | 0 | 0.0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32860 | Y | N
Old Project | No Change | 10TPIT0049 | Koppe Bridge to Wellborn Transmission | Build (5.8) miles of 138 kV line(s) to serve station |  | Koppe Bridge | Wellborn | planned | 10TPIT0048 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-09-30 |  | 138 | 6.2 | 0 | 0.0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  | 32860 32895 | Y | N
Old Project | No Change | 11TPIT0111 | Snook to Koppe Bridge Transmission Line | Build 13 miles of 1033ACSR transmission line (operated at 138 kV) to Koppe Bridge substation. | The Thompson Creek to Koppe Bridge Line is now broken into two segments with different completion dates. | Snook Substation | Koppe Bridge | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-09-30 |  | 138 | 13 | 0 | 0.0 | 0 | BURLESON | BRAZOS | Tier 4 |  |  |  | 32863 32860 | Y | N
Old Project | No Change | 13TPIT0015 | Wellborn Switching Sub | Install (3) Breaker ring to include (2) 138 lines and (1) 138/69 auto transformer relocated from Greens Prairie |  | Wellborn | Wellborn | planned | 10TPIT0049 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-09-30 |  | 138 | 0 | 0 | 20.0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32895 (138) 32898 (69) | Y | N
Old Project | No Change | 13TPIT0016 | Greens Prairie to Wellborn Transmission | ReBuild-Reconductor (3.75) miles of 69kV line converting to 138 kV to serve Wellborn |  | Greens Prairie | Wellborn | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-09-30 |  | 138 | 0 | 3.82 | 0.0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  | 32878 32895 | Y | N
Old Project | No Change | 13TPIT0017 | Greens Prairie Substation | Install (1) Breaker in existing ring bus for a 138 line from Wellborn/Millican Substation(s) |  | Greens Prairie | Greens Prairie | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-09-30 |  | 138 | 0 | 0 | 0.0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32878 | Y | N
Old Project | No Change | 13TPIT0083 | Snook Substation | Install (3) Breaker ring to include (2) 138 lines and (1) 138/69 auto transformer relocated from Thompson Creek. |  | Snook Substation | Snook Substation | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-09-30 |  | 138 | 0 | 0 | 0.0 | 0 | BURLESON |  | Tier 4 |  |  |  | 32857 32865 | Y | N
Old Project | No Change | 13TPIT0174 | Piloncillo 138 kV Station: Install breaker ring bus | Construct 4 CB ring bus at new Piloncillo station on Asherton to North Laredo 138 kV line |  | Piloncillo |  | Under Construction | 600 - 0762 | AEP/TCC | Michael Tallon 918-599-2664 | 3469 | 2013-09-30 |  | 138 | 0 | 0 | 0 | 0 | DIMMIT |  | Tier 4 |  |  |  | 89630 | Y | N
Old Project | Change in Service Date. Changed from 5/31/2013 to 9/30/2013 | 13TPIT0188 | Crabb River Road Substation Reconfiguration | Reconfigure 138kV Crabb River Road substation from loop to double tap. Tap Ckt.80 between WA Parish and Imperial. | Delay in project schedule | Crabb River Road | WA Parish/ Imperial | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-09-30 |  | 138 | 0.2 | 0 | 0.0 | 0 | FORT BEND | FORT BEND | Tier 4 |  |  |  | 44010, 44171, 44172, 44341, 44170 | Y | N |  | Part of Fort Bend Area Upgrades.
Old Project | Change in Service Date. Changed from 12/31/2013 to 9/30/2013 | 13TPIT0212 | Mont Belvieu Area Upgrades | Upgrade 138kV Ckt. 86 Crosby to Bender to increase thermal ratings. | Accelerated project schedule | CROSBY | BENDER | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-09-30 |  | 138 | 0 | 1.4 | 0.0 | 0 | HARRIS | CHAMBERS | Tier 4 |  |  |  | 402390, 40155 | Y | N |  | Cost included in main project. This TPIT entry includes the completion of the circuit segment upgrade which is scheduled to be complete by Dec 2013
Old Project | No Change | 13TPIT0033 | Edith Clarke to West Shackelford double circuit 345kV line (Clear Crossing to West Shackelford portion) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | Clear Crossing | West Shackleford | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2386 | 2013-09-30 |  | 345 | 67.6 | 0 | 0 | 0 | COTTLE | SHACKELFORD | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0054 | Gray to Alibates, build double circuit 345 kV line | Build 345 kV double circuit line from Gray to Alibates | Updated station names. | Gray | Alibates | Under Construction |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-09-30 |  | 345 | 83 | 0 | 0.0 | 0 | GRAY | CARSON | CREZ |  |  |  | 79000-79500,CKT 1 & 79000-79500,CKT 2 | Y | N
Old Project | Change in Service Date. Changed from 6/30/2013 to 9/30/2013 | 13TPIT0109 | Ajo to Rio Hondo: Reconductor 345kV line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo | Updated Schedule | Ajo | Rio Hondo | Planned | 071 - 0281 | AEP/ETT/TCC | Glen Reed 918-599-2664 | 3182 | 2013-09-30 |  | 345 | 0 | 66.708 | 0 | 0 | KENEDY | CAMERON | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 80076, 8318 | Y | N
Old Project | No Change | 13TPIT0169 | Eiland Substation | Construct new 2257 Eiland Substation, 30 MVA, with bi-directional interconnection to Oncor's Spraberry to Morgan Creek 138 Kv transmission line to transfer new and existing load into ERCOT, 2372 St LawerenceSubstation, 2168 Stiles Substaion, New 2570 East Stiles Substation | New | Oncor Spraberry Switch Yard | Oncor Morgan Creek Switch Yard | Planned |  | SU | Dwight Yarbrough (956) 279-6902 dyarbrough@sharyland.com |  | 2013-10-01 |  | 138 | 2 | 0 | 0 | 0 | GLASSCOCK |  | Tier 4 |  |  | N/A |  | N | N
Old Project | No Change | 13TPIT0209 | Mockingbird Substation Addition | Construct a new substation named Mockingbird (78259) on the Glidden - Fayetteville 138-kV transmission line. |  | Mockingbird | Glidden/Fayetteville | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-10-01 |  | 138 | 0 | 0 | 0 | 0 | COLORADO |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | Coordinate with AEP
Old Project | No Change | 13TPIT0224 | Nevada Substation | Reconfigure 138kV Shelby to Royce Line to accommodate new 138kV Nevada substation |  | Nevada | Shelby | Planned |  | TMPA | Tom Chambers 936-873-1125 tchambers@texasmpa.org | T13004 | 2013-10-01 |  | 138 | 0 | 0.25 | 0 | 0 | Collin |  | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 12TPIT0192 | Triangle Switch Yard | Construct a four position breaker station with a 30 MVA transformer | New | Oncor Stanton East | Oncor Midland East | Planned |  | SU | Dwight Yarbrough (956) 279-6902 dyarbrough@sharyland.com |  | 2013-10-13 |  | 138 | 0 | 0 | 0.0 | 0 | MARTIN |  | Tier 4 | 2011-01-01 | 2011-05-24 | N/A | 79619, 79609 | Y | N |  | Docket #37090
Old Project | No Change | 12TPIT0098 | Bruni relay upgrade | Additional relays will be installed to allow the autotransformer to be normally closed. |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-10-28 |  | 138 | 0 | 0 | 0.0 | 0 | WEBB |  | Tier 4 |  |  |  | 5887, 5888 | Y | N
Old Project | No Change | 12TPIT0174 | Pointer, Build new three breaker ring bus | Construct new Pointer station along the Munday to Rule 69 kV line |  | Munday | Rule | Under Construction | 504 - 0715 | AEP/TNC | Terry Weeks 918-599-2664 | 2496 | 2013-10-31 |  | 69 | 0 | 0 | 0 | 0 | KNOX |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0116 | North Brady: Add two 7.2 Mvar capacitor banks | Add two 7.2 Mvar capacitor banks at North Brady and add 7.2 Mvar capacitor bank at Katemcy | Contact Update | North Brady |  | Planned | 559 - 0722 | AEP/TNC | Eric Scott 918-599-2664 | 2561 | 2013-10-31 |  | 69 | 0 | 0 | 0 | +14.4 | MCCULLOCH |  | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 12/31/2013 to 10/31/2013 | 13TPIT0173 | Friend Ranch: Remove 10 MVA DRCS | Add 3.6 Mvar capacitor bank at Barnhart SWTEC and add 10 MVA DRCS with 7.2 Mvar capacitor bank at Yucca | Schedule Update | Friend Ranch |  | Planned | 558 - 0721 | AEP/TNC | Michael Tallon 918-599-2664 | 2564 | 2013-10-31 |  | 69 | 0 | 0 | 0 | 0 | CROCKETT | 0 | Tier 4 | 0 | 0 | 0 | 0 | Y | N | 0 | 0
New Project | New Project | 13TPIT0229 | Harrisburg Cap Bank | Move existing 7.2MVAR cap bank at South Houston 69kV substation to Harrisburg 69kV substation. |  | Harrisburg |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-10-31 |  | 69 | 0 | 0 | 0.0 | 0 | HARRIS |  | Tier 4 |  |  |  | 40800 | Y | N |  | Part of South Houston conversion project
Old Project | Change in Service Date. Changed from 12/1/2015 to 10/31/2013 | 10TPIT0010 | Coppell to Roanoke Reconductor | Reconductor existing Coppell to Roanoke 138kv line with 959ACSS conductor |  | Coppell | Roanoke | planned | 12TPIT0079 | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 02005 | 2013-10-31 |  | 138 | 0 | 17 | 0.0 | 0 | TARRANT | DALLAS | Tier 4 |  |  |  | 1852, 661, 556, 555, 648 | Y | N |  | construction by Oncor
Old Project | Change in Service Date. Changed from 5/31/2013 to 10/31/2013 | 12TPIT0190 | Boots: Build 138 kV Box Bay Structure with three breakers | Interconnect White Camp Solar Farm at Boots to connect White Camp to the Spur to Sun 138 kV line | Schedule Update | Spur | Sun | Under Construction | 507 - 0718 | AEP/TNC | Eric Scott 918-599-2664 | 2502 | 2013-10-31 |  | 138 | 0 | 0 | 0 | 0 | KENT |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0158 | Bruni to MEC Bruni: Rebuild 138 kV line | Reterminate MEC Bruni tap into Bruni sub-station and upgrade sub-station to 4 breaker ring bus | Reformated project number to match other numbers | Bruni | MEC Bruni | Under Construction | 572 - 0749 | AEP/TCC | Michael Tallon 918-599-2664 | 3450 | 2013-10-31 |  | 138 | 0.5 | 0.1 | 0 | 0 | WEBB | WEBB | TIER 4 | 0 |  |  | 8297, 8958 | Y | N
Old Project | No Change | 13TPIT0159 | Bruni 138 kV station: Install 138 kV breakers ring bus | Reterminate MEC Bruni tap into Bruni sub-station and upgrade sub-station to 4 breaker ring bus | Reformated project number to match other numbers | Bruni |  | Under Construction | 572 - 0749 | AEP/TCC | Michael Tallon 918-599-2664 | 3453 | 2013-10-31 |  | 138 | 0 | 0 | 0 | 0 | WEBB | 0 | TIER 4 |  |  |  | 8297 | N | N
Old Project | No Change | 13TPIT0217 | Jardin substation 138kV: STEC Interconnect | Jardin substation 138kV: STEC Interconnect | Changed associated Project number format, and changed status | Jardin |  | Under Construction | 565 - 0733 | AEP/TCC | Mike Tallon 918-599-2664 | 3443 | 2013-10-31 |  | 138 | 0 | 0 | 0 | 0 | LA SALLE |  | Tier 4 |  |  |  | 8611 | Y | N
Old Project | No Change | 13TPIT0221 | Greenville 138kV Line Rebuild Olinger to Interchange to Shelby Tap (Segment 2) | Replace wooden transmission structures and install new conductor on approximately 3 miles of line | Split project in two line segments to facilitate outage coordination | Olinger | Greenville Interchange | Under Construction |  | TMPA | Tom Chambers 936-873-1125 tchambers@texasmpa.org | T13006 | 2013-10-31 |  | 138 | 0 | 3 | 0.0 | 0 | Hunt |  | Tier 4 |  |  |  |  | N | N
New Project | New Project | 13TPIT0228 | Hall/ Mary's Creek Circuit Reconfiguration | Move existing Hall/ Mary's Creek tap from Ckt.91 to Ckt.92. |  | Hall | Garden Villas/ South Houston | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-10-31 |  | 138 | 0.1 | 0 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 42680, 42762, 42922, 43272 | Y | N |  | Part of South Houston conversion project
Old Project | Change in Service Date. Changed from 12/9/2013 to 10/31/2013 | 13TPIT0029 | Big Hill to Kendall Series Compensation (Edison) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Edison |  | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2398 | 2013-10-31 |  | 345 | 0 | 0 | 0 | +933 | SCHLEICHER | KENDALL | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 9/30/2013 to 10/31/2013 | 13TPIT0030 | Dermott to Willow Creek (Dermott to Clear Crossing portion) double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | Schedule Update | Dermott | Clear Crossing | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2391 | 2013-10-31 |  | 345 | 180.6 | 0 | 0 | 0 | SCURRY | HASKELL | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 9/25/2013 to 10/31/2013 | 13TPIT0032 | Edith Clarke to West Shackelford double circuit 345kV line (Edith Clarke to Clear Crossing portion) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | Schedule Update | Edith Clarke | Clear Crossing | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2385 | 2013-10-31 |  | 345 | 158.4 | 0 | 0 | 0 | COTTLE | SHACKELFORD | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 12/31/2013 to 10/31/2013 | 13TPIT0084 | Big Hill to Kendall Series Compensation (Orsted) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Orsted |  | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2485 | 2013-10-31 |  | 345 | 0 | 0 | 0 | +933 | KENDALL |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 9/30/2013 to 10/31/2013 | 13TPIT0085 | Clear Crossing 345 kV station | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT | Schedule Update | Clear Crossing |  | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2486 | 2013-10-31 |  | 345 | 0 | 0 | 0 | 0 | HASKELL |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 9/30/2013 to 10/31/2013 | 13TPIT0088 | Clear Crossing add six 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Clear Crossing |  | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2489 | 2013-10-31 |  | 345 | 0 | 0 | 0 | -300 | HASKELL |  | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0090 | Hamilton Road, add dynamic reactive compensation | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study |  | Hamilton Road |  | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2492 | 2013-10-31 |  | 345 | 0 | 0 | 0 | +200 / -50 | VALVERDE |  | CREZ Modified |  |  |  |  | Y | N
New Project | New Project | 13TPIT0230 | Cedar Bayou to Center Ckt.97 | Upgrade 345kV Ckt.97 Cedar Bayou to Center to increase thermal ratings. |  | Cedar Bayou | Center | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-10-31 |  | 345 | 0 | 9.5 | 0.0 | 0 | CHAMBERS | HARRIS | Tier 4 |  |  |  | 40000, 40240 | Y | N
New Project | New Project | 13TPIT0230a | Cedar Bayou to Center Ckt.97 | Upgrade 345kV Ckt.97 Center to PH Robinson to increase thermal ratings. |  | Center | PH Robinson | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-10-31 |  | 345 | 0 | 16.5 | 0.0 | 0 | HARRIS | GALVESTON | Tier 4 |  |  |  | 40240, 42000 | Y | N |  | Cost is included in main project.
Old Project | Change in Service Date. Changed from 8/1/2013 to 11/1/2013 | 12TPIT0156 | Brundage Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-11-01 |  | 69 | 0 | 0 | 0.0 | 9.6 | DIMMIT |  | Tier 4 |  |  |  | 5870 | Y | N
Old Project | No Change | 11TPIT0114 | Alberta Switch-Doedyns 138kV Line | Rebuild 3.1 Miles of 138kV line from Alberta Switch to Doedyns Substation | Pending completion of Doedyns-Sioux 11TPIT0085 | Alberta Switch | Doedyns | Planned | 07TPIT7777 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-11-01 |  | 138 | 0 | 3.1 | 0.0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8753 - 8759 | Y | N
Old Project | No Change | 13TPIT0162 | Colorado City to Barber Lake 138 Kv Transmission Line | Construct 3.1 miles of new 138 Kv transmission line between 3852 Colorado City Substation and new Oncor Ring Bus Breaker Station between Morgan Creek and China Grove, and Colorado City upgrades and transfer remaining substations into ERCOT, 1440 Salem, 2254 South Midland, 2478 Vealmoor, 2664 Fairview, 2850 Elbow, and 1548 Greenwood Substations | New | 3852 Colorado City Substation | New Oncor Breaker Station | Planned |  | SU | Dwight Yarbrough (956) 279-6902 dyarbrough@sharyland.com |  | 2013-11-01 |  | 138 | 3.09 | 0 | 0.0 | 0 | MITCHELL | MITCHELL | Tier 4 | 2011-01-01 | 2011-05-24 | N/A | 1189, 79605 | Y | N |  | Docket #37090
Old Project | No Change | 12TPIT0075 | Knob Creek 345 kV Switching Station Phase I | Construct 345 kV switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R749A-E | 2013-11-01 |  | 345 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 13413 | Y | N
Old Project | No Change | 13TPIT0208 | Nevada 138 kV new substation and its connections to Shelby and to Royse City | New load serving | On Hold For Funding | New switches at new Nevada | Switches at Shelby and at Royse City | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2013-11-06 |  | 138 | 0 | 0 | 0.0 | 0 | HUNT | DALLAS | Tier 4 |  |  |  | 811, 960, 2471 | Y | N |  | This project is a new load serving project
Old Project | No Change | 13TPIT0050 | LS05 Silverton to White Deer | Construct a new 345kV double circuit line from Silverton switching station to White Deer switching station | New | Silverton | White Deer | Under Construction |  | SU | Mark Caskey, (214) 978-8243, mcaskey@sharyland.com |  | 2013-11-25 |  | 345 | 68.2 | 0 | 0.0 | 0 | BRISCOE | CARSON | CREZ |  |  |  | 99103-99201 | Y | N
Old Project | No Change | 13TPIT0119a | Vanderbilt to El Campo 69 kV rebuild | Rebuild single circuit 4/0 ACSR 69 kV to double circuit 138 kV capable structures. Initially operate with one 69 kV circuit. |  | Vanderbilt | El Campo | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-11-30 |  | 69 | 0 | 48 | 0.0 | 0 | JACKSON | WHARTON | Tier 2 | 2011-10-07 | 2012-01-26 | N/A | 5582, 5516, 5518, 5522, 5524, 5525, 5528, 5532, 5530, 5535, 5538 | Y | N
Old Project | No Change | 13TPIT0099 | League City-Magnolia rebuild | Rebuild League City to Magnolia 138 kV transmission line with 795 ACSS conductor. |  | League City | Magnolia | Planned |  | TNMP | Tony Hudson, 281-581-4712, Anthony.Hudson@tnmp.com | STE07513 | 2013-11-30 |  | 138 | 0 | 3.62 | 0.0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 38920, 38930, 38950 | Y | N
Old Project | No Change | 13TPIT0195 | Arcola Substation Conversion | Convert Arcola substation from double-tap to 138kV loop service Ckt.82. |  | Arcola | Thompsons/ Karsten | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-11-30 |  | 138 | 0 | 0.2 | 0.0 | 0 | FORT BEND |  | Tier 4 |  |  |  | 44722, 44032, 44390 | Y | N
Old Project | No Change | 13TPIT0021 | Cottonwood to Edith Clarke double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | Cottonwood | Edith Clarke | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2383 | 2013-11-30 |  | 345 | 178 | 0 | 0 | 0 | DICKENS | COTTLE | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 12/9/2013 to 11/30/2013 | 13TPIT0031 | Dermott to Clear Crossing Series Compensation (Kirchhoff) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Title & Schedule Update | Kirchhoff |  | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2392 | 2013-11-30 |  | 345 | 0 | 0 | 0 | +737 | SCURRY | HASKELL | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 12/9/2013 to 11/30/2013 | 13TPIT0034 | Edith Clarke to West Shackelford Series Compensation (Gauss) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Gauss |  | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2388 | 2013-11-30 |  | 345 | 0 | 0 | 0 | +737 | COTTLE | COTTLE | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 10/31/2013 to 11/30/2013 | 13TPIT0089 | Tesla, add dynamic reactive compensation | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule Update | Tesla |  | Planned | 478 - 0680 | AEP/ETT | Glen Reed 918-599-2664 | 2491 | 2013-11-30 |  | 345 | 0 | 0 | 0 | +300 / -100 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | No Change | 07TPIT0078 | Devine to Lytle: Rebuild 69 kV Line | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle |  | Devine | Lytle | Under Construction | 028 - 0028 | AEP/ETT | Terry Weeks (AEP) 918-599-2664 | 1778 | 2013-12-01 |  | 69 | 0 | 7 | 0 | 0 | MEDINA | MEDINA | Tier 4 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 8223, 8622 | Y | N
Old Project | Change in Service Date. Changed from 6/1/2013 to 12/1/2013 | 12TPIT0142 | Choate to Fashing Rebuild | Rebuild 4/0 ACSR 69 kV to 138 capable 795 ACSR. | The Fashing to Coy City line section is now needed due to newest load forecast. Changes prior quarter comment. | Choate | Coy City | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-12-01 |  | 69 | 0 | 30 | 0.0 | 0 | ATASCOSA | KARNES | Tier 2 | 2011-12-16 | 2012-04-25 | N/A | 5729, 5722, 5720 | Y | N
Old Project | Change in Service Date. Changed from 9/30/2013 to 12/1/2013 | 13TPIT0177 | Colorado - Nada Transmission Line Upgrade | Upgrade the 20 mile Colorado (7636) - Nada (5536) 69-kV transmission line to 795 ACSR 69-kV, 111 MVA. |  | Colorado | Nada | Planned | 13TPIT0150 (STEC) | LCRA TSC/STEC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-12-01 |  | 69 | 0 | 20 | 0.0 | 0 | COLORADO | COLORADO | Tier 2 | 2012-02-01 |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 13TPIT0154 | Barber Lake 138 kV Switching Station | Construct new switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8060-E | 2013-12-01 |  | 138 | 0 | 0 | 0.0 | 0 | MITCHELL |  | Tier 4 |  |  |  | 1189 | Y | N
Old Project | No Change | 13TPIT0210 | Mountain Top 138kV Bus Upgrade | Upgrade existing 138kV operate and transfer busses from 795ACSR to bundled 795ACSR |  | Mountain Top |  | Planned |  | PEC | Tony Perez (830) 868-5158 |  | 2013-12-01 |  | 138 | 0 | 0 | 0 | 0 | BLANCO | BLANCO | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | N | N
New Project | New Project | 13TPIT0233 | Polecat Creek 138 kV Switching Station | Construct 138 kV switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8172-E | 2013-12-01 |  | 138 | 0 | 0 | 0 | 0 | GLASSCOCK |  | Tier 4 |  |  |  | 11337 | Y | N
Old Project | No Change | 14TPIT0054 | Odessa - Odessa North 138 kV line | Reconductor existing 138 kV line |  | Odessa | Odessa North | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8019-E | 2013-12-01 |  | 138 | 0 | 7.2 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1126, 1122 | N | N
Old Project | No Change | 14TPIT0088 | Moss - Holt Switch 138 kV line | Reconductor existing 138 kV line |  | Moss | Holt Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8065B-E | 2013-12-01 |  | 138 | 0 | 18 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 11140, 1141 | Y | N
Old Project | No Change | 10TPIT0020 | Anna Switch - Krum W. Switch 345 kV line | Construct a double-circuit 345 kV line |  | Anna Switch | Krum W. Switch | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C060-E | 2013-12-01 |  | 345 | 140 | 0 | 0.0 | 0 | DENTON | COLLIN | CREZ |  |  |  | 1730, 2373 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0035 | Willow Creek - Clear Crossing - Dermott Switch (Central B) 345 kV line (Oncor Electric Delivery section) | Construct double-circuit 345 kV line |  | Willow Creek | Dermott Switch | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C054-E | 2013-12-01 |  | 345 | 220 | 0 | 0.0 | 0 | WISE | HASKELL | CREZ |  |  |  | 1421 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0041 | Anna Switch circuit breakers | Install 345 kV circuit breakers |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C015-E | 2013-12-01 |  | 345 | 0 | 0 | 0.0 | 0 | COLLIN |  | CREZ |  |  |  | 1730 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0072 | Scurry County South Switch (Central A) | Install shunt capacitor |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC0088-E | 2013-12-01 |  | 345 | 0 | 0 | 0.0 | 160 | SCURRY |  | CREZ |  |  |  | 11318 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0073 | Killeen Switch | Install shunt capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC0089-E | 2013-12-01 |  | 345 | 0 | 0 | 0.0 | 160 | BELL |  | CREZ |  |  |  | 3422 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0075 | Graham Switching Station | Install shunt reactor |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC083-E | 2013-12-01 |  | 345 | 0 | 0 | 0.0 | -200 | YOUNG |  | CREZ |  |  |  | 1430 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0076 | Parker Switching Station | Install a dynamic reactive device |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC087-E | 2013-12-01 |  | 345 | 0 | 0 | 0.0 | 300 -265 | PARKER |  | CREZ |  |  |  | 1436 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0081 | Brown Switch capacitors | Install shunt capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC082-E | 2013-12-01 |  | 345 | 0 | 0 | 0.0 | 240 | BROWN |  | CREZ |  |  |  | 1444 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. The estimated cost is included in the estimated cost of Brown Switch (12TPIT0045).
Old Project | No Change | 13TPIT0082 | Brown Switch dynamic reactive device | Install two dynamic reactive devices |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC086-E | 2013-12-01 |  | 345 | 0 | 0 | 0.0 | 600, -530 | BROWN |  | CREZ |  |  |  | 1444 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. The estimated cost is included in the estimated cost of Brown Switch (12TPIT0045).
Old Project | No Change | 13TPIT0095 | Krum West Switch capacitors | Install shunt capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C085-E | 2013-12-01 |  | 345 | 0 | 0 | 0.0 | 80 | DENTON |  | CREZ |  |  |  | 2373 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0180 | Salem Autotransformer Replacement | Replace failed autotransformer at the Salem substation | A spare autotransformer will be in service at Salem temporarily until the replacement is installed. The in-service date for the spare is June 15, 2012 |  |  | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-12-01 |  | 345 | 0 | 0 | 600.0 | 0 | WASHINGTON |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | Cost will be determined during the September TPIT.
Old Project | No Change | 13TPIT0204 | Wink Substation Ring Bus | Build ring bus for 69 kV system in TNMP's Wink Substation |  | Wink |  | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE03313 | 2013-12-13 |  | 69 | 0 | 0 | 0 | 0 | WINKLER |  | Tier 4 |  |  |  | 37920 | N | N
Old Project | Change in Service Date. Changed from 6/1/2013 to 12/13/2013 | 14TPIT0035 | Northgate Substaton Addition | Build new distibution substation in BTU buss at TAMU Substation. |  | CSU Northgate | CSU Northgate | Planned |  | COCS/BTU | Tony Michalsky 979- 764-3438 tmichalsky@cstx.gov |  | 2013-12-13 |  | 138 | 0 | 0 | 0.0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32006 | Y | N
New Project | New Project | 13TPIT0226 | 345kV Railhead Substation | Build a 345kV ring bus in a breaker and a half configuation in the Gray to Alibates line. | New project - new bus will be added to the SSWG cases during the TPIT Update. | - | - | Planned |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-12-15 |  | 345 | 0 | 0 | 0.0 | 0 | CARSON | - | Tier 4 |  |  |  | 79005 | N | N
Old Project | No Change | 12TPIT0181 | Lon Hill to Calallen: Rebuild 69kV line | Rebuild Lon Hill - Calallan 69kV Line | Reformated project number to match other numbers, Changed Status and contact | Lon Hill | Calallan | Planned | 581 - 0736 | AEP/TCC | Teresa Trotman 918-599-2664 | 3461 | 2013-12-31 |  | 69 | 0 | 2.1 | 0 | 0 | SAN PATRICIO | SAN PATRICIO | Tier 4 |  |  |  | 5626, 8448 | Y | N |  | 0
Old Project | Change in Service Date. Changed from 3/29/2013 to 12/31/2013 | 12TPIT0199 | Pecos cap bank | Install 10 MVAR, 69kV cap bank at Pecos Substation |  | Pecos |  | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE03812 | 2013-12-31 |  | 69 | 0 | 0 | 0.0 | 10 | Reeves |  | Tier 4 |  |  |  | 38090 | Y | N
Old Project | No Change | 13TPIT0155 | Yucca: Add 10 MVA DRCS with 7.2 Mvar capacitor bank | Add 3.6 Mvar capacitor bank at Barnhart SWTEC and add 10 MVA DRCS with 7.2 Mvar capacitor bank at Yucca |  | Yucca |  | Planned | 558 - 0721 | AEP/TNC | Michael Tallon 918-599-2664 | 2563 | 2013-12-31 |  | 69 | 0 | 0 | 0 | +17.2 / -10 | CROCKETT | 0 | Tier 4 | 0 | 0 | 0 | 0 | Y | N | 0 | 0
Old Project | Change in Service Date. Changed from 5/31/2013 to 12/31/2013 | 13TPIT0156 | Katemcy: Add 7.2 Mvar capacitor bank | Add two 7.2 Mvar capacitor banks at North Brady and add 7.2 Mvar capacitor bank at Katemcy | Contact & Schedule Update | Katemcy |  | Planned | 559 - 0722 | AEP/TNC | Eric Scott 918-599-2664 | 2562 | 2013-12-31 |  | 69 | 0 | 0 | 0 | +7.2 | MCCULLOCH | 0 | Tier 4 | 0 | 0 | 0 | 0 | Y | N | 0 | 0
New Project | New Project | 13TPIT0231 | South Houston Conversion | De-energize 69kV Deepwater to South Houston to Webster Ckt.13. Use portions of de-energized circuit to reconfigure South Houston substation. |  | South Houston | Deepwater/ Webster | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-12-31 |  | 69 | 0 | 0 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 40470, 43171, 43170, 43174, 43510 | Y | N
Old Project | No Change | 12TPIT0090 | Whitney 2nd Auto | Replace 60 MVA, 138/69 kV auto with 75 MVA auto |  | Whitney |  | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10048 | 2013-12-31 |  | 138 | 0 | 0 | 75 | 0 | BOSQUE |  | Tier 4 |  |  |  | 241, 243 | Y | N
Old Project | No Change | 13TPIT0100 | Westminster Substation and transmission line | Build Westminster 138 kV Substation and transmission line tap from Oncor's Anna Switch - Van Alstyne 138 kV line. |  |  |  | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE07612 | 2013-12-31 |  | 138 | 0 | 0 | 0.0 | 0 | COLLIN |  | Tier 4 |  |  |  | 37270 | Y | N
Old Project | No Change | 13TPIT0160 | Whitepoint: Add 138 kV breaker terminal for WF interconnect | Construct a 138 kV breaker terminal at Whitepoint for the Midway WF Interconnect | Reformated project number to match other numbers | Whitepoint |  | Planned | 573 - 0750 | AEP/TCC | Frank Pritzlaff (AEP) 918-599-2664 | 3454 | 2013-12-31 |  | 138 | 0 | 0 | 0 | 0 | SAN PATRICIO |  | TIER 4 |  |  |  | 8961 | Y | N
Old Project | No Change | 13TPIT0190 | Busch Substation Conversion | Convert Busch substation from double-tap to 138kV loop service Ckt. 08. |  | Busch | Anbush/ Clinton | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-12-31 |  | 138 | 0 | 0.2 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 40100, 40230, 40351 | Y | N
Old Project | No Change | 13TPIT0194 | Cardiff Substation Conversion | Convert Cardiff substation from double-tap to 138kV loop service Ckt. 96. |  | Cardiff | South/ Deer Park | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-12-31 |  | 138 | 0 | 0.2 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 43250, 42241, 40442 | Y | N
Old Project | No Change | 13TPIT0203 | Blossom - New Substation | Build Blossom 138-22 kV substation to serve new load and relieve Oncor Deport Substation |  | Blossom |  | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE02916 | 2013-12-31 |  | 138 | 0 | 0 | 0 | 0 | LAMAR |  | Tier 4 |  |  |  | 11687 | Y | N
New Project | New Project | 13TPIT0227 | Langston 138kV Substation | Construct service to new 138kV Langston customer-owned substation. Loop through Ckt.86 Brine to Mont Belvieu. |  | Langston | Brine/ Mont Belvieu | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-12-31 |  | 138 | 1.2 | 0 | 0.0 | 0 | CHAMBERS |  | Tier 4 |  |  |  | 40775 | Y | N
New Project | New Project | 13TPIT0231a | South Houston Conversion | Convert the 69kV portion of South Houston substation to 138kV and use portion of de-energized Ckt.13 to create a new Ckt.91 tap to South Houston & Spencer. |  | South Houston | PH Robinson/ Cougar | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-12-31 |  | 138 | 0 | 4.2 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 43172, 43272 | Y | N |  | Cost is included in main project.
Old Project | No Change | 14TPIT0058e | Mont Belvieu Area Upgrades | Loop existing Ckt.86 DUNCAN - BENDER into new 138kV JORDAN substation to create new Ckt.48 JORDAN - DUNCAN. |  | JORDAN | DUNCAN | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-12-31 |  | 138 | 0 | 0 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 3 | 2012-02-03 | 2012-03-05 | N/A | 40855, 40360 | Y | N |  | Cost included in main project
Old Project | No Change | 14TPIT0058f | Mont Belvieu Area Upgrades | Loop existing Ckt.86 DUNCAN - BENDER into new 138kV JORDAN substation to create new Ckt.86 JORDAN - BENDER. |  | JORDAN | BENDER | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-12-31 |  | 138 | 0 | 0 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 3 | 2012-02-03 | 2012-03-05 | N/A | 40855, 40155 | Y | N |  | Cost included in main project
Old Project | No Change | 14TPIT0058g | Mont Belvieu Area Upgrades | Loop existing Ckt.86 ENPROD - CITIES into new 138kV JORDAN substation to create new Ckt.48 JORDAN - ENPROD. |  | JORDAN | ENPROD | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-12-31 |  | 138 | 0 | 0 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 3 | 2012-02-03 | 2012-03-05 | N/A | 40855, 40510 | Y | N |  | Cost included in main project
Old Project | No Change | 14TPIT0058h | Mont Belvieu Area Upgrades | Loop existing Ckt.86 ENPROD - CITIES into new 138kV JORDAN substation to create new Ckt.86 JORDAN - CITIES. |  | JORDAN | CITIES | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-12-31 |  | 138 | 0 | 0 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 3 | 2012-02-03 | 2012-03-05 | N/A | 40855, 40340 | Y | N |  | Cost included in main project
Old Project | No Change | 14TPIT0074 | Thompson Creek to Snook Transmission Line | Build 6 miles of 1033ACSR transmission line (operated at 138 kV) to Snook substation. | The Thompson Creek to Koppe Bridge Line is now broken into two segments with different completion dates. | Thompson Creek | Snook Substation | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-12-31 |  | 138 | 2.4 | 3.6 | 0 | 0 | BRAZOS | BURLESON | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 15TPIT0015 | Hastings-Friendswood rebuild | Rebuild Hastings to Friendswood 138 kV transmission line with 795 ACSS conductor. Upgrade terminal equipment at Friendswood Substation. |  | Hastings | Friendswood | Planned |  | TNMP | Tony Hudson, 281-581-4712, Anthony.Hudson@tnmp.com | STE07412 | 2013-12-31 |  | 138 | 0 | 7.3 | 0.0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 38980, 39010 | Y | N
Old Project | No Change | 12TPIT0026 | North McCamey (76000) to Odessa EHV (11028) | Construct a new double circuit capable 345 kV transmission line (approximately 50 miles) between the existing LCRA TSC North McCamey (McCamey A) and the existing Oncor Odessa EHV stations. The new transmission line will consist of 2x1590 ACSR Falcon conductor to provide a thermal rating of 1678 MVA. | Project reassigned by PUCT to STEC from LCRA. | Odessa | North McCamey | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-12-31 |  | 345 | 59.6 | 0 | 0.0 | 0 | UPTON | ECTOR | CREZ |  |  |  | 76000-11028 | Y | N |  | Cost estimates for this project include TPIT project # 12TPIT0027. Both projects will be filed in one PUCT Project # in 2011.
Old Project | No Change | 12TPIT0027 | North McCamey (76000) to Bakersfield (76002) | Construct a new double circuit capable 345 kV transmission line (approximately 12 miles) between the LCRA TSC North McCamey (76000) and Bakersfield (76002) stations. The new transmission line will consist of 2x1590 ACSR Falcon conductor to provide a thermal rating of 1678 MVA | Project reassigned by PUCT to STEC from LCRA. | Bakersfield | North McCamey | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-12-31 |  | 345 | 15.9 | 0 | 0.0 | 0 | UPTON | PECOS | CREZ |  |  |  | 76000-76002 | Y | N |  | Cost estimates for this project have been included with TPIT project # 12TPIT0026. Both projects will be filed in one PUCT Project # in 2011.
Old Project | No Change | 13TPIT0111 | WA Parish Split Bus | Split WA Parish 345kV Bus 44000 |  |  |  | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-12-31 |  | 345 | 0 | 0 | 0.0 | 0 | FORT BEND |  | Tier 2 | 2011-02-08 | 2011-09-22 | N/A | 44000, 44005 | Y | N
Old Project | No Change | 07TPIT0050 | Dunlap to Techridge 138kV Circuit Relocation/Reconductor | This project will reroute the existing Ckt 975 Dunlap-Techridge from near the intersection of Howard Lane and Dessau Road to the Techridge substation. The reroute will use 3000 amp bundled 795 ACSS Drake conductor. |  | Dunlap Substation | Techridge Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P071 | 2014-01-01 |  | 138 | 0 | 2.7 | 0.0 | 0 | TRAVIS | TRAVIS | Tier 2 | 2009-01-26 | 2009-06-01 | N/A | 9045, 9190 | Y | N
Old Project | Change in Service Date. Changed from 6/1/2014 to 1/1/2014 | 13TPIT0123 | Tordillo Station and Autotransformer | Build new Tordillo station with 138/69 kV 150 MVA autotransformer close to Fashing station with a short 69 kV line Fashing. | Project was renamed from Fashing Autotransformer and modifed due to property constraints. |  |  | Planned | 13TPIT0130 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-01-01 |  | 138 | 0 | 0 | 150 | 0 | ATASCOSA |  | Tier 3 | 2011-12-16 | 2012-04-25 | N/A | 5715 - 5717 | Y | N
Old Project | Change in Service Date. Changed from 6/1/2014 to 1/1/2014 | 13TPIT0130 | San Miguel to Fashing Conversion | Convert 69 kV line to 138 kV line. The line was originally built for 138 kV operation. 138 kV circuit will terminate at Tordillo | Likely to be sped up with new load forecast | San Miguel | Fashing | Planned | 13TPIT0123 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-01-01 |  | 138 | 0 | 23.05 | 0 | 0 | ATASCOSA | ATASCOSA | Tier 3 | 2011-12-16 | 2012-04-25 | N/A | 5706, 5715 | Y | N
Old Project | Change in Service Date. Changed from 3/1/2014 to 1/1/2014 | 14TPIT0097 | Colorado - Nada 138 kV Transmission Line Conversion | Convert the 20 mile Colorado (7636) - Nada (5536) 69-kV transmission line to 138-kV, 220 MVA. |  | Colorado | Nada | Planned | 13TPIT0150 (STEC) | LCRA TSC/STEC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2014-01-01 |  | 138 | 0 | 20 | 0 | 0 | COLORADO | COLORADO | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | Coordinate with STEC Coordinate with SBEC
Old Project | No Change | 13TPIT0011 | Palo Alto - New 138kV Substation | Loop new 138kV substation into the existing 138kV Leon Creek to Chavaneaux line |  | Palo Alto | Leon Creek/Chavaneaus | Conceptual |  | CPS | Blake Williams | S-0527 | 2014-01-31 |  | 138 | 0.1 | 0 | 0.0 | 0 | BEXAR | BEXAR | Tier 4 | 2011-02-08 | 2011-09-22 | N/A | 5330 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 13TPIT0142 | Broadview 72 MVAR Capacitor Bank | Install 72 MVAR capacitor bank on the East bus and remove both back-to-back capacitor banks from the West bus |  |  |  | Planned |  | CPS | PM: Hector Torres | S-0395 | 2014-01-31 |  | 138 | 0 | 0 | 0.0 | 72 | BEXAR | BEXAR | Tier 4 |  |  |  | 5040 | Y | N |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 6/29/2014 to 1/31/2014 | 14TPIT0040 | Springwoods 138kV Substation | Build new 138kV Springwoods distribution substation. Loop through Ckt.66 Rayford to Westfield. | Accelerated project schedule | Springwoods | Rayford/ Louetta | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-01-31 |  | 138 | 6.2 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 46270, 46295, 46051 | Y | N
New Project | New Project | 14TPIT0112 | SEADOC 138kV Substation | Construct service to new 138kV SEADOC customer-owned double-tap substation. Tap existing Ckt.02 Velasco to Brazosport. |  | SEADOC | Velasco/ Brazosport | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-01-31 |  | 138 | 5.3 | 0 | 0.0 | 0 | BRAZORIA |  | Tier 4 |  |  |  | 43222 | Y | N
New Project | New Project | 14TPIT0112a | SEADOC 138kV Substation | Construct service to new 138kV SEADOC customer-owned double-tap substation. Tap existing Ckt.02 Booster to Seaway Switchrack. |  | SEADOC | Booster/ Seaway Switchrack | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-01-31 |  | 138 | 0.1 | 0 | 0.0 | 0 | BRAZORIA |  | Tier 4 |  |  |  | 43220 | Y | N |  | Cost is included in main project.
Old Project | No Change | 09TPIT0032 | Williamson 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Williamson substation. |  | Williamson Substation | Williamson Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P063 | 2014-02-01 |  | 138 | 0 | 0 | 0.0 | 31.2 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9295 | Y | N
Old Project | No Change | 13TPIT0145 | Rangerville Sub- 138kV Breaker Addition | Install 138kV Breakers |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-02-01 |  | 138 | 0 | 0 | 0.0 | 0 | CAMERON |  | Tier 4 |  |  |  | 8747 | Y | N
Old Project | Change in Service Date. Changed from 3/31/2014 to 2/28/2014 | 14TPIT0058c | Mont Belvieu Area Upgrades | Build new circuit out of JORDAN 138kV substation and reconnect portion of existing DUNCAN - BARHIL circuit to create new Ckt.59 JORDAN - BARHIL. | Accelerated project schedule | JORDAN | BARHIL | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-02-28 |  | 138 | 0.87 | 0 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 3 | 2012-02-03 | 2012-03-05 | N/A | 40855, 40150 | Y | N |  | Cost included in main project
Old Project | Change in Service Date. Changed from 3/31/2014 to 2/28/2014 | 14TPIT0058d | Mont Belvieu Area Upgrades | Build new circuit out of JORDAN 138kV substation and reconnect portion of existing ENPROD - HACHER circuit to create new Ckt.59 JORDAN - RALYND. | Accelerated project schedule | JORDAN | RALYND | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-02-28 |  | 138 | 0.87 | 0 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 3 | 2012-02-03 | 2012-03-05 | N/A | 40855, 40762 | Y | N |  | Cost included in main project
Old Project | Change in Service Date. Changed from 3/31/2014 to 2/28/2014 | 14TPIT0058i | Mont Belvieu Area Upgrades | Reconfigure existing Ckt.86 DUNCAN - BARHIL and Ckt.86 ENPROD - HACHER to create new Ckt.48 DUNCAN - ENPROD. | Accelerated project schedule | DUNCAN | ENPROD | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-02-28 |  | 138 | 0 | 0 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 3 | 2012-02-03 | 2012-03-05 | N/A | 40360, 40510 | Y | N |  | Cost included in main project
New Project | New Project | 14TPIT0111 | CONNOR 138kV Substation | Construct service to new 138kV CONNOR customer-owned substation. Loop through Ckt.86 Crosby to Bender |  | CONNOR | Crosby/ Bender | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-02-28 |  | 138 | 1.8 | 0 | 0.0 | 0 | CHAMBERS |  | Tier 4 |  |  |  | 40665 | Y | N
Old Project | No Change | 13TPIT0108 | Nelson Sharpe to Ajo: Reconductor 345kV line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo |  | Nelson Sharpe | Ajo | Planned | 071 - 0281 | AEP/ETT/TCC | Glen Reed 918-599-2664 | 3181 | 2014-02-28 |  | 345 | 0 | 37.044 | 0 | 0 | KLEBERG | KENEDY | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 85000, 80076 | Y | N
Old Project | No Change | 13TPIT0013 | Perry to Midway Rebuild | Rebuild Perry to Midway with 959ACSS |  | Perry | Midway | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 08050 | 2014-03-28 |  | 69 | 0 | 12.4 | 0.0 | 0 | FALLS | FALLS | Tier 4 |  |  |  | 92185 | Y | N
Old Project | Change in Service Date. Changed from 9/2/2013 to 3/28/2014 | 13TPIT0105 | Silver City to Calvert Switch | Install additional poles and modify existing structures to raise normal operating temperature to 100° C |  | Silver City | Calvert Switch | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11051 | 2014-03-28 |  | 69 | 0 | 7.95 | 0.0 | 0 | MILAM | MILAM | Tier 4 |  |  |  | 65, 73 | Y | N
Old Project | No Change | 13TPIT0119b | Vanderbilt to Ricebird 138 kV circuit | Install 795 ACSR 138 kV on other side of new towers once CCN is complete. Includes building new load serving station with a 2 mile double circuit that loops into the 138 kV line near the Cordele substation. |  | Vanderbilt | Ricebird | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-03-30 |  | 138 | 52 | 0 | 0.0 | 0 | JACKSON | WHARTON | Tier 2 | 2011-10-07 | 2012-01-26 | N/A | 5584, 5523, 78104 | Y | N |  | Project costs are included with 13TPIT0119a
Old Project | No Change | 13TPIT0110 | Rio Hondo: Reconfigure 345 kV Series Capacitors | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo |  | Rio Hondo |  | Planned | 071 - 0281 | AEP/TCC | Glen Reed 918-599-2664 | 3185 | 2014-03-31 |  | 345 | 0 | 0 | 0 | 0 | CAMERON |  | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 8318 | Y | N
Old Project | No Change | 13TPIT0148 | Cotulla Autotransformer | Expand Cotulla station to have 138 kV and add a 150 MVA 138/69 kV autotransformer at Cotulla. |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-04-01 |  | 69 | 0 | 0 | 150.0 | 0 | LA SALLE |  | Tier 1 | 2012-04-16 | 2012-08-30 | 2012-09-18 | 5875 , 5876 | Y | N
Old Project | Change in Service Date. Changed from 6/1/2013 to 4/1/2014 | 13TPIT0150 | Glidden to Colorado Transmission upgrade | Rebuild entire line from Glidden to Colorado substation to 795 MCM 138 Kv insulation | ERCOT approval through RPG review process was granted March 27,2012 | Glidden | Colorado | Under construction |  | SBEC | Don Roberts | WO#12-6056 WO#12-6057 WO#12-6058 WO#12-6061 WO#12-5315 WO#12-5316 WO#12-5317 WO#12-5327 WO#12-5328 WO#12-5329 WO#12-5330 WO#12-5331 | 2014-04-01 |  | 138 | 0 | 27 | 0.0 | 0 | Colorado | Colorado | Tier 3 | 2012-02-27 | 2012-03-27 | N/A | SEE PROJECT DESCRIPTION | N | N
Old Project | No Change | 11TPTI0173 | Substation CIP Security Project | Install physical and cyber security measures at each of TMPA's critical substations | Changes in CIP compliance timeframe for TMPA | Gibbons Creek, Shelby, Interchange | Gibbons Creek, Shelby, Interchange | Under Construction |  | TMPA | Tom Chambers 936-873-1125 tchambers@texasmpa.org | T11009 | 2014-04-01 |  | 345 | 0 | 0 | 0.0 | 0 | Grimes, Hunt |  | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 10TPIT0063 | Geronimo(7604)-CMC Tap-McQueeney T-Line | Rebuild 5.5 miles of existing 69kV t-line to 138 kV, 1192 ACSR between Geronimo and McQueeny substations on existing right-of-way |  | Geronimo | McQueeney | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2014-04-30 |  | 138 | 0 | 5.5 | 0 | 0 | GUADALUPE | GUADALUPE | Tier 4 | 2012-12-19 | on-going | N/A | See Project Title | N | N
Old Project | No Change | 07TPIT0077 | Big Foot to Devine: Rebuild 69 kV Line | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle |  | Big Foot | Devine | Under Construction | 028 - 0028 | AEP/ETT | Terry Weeks (AEP) 918-599-2664 | 1777 | 2014-05-01 |  | 69 | 0 | 6.1 | 0 | 0 | FRIO | MEDINA | Tier 4 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 8218, 8223 | Y | Y
Old Project | No Change | 07TPIT0116 | Handley - Duval 69 kV line | Upgrade existing 69 kV line |  | Handley | Duval | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5116-E | 2014-05-01 |  | 69 | 0 | 5.4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1952, 2158 | Y | N
Old Project | No Change | 13TPIT0199 | Burrows 69 kV Capacitors | Install shunt capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R513-E | 2014-05-01 |  | 69 | 0 | 0 | 0 | 18.4 | HUNT |  | Tier 4 |  |  |  | 1829 | Y | N
Old Project | No Change | 14TPIT0048 | Clear Fork Substation (fka Maxwell) | Construct 69kV/12.5kV distribution substation Clear Fork (7195) on T-519 between Reedville and Lockhart. | Name Change | Clear Fork | Reedville/Lockhart | Planned |  | BBEC | Thomas Ellis |  | 2014-05-01 |  | 69 | 0 | 0 | 0 | 0 | CALDWELL |  | Tier 4 |  |  |  | see project description | Y | N
Old Project | No Change | 14TPIT0083 | Electra 69 kV capacitors | Install capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R561-E | 2014-05-01 |  | 69 | 0 | 0 | 0 | 9.2 | WICHITA |  | Tier 4 |  |  |  | 1538 | Y | N
Old Project | No Change | 07TPIT0017 | Handley - Hurst 138 kV line | Reconductor existing 138 kV line |  | Handley | Hurst | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M572-WAC | 2014-05-01 |  | 138 | 0 | 18.7 | 0.0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1950, 2110, 2109, 1951 | Y | N |  | Interim rating increase was implemented in May 2012.
Old Project | No Change | 08TPIT0109 | Payne - Collin Switching Station 138 kV line | Rebuild existing 138 kV line |  | Payne | Collin Switching Station | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R519-E | 2014-05-01 |  | 138 | 0 | 31.75 | 0 | 0 | GRAYSON | COLLIN | Tier 3 |  |  |  | 1758, 1757, 2350, 2366, 2349, 2364, 2370 | N | N | 2009-R12 | Payne - EPCO section will be completed by 12/2013.
Old Project | No Change | 09TPIT0044 | E. Richardson - Apollo 138 kV line (Oncor Electric Delivery section) | Upgrade existing 138 kV line |  | E. Richardson | Apollo | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3033-WA | 2014-05-01 |  | 138 | 0 | 2.32 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 802, 2690 | N | N
Old Project | Change in Service Date. Changed from 6/1/2014 to 5/1/2014 | 10TPIT0013 | Apollo to East Richardson | BEPC's portion of the line. | changed to match Oncor date | Apollo | East Richardson | planned | 09TPIT0044 | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 05010 | 2014-05-01 |  | 138 | 0 | 1.4 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 802, 2690 | Y | N |  | mileage shown is for Bepc portion of line Oncor to rebuild BEPC's portion of the line
Old Project | No Change | 13TPIT0136 | Odessa North 138 kV Switching Station | Construction 138 kV switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8050B-E | 2014-05-01 |  | 138 | 0 | 0 | 0 | 0 | ECTOR |  | Tier 4 |  |  |  | 1122, 1123 | Y | N
Old Project | No Change | 13TPIT0137 | Odessa North - Goldsmith Junction 138 kV line | Rebuild existing 69 kV line to create a double-circuit line with 69 kV and 138 kV circuits |  | Odessa North Switch | Goldsmith Junction | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8050C-E | 2014-05-01 |  | 138 | 13.3 | 0 | 0 | 0 | ECTOR | ECTOR | Tier 3 |  |  |  | 11256, 1123 | Y | N
Old Project | No Change | 13TPIT0152 | Wink Switch - Loving - El Mar - Mason 138 kV line | Upgrade existing 138 kV line |  | Wink Switch | Mason | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8066-E | 2014-05-01 |  | 138 | 0 | 40 | 0 | 0 | WINKLER | REEVES | Tier 3 | 2012-05-02 | 2012-06-06 | N/A | 1092, 1074, 1093, 1094 | Y | N |  | Wink - Loving complete in 11/2013, Loving - El Mar complete in 12/2013 and El Mar - Mason complete in 5/2014
Old Project | No Change | 14TPIT0049 | Big Foot SW Station: Install 138 kV Ring Bus | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle |  | Big Foot |  | Under Construction | 028 - 0028 | AEP/TCC | Terri Weeks 918-599-2664 | 1786 | 2014-05-01 |  | 138 | 0 | 0 | 0 | 0 | FRIO | FRIO | Tier 4 |  |  |  | 8218 | N | N
Old Project | No Change | 14TPIT0052 | Stanton East - Triangle (SU) - Midland E138 kV line | Upgrade existing line |  | Midland East | Stanton East | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8025-E | 2014-05-01 |  | 138 | 0 | 27.2 | 0 | 0 | MARTIN | MIDLAND | Tier 4 |  |  |  | 1326, 79549, 1023 | Y | N
Old Project | No Change | 14TPIT0053 | Moss - Westover 138 kV line | Upgrade existing line |  | Moss | Westover | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8016-E | 2014-05-01 |  | 138 | 0 | 3.4 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1019, 1129 | Y | N
Old Project | No Change | 14TPIT0060 | Arco Station Upgrade | Upgrade Krugerville line terminal and station transfer bus equipment and associated relay and SCADA systems | Existing station property too small to accommodate rebuild. Purchase land and build new station. | Arco | Arco | Planned |  | TMPA | Tom Chambers 936-873-1125 tchambers@texasmpa.org | T12001 | 2014-05-01 |  | 138 | 0 | 0 | 0 | 0 | Denton |  | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 14TPIT0101 | Penwell 138 kV Switching Station | Construct new switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8106-E | 2014-05-01 |  | 138 | 0 | 0 | 0 | 0 | ECTOR |  | Tier 4 |  |  |  | 1011 | Y | N
New Project | New Project | 14TPIT0104 | Mason 138 kV capacitors | Install shunt capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8085-E | 2014-05-01 |  | 138 | 0 | 0 | 0 | 52.4 | REEVES |  | Tier 4 |  |  |  | 1094 | Y | N
Old Project | No Change | 07TPIT0126 | Tri Corner - Seagoville Switch 345 kV line | Upgrade existing 345 kV line |  | Tri Corner | Seagoville Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4044-E | 2014-05-01 |  | 345 | 0 | 9.4 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2432, 2433 | Y | N
Old Project | No Change | 09TPIT0042 | Collin 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M318-E | 2014-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  | Tier 4 |  |  |  | 2370, 2372 | N | N | 2009-R15
Old Project | Change in Service Date. Changed from 11/1/2014 to 5/1/2014 | 14TPIT0090 | Monticello shunt reactors | Install shunt reactors | Construction schedule change |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R919-E | 2014-05-01 |  | 345 | 0 | 0 | 0 | -100 | TITUS |  | Tier 4 |  |  |  | 1695 | Y | N
Old Project | No Change | 14TPIT0091 | Riley (Oklaunion) - Fisher Road 345 kV line relocation | Relocate 345 kV line |  | Oklaunion | Fisher Road | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R921-E | 2014-05-01 |  | 345 | 6.91 | 0 | 0 | 0 | WILBARGER | WICHITA | Tier 4 |  |  |  | 6101, 1425 | Y | N
Old Project | Change in Service Date. Changed from 11/1/2014 to 5/1/2014 | 14TPIT0093 | Paris Switch shunt reactor | Install shunt reactor | Construction schedule change |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R920-E | 2014-05-01 |  | 345 | 0 | 0 | 0 | -100 | LAMAR |  | Tier 4 |  |  |  | 1692 | Y | N
Old Project | No Change | 14TPIT0103 | Moss Switching Station | Install 345 kV breakers |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8130-E | 2014-05-01 |  | 345 | 0 | 0 | 0 | 0 | ECTOR |  | Tier 4 |  |  |  | 1018 | Y | N
Old Project | Change in Service Date. Changed from 6/14/2013 to 5/30/2014 | 14TPIT0095 | Railroad DC Tie Expansion | Expansion of existing 138kV Transmission Interconnection HVDC tie with Comision Federal de Electricidad (CFE) |  | Railroad Substation |  | Under Construction |  | SU | Mark Caskey, (214) 978-8243, mcaskey@sharyland.com |  | 2014-05-30 |  | 138 | 0 | 0 | 0 | 87 MVAR 138kV | Hidalgo |  | Tier 3 | 2011-06-01 | 2012-07-01 | N/A | 8824 (ERCOT side) 8825 (CFE side) | Y | N |  | Reactive Capability added 87 MVAR 138kV connected capacitor banks on each end of the DC Tie (preliminary and may change after detailed studies are performed)
Old Project | No Change | 11TPIT0107 | Happy Valley: Tie 69 kV tap into Steamboat | Happy Valley: Tie 69 kV tap into Steamboat |  | Happy Valley | Happy Valley | Planned | 341 - 0515 | AEP/ETT | Teresa Trotman 918-599-2664 | 2092 | 2014-05-31 |  | 69 | 0 | 0.6 | 0 | 0 | TAYLOR | TAYLOR | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 12/31/2013 to 5/31/2014 | 13TPIT0114 | Silver to Silver Tap 1: Reterminate the 69 kV line into the Cedar Hill 69 kV station and add 7.2 Mvar capacitor bank at Silver | Reterminate Silver Tap 1 to Silver with 795 ACSR and add 7.2 Mvar capacitor bank at Silver | Schedule Update | Cedar Hill | Silver Tap 1 | Planned | 557 - 0719 | AEP/TNC | Glen Reed 918-599-2664 | 2559 | 2014-05-31 |  | 69 | 0.02 | 0 | 0 | +7.2 | COKE | COKE | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0157 | Cactus to Ft. Lancaster: Rebuild 69 kV line | Rebuild Cactus to Ft. Lancaster 69 kV line with 795 ACSS |  | Cactus | Ft. Lancaster | Planned | 569 - 0743 | AEP/TNC | Glen Reed 918-599-2664 | 2573 | 2014-05-31 |  | 69 | 0 | 9.28 | 0 | 0 | CROCKETT | PECOS | Tier 4 |  |  |  |  | Y | N
New Project | New Project | 14TPIT0106 | SW Vernon to Vernon Main: Rebuild 69 kV line with 795 ACSS | Rebuild SW Vernon to Vernon Main 69 kV line with 795 ACSS | NEW | SW Vernon | Vernon Main | Conceptual | 315 - 0470 | AEP/ETT | Dave Goetz 918-599-2664 | 3154 | 2014-05-31 |  | 69 | 0 | 4.6 | 0 | 0 | WILBARGER | WILBARGER | Tier 4 |  |  |  |  | Y | N
New Project | New Project | 14TPIT0107 | Bond Road: Build new 138 kV Box Bay Switch Structure and add two 7.2 Mvar capacitor banks | Construct new Bond Road station along the Sonora to Uvalde 69 kV line and add two 7.2 Mvar capacitor banks | NEW | Sonora | Uvalde | Conceptual | 587 - 0768 | AEP/ETT | Glen Reed 918-599-2664 | 2804 | 2014-05-31 |  | 69 | 0 | 0 | 0 | +14.4 | SUTTON | SUTTON | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 10TPIT0148 | Las Pulgas Tap - Renamed from Willacy Tap Switch 138kV | Move normally open 138kV connection to the AEP Raymondville #2 bus and add breakers at Las Pulgas to serve E Raymondville and La Sara from Las Pulgas. |  |  |  | Planned | 12TPIT0103 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-05-31 |  | 138 | 0 | 0 | 0.0 | 0 | WILLACY | WILLACY | Tier 4 |  |  |  | 80309 | N | N
Old Project | No Change | 13TPIT0171 | Farmersville West - New Substation | Build a new 138-12.47 kV substation to accommodate load growth in Farmersville. Cut Oncor's Princeton - Royce City 138 kV line into the new substation. |  |  |  | Planned | 16TPIT0005 | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2014-05-31 |  | 138 | 0 | 0 | 0 | 0 | Collin |  | Tier 4 |  |  |  | 12527, 37291 | Y | N
Old Project | Change in Service Date. Changed from 11/30/2013 to 5/31/2014 | 13TPIT0193 | Tomball Reactor | Install 50MVAR reactor at Tomball substation. | Delay in project schedule | Tomball |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-05-31 |  | 138 | 0 | 0 | 0 | -50 | HARRIS |  | Tier 4 |  |  |  | 46510 | Y | N
Old Project | No Change | 14TPIT0072 | Las Pulgas: Complete Ringbus, Add Breakers, Terminate STEC East Raymondville 138 kV Line | Loop STEC radial 138 kV Raymondville #2 to East Raymondville line into Las Pulgas |  | Las Pulgas |  | Conceptual | 615 - 3446 | AEP/TCC | Glen Reed (AEP) 918-599-2664 Doug Evans (STEC) 361-485-6459 | 516 | 2014-05-31 |  | 138 | 0 | 0 | 0 | 0 | WILLACY |  | Tier 4 |  |  |  | 80309 | Y | N |  | Associated STEC Project: 10TPIT0148
New Project | New Project | 14TPIT0110 | MCCABE 138kV Substation | Construct service to new 138kV MCCABE customer-owned substation. Loop through Ckt.96 Bayou to Bimont. |  | MCCABE | Bayou/ Bimont | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-05-31 |  | 138 | 0.2 | 0 | 0.0 | 0 | HARRIS |  | Tier 4 |  |  |  | 42350 | Y | N
Old Project | Change in Service Date. Changed from 3/31/2014 to 5/31/2014 | 14TPIT0058 | Mont Belvieu Area Upgrades | Build new 345kV JORDAN substation. Install new 800 MVA autotransformer. | Delay in project schedule |  |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-05-31 |  | 345 | 0 | 0 | 800 | 0 | CHAMBERS |  | Tier 3 | 2012-02-03 | 2012-03-05 | N/A | 40850, 40855, 49077 | Y | N
Old Project | Change in Service Date. Changed from 3/31/2014 to 5/31/2014 | 14TPIT0058a | Mont Belvieu Area Upgrades | Loop existing Ckt.99 Cedar Bayou - Northbelt into new JORDAN substation to create new Ckt.99 JORDAN - Cedar Bayou. | Delay in project schedule | JORDAN | Cedar Bayou | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-05-31 |  | 345 | 0.2 | 0 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 3 | 2012-02-03 | 2012-03-05 | N/A | 40850, 40000 | Y | N |  | Cost included in main project
Old Project | Change in Service Date. Changed from 3/31/2014 to 5/31/2014 | 14TPIT0058b | Mont Belvieu Area Upgrades | Loop existing Ckt.99 Cedar Bayou - Northbelt into new JORDAN substation to create new Ckt.99 JORDAN - Northbelt. | Delay in project schedule | JORDAN | Northbelt | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-05-31 |  | 345 | 0.2 | 0 | 0 | 0 | CHAMBERS | CHAMBERS | Tier 3 | 2012-02-03 | 2012-03-05 | N/A | 40850, 46100 | Y | N |  | Cost included in main project
Old Project | No Change | 14TPIT0066 | Jim Treece: Build new three breaker ring bus | Interconnect Blue Summit Wind Farm at Jim Treece to connect Blue Summit to the Riley to Tesla 345 kV line |  | Riley | Tesla | Planned | 512 - 0724 | AEP/ETT | Dave Goetz 918-599-2664 | 2515 | 2014-05-31 |  | 345 | 0 | 0 | 0 | 0 | WILBARGER |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 14TPIT0077 | PH Robinson Autotransformer Upgrade | Replace existing 400MVA PH Robinson autotransformer A1 with 800MVA autotransformer. |  | PH Robinson |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-05-31 |  | 345 | 0 | 0 | 400.0 | 0 | GALVESTON |  | Tier 4 |  |  |  | 42000, 42015, 49026 | Y | N
Old Project | No Change | 12TPIT0109 | Laguna to Naval Base | Upgrade the 3.09-mile Laguna (8494)-Naval Base (8495) 69 kV transmission line to 69kV 959.6 ACSS , 194.71 MVA with 138 kV capable structures. | LCRA TSC working with ERCOT staff to determine scope and in-service year. | Laguna | Naval Base | Planned | 12TPIT0014 (AEP) | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2014-06-01 |  | 69 | 0 | 3.09 | 0.0 | 0 | NUECES | NUECES | Tier 4 | 2012-07-06 | 2012-12-20 | 2013-01-15 | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 12TPIT0140 | South Batesville breaker addition | Adds breakers to South Batesville to allow closing of normally open South Batesville to Frio Town. Creates 3- terminal switching station |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-06-01 |  | 69 | 0 | 0 | 0.0 | 0 | ZAVALA |  | Tier 4 |  |  |  | 5848 | Y | N
Old Project | No Change | 12TPIT0143 | Danevang Switch to El Campo Rebuild | Rebuild 4/0 ACSR 69 kV to 138 capable 795 ACSR. |  | Danevang Switch | El Campo | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-06-01 |  | 69 | 0 | 12.75 | 0.0 | 0 | WHARTON | WHARTON | Tier 4 |  |  |  | 5544, 5540 5543, 5538 | Y | N
Old Project | No Change | 12TPIT0180 | Lon Hill to City of Robstown: Rebuild 69kV line | Rebuild Lon Hill - City of Robstown 69kV Line | Reformated project number to match other numbers | Lon Hill | City of Robstown | Conceptual | 582 - 0735 | AEP/TCC | Glen Reed 918-599-2664 | 3460 | 2014-06-01 |  | 69 | 0 | 4.6 | 0 | 0 | SAN PATRICIO | SAN PATRICIO | Tier 4 |  |  |  | 8448, 8884 | Y | N |  | 0
Old Project | No Change | 13TPIT0128 | Danevang Switch to Danevang Substaton Rebuild | Rebuild 4/0 ACSR 69 kV to 138 capable 795 ACSR. |  | Danevang Switch | Danevang Substation | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-06-01 |  | 69 | 0 | 2.2 | 0.0 | 0 | WHARTON | WHARTON | Tier 4 |  |  |  | 5544, 5548 | Y | N
Old Project | No Change | 14TPIT0079 | Glen Rose to Meridian Rebuild | Rebuild Glen Rose to Meridian with 959 ACSS, 138 kV construction (operate at 69 kV) |  | Glen Rose | Meridian | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 12044 | 2014-06-01 |  | 69 | 0 | 18.18 | 0 | 0 | SOMERVELL | BOSQUE | Tier 4 |  |  |  | 315, 319 | Y | N
Old Project | No Change | 10TPIT0038 | College-Brand 138 kV line | Line reconductor | On Hold For Funding | Switch 8832 at College | Switch 1364 at Brand | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2014-06-01 |  | 138 | 0 | 4.2 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 829, 827 | Y | N |  | This project is a line reconductor for solving overload
Old Project | Change in Service Date. Changed from 6/3/2013 to 6/1/2014 | 10TPIT0095 | VH Braunig - Grandview 138kV Line Reroute | Reroute VH Braunig - Grandview to become VH Braunig - Coliseum Rd | Delayed due to Rail Road permit | VH Braunig | Grandview | Planned | S-0554 | CPS | PM: Ulrich Skerhut | T-0130 | 2014-06-01 |  | 138 | 2.1 | 0 | 0.0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5030 5095 5175 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 11TPIT0009 | Dunlap 138kV substation | Install one 30MVA Transformer at Dunlap Substation |  | Dunlap Substation | Dunlap Substation | Under Construction |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | 3230_117_2930 3230_117_2933 3240_117_4930 3240_117_4933 | 2014-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9045 | Y | N
Old Project | No Change | 12TPIT0123 | Braunig West Bus - 138 kV Substation Equipment Upgrade | Upgrade Terminals at Braunig West for Valley Rd., Mauermann Rd., Streich Rd. circuits and upgrade terminals at remote ends to ensure a 2420 A rating and remove the existing MLSE on the 138kV transmission lines. |  | Braunig_W | Valley Rd Mauermann Streich Rd | Planned | T-0181 | CPS | Blake Williams | S-0658 | 2014-06-01 |  | 138 | 0 | 0 | 0.0 | 0 | BEXAR | BEXAR | Tier 4 | 2011-12-16 | 2012-04-25 | N/A | 5025 5465 5297 5417 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 12TPIT0184 | Lon Hill: Replace 138/69kV Autotransformers #1 and #2 | Upgrade Both 138/69kV Autotransformers at Lon Hill to 240MVA | Changed Contact and project number format | Lon Hill |  | Planned | 580 - 0734 | AEP/TCC | Teresa Trotman 918-599-2664 | 3463 | 2014-06-01 |  | 138 | 0 | 0 | 240 | 0 | SAN PATRICIO |  | Tier 4 |  |  |  | 8452, 8448 | Y | N |  | 0
Old Project | No Change | 12TPIT0185 | Airline to Westside: Add 138kV Circuit | Add a Second 138kV Circuit between Airline and Westside | Reformated project number to match other numbers | Airline | Cabaniss | Conceptual | 584 - 0747 | AEP/TCC | Glen Reed 918-599-2664 | 3464 | 2014-06-01 |  | 138 | 0 | 5.5 | 0 | 0 | NUECES | NUECES | Tier 4 |  |  |  | 8490, 8485 | Y | N |  | 0
Old Project | No Change | 13TPIT0058 | Circuit 941 Summit - Williamson Reconductor | Reconductor the 3.54 miles circuit from single 795 ACSR to single 795 ACSS Drake conductor. |  | Summit Substation | Williamson Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_079 | 2014-06-01 |  | 138 | 0 | 3.54 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9279, 9295 | Y | N
Old Project | No Change | 14TPIT0042 | Five Points to Broadview - 138 kV Transmission Line Rebuild | Rebuild 9.4 miles of 138 kV transmission line from Five Points to Broadview and ensure a minimum conductor rating of 331 MVA |  | Five Points | Broadview | Conceptual |  | CPS | Blake Williams | T-0208 | 2014-06-01 |  | 138 | 0 | 9.4 | 0 | 0 | BEXAR | BEXAR | Tier 3 |  |  |  | 5025 5428 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 14TPIT0044 | Helotes to Hill Country - 138 kV Substation Equipment Upgrade | Upgrade terminals at Helotes and Hill Country to ensure a 2420 A rating and remove existing MLSE on Helotes to Hill Country 138 kV transmission line |  | Helotes | Hill Country | Conceptual |  | CPS | Blake Williams | S-0651 | 2014-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5200 5210 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 14TPIT0045 | Anderson to Cagnon - 138 kV Substation Equipment Upgrade | Upgrade terminals at Anderson and Cagnon to ensure at 2420 A rating and remove the existing MLSE on Anderson to Cagnon 138kV transmission line |  | Anderson | Cagnon | Conceptual |  | CPS | Blake Williams | S-0479 | 2014-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5054 5003 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 14TPIT0046 | Hill Country to La Sierra - 138 kV Substation Equipment Upgrade | Upgrade termainls at Hill Country and La Sierrra to ensure a 2420 A rating and remove the existing MLSE on Hill Country to La Sierra 138kV transmission line |  | Hill Country | La Sierra | Conceptual |  | CPS | Blake Williams | S-0485 | 2014-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5209 5257 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 14TPIT0100 | Tilden Capacitor | Add 19.2 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-06-01 |  | 138 | 0 | 0 | 0.0 | 19.2 | MCMULLEN |  | Tier 4 |  |  |  | 5701 | Y | N
Old Project | No Change | 15TPIT0019 | Blockhouse (7527) | Add a 31.2 MVAR Capacitor Bank at the Blockhouse (7527) substation |  | Blockhouse |  | Planned |  | PEC | Tony Perez (830) 868-5158 |  | 2014-06-01 |  | 138 | 0 | 0 | 0 | 31.2 | WILLIAMSON |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | N | N
Old Project | Change in Service Date. Changed from 12/1/2013 to 6/1/2014 | 13TPIT0186 | Trinidad second 345/138 kV autotransformer | Install 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6015-E | 2014-06-01 |  | 345 | 0 | 0 | 600 | 0 | HENDERSON |  | Tier 4 |  |  |  | 3124, 3127 | Y | N
Old Project | No Change | 14TPIT0043 | Tri-County - New 138kV Substation | Loop new 138kV substation into the existing Skyline to Wiederstein and Green Mountain to Parkway transmission lines. |  | Skyline Green Mountain | Tri_County/Wiederstein Tri_County/Parkway | Conceptual | T-0191 | CPS | Blake Williams | S-0620 | 2014-06-06 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5370 5445 7461 5180 5445 7611 | Y | N |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 6/30/2018 to 6/14/2014 | 10TPIT0062 | Weil Road (Marion South) - New Substation | Build new 138-26.18 kV 40 MVA substation on the GVEC Marion(7178)-Cibolo(7608) 138 kV transmission line by the Marion Interchange |  | Weil Road | Marion/Cibolo | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2014-06-14 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 14TPIT0032 | Downing to Mountary | Existing 69 kV line. |  | Downing | Mountary | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10044 | 2014-06-15 |  | 69 | 0 | 15 | 0 | 0 | COMANCHE | COMANCHE | Tier 4 |  |  |  | 281, 294 | Y | N | 2009-R29
Old Project | No Change | 14TPIT0069 | Expansion of 138kV Palo Alto station | Add one more bay position to existing 138kV Palo Alto station | New | Palo Alto |  | Planned |  | SU | Bill Bojorquez 512-771-0965 BBojorquez@hunttransmission.com |  | 2014-06-16 |  | 138 | 0 | 0 | 0 | 0 | Cameron |  | Tier 1 | 2011-05-03 | 2011-12-19 | 2012-01-17 |  | Y | N
Old Project | No Change | 14TPIT0070 | New 138kV line from LaPalma to Palo Alto | Construct new La Palma – Palo Alto 138 kV line (~12 mi) and station upgrades | Change Contact info for TCC | LaPalma | Palo Alto | Planned |  | SU/TCC | Bill Bojorquez (SU) 512-771-0965 Glen Reed 918-599-2664 |  | 2014-06-16 |  | 138 | 12 | 0 | 0 | 0 | Cameron | Cameron | Tier 1 | 2011-05-03 | 2011-12-19 | 2012-01-17 |  | Y | N |  | RPG approved $274.7MM for the entire project with $18.5MM allocated for this piece as follows: $12.5MM - Line, $.5MM - Palo Alto, $5.4MM - La Palma
Old Project | Change in Service Date. Changed from 9/13/2013 to 6/27/2014 | 15TPIT0013 | Seymour to Lake Kemp Switch | Rebuild Seymour to Lake Kemp Switch 69 kV line with 795 ACSR |  | Seymour | Lake Kemp Switch | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10047 | 2014-06-27 |  | 69 | 0 | 6.9 | 0.0 | 0 | BAYLOR | BAYLOR | Tier 4 |  |  |  | 779, 782 | Y | N
Old Project | Change in Service Date. Changed from 6/1/2014 to 6/30/2014 | 12TPIT0182 | Crystal City - Turtle Creek: Reconductor 69kV Line | Reconductor Crystal City - Turtle Creek 69kV Line | Reformated project number to match other numbers, changed ISD, and Dollars. PM Updated | Crystal City | Turtle Creek | Planned | 591 - 0761 | AEP/TCC | Terry Weeks 918-599-2664 | 3468 | 2014-06-30 |  | 69 | 0 | 3.3 | 0 | 0 | ZAVALA | ZAVALA | Tier 4 |  |  |  | 8242, 8243 | Y | N |  | 0
New Project | New Project | 14TPIT0105 | Wink_All American Pipeline_Lonestar_Barstow_Pecos 69kV rebuild | Rebuild TNMP Wink - All American Pipeline-Lonestar-Barstow - Pecos 69 kV lines with 795 ACSR conductor. Upgrade terminal equipment at Wink AAPipeline, and Pecos station. |  | Wink | Pecos | Planned |  | TNMP | Tony Hudson, 281-581-4712, Anthony.Hudson@tnmp.com | NTE09513 | 2014-06-30 |  | 69 | 0 | 32.8 | 0 | 0 | REEVES | Winkler | Tier 3 |  |  |  | 37920, 38230, 38180, 38150, 38090 | Y | N |  | Need to submit RPG to ERCOT.
Old Project | No Change | 05TPIT0065 | Highway 32-Wimberley | Construct a new 795 ACSR (220-MVA) 138-kV double circuit transmission line (approximately four miles) between the Highway 32(7546) and Wimberley(7496) substations. |  | Highway 32 | Wimberley | Planned |  | PEC | Tony Perez (830) 868-5158 |  | 2014-06-30 |  | 138 | 4 | 0 | 0 | 0 | HAYS | HAYS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | N | N
Old Project | No Change | 14TPIT0004 | Cushman-Highway 123 | Construct a new 6.2 mile single 795 ACSR 138 kV transmission line (rated 220 MVA) from the new Highway 123 substation (7221) located near the intersection of State Highway 123 and the GVEC Hickory Forest (7225)-New Berlin (7612) 138 kV (T–529) transmission line to the LCRA TSC Cushman substation (7226). |  | Highway 123 | Cushman/New Berlin/Hickory Forrest | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2014-06-30 |  | 138 | 6.2 | 0 | 0 | 0 | GUADALUPE |  | Tier 2 | 2009-02-06 | 2009-06-01 | N/A | SEE PROJECT DESCRIPTION | Y | N |  | Coordinate with GVEC
Old Project | No Change | 14TPIT0021 | Buttercup-Whitestone Upgrade | Upgrade the 2.3-mile Buttercup (7531)-Whitestone (7529) 795 ACSR (220-MVA) 138-kV transmission line to bundled 795 ACSR (440MVA). |  | Buttercup Substation | Whitestone Substation | Planned |  | PEC | Tony Perez (830) 868-5158 |  | 2014-06-30 |  | 138 | 0 | 2.3 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 14TPIT0076 | Fry Road 138kV Substation | Build new 138kV Fry Road distribution substation. Double tap off Ckt.09 Zenith - Gertie tap and Ckt.76 Zenith - Gertie tap. |  | Fry Road | Zenith/ Gertie | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-06-30 |  | 138 | 0.1 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 44910, 45811, 45801, 45812, 45802 | Y | N
Old Project | No Change | 14TPIT0075 | Millican to BEC HWY 6Line | Build(6) miles of new 1033 ACSR energized at 138 kV to planned BEC HWY 6 substation as part of Dobbin Project |  | Millican Substation | BEC HWY 6 Substation | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2014-07-21 |  | 138 | 6 | 0 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 14TPIT0073 | Kokernut Substation | Build a new 138x69-26.18 kV 12/16/20 MVA substation on the GVEC Gonzales-GVEC Shiner 69 kV transmission line |  | Kokernut | Gonzales/Shiner | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2014-07-30 |  | 69 | 0 | 0 | 0 | 0 | GONZALES |  | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 15TPIT0026 | Wellborn to Millican Upgrade | ReBuild-Reconductor (3.6) miles of 69kV line converting to 138 kV as part of 138 kV BEC Roans Prairie Project |  | Wellborn Susbstation | Millican Substation | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2014-07-31 |  | 138 | 0 | 3.6 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 15TPIT0027 | Millican Substation Upgrade | Install (3) Breaker ring to support (2) 138kV lines and (1) 138/69 auto-transformer |  | Millican Substation | Millican Substation | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2014-07-31 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 5/31/2014 to 8/31/2014 | 14TPIT0065 | Concho: Replace 138/69 kV autotransformer & build four breaker ring bus | Build new Concho 138 kV station and replace 138/69 kV autotransformer at Concho | Description, Contact & Schedule Update | Concho |  | Planned | 567 - 0741 | AEP/TNC | Eric Scott 918-599-2664 | 2571 | 2014-08-31 |  | 138 | 0 | 0 | 90 | 0 | TOM GREEN |  | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 5/31/2015 to 9/30/2014 | 15TPIT0043b | Fort Bend Area Upgrades | Remove COLLIN substation from CNP transmission service | Accelerated project schedule | COLLIN |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-09-30 |  | 69 | 0 | 0 | 0.0 | 0 | FORT BEND |  | Tier 4 |  |  |  | 44160 | Y | N |  | Cost is included in main project.
Old Project | No Change | 14TPIT0061 | Atkins to Briarcrest Upgrade | Upgrade to 795 ACSR to alleviate overload during double contingency situations. Add OPGW. Add new poles/structures. |  | Atkins Substation | Briarcrest Substation | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2014-09-30 |  | 138 | 0 | 3.4 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 11/1/2014 | 13TPIT0094 | Lamesa - Ackerly Vealmoor 138 kV line | Add second circuit to existing line | Construction schedule change | Lamesa | Ackerly Vealmoor | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8032-E | 2014-11-01 |  | 138 | 21.5 | 0 | 0 | 0 | DAWSON | HOWARD | Tier 2 | 2008-10-01 | 2011-01-01 |  | 1355, 1163 | Y | N
Old Project | No Change | 13TPIT0198 | Seawillow Substation | Construct 138kV/12.5kV distribution substation Seawillow (7559) on T-184 Lockhart and Luling. |  | Seawillow | Luling/Lockhart | Planned |  | LCRA TSC/BBEC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2014-11-01 |  | 138 | 0 | 0 | 0 | 0 | CALDWELL |  | Tier 4 |  |  |  | see project description | N | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 11/1/2014 | 14TPIT0084 | Ackerly Vealmoor 138 kV Switching Station | Install 138 kV circuit breakers | Construction schedule change |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8034-E | 2014-11-01 |  | 138 | 0 | 0 | 0 | 0 | DAWSON |  | Tier 4 |  |  |  | 1355 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 11/1/2014 | 14TPIT0085 | Lamesa Switching Station | Install 138 kV circuit breakers | Construction schedule change |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8033-E | 2014-11-01 |  | 138 | 0 | 0 | 0 | 0 | HOWARD |  | Tier 4 |  |  |  | 1163 | Y | N
Old Project | No Change | 14TPIT0102 | Penwell - Moss 138 kV line | Uprgade existing 138 kV line |  | Penwell | Moss | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8107-E | 2014-11-01 |  | 138 | 0 | 6.8 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1011, 1019 | Y | N
New Project | New Project | 14TPIT0118 | Permian Basin - Wink 138 kV line | Upgrade existing 138 kV line |  | Permian Basin | Wink | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8105-E | 2014-11-01 |  | 138 | 0 | 16.5 | 0 | 0 | WARD | WINKLER | Tier 4 |  |  |  | 1010, 1074 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 11/1/2014 | 14TPIT0092 | Temple Switch - Bell County East 345 kV line | Upgrade existing 345 kV line | Construction schedule change | Temple Switch | Bell County East | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R764-E | 2014-11-01 |  | 345 | 0 | 24 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3687, 3414 | Y | N
Old Project | No Change | 14TPIT0071 | Princeton South - New Substation | Build a new 138-12.47 kV substation to accommodate load growth in Princeton. |  |  |  | Planned | 16TPIT0005 | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2014-11-29 |  | 138 | 0 | 0 | 0 | 0 | Collin |  | Tier 4 |  |  |  | 37295 | Y | N
Old Project | No Change | 16TPIT0005 | Farmersville West to Princeton South - new 138 kV line. | Build approximately 7.5 miles of 138 kV transmission line from Farmersville West Substation to Princeton South Substation. |  | Farmersville West | Princeton South | Planned | New projects added on rows 18 and 19. Please add TPIT numbers here after they have been assigned. | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE07213 | 2014-11-30 |  | 138 | 7.5 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 37291, 37295 | Y | N
Old Project | No Change | 14TPIT0059 | Bevo Station and Autotransformer | Build new Bevo substation west of Cotulla where 138 and 69 kV lines cross and add a 150 MVA 139/69 kV autotransformer |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2014-12-01 |  | 69 | 0 | 0 | 150 | 0 | DIMMIT |  | Tier 1 | 2012-04-16 | 2012-08-30 | 2012-09-18 | 5871, 78280 | Y | N
Old Project | No Change | 14TPIT0078 | Advance Capacitor Bank | Install 15 MVAR at Advance substation |  | Advance | Advance | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 12011 | 2014-12-01 |  | 69 | 0 | 0 | 0 | 15 | PARKER |  | Tier 4 |  |  |  | 518 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 12/1/2014 | 08TPIT0153 | Elkton - Athens 138 kV line | Upgrade existing 138 kV line | Construction schedule change | Elkton | Athens | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R651-E | 2014-12-01 |  | 138 | 0 | 27.9 | 0 | 0 | HENDERSON | HENDERSON | Tier 4 | 2007-11-26 |  |  | 3177, 3178, 3172, 3131 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 12/1/2014 | 13TPIT0060 | Cedar Hill Switch - Mountain Creek 138 kV line | Upgrade existing line | Construction schedule change | Cedar Hill Switch | Mountain Creek | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4068-E | 2014-12-01 |  | 138 | 0 | 11.4 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2422, 2421, 2412, 2411 | Y | N
Old Project | No Change | 13TPIT0153 | Moss - Odessa Southwest - Odessa EHV 138 kV line | Upgrade existing 138 kV line |  | Moss | Odessa EHV | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8064-E | 2014-12-01 |  | 138 | 0 | 14.2 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1019, 1027 | Y | N
Old Project | No Change | 14TPIT0081 | Bowie Capacitor Bank | Install 15 MVAR at Bowie substation |  | Bowie | Bowie | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 12012 | 2014-12-01 |  | 138 | 0 | 0 | 0 | 15 | MONTAGUE |  | Tier 4 |  |  |  | 620, 621 | N | N
Old Project | No Change | 14TPIT0096 | Nevada-Olinger 138 kV line | Line upgrade | On Hold For Funding | A new switch at new Nevada | A switch at Olinger | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2014-12-01 |  | 138 | 0 | 9.5 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 811, 818 | Y | N |  | This project is a new line for new load serving at Nevada
Old Project | No Change | 14TPIT0080 | Oran to Advance Rebuild | Rebuild Oran to Advance with 959 ACSS, 138 kV construction (operate at 69 kV) |  | Oran | Advance | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 12010 | 2014-12-03 |  | 69 | 0 | 13.7 | 0 | 0 | PALO PINTO | PARKER | Tier 4 |  |  |  | 518, 519, 785 | Y | N
Old Project | Change in Service Date. Changed from 12/12/2013 to 12/12/2014 | 07TPIT0096 | Pockrus Substation - Reconstruct 138kV Section of the Station | Reconstruct the 138kV section of the station to install transmission circuit breakers in a breaker-and-a-half configuration | On schedule |  |  | Planned | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600852 | 2014-12-12 |  | 138 | 0 | 0 | 0.0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 917 | Y | N
Old Project | No Change | 09TPIT0073 | Jupiter-Apollo 69 kV line | Line reconductor | On Hold For Funding | Switch 1377 at Jupiter | Switch 6612 at Apollo | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2014-12-28 |  | 138 | 0 | 2 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 806, 802 | Y | N |  | This project is a line reconductor for solving overload
Old Project | No Change | 09TPIT0074 | Jupiter-Lawler 69 kV line | Line reconductor | On Hold For Funding | Switch 1378 at Jupiter | Switch 931 at Lawler Tap | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2014-12-28 |  | 138 | 0 | 1.5 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 806, 815, 820 | Y | N |  | This project is a line reconductor for solving overload
Old Project | No Change | 09TPIT0076 | Lawler-College 69 kV line | Line reconductor | On Hold For Funding | Switch 932 at Lawler Tap | Switch 6832 at College | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2014-12-28 |  | 138 | 0 | 2 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 803, 815, 820 | Y | N |  | This project is a line reconductor for solving overload
Old Project | Change in Service Date. Changed from 12/1/2013 to 12/31/2014 | 09TPIT0039 | Woodrow to Kings Row 69kV Transmission Line Reconstruction | Reconstruct 4.2 miles of existing 69V transmission line | On schedule | Woodrow Substation PSS/E Bus 901 | Kings Row Substation PSS/E Bus 909 | Planned | 12TPIT0008 12TPIT0088 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600483 | 2014-12-31 |  | 69 | 0 | 4 | 0.0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 901, 909 | Y | N
Old Project | Change in Service Date. Changed from 12/31/2013 to 12/31/2014 | 12TPIT0008 | Kings Row to Denton North 69kV Transmission Line Reconstruction | Reconstruct 1.91 miles of existing 69V transmission line | On schedule | Kings Row Substation PSS/E Bus 909 | Denton North Interchange PSS/E Bus 912 | Planned | 09TPIT0039 12TPIT0088 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602674 | 2014-12-31 |  | 69 | 0 | 2 | 0.0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 909, 912 | Y | N
Old Project | Change in Service Date. Changed from 12/31/2013 to 12/31/2014 | 12TPIT0088 | Kings Row Substation Reconstruction | Completely reconstruct the Kings Row Substation | On schedule |  |  | Planned | 09TPIT0039 12TPIT0008 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602931 | 2014-12-31 |  | 69 | 0 | 0 | 0.0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 909 | Y | N
Old Project | No Change | 14TPIT0064 | West Yates to Air Products: Rebuild 69 kV line | Rebuild West Yates to Air Products 69 kV line with 795 ACSS |  | West Yates | Air Products | Planned | 570 - 0744 | AEP/TNC | Glen Reed 918-599-2664 | 2574 | 2014-12-31 |  | 69 | 0 | 2.28 | 0 | 0 | PECOS | CROCKETT | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 14TPIT0094 | Pecos Substation Ring Bus | Build ring bus for 69 kV system in TNMP's Pecos Substation |  | Pecos |  | Conceptual |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE03414 | 2014-12-31 |  | 69 | 0 | 0 | 0 | 0 | REEVES |  | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 14TPIT0099 | Treaschwig - Westfield Ckt.66 | Upgrade 138kV Ckt. 66 Treaschwig to Westfield to increase thermal ratings. |  | Treaschwig | Westfield | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-12-31 |  | 138 | 0 | 0 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 46550, 46570 | Y | N |  | Project is part of the 2012 ERCOT 5-Year Plan.
New Project | New Project | 14TPIT0108 | Kenedy 138/69 kV Switching Station: Upgrade | A 138 kV circuit from Kenedy Switch Station to Pettus energized at 69 kV. | NEW Corrected Assoc Parts Number Format | Kenedy 138/69 kV Switching Station |  | Planned | 603 - 0765 | AEP/TCC | Glen Reed 918-599-2664 | 3482 | 2014-12-31 |  | 138 | 0 | 0 | 0 | 0 | KARNES |  | Tier 3 |  |  |  |  | N | N
New Project | New Project | 14TPIT0117 | Cooper Creek Substation | Construct new 138kV - 13.2kV substation | New Project |  |  | In Design and Procurement | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 603112 | 2014-12-31 |  | 138 | 0 | 0 | 0.1 | 1 | DENTON | DENTON | Tier 5 |  |  | NA | 906 | Y | N
Old Project | Change in Service Date. Changed from 6/14/2016 to 12/31/2014 | 16TPIT0023 | South McAllen - Stewart Road: Rebuild 138kV Line | Rebuild South McAllen - Stewart Road 138kV Line | Reformated project number to match other numbers, Chnaged ISD | South McAllen | Stewart Road | Planned | 601 - 0763 | AEP/TCC | Glen Reed 918-599-2664 | 3470 | 2014-12-31 |  | 138 | 0 | 9.8 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8371, 8758, 8951 | Y | N |  | 0
Old Project | Change in Service Date. Changed from 12/31/2016 to 12/31/2014 | 16TPIT0031 | Ringtail: Build new four breaker ring bus | Construct new Ringtail station along the Big Lake to Friend Ranch 138 kV line | Schedule Update | Ringtail |  | Planned | 585 - 0738 | AEP/TNC | Glen Reed 918-599-2664 | 2576 | 2014-12-31 |  | 138 | 0 | 0 | 0 | 0 | CROCKETT |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0124 | Airport 69 kV Substation | Build new load serving station in the 69 kV line from Lone Tree to Twin Pines Switch. |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2015-01-01 |  | 69 | 0 | 0 | 0 | 0 | VICTORIA |  | Tier 4 |  |  |  | 5601 | Y | N
Old Project | Change in Service Date. Changed from 12/15/2018 to 1/30/2015 | 18TPIT0001 | Wiederstein Substation | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Wiederstein |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2015-01-30 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | Change in Service Date. Changed from 11/15/2015 to 3/27/2015 | 15TPIT0042 | FM 237 Yorktown Substation | Replace T1, 138kV-26.18 kV, 20 MVA PWT w/associated bus, structures, panels, etc |  | FM 237 |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2015-03-27 |  | 138 | 0 | 0 | 0.0 | 0 | DeWitt |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 07TPIT0210 | Hilltop - White Settlement 69 kV line | Rebuild 4/0 ACSR section of line |  | Hilltop | White Settlement | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5135-E | 2015-05-01 |  | 69 | 0 | 14.33 | 0 | 0 | PARKER | TARRANT | Tier 4 |  |  |  | 502, 1588, 2089 | Y | N
Old Project | No Change | 07TPIT0236 | N. Terrell Tap - Rose Hill 138 kV line | Rebuild existing line |  | N. Terrell Tap | Rose Hill | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3059-E | 2015-05-01 |  | 138 | 0 | 8.68 | 0 | 0 | KAUFMAN | KAUFMAN | Tier 4 |  |  |  | 2715, 2717, 2714, 2723, 2719 | Y | N
Old Project | No Change | 08TPIT0172 | Gunsight 138 kV Switching Station | Construct new switching station to connect a new wind farm |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R829-WA | 2015-05-01 |  | 138 | 0 | 0 | 0.0 | 0 | HOWARD |  | Tier 4 |  |  |  | 1360 | Y | N
Old Project | No Change | 09TPIT0117 | Stryker Creek - Dialville 138 kV line | Upgrade existing 138 kV line |  | Stryker Creek | Dialville | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R664-E | 2015-05-01 |  | 138 | 0 | 15.2 | 0 | 0 | CHEROKEE | CHEROKEE | Tier 4 |  |  |  | 3110, 3160 | Y | N
Old Project | No Change | 10TPIT0017 | Allen Switch - Plano Custer - Collin Junction 138 kV line | Upgrade existing double-circuit 138 kV line |  | Allen Switch | Collin Junction | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3047-E | 2015-05-01 |  | 138 | 0 | 9 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 2509, 2525, 2510,2526,2524 | Y | N
Old Project | No Change | 11TPIT0015 | Sherry - Park Row - Grand Prairie 138 kV line | Upgrade existing 138 kV line |  | Sherry | Grand Prairie | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5121-E | 2015-05-01 |  | 138 | 0 | 11.4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1919, 1920, 2257, 2258 | Y | N
Old Project | No Change | 11TPIT0032 | NW Carrollton - Collin second 138 kV circuit | Rebuild existing 138 kV line for double-circuit operation. |  | NW Carrollton | Collin | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M368-E | 2015-05-01 |  | 138 | 16.93 | 16.93 | 0 | 0 | DALLAS | COLLIN | Tier 4 |  |  |  | 2363, 2370 | Y | N | 2009-R13
Old Project | No Change | 14TPIT0015 | Troup - Walnut Grove - Whitehouse - Tyler Grande 138 kV line | Upgrade existing line |  | Troup | Tyler Grande | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6002-WAC | 2015-05-01 |  | 138 | 0 | 13.34 | 0.0 | 0 | CHEROKEE | SMITH | Tier 4 |  |  |  | 3147, 3227, 3156 | Y | N |  | A SPS has been modified to manage flow on this line.
Old Project | No Change | 14TPIT0016 | West Mesquite - Prairie Creek 138 kV line | Upgrade existing line |  | West Mesquite | Prairie Creek | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4069-E | 2015-05-01 |  | 138 | 0 | 2.8 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2754, 2441 | Y | N | 2009-R19
Old Project | No Change | 14TPIT0055 | Seagoville - Wilmer 138 kV line | Upgrade existing line |  | Seagoville | Wilmer | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4081-E | 2015-05-01 |  | 138 | 0 | 10.9 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 3076, 3083 | Y | N
Old Project | No Change | 14TPIT0057 | Cedar Hill - Mayfield Tap North 138 kV line | Upgrade existing line |  | Cedar Hill Switch | Mayfield Tap North | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5041-E | 2015-05-01 |  | 138 | 0 | 4.3 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2422, 2421, 1912 | Y | N
Old Project | No Change | 14TPIT0086 | Allen Switch - Parker Maxwell Creek - Ben Davis 138 kV line | Upgrade existing line |  | Allen Switch | Ben Davis Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4102-E | 2015-05-01 |  | 138 | 0 | 9.4 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 12509, 2477, 968 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 5/1/2015 | 14TPIT0089 | North Main Switch third transmission source | Construct a third 138 kV line into North Main Switch | Studies indicate timing of project should be changed | North Main Tap | North Main Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5161-E | 2015-05-01 |  | 138 | 4.4 | 4.4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1961 | Y | N
Old Project | No Change | 15TPIT0039 | Plano Tennyson Road - Preston Meadows | Upgrade 138 kV line |  | Plano Tennyson Road | Preston Meadows | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4103-E | 2015-05-01 |  | 138 | 0 | 2.6 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 2523, 10010 | Y | N
New Project | New Project | 15TPIT0058 | Permian Basin - Ward Gulf Tap - Wink 138 kV line | Upgrade existing 138 kV line |  | Permian Basin | Wink | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8189-E | 2015-05-01 |  | 138 | 0 | 16.5 | 0 | 0 | WARD | WINKLER | Tier 4 |  |  |  | 1010, 1087, 1074 | Y | N
Old Project | No Change | 12TPIT0080 | Forney Sw. Sta. Second 600 MVA, 345/138 kV Autotransformer | Add second 345/138 autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4037 | 2015-05-01 |  | 345 | 0 | 0 | 600 | 0 | KAUFMAN |  | Tier 4 | 2008-06-01 | 2008-07-01 |  | 2437, 2438 | Y | N | 2007-R2
Old Project | No Change | 13TPIT0113 | Renner | Replace existing 345/138 kV autotransformer with larger autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3099-E | 2015-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  | Tier 4 |  |  |  | 2355, 2354, 2355 | Y | N
Old Project | No Change | 15TPIT0040 | Temple Switch 345/138 kV autotransformer | Replace existing autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R758-E | 2015-05-01 |  | 345 | 0 | 0 | 600 | 0 | BELL |  | Tier 4 |  |  |  | 3414, 3415 | Y | N
Old Project | No Change | 15TPIT0041 | Knob Creek 345 kV Switching Station Phase II | Expand 345 kV switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R749B-E | 2015-05-01 |  | 345 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 13413 | Y | N
Old Project | No Change | 15TPIT0047 | Permian Basin - Moss 345 kV Line | Construct new double-circuit line. |  | Moss | Permian Basin | Conceptual | R8135-E & R8100B-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8100C-E | 2015-05-01 |  | 345 | 90 | 0 | 0 | 0 | ECTOR | WARD | Tier 1 | 2013-02-01 | on-going | TBD | 1018, 11010 | Y | N
Old Project | No Change | 15TPIT0048 | Odessa EHV - Moss 345 kV Line | Add second circuit to an existing line |  | Odessa EHV | Moss | Conceptual | R8100-E & R8100B-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8135- E | 2015-05-01 |  | 345 | 15 | 0 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1028, 1018 | Y | N |  | Estimated cost is included in total estimated cost for 15TPIT0047.
Old Project | No Change | 15TPIT0049 | Permian Basin 345 kV Switching Station | Construct 345 kV switching station and install 345/138 kV autotransformer |  |  |  | Conceptual | R8100C-E & R8100B-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8100B-E | 2015-05-01 |  | 345 | 0 | 0 | 600 | 0 | WARD |  | Tier 4 |  |  |  | 11010, 1010 | Y | N |  | Estimated cost is included in total estimated cost for 15TPIT0047.
Old Project | No Change | 14TPIT0063 | Munday to BEC Munday: Rebuild 69 kV line | Rebuild Munday to BEC Munday 69 kV line with 795 ACSR |  | Munday | BEC Munday | Planned | 568 - 0742 | AEP/TNC | Glen Reed 918-599-2664 | 2572 | 2015-05-31 |  | 69 | 0 | 3.57 | 0 | 0 | KNOX | KNOX | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 15TPIT0043a | Fort Bend Area Upgrades | Remove Richmond substation from CNP transmission service |  | Richmond |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 69 | 0 | 0 | 0.0 | 0 | FORT BEND |  | Tier 4 |  |  |  | 44580 | Y | N |  | Cost is included in main project.
Old Project | Change in Service Date. Changed from 6/30/2016 to 5/31/2015 | 16TPIT0027 | Beeville - Sinton: Rebuild 69kV Line | Rebuild Beeville - Sinton 69kV Line for future 138 kV operation | Reformated project number to match other numbers, changed date | Pettus | Sinton | Conceptual | 579 - 0737 | AEP/TCC | Glen Reed 918-599-2664 | 3465 | 2015-05-31 |  | 69 | 0 | 29.5 | 0 | 0 | SAN PATRICIO | BEE | Tier 3 | 2012-08-31 | on-going | N/A | 8413, 8405, 8198 | Y | N |  | 0
Old Project | No Change | 12TPIT0062 | UTMB - New Substation | Build a new 138-12.47 kV substation to serve proposed UTMB Medical Center at Victory Lakes in League City. |  |  |  | Planned |  | TNMP | Tony Hudson, 281-581-4712, Anthony.Hudson@tnmp.com | STE04512 | 2015-05-31 |  | 138 | 0 | 0 | 0 | 0 | GALVESTON |  | Tier 4 |  |  |  | 38930 | Y | N |  | Project pushed out based on revised load forecast from UTMB.
Old Project | Change in Service Date. Changed from 12/31/2014 to 5/31/2015 | 14TPIT0082 | Kenedy Switch - Pettus: Rebuild 69 kV line | Add 138 kV circuit from Kenedy Switch Station to Pettus energized at 69 kV. | Changed: ISD and Project Description | Kenedy | Pettus | Planned | 603 - 0765 | AEP/TCC | Frank Pritzlaff (AEP) 918-599-2664 | 3473 | 2015-05-31 |  | 138 | 0 | 15.9 | 0 | 0 | Karnes | Bee | Tier 4 |  |  |  | 8184, 8186, 8188, 8590 | Y | N
New Project | New Project | 14TPIT0109 | Kenedy Switch to Tuleta: Build 138 kV line | Build 138 kV line with double circuit capable | NEW Corrected Assoc Parts Number Format | Kenedy | Tuleta | Planned | 603 - 0765 | AEP/TCC | Glen Reed 918-599-2664 | 3483 | 2015-05-31 |  | 138 | 0 | 16.9 | 0 | 0 | KARNES | Bee | Tier 3 |  |  |  | 8184, 8186, 8188, 8590 | Y | N
Old Project | No Change | 15TPIT0030 | Mainland - New Substation | Build a new 138-12.47 kV substation to accommodate load growth along I45 between Texas City and Dickinson. Cut TNMP's Freeway Park - Alvin 138 kV line into the new substation. |  | Mainland |  | Planned |  | TNMP | Tony Hudson, 281-581-4712, Anthony.Hudson@tnmp.com |  | 2015-05-31 |  | 138 | 0 | 0 | 0 | 0 | Galveston |  | Tier 4 |  |  |  | 38830 | Y | N
Old Project | No Change | 15TPIT0034 | Freeport Area Upgrades and Conversion to 138kV | Convert to 138kV and upgrade Ckt. 47 Velasco to Freeport |  | Velasco | Freeport | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 4.5 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 3 | 2012-06-14 | 2012-07-24 | N/A | 43370, 42640, 43360, 46640 | Y | N |  | Part of ERCOT RPG Freeport Area Upgrades
Old Project | No Change | 15TPIT0034a | Freeport Area Upgrades and Conversion to 138kV | Convert to 138kV and upgrade Ckt. 47 Freeport to Quintana |  | Freeport | Quintana | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 0 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 3 | 2012-06-14 | 2012-07-24 | N/A | 42640, 43135, 46640, 46135 | Y | N |  | Part of ERCOT RPG Freeport Area Upgrades. Cost included in main project.
Old Project | No Change | 15TPIT0034b | Freeport Area Upgrades and Conversion to 138kV | Convert to 138kV Ckt. 47 Freeport to Bryan |  | Freeport | Bryan | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 2.4 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 3 | 2012-06-14 | 2012-07-24 | N/A | 42640, 42200, 46640, 45200 | Y | N |  | Part of ERCOT RPG Freeport Area Upgrades. Cost included in main project.
Old Project | No Change | 15TPIT0034C | Freeport Area Upgrades and Conversion to 138kV | Convert to 138kV and upgrade Ckt. 47 Surfside to Quintana |  | Surfside | Quintana | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 2.1 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 3 | 2012-06-14 | 2012-07-24 | N/A | 43135, 43310, 46135, 46310 | Y | N |  | Part of ERCOT RPG Freeport Area Upgrades. Cost included in main project.
Old Project | No Change | 15TPIT0034d | Freeport Area Upgrades and Conversion to 138kV | Convert to 138kV and upgrade Ckt. 10 Velasco to Surfside |  | Velasco | Surfside | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 2.5 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 3 | 2012-06-14 | 2012-07-24 | N/A | 43310, 43370, 46310, 43360 | Y | N |  | Part of ERCOT RPG Freeport Area Upgrades. Cost included in main project.
Old Project | No Change | 15TPIT0035 | Velasco to West Columbia Upgrades and Conversion to 138kV | Convert Retrieve substation to 138kV and energize with existing Ckt. 02 Lake Jackson to West Columbia. Upgrade Ckt. 02 Lake Jackson to Retrieve and parallel bundle a portion of the line with converted 69kV Ckt.47 Velasco to West Columbia. |  | Lake Jackson | Retrieve | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 5.34 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 3 | 2012-06-14 | 2012-07-24 | N/A | 42880, 43145 | Y | N |  | Part of ERCOT RPG Freeport Area Upgrades
Old Project | No Change | 15TPIT0035a | Velasco to West Columbia Upgrades and Conversion to 138kV | Upgrade Ckt. 02 Retrieve to West Columbia. Parallel bundle a portion of the line with converted 69kV Ckt.47 Velasco to West Columbia. |  | Retrieve | West Columbia | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 11.9 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 3 | 2012-06-14 | 2012-07-24 | N/A | 43145, 43380 | Y | N |  | Part of ERCOT RPG Freeport Area Upgrades. Cost included in main project.
Old Project | No Change | 15TPIT0035b | Velasco to West Columbia Upgrades and Conversion to 138kV | Parallel bundle a portion of Ckt. 02 Hofman to Lake Jackson with converted 69kV Ckt.47 Velasco to West Columbia. |  | Hofman | Lake Jackson | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 3.9 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 3 | 2012-06-14 | 2012-07-24 | N/A | 42810, 42880 | Y | N |  | Part of ERCOT RPG Freeport Area Upgrades. Cost included in main project.
Old Project | No Change | 15TPIT0035c | Velasco to West Columbia Upgrades and Conversion to 138kV | Parallel bundle a portion of Ckt. 02 BASF to Hofman with converted 69kV Ckt.47 Velasco to West Columbia. |  | BASF | Hofman | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 0.84 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 3 | 2012-06-14 | 2012-07-24 | N/A | 42150, 42810 | Y | N |  | Part of ERCOT RPG Freeport Area Upgrades. Cost included in main project.
Old Project | No Change | 15TPIT0035d | Velasco to West Columbia Upgrades and Conversion to 138kV | Parallel bundle a portion of Ckt. 02 Brazosport to Velasco with converted 69kV Ckt.47 Velasco to West Columbia. |  | Brazosport | Velasco | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 1.32 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 3 | 2012-06-14 | 2012-07-24 | N/A | 42210, 43360 | Y | N |  | Part of ERCOT RPG Freeport Area Upgrades. Cost included in main project.
Old Project | No Change | 15TPIT0043 | Fort Bend Area Upgrades | Convert FOSTER substation from 69kv service to 138kv tap off of Ckt.25 Flewellen - Peters |  | FOSTER | Peters/ Flewellen | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 1.3 | 0.0 | 0 | FORT BEND | FORT BEND | Tier 4 |  |  |  | 44230, 44250, 46220 | Y | N |  | Cost is included in main project.
Old Project | No Change | 15TPIT0043c | Fort Bend Area Upgrades | Convert 69kv Rosenberg substation to 138kv and reconfigure existing circuits to create new Ckt.60 Orchard - Rosenberg - Fort Bend. |  | Rosenberg | Orchard/ Fort Bend | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 1.5 | 0.0 | 0 | FORT BEND | FORT BEND | Tier 4 |  |  |  | 44540, 44611, 44300, 44280 | Y | N |  | Cost is included in main project.
Old Project | No Change | 15TPIT0043d | Fort Bend Area Upgrades | Remove 69kv facilities at Flewellen substaton and reconfigure existing circuit to create new Ckt.49 Flewellen - Fort Bend. |  | Flewellen | Fort Bend | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-05-31 |  | 138 | 0 | 9.3 | 0.0 | 0 | FORT BEND | FORT BEND | Tier 4 |  |  |  | 44230, 44280 | Y | N |  | Cost is included in main project.
New Project | New Project | 15TPIT0052 | Molina to Wormser: Cut-In | Construct 345 kV circuit from Lobo to Molina energized at 138 kV on the open position of the Lobo to North Edinburg 345kV line. Upgrade Lobo and Molina 138kV stations. | NEW Corrected Assoc Parts Number Format | Molina | Wormser | Planned | 206 - 0288 | AEP/ETT | Kenneth 'Rich' Haley 918-599-2664 | 38190 | 2015-05-31 |  | 138 | 1 | 0 | 0 | 0 | WEBB | WEBB | Tier 3 | 2012-03-12 | 2012-04-02 | 2012-04-27 |  | Y | N
New Project | New Project | 15TPIT0053 | Molina to Zapata: Cut-In | Construct 345 kV circuit from Lobo to Molina energized at 138 kV on the open position of the Lobo to North Edinburg 345kV line. Upgrade Lobo and Molina 138kV stations. | NEW Corrected Assoc Parts Number Format | Molina | Zapata | Planned | 206 - 0288 | AEP/ETT | Kenneth 'Rich' Haley 918-599-2664 | 38191 | 2015-05-31 |  | 138 | 2 | 0 | 0 | 0 | WEBB | WEBB | Tier 3 | 2012-03-12 | 2012-04-02 | 2012-04-27 |  | Y | N
Old Project | No Change | 16TPIT0020 | Constrcut: Molina 138 kV Station | Construct 345 kV circuit from Lobo to Molina energized at 138 kV on the open position of the Lobo to North Edinburg 345kV line. Upgrade Lobo and build Molina 138kV stations. | Changed Project Title and project description | Molina |  | Planned | 206 - 0288 | AEP/TCC | Kenneth 'Rich' Haley 918-599-2664 | 900 | 2015-05-31 |  | 138 | 0 | 0 | 0 | 0 | WEBB | 0 | Tier 3 | 2012-03-12 | 2012-04-02 | 2012-04-27 |  | Y | N
Old Project | No Change | 11TPIT0001 | Lobo to Molina, build 345 kV circuit energized at 138kV | Construct 345 kV circuit from Lobo to Molina energized at 138 kV on the open position of the Lobo to North Edinburg 345kV line. Upgrade Lobo and Molina 138kV stations. | Updated dollars | Lobo | Rio Bravo | Planned | 206 - 0288 | AEP/ETT | Kenneth 'Rich' Haley 918-599-2664 | 880 | 2015-05-31 |  | 345 | 26 | 0 | 0 | 0 | WEBB | WEBB | Tier 3 | 2012-03-12 | 2012-04-02 | 2012-04-27 |  | Y | N
Old Project | No Change | 14TPIT0067 | San Angelo Area: Replace both 345/138 kV autotransformers | Build new 138 kV station south of San Angelo, add a 345/138 kV auto and loop in the SAPS to Live Oak 138 kV line | Description Update | Red Creek |  | Planned | 566 - 0740 | AEP/TNC | Glen Reed 918-599-2664 | 2570 | 2015-05-31 |  | 345 | 0 | 0 | 800 | 0 | TOM GREEN |  | Tier 3 |  |  |  |  | Y | N
Old Project | No Change | 16TPIT0019 | Lobo 138 kV station: install 2 additional CB | Construct 345 kV circuit from Lobo to Rio Bravo energized at 138 kV on the open position of the Lobo to North Edinburg 345kV line. Upgrade Lobo and Rio Bravo 138kV stations. |  | Lobo |  | Planned | 206 - 0288 | AEP/ETT | Kenneth 'Rich' Haley 918-599-2664 | 634 | 2015-05-31 |  | 345 | 0 | 0 | 0 | 0 | WEBB | 0 | Tier 3 | 2012-03-12 | 2012-04-02 | 2012-04-27 |  | Y | N
Old Project | No Change | 15TPIT0002 | Hickory Substation to Locust Substation 69kV Transmission Line Reconstruction | Reconstruct 2.5 miles of existing 69V transmission line | On schedule | Hickory Substation, 910 | Locust Substation, 914 | Planned | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602949 | 2015-06-01 |  | 69 | 0 | 2.5 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 910, 914 | N | N
Old Project | No Change | 15TPIT0011 | Shannon to Montague | Rebuild Shannon to Montague 69 kV line with 959 ACSS. |  | Shannon | Montague | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10045 | 2015-06-01 |  | 69 | 0 | 23.36 | 0 | 0 | CLAY | MONTAGUE | Tier 4 |  |  |  | 772, 769, 768, 633 | Y | N
Old Project | No Change | 09TPIT0037 | Blossom - New 138 kV Substation | Loop new 138 kV substation into the existing 138kV Harmony Hills to Skyline line | Delayed due to budget constraint | Blossom | Harmony Hills/Skyline | Planned | T-0178 | CPS | PM: Ulrich Skerhut | S-0602 | 2015-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5022 | N | N |  | There are no transformers associated with this project
Old Project | No Change | 10TPIT0001 | Trumbo - New 138 kV Substation | Loop new 138 kV substation into the existing 138kV Leon Creek to Pleasanton Rd/Loxley (AEP) line | Accelarated by Disribution Planning | Trumbo | Leon Creek/Pleasanton Rd | Conceptual | T-0082 | CPS | Blake Williams | S-0181 | 2015-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5429 | Y | N |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 12/27/2013 to 6/1/2015 | 12TPIT0083 | Firewheel-Lookout 138 kV line | Line upgrade | On Hold For Funding | Switch 8512 at Firewheel | A new switch at new Lookout | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2015-06-01 |  | 138 | 0 | 1.3 | 0.0 | 0 | DALLAS |  | Tier 4 |  |  |  | 821, 828 | Y | N |  | This project is a line reconductor for solving overload
Old Project | Change in Service Date. Changed from 12/27/2013 to 6/1/2015 | 12TPIT0084 | Lookout 138 kV new substation | New load serving | On Hold For Funding |  |  | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2015-06-01 |  | 138 | 0 | 0 | 0.0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 828 | Y | N |  | This project is a line reconductor for solving overload
Old Project | Change in Service Date. Changed from 12/27/2013 to 6/1/2015 | 12TPIT0085 | Apollo-Lookout 138 kV line | Line upgrade | On Hold For Funding | Switch 8622 at Apollo | A new switch at new Lookout | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2015-06-01 |  | 138 | 0 | 2.8 | 0.0 | 0 | DALLAS |  | Tier 4 |  |  |  | 802, 828 | Y | N |  | This project is a line reconductor for solving overload
Old Project | No Change | 13TPIT0149 | Oaks to Loxley | Build new 138 kV 795 ACSR circuit from Oaks to a new AEP switching station Loxley in the Leon Creek to Pleasanton line |  | Oaks | Loxley | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2015-06-01 |  | 138 | 6 | 0 | 0 | 0 | ATASCOSA | ATASCOSA | Tier 2 | 2011-12-16 | 2012-04-25 | N/A | 5713, 80491 | Y | N
Old Project | No Change | 14TPIT0003 | Ranchtown - New 138 kV Substation | Loop new 138kV substation into the existing 138kV Helotes to Menger Creek line |  | Ranchtown | Helotes/Menger Creek | Conceptual | T-0175 | CPS | Blake Williams | S-0567 | 2015-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5200 5358 7663 | Y | N |  | There are no transformers associated with this project. There is no transmission line additions associated with this project
Old Project | No Change | 14TPIT0020 | Spencer Interchange to Pockrus 138kV Transmission Line New Construction | Construct 3.25 miles of new 138V transmission line | On schedule | Spencer Interchange PSS/E Bus 982 | Pockrus Substation PSS/E Bus 917 | Planned | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600755 | 2015-06-01 |  | 138 | 3.25 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 982, 917 | N | N
Old Project | No Change | 15TPIT0007 | Green Mountain to Stonegate - 138kV 2nd Circuit | Build second 138kV transmission line from Green Mountain to Stonegate on existing transmission structures |  | Green Mountain | Stonegate | Conceptual | S-0608 | CPS | Blake Williams | T-0179 | 2015-06-01 |  | 138 | 11.5 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5180 5415 | Y | N |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 10/1/2014 to 6/1/2015 | 15TPIT0018 | Kerrville Stadium to Raymond F. Barker | Upgrade the 10.1-mile Kerrville Stadium (7136) – Kerrville Travis (7162) – Kerrville Legion (7160) - Raymond F. Barker (7159) 69 kV transmission lines to 795 ACSR, 138 kV (220 MVA / 920 Amperes) and OPGW. |  | Kerrville Stadium | Raymond F Barker | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2015-06-01 |  | 138 | 0 | 10.1 | 0 | 0 | KERR | KERR | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | Coordinate with KPUB
Old Project | No Change | 15TPIT0023 | Seaton Auto | Upgrade 138/69 kV auto to 100 MVA |  | Seaton | Seaton | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11036 | 2015-06-01 |  | 138 | 0 | 0 | 100 | 0 | BELL |  | Tier 4 |  |  |  | 130, 131 | Y | N
Old Project | No Change | 15TPIT0037 | Rhome to Rhome | Loop Oncor's Rhome to Decatur Line into BEPC's Rome switching station |  | Rhome | Decatur | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 12015 | 2015-06-01 |  | 138 | 4 | 0 | 0 | 0 | WISE | WISE | Tier 4 |  |  |  | 576, 1570, 1594 | Y | N
Old Project | No Change | 15TPIT0044 | Fowlerton Capacitor | Add 19.2 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2015-06-01 |  | 138 | 0 | 0 | 0.0 | 19.2 | LA SALLE |  | Tier 4 |  |  |  | 5703 | Y | N
Old Project | No Change | 15TPIT0045 | ETP Capacitor | Add 19.2 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2015-06-01 |  | 138 | 0 | 0 | 0.0 | 19.2 | JACKSON |  | Tier 4 |  |  |  | 5523 | Y | N
Old Project | No Change | 15TPIT0050 | Loxley 138kV substation: STEC Interconnect | Loxley 138kV substation: STEC Interconnect | Reformated project number to match other numbers | Loxley |  | Conceptual | 044 - 0420 | AEP/TCC | Glen Reed 918-599-2664 | 3472 | 2015-06-01 |  | 138 | 0 | 0 | 0 | 0 | ATASCOSA |  | Tier 4 |  |  |  | 80491, 5713 | Y | N
New Project | New Project | 15TPIT0057 | Wylie 138 kV switchyard and its connections to Olinger, to Firewheel, to Elm Grove, to Ben Davis, and to Nevada | New switchyard | On Hold For Funding | New switches at Wylie | Switches at Olinger, at Firewheel, at Elm Grove, at Ben Davis, and at Nevada | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2015-06-01 |  | 138 | 0 | 54 | 0.0 | 0 | COLLIN | DALLAS | Tier 4 |  |  |  | 811, 833, 818, 821, 855, 968 | Y | N |  | This project is a new switchyard project for solving overloads
Old Project | Change in Service Date. Changed from 6/1/2019 to 6/1/2015 | 14TPIT0031 | Cagnon - Install a Fourth 345kV Autotransformer and Change Position of Existing Autotransformer | Install one 600 MVA autotransformer and move current autotransformer #3 to new position |  |  |  | Planned | T-0176 | CPS | Blake Williams | S-0588 | 2015-06-01 |  | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5056 5055 | Y | N |  | There are no transmission line additions associated with this project
Old Project | Change in Service Date. Changed from 10/31/2014 to 6/26/2015 | 14TPIT0098 | Cost Substation Addition | Replace existing station, add 138x69kV-13.09x26.18 dual kV, 12/16/20 MVA PWT w/associated structures, bus, panels, etc |  | Cost |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2015-06-26 |  | 69 | 0 | 0 | 0.0 | 0 | GONZALES |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 13TPIT0121 | Tilden to Reveille 138 kV line | Construct a new 138 kV double circuit capable line from Tilden to Reveille. For new Eagleford shale oil and gas needs. |  | Tilden | Reveille | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2015-06-30 |  | 138 | 47 | 0 | 0 | 0 | MCMULLEN | LA SALLE | Tier 1 | 2012-04-16 | 2012-08-30 | 2012-09-18 | 5701, 8612 | Y | N
Old Project | No Change | 15TPIT0051 | Kenedy Switch - Nixon - Seguin Transmission Line Upgrade | Upgrade the 54.2-mile Kenedy Switch (8184) - Nixon (78580) - Deer Creek (7595 - New Substation) 69kV line to 138 kV 795 ACSR Drake, 223 MVA |  | Kenedy Switch | Deer Creek | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2015-06-30 |  | 138 | 0 | 54.2 | 0 | 0 | KARNES | GUADALUPE | Tier 1 | 2012-09-24 | 2013-01-29 | 2013-03-19 | SEE PROJECT DESCRIPTION | Y | N |  | Coordinate this project with GVEC, STEC and AEP
Old Project | No Change | 14TPIT0050 | Lon Hill to North Edinburg: Reconductor 345kV line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo |  | Lon Hill | North Edinburg | Planned | 071 - 0281 | AEP/TCC | Glen Reed 918-599-2664 | 3183 | 2015-06-30 |  | 345 | 0 | 122.94 | 0 | 0 | NUECES | HIDALGO | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 8455, 8383 | Y | N
Old Project | No Change | 14TPIT0051 | North Edinburg: Reconfigure 345 kV Series Capacitors and Terminate 345 kV Lobo Line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo |  | North Edinburg |  | Planned | 071 - 0281 | AEP/TCC | Glen Reed 918-599-2664 | 3184 | 2015-06-30 |  | 345 | 0 | 0 | 0 | 0 | HIDALGO |  | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 8455 | Y | N
Old Project | No Change | 16TPIT0003 | Longneck to Princeton South - new 138 kV line | Build 3.5 miles of 138kV transmission line from Longneck Substation to Princeton South Substation. |  | Longneck | Princeton South | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE07314 | 2015-08-31 |  | 138 | 3.5 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 37295, 37250 | Y | N
Old Project | No Change | 14TPIT0062 | Kurten Substation Upgrage | Install (3) Breaker ring to support (2) existing 138 lines and (1) existing 138/12.5 transformer |  | Kurten Substation | Kurten Substation | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2015-09-30 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 11/29/2014 to 10/30/2015 | 13TPIT0070 | Nash Creek Substation | Replace existing PWT with new 69kVx13.09 kV, PWT w/associated CSW, structures, bus, panels, etc |  | Nash Creek |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2015-10-30 |  | 69 | 0 | 0 | 0.0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 06TPIT0043 | Sherry - Liggett 138 kV line & Liggett - International Airport 138 kV line | Upgrade 138 kV line |  | Sherry | Liggett | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5042-WA | 2015-11-01 |  | 138 | 0 | 13 | 0 | 0 | TARRANT | DALLAS | Tier 4 |  |  |  | 1920, 2140, 1922, 2124, 2128, 2133, 2137 | Y | N |  | Sherry - GM section was completed in 2009.
Old Project | No Change | 08TPIT0104 | Elgin Switching Station - Elgin 69 kV line conversion to 138 kV | Rebuild existing 69 kV line and convert to 138 kV operation |  | Elgin Switching Station | Elgin | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R471-E | 2015-11-01 |  | 138 | 0 | 5.9 | 0 | 0 | WILLIAMSON | BASTROP | Tier 4 |  |  |  | 3655, 3650 | Y | N
Old Project | No Change | 13TPIT0063 | Salado 138 kV Switch | Construct 138 kV switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R445B-E | 2015-11-01 |  | 138 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 13640 | Y | N
Old Project | No Change | 15TPIT0025 | Monticello SES - Monticello Tap 138 kV line | Upgrade existing line |  | Monticello SES | Monticello Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R906-E | 2015-11-01 |  | 138 | 0 | 20.1 | 0 | 0 | TITUS | FRANKLIN | Tier 4 |  |  |  | 1795, 1994 | Y | N
Old Project | No Change | 15TPIT0029 | CMC Tap to CMC (SMI) 138 kV Transmission Line | Build 2 miles of new double ckt 138 kV t-line loop, 1192 ACSR between CMC Tap and CMC (SMI) substation |  | CMC Tap | CMC (SMI) | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2015-11-18 |  | 138 | 2.2 | 0 | 0 | 0 | GUADALUPE | GUADALUPE | Tier 4 |  |  |  | See Project Title | N | N
Old Project | Change in Service Date. Changed from 12/1/2014 to 12/1/2015 | 14TPIT0068 | North Lakes Substation to Bonnie Brae Substation 69kV Transmission Line Reconstruction | Reconstruct approximately 1.2 miles of existing 69V transmission line | On schedule | North Lakes Substation PSS/E Bus 915 | Bonnie Brae Substation PSS/E Bus 905 | Planned | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602946 | 2015-12-01 |  | 69 | 0 | 1.2 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 915, 905 | Y | N
Old Project | No Change | 15TPIT0028 | Spencer Switch to Locust Substation 69kV Transmission Line Reconductor | Reconductor approximately 1.91 miles of existing 69V transmission line to increase capacity | On schedule | Spencer Switch PSS/E Bus 908 | Locust Substation PSS/E Bus 914 | Planned | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602948 | 2015-12-01 |  | 69 | 0 | 1.91 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 908, 914 | Y | N
Old Project | Change in Service Date. Changed from 11/1/2014 to 12/1/2015 | 11TPIT0012 | Euless - Grapevine Ball Street 138 kV line | Upgrade existing 138 kV line | Construction schedule change | Euless | Grapevine Ball Street | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5131-E | 2015-12-01 |  | 138 | 0 | 11.8 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2016, 2021 | Y | N |  | Euless - Highway 360 Substation section by 5/2014
Old Project | No Change | 12TPIT0079 | Roanoke Switch - Southlake - Grapevine Junction - Coppell 138 kV line (See comments in Other Column.) | Rebuild 138 kV line |  | Roanoke Switch | Coppell | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5118 | 2015-12-01 |  | 138 | 0 | 19.63 | 0 | 0 | Denton | Tarrant | Tier 4 |  |  |  | 1852, 2018, 2020 | Y | N | 2007-R4 | Interim rating increase for Coppell - Grapevine Junction section was implemented in May 2012, and an interim rating increase for the Roanoke Switch - Roanoke West line section was implemented in July 2012. Grapevine Junction - Coppell section will be completed by 5/2014, Roanoke Switch - Southlake section will be completed by 12/2014 and Southlake - Grapevine Junction will be completed by 12/2015.
Old Project | No Change | 13TPIT0047 | Parkway to EC Mornhinweg | Construct a new 138 kV 795 ACSR transmission line between the new EC Mornhinweg substation (7463) and the Parkway substation (7611). |  | Parkway | EC Mornhinweg | Planned | 13TPIT0066 (NBU) | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2015-12-01 |  | 138 | 8 | 0 | 0 | 0 | COMAL | GUADALUPE | Tier 2 | 2009-02-06 | 2009-06-01 | N/A | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 15TPIT0032 | Fort Sam to Tenth Street - 138 kV Transmission Line Rebuild | Rebuild approximately five circuit miles of 138 kV transmission from Ft. Sam to Tenth Street |  | Fort Sam | Tenth St | Conceptual |  | CPS | Blake Williams | T-0188 | 2015-12-01 |  | 138 | 0 | 5 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5160 5420 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 15TPIT0033 | Randolph - 138 kV Substation Equipment Upgrade | Upgrade the Weiderstein and Tuttle terminals and ensure a 2000 A rating (minimum). Reconfigure and/or upgrade the main bus to ensure a 2000 A rating (minimum). |  | Randolph | Tuttle/Weiderstein | Conceptual |  | CPS | Blake Williams | S-0645b | 2015-12-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5360 5435 7461 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 15TPIT0036 | Bethel Area Improvements | Build Bethel Switching Station, Rebuild Sardis to Reqgor Springs with 959 ACSS and 138 kV construction. Relocate Auto from Sardis to Bethel Switching Station. Connect Bethel Switching Station to Oncor's 138 kV system in the area (Ennis to Waxahachie 138 kV line. |  | Multiple | Multiple | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 12016 | 2015-12-01 |  | 138 | 14 | 4 | 40 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 202, 203, 204, 205, 210, 2241, 2321 | Y | N | load serving project: improvments are requires to serve furture Enterprise pipleline pumping stations
Old Project | No Change | 13TPIT0064 | Rocky Mound Switching Station series capacitors | Install series capacitors for Willow Creek - Clear Crossing - Dermott Switch (Central B) 345 kV line (Oncor Electric Delivery part) |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C079-E | 2015-12-01 |  | 345 | 0 | 0 | 0.0 | 0 | HASKELL |  | CREZ |  |  |  | 17012, 17013, 17014, 17015 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
New Project | New Project | 15TPIT0054 | Barney Davis to Naval Base, Construct 138 kV transmission line | Construct new 138 kV line and add tranformation at Laguna to remove contingency overloads during off-peak maintenance | NEW Corrected Assoc Parts Number Format | Barney Davis | Naval Base | Planned | 607 - 0772 | AEP/ETT | Michael Glueck 918-599-2664 | 3484 | 2015-12-31 |  | 138 | 4.2 | 0 | 0 | 0 | NUECES | NUECES | Tier 1 | 2009-03-26 | 2009-10-09 | 2009-12-01 |  | Y | N
New Project | New Project | 15TPIT0055 | Naval Base: Add 138/69 kV Auto | Construct new 138 kV line and add tranformation at Laguna to remove contingency overloads during off-peak maintenance | NEW Corrected Assoc Parts Number Format | Naval Base |  | Planned | 607 - 0772 | AEP/ETT/TCC | Michael Glueck 918-599-2664 | 3485 | 2015-12-31 |  | 138 | 0 | 0 | 240 | 0 | NUECES |  | Tier 1 | 2009-03-24 | 2009-10-09 | 2009-12-01 |  | Y | N
Old Project | Change in Service Date. Changed from 4/30/2016 to 12/31/2015 | 15TPIT0024 | Lon Hill to Nelson Sharpe: Reconductor 345kV line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo | Updated Schedule | Lon Hill | Nelson Sharpe | Planned | 071 - 0281 | AEP/TCC | Glen Reed 918-599-2664 | 3180 | 2015-12-31 |  | 345 | 0 | 20.81 | 0 | 0 | NUECES | KLEBERG | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 8455, 85000 | Y | N
New Project | New Project | 16TPIT0036 | Dunlap to Techridge 138kV Circuit Reconductor | This project will upgrade the last remaining section of 2000 amp conductor on the existing Ckt 975 Dunlap-Techridge. The upgrade will be completed from Yager Corner to near the intersection of Howard Lane and Dessau Road. This upgrade will use 3000 amp bundled 795 ACSS Drake conductor. |  | Dunlap Substation | Techridge Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com |  | 2016-01-01 |  | 138 | 0 | 1.8 | 0.0 | 0 | TRAVIS | TRAVIS | Tier 2 | 2009-01-26 | 2009-06-01 | N/A | 9045, 9190 | Y | N
Old Project | No Change | 11TPIT0050 | Roanoke Switch - Elizabeth Creek 138 kV line | Construct new line. |  | Roanoke Switch | Elizabeth Creek | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M509-E | 2016-05-01 |  | 138 | 3.75 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1850, 1852, 1866, 1867 | Y | N
Old Project | No Change | 11TPIT0179 | Hicks Switch - Elizabeth Creek 138 kV line | Construct new 138 kV line |  | Hicks Switch | Elizabeth Creek | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M523-E | 2016-05-01 |  | 138 | 10 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 2 | 2013-02-06 | 2013-03-07 | N/A | 1866, 1867, | Y | N
Old Project | No Change | 14TPIT0047 | Denton 138kV System Upgrades | Reliability projects necessary for the Denton area. Reconductoring 138kV loop line segments, adding second circuits, substation expansions, etc. |  | West Denton, North Denton, Jim Cristal, Arco, Pockrus, Teasley, Industrial | West Denton, North Denton, Jim Cristal, Arco, Pockrus, Teasley, Industrial | Under Construction |  | TMPA | Tom Chambers 936-873-1125 tchambers@texasmpa.org | T12001 | 2016-05-01 |  | 138 | 19.1 | 26.3 | 0 | 0 | Denton | Denton | Tier 3 | 2012-02-09 | 2012-04-20 | N/A |  | Y | N
Old Project | Change in Service Date. Changed from 5/1/2015 to 5/1/2016 | 15TPIT0046 | Permian Basin - Culberson 138 kV line | Construct new line. | Project schedule changed to reflect time needed to obtain a Certificate of Convenience and Necessity | Permian Basin | Culberson | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8070-E | 2016-05-01 |  | 138 | 80 | 0 | 0 | 0 | WARD | CULBERSON | Tier 1 | 2013-02-01 | 2013-02-01 | N/A | 1010, 1097 | Y | N
New Project | New Project | 16TPIT0033 | Culberson - Mason 138 kV Line | Upgrade existing 138 kV line |  | Culberson | Mason | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8173-E | 2016-05-01 |  | 138 | 0 | 33 | 0 | 0 | CULBERSON | LOVING | Tier 3 |  |  |  | 1094 | Y | N
Old Project | No Change | 16TPIT0018 | Hicks Switch Autotransformer | Install 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5145-E | 2016-05-01 |  | 345 | 0 | 0 | 600 | 0 | TARRANT |  | Tier 4 |  |  |  | 2081 | Y | N
Old Project | No Change | 15TPIT0021 | PH Robinson-South Shore rebuild | Rebuild PH Robinson to South Shore 138 kV transmission line with 795 ACSS conductor. |  | PH Robinson | South Shore | Planned |  | TNMP | Tony Hudson, 281-581-4712, Anthony.Hudson@tnmp.com | STE08410 | 2016-05-30 |  | 138 | 0 | 5.6 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 38890, 42015 | Y | N
New Project | New Project | 16TPIT0034 | Coleto Creek - Tuleta: New 138 kV Line | Build a 138 kV circuit from Coleto Creek station to new Tuleta station. | NEW Corrected Assoc Parts Number Format | Coleto Creek | Tuleta | Planned | 606 - 0771 | AEP/TCC | Glen Reed 918-599-2664 | 3481 | 2016-05-31 |  | 138 | 56 | 0 | 0 | 0 | GOLIAD | BEE | Tier 1 | 2012-08-31 | 2012-12-27 |  |  | Y | N
Old Project | No Change | 07TPIT0060 | Howard Lane to Techridge Reconductor | The project re-conductors Circuit 1004 (Techridge to Howard Lane) using 795 ACSS Drake conductors to increase the capacity to 3000 Amp. |  | Howard Lane Substation | Techridge Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P067 PLAN_117_P194 | 2016-06-01 |  | 138 | 0 | 1.72 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9190, 9217 | Y | N
Old Project | No Change | 10TPIT0025 | Rinard Creek 138kV substation | Establish 138kV Rinard Ck substation with (2) 30MVA transformers and will cut into existing Ckt 987 (Lytton Springs to Slaughter Lane). |  | Rinard Creek substation | Rinard Creek Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P151 PLAN_117_P152 | 2016-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9262 | Y | N
Old Project | Change in Service Date. Changed from 6/1/2013 to 6/1/2016 | 13TPIT0187 | Harlandale to Sommers - 138 kV Transmission Line Rebuild | Rebuild approximately 40 circuit miles of 138 kV transmission from Harlandale to Sommers |  | Harlandale | Sommers | Conceptual | S-0732 | CPS | Blake Williams | T-0192 | 2016-06-01 |  | 138 | 0.1 | 40 | 0 | 0 | BEXAR | BEXAR | Tier 3 |  |  |  | 5190 5395 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 14TPIT0038 | Northland to Mag Plant Circuit 979 Upgrade | Reconductor the existing Northland to Mag Plant circuit from single 795SCAR to bundle 795 ACSR Drake and increase rating to 2000 Amp |  | Northland Substation | Mag Plant Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | NEW | 2016-06-01 |  | 138 | 0 | 4.11 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9128, 9238 | Y | N |  | Will add the project to the base case
Old Project | No Change | 15TPIT0004 | Converse - New 138kV Substation | Loop new 138kV substation into existing 138kV Deely to Skyline line |  | Converse | Deely/Skyline | Conceptual | T-0177 | CPS | Blake Williams | S-0601 | 2016-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5098 5110 5370 | Y | N |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 12/1/2015 to 6/1/2016 | 15TPIT0020 | Braunig to Highland Hills/Brooks - 138 kV Substation Equipment Upgrade | Replace Line and Bus Switches at Brooks and ensure a 1385 A rating and remove existing MLSE on the Braunig to Brooks 138 kV transmission line |  | Braunig_W | Highland Hills/Brooks | Conceptual | T-0194 | CPS | Blake Williams | S-0669 | 2016-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 3 |  |  |  | 5025 5045 5205 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 16TPIT0007 | McNeil to MagPlant Ckt 977 Upgrade | Reconductor existing McNeil to MagPlant circuit from 2000 to 3000 Amp. Relocate McNeil to Summit Circuit 907 and McNeil to MagPlant Circuit 977 to separate structures |  | McNeil Substation | Mag Plant Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | P396 | 2016-06-01 |  | 138 | 0 | 3.24 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9077, 9238 | Y | N |  | Will add the ptoject to the base case.
Old Project | No Change | 16TPIT0011 | JT Deely to Streich - 138 kV Substation Equipment Upgrade | Upgrade terminals at JT Deely and Streich Rd. to ensure a 2420 A rating and remove existing MLSE on JT Deely to Streich 138 kV transmission line |  | JT Deely | Streich Rd | Conceptual |  | CPS | Blake Williams | S-0674 | 2016-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5110 5417 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 16TPIT0012 | Encino to Skyline - 138 kV Substation Equipment Upgrade | Upgrade terminals at Encino and Skyline to ensure a 2420 A rating and remove existing MLSE on Encino to Skyline 138 kV transmission line |  | Encino | Skyline | Conceptual |  | CPS | Blake Williams | S-0671 | 2016-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5140 5369 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 08TPIT0033 | Gilleland to Techridge 138kV Circuit | Establish a new 138kV circuit from Gilleland to Techridge and maintain a normally close tie between AEN and LCRA's switchyard at Gilleland. |  | Gilleland Substation | Techridge Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_4276 PLAN_117_P207 | 2016-06-01 |  | 345 | 8 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 1 |  |  | 2004-12-01 | 9053, 9054 | Y | N
Old Project | No Change | 09TPIT0012 | Hill Country to Skyline - 345 kV 2nd Circuit | Build second 345 kV line from Hillcountry to Skyline. The second circuit will be installed on existing transmission structures |  | Hill Country | Skyline | Conceptual | S-0470 | CPS | Blake Williams | T-0052 | 2016-06-01 |  | 345 | 11 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5211 5371 | N | N |  | There are no transformers associated with this project
Old Project | No Change | 16TPIT0013 | Skyline to Spruce - 345 kV Substation Equipment Upgrade | Replace the Line MDS at Skyline and Spruce (both circuits) and ensure all terminals have a 2420 A rating and remove existing MLSE on Skyline to Spruce 345 kV transmission lines (both circuits) |  | Skyline | Spruce | Conceptual |  | CPS | Blake Williams | S-0468 | 2016-06-01 |  | 345 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5371 5400 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 15TPIT0000 | Bird Pond Substation | Install (3) Breaker ring to include (2) 138 lines and (1) 138/12.5 transformer |  | Bird Pond | Bird Pond | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2016-06-11 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 16TPIT0024 | Hamilton Road to Escondido: Rebuild 138kV Line | Rebuild Hamilton Road to Escondido 138 kV line | Reformated project number to match other numbers | Hamilton Road | Escondido | Conceptual | 602 - 0764 | AEP/TCC | Glen Reed 918-599-2664 | 3471 | 2016-06-14 |  | 138 | 0 | 53.7 | 0 | 0 | VAL VERDE | MAVERICK | Tier 3 |  |  |  | 8255, 8692, 8263, 8260 | Y | N |  | 0
Old Project | No Change | 16TPIT0029 | New 345kV Loma Alta Station | Construct a new 345 kV Loma Alta station with one 345/138kV 450 MVA auto with 345 kV line terminal | New | Loma Alta |  | Planned |  | SU | Bill Bojorquez 512-771-0965 BBojorquez@hunttransmission.com |  | 2016-06-16 |  | 345 | 0 | 0 | 450 | 0 | Cameron |  | Tier 1 | 2011-05-03 | 2011-12-19 | 2012-01-17 |  | Y | N
Old Project | No Change | 16TPIT0030 | New 345kV line from Loma Alta to N Edinburgh | Construct a new 345 kV transmission line from N.Edinburg to Loma Alta (~106.5 mi) and station upgrades | Change Contact info for ETT | Loma Alta | N Edinburgh | Planned |  | SU/ETT | Bill Bojorquez (SU) 512-771-0965 Glen Reed 918-599-2664 |  | 2016-06-16 |  | 345 | 106.5 | 0 | 0 | 0 | Cameron | Hidalgo | Tier 1 | 2011-05-03 | 2011-12-19 | 2012-01-17 |  | Y | N |  | RPG approved $274.7MM for the entire project with $256.2MM allocated for this piece as follows: $235MM - Line, $3.4MM - N Edinburh, $17.8MM - Loma Alta
Old Project | Change in Service Date. Changed from 6/14/2016 to 6/30/2016 | 16TPIT0026 | Lon Hill to Smith: Rebuild 69kV line | Rebuild Lon Hill - Smith 69kV Line | Reformated project number to match other numbers, changed date | Lon Hill | Smith | Conceptual | 583 - 0739 | AEP/TCC | Glen Reed 918-599-2664 | 3462 | 2016-06-30 |  | 69 | 0 | 3.1 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8448, 8866 | Y | N |  | 0
Old Project | No Change | 11TPIT0084 | Hidden Lakes - New Substation | Build a new 138-12.47 kV substation to accommodate new subdivision growth along the FM 517 and FM 646 corridors in Dickinson, Texas |  | Leave blank | Leave blank | Planned |  | TNMP | Tony Hudson, 281-581-4712, Anthony.Hudson@tnmp.com | STE02411 | 2016-06-30 |  | 138 | 0 | 0 | 0 | 0 | GALVESTON |  | Tier 4 |  |  |  | 38900 | Y | N
Old Project | No Change | 16TPIT0006 | Climax to Longneck - Rebuild and conversion from 69 kV to 138 kV | Rebuild Climax to Longneck 69 kV transmission line and convert to 138 kV. |  | Climax | Longneck | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE07214 | 2016-06-30 |  | 138 | 7.5 | 4.2 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 37250, 37260 | Y | N
Old Project | No Change | 11TPIT0002 | Lobo to North Edinburg: Construct 345 kV line | Construct 345 kV series compensated line from Lobo to Rio Bravo to Del Sol to North Edinburg | Changed Contact | Lobo | North Edinburg | Planned | 065 - 0273 | AEP/ETT | Rich Haley 918-599-2664 | 3421 | 2016-06-30 |  | 345 | 163 | 0 | 0 | 0 | WEBB | HIDALGO | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-20 | 80219, 80220, 80355, 8383 | Y | N
Old Project | No Change | 16TPIT0000 | Del Sol : Add a 24 Ohm, 3600 A Series Capacitor | Construct 345 kV series compensated line from Lobo to Rio Bravo to Del Sol to North Edinburg | Changed Contact | Del Sol |  | Planned | 065 - 0273 | AEP/ETT | Rich Haley 918-599-2664 | 629 | 2016-06-30 |  | 345 | 0 | 0 | 0 | +368.5 | HIDALGO |  | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-20 | 80355 | Y | N
Old Project | No Change | 16TPIT0017 | Cenizo: Add a 24 Ohm, 3600 A Series Capacitor | Construct 345 kV series compensated line from Lobo to Cenizo to Del Sol to North Edinburg | Changed Contact | Cenizo |  | Planned | 065 - 0273 | AEP/ETT | Rich Haley 918-599-2664 | 630 | 2016-06-30 |  | 345 | 0 | 0 | 0 | +368.5 | WEBB |  | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 80220 | Y | N
Old Project | Change in Service Date. Changed from 10/30/2019 to 10/28/2016 | 12TPIT0007 | FM-725 - New Substation | Build a new 138-26.18 kV, 40 MVA substation on the GVEC McQueeney(7606) - Schumansville(7609) 138 kV transmission line |  | FM 725 | McQueeney/Schumansville | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2016-10-28 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 07TPIT0140 | Trinidad - Tri Corner - Watermill 345 kV line | Upgrade existing 345 kV line |  | Trinidad | Watermill | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4045-E | 2016-11-01 |  | 345 | 0 | 52 | 0 | 0 | HENDERSON | DALLAS | Tier 3 |  |  |  | 2427, 3123 | Y | N
Old Project | No Change | 16TPIT0028 | Denton North Interchange to North Lakes Substation 69kV Transmission Line Recconstruction and Reconductor | Reconductor approximately 1.25 miles and reconstructu approximately 0.75 miles of existing 69kV transmission line to increase capacity. | On schedule | Denton North Interchange PSS/E Bus 912 | Noth Lakes Substation PSS/E Bus 915 | Planned | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602947 | 2016-12-01 |  | 69 | 0 | 2.25 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 912, 915 | Y | N
Old Project | No Change | 16TPIT0009 | Five Points to Westside - 138 kV Transmission Line Rebuild | Rebuild 3.8 miles of 138 kV transmission line from Five Points to Westside and ensure a minimum conductor rating of 331 MVA |  | Five Points | Westside | Conceptual |  | CPS | Blake Williams | T-0195 | 2016-12-01 |  | 138 | 0 | 3.8 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5150 5490 | Y | N |  | There are no transformers associated with this project
New Project | New Project | 16TPIT0035 | Rebuild BEC Munday to Gillespie 69 kV line with 795 ACSR | Rebuild BEC Munday to Gillespie 69 kV line with 795 ACSR | NEW | BEC Munday | Gillespie | Conceptual | 568 - 0742 | AEP/TNC | Glen Reed 918-599-2664 | 2578 | 2016-12-31 |  | 69 | 0 | 7.5 | 0 | 0 | KNOX | KNOX | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 16TPIT0032 | Ringtail to Yucca: Build 138 kV line | Build new 138 kV line from Ringtail to Yucca with 795 ACSS | Description & Associated Projects Update | Ringtail | Yucca | Planned | 585 - 0738 | AEP/TNC | Glen Reed 918-599-2664 | 2577 | 2016-12-31 |  | 138 | 13 | 0 | 0 | 0 | CROCKETT |  | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 12/1/2014 to 1/1/2017 | 13TPIT0106 | Killeen SS to Ding Dong | Rebuild 477 ACSR line with 955 ACSS |  | Killeen SS | Ding Dong | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11037 | 2017-01-01 |  | 138 | 0 | 23.8 | 0.0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3423, 136, 117, 115 | Y | N
Old Project | No Change | 14TPIT0022 | Sand Dollar 345 kV: Construct GIS 4 Breaker Ring Bus | Construct new Sand Dollar 345 kV station for direct interconnections with Las Brisas Energy Center. Construct 345 kV lines connecting Sand Dollar to existing Lon Hill and new Napalito 345 kV stations. |  | Sand Dollar |  | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2664 | 3388 | 2017-01-31 |  | 345 | 0 | 0 | 0 | 0 | NUECES |  | Tier 3 |  |  |  |  | Y | N |  | 0
Old Project | No Change | 14TPIT0024 | Lon Hill to Sand Dollar 345 kV: Construct New 345 kV Transmission Line | Construct new Sand Dollar 345 kV station for direct interconnections with Las Brisas Energy Center. Construct 345 kV lines connecting Sand Dollar to existing Lon Hill and new Napalito 345 kV stations. |  | Lon Hill | Sand Dollar | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2664 | 3389 | 2017-01-31 |  | 345 | 11.5 | 0 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y | N |  | 0
Old Project | No Change | 14TPIT0026 | Sand Dollar to Las Brisas Energy Center #1 345 kV: Construct New 345 kV Transmission Line | Construct new Sand Dollar 345 kV station for direct interconnections with Las Brisas Energy Center. Construct 345 kV lines connecting Sand Dollar to existing Lon Hill and new Napalito 345 kV stations. |  | Sand Dollar | Las Brisas | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2664 | 3392 | 2017-01-31 |  | 345 | 2 | 0 | 0 | 0 | NUECES | NUECES | Tier 2 |  |  |  |  | Y | N |  | Backfeed 13 months prior to commercial operation date
New Project | New Project | 17TPIT0008 | Marion to Cibolo T-Line (T-302) Circuit Addition | Add another 138 kV circuit, to existing Marion to Cibolo T-Line (T-302), 1192 ACSR, 4.81 miles |  | Marion | Cibolo | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2017-04-30 |  | 138 | 0 | 4.81 | 0 | 0 | GUADALUPE | GUADALUPE | Tier 4 |  |  |  | See Project Title | N | N
Old Project | Change in Service Date. Changed from 5/15/2020 to 5/26/2017 | 20TPIT0000 | Parkway Substation | Replace T1, 20 MVA with a 40 MVA 138-13.09 kV transformer |  | Parkway |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2017-05-26 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 11TPIT0008 | Rainey St 138kV substation | Establish a new 138kV Rainey St substation with (2) 50MVA transformers and cut into existing Ckt 1015 (Pedernales to Seaholm). |  | Rainey St Substation | Rainey St Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P158 PLAN_117_P166 PLAN_117_P167 | 2017-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9261 | Y | N
Old Project | Change in Service Date. Changed from 6/1/2015 to 6/1/2017 | 15TPIT0031 | Brooks to Chavaneaux - 138 kV Transmission Line Rebuild | Rebuild approximately four circuit miles of 138 kV transmission from Brooks to Chavaneaux |  | Brooks | Chavaneaux | Conceptual | S-0733 | CPS | Blake Williams | T-0207 | 2017-06-01 |  | 138 | 0.1 | 4 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5045 5085 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 16TPIT0010 | Bulverde - New 138kV Substation | Loop new 138kV substation into the existing Hill Country to Stonegate transmission line |  | Hill Country | Bulverde/Stonegate | Conceptual | T-0189 | CPS | Blake Williams | S-0665 | 2017-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5210 5051 5415 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 17TPIT0003 | Breaker Replacement Program | Replace 36 aging and underrated circuit breakers and associated disconnect switches at both 345kV and 138kV |  | Gibbons Creek, Ben Davis, Spencer Steam, West Denton, North Denton, Dansby, Bryan East | Gibbons Creek, Ben Davis, Spencer Steam, West Denton, North Denton, Dansby, Bryan East | Under Construction |  | TMPA | Tom Chambers 936-873-1125 tchambers@texasmpa.org | T13001 | 2017-09-02 |  | 345 | 0 | 0 | 0.0 | 0 | Grimes, Denton, Hunt, Dallas |  | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 17TPIT0006 | System Relay and SCADA Upgrades | Modernize relay and SCADA designs and replace existing legacy equipment based on new TMPA standards |  | N/A | N/A | Planned |  | TMPA | Tom Chambers 936-873-1125 tchambers@texasmpa.org | T13002 | 2017-09-30 |  | 345 | 0 | 0 | 0 | 0 | Grimes, Brazos, Denton, Hunt, Dallas |  | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 14TPIT0041 | Coliseum to Kirby - 138 kV Transmission Line Rebuild | Rebuild 4.2 miles of 138 kV transmission line from Coliseum to Holbrook to Kirby and ensure a minimum conductor rating of 331 MVA |  | Colesium | Kirby | Conceptual |  | CPS | Blake Williams | T-0164 | 2017-12-01 |  | 138 | 0 | 4.2 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5095 5218 5250 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 17TPIT0001 | 36th St to Merida - 138 kV Transmission Line Rebuild | Rebuild approximately four circuit miles of 138 kV transmission from 36th Street to Merida |  | 36th Street | Merida | Conceptual |  | CPS | Blake Williams | T-0196 | 2017-12-01 |  | 138 | 0 | 4 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5427 5310 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 17TPIT0002 | Hunt Lane to Pinn Road - 138 kV Transmission Line Rebuild | Rebuild approximately eight circuit miles of 138 kV transmission from Hunt Lane to Pinn Road |  | Hunt Lane | Pinn Rd | Conceptual |  | CPS | Blake Williams | T-0190 | 2017-12-01 |  | 138 | 0 | 8 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5234 5345 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 17TPIT0004 | Frisco to Krugerville Second Circuit | Add second circuit from Frisco to Krugerville |  | Frisco | Krugerville | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 12042 | 2017-12-01 |  | 138 | 12 | 0 | 0 | 0 | COLLIN | DENTON | Tier 4 |  |  |  | 649, 662, 1993, 1994, 2370 | Y | N
Old Project | No Change | 17TPIT0005 | St. Jo Autos | Replace 40 MVA autos with 60 MVA autos |  | St. Jo | St. Jo | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 12005 | 2017-12-01 |  | 138 | 0 | 0 | 40 | 0 | COOKE |  | Tier 4 |  |  |  | 746, 750 | Y | N
New Project | New Project | 17TPIT0007 | Rebuild Gillespie to Pointer 69 kV line with 795 ACSR | Rebuild Gillespie to Pointer 69 kV line with 795 ACSR | NEW | Gillespie | Pointer | Conceptual | 568 - 0742 | AEP/TNC | Glen Reed 918-599-2664 | 2579 | 2017-12-31 |  | 69 | 0 | 4.6 | 0 | 0 | KNOX | KNOX | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 14TPIT0023 | Nopalito 345 kV: Construct 5 Breaker Ring Bus | Construct new Sand Dollar 345 kV station for direct interconnections with Las Brisas Energy Center. Construct 345 kV lines connecting Sand Dollar to existing Lon Hill and new Napalito 345 kV stations. |  | Napalito |  | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2664 | 3390 | 2018-01-31 |  | 345 | 0 | 0 | 0 | 0 | SAN PATRICIO |  | Tier 3 |  |  |  |  | Y | N |  | 0
Old Project | No Change | 14TPIT0025 | Nopalito to Sand Dollar 345 kV: Construct New 345 kV Transmission Line | Construct new Sand Dollar 345 kV station for direct interconnections with Las Brisas Energy Center. Construct 345 kV lines connecting Sand Dollar to existing Lon Hill and new Napalito 345 kV stations. |  | Nopalito | Sand Dollar | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2664 | 3391 | 2018-01-31 |  | 345 | 14.5 | 0 | 0 | 0 | NUECES | SAN PATRICIO | Tier 2 |  |  |  |  | Y | N |  | 0
Old Project | No Change | 15TPIT0003 | Sand Dollar to Las Brisas Energy Center #2 345 kV: Construct New 345 kV Transmission Line | Construct new Sand Dollar 345 kV station for direct interconnections with Las Brisas Energy Center. Construct 345 kV lines connecting Sand Dollar to existing Lon Hill and new Napalito 345 kV stations. |  | Sand Dollar | Las Brisas | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2664 | 3393 | 2018-01-31 |  | 345 | 2 | 0 | 0 | 0 | NUECES | NUECES | Tier 2 |  |  |  |  | Y | N |  | Backfeed 13 months prior to commercial operation date
Old Project | No Change | 14TPIT0012 | Mountain Creek - Norwood 138 kV line | Upgrade existing line |  | Mountain Creek | Norwood | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4074-E | 2018-05-01 |  | 138 | 0 | 7.2 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2412, 2804, 2805, 2407 | Y | N
Old Project | Change in Service Date. Changed from 5/15/2022 to 5/15/2018 | 22TPIT0000 | Parkway Substation | Replace T2, 20 MVA with a 40 MVA 138-13.09 kV transformer |  | Parkway |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2018-05-15 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 11TPIT0011 | Northeast 138kV Substation | Establish a 138kV substation with (2) 30MVA transformers and 4 distribution circuits with underground get-a-ways. The station will cut into existing Gilleland - Techridge line. | Original Project title is "East Substation" | Northeast Substation | Northeast Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P142 PLAN_117_P143 PLAN_117_P144 | 2018-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9195 | Y | N
Old Project | No Change | 12TPIT0009 | Masterson Rd - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to Valley Rd line. |  | Masterson Rd. | Cagnon/Valley | Planned | T-0910 | CPS | Blake Williams | S-0538 | 2018-06-01 |  | 138 | 20 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 2 |  |  |  | 5296 5465 5053 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 15TPIT0022 | Dobbin to Sota | Build 23 miles of 138 kV transmission line with 959 ACSS |  | Dobbin | Highway 6 | planned | 13TPIT0107 15TPIT0022 16TPIT0016 | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11047 | 2018-06-01 |  | 138 | 23 | 0 | 0 | 0 | MONTGOMERY | BRAZOS | Tier 1 | 2010-10-04 | 2010-12-20 | 2011-05-05 | 3, 5, 6 | Y | N
Old Project | No Change | 18TPIT0002 | Martinez - New 138kV Substation | Loop new 138kV substation into the existing 138kV Deely to Walzem line and the future 138kV Deely to Converse line |  | Deely | Walzem Converse | Conceptual |  | CPS | Blake Williams |  | 2018-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5110 5294 5485 5098 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 13TPIT0107 | Dobbin switching station | Construct 345/138 kV switching station in CNP's Roans Prairie to Kuykendahl line |  | Dobbin | Dobbin | planned | 13TPIT0107 15TPIT0022 16TPIT0016 | BRAZOS-CNP | Brion Ryan, 254-750-6353, Wayne E. Kemper 713 207 2192 | 11045 | 2018-06-01 |  | 345 | 0 | 0 | 700 | 0 | MONTGOMERY |  | Tier 1 | 2010-10-04 | 2010-12-20 | 2011-05-05 | 40630, 3 | Y | Y
Old Project | No Change | 16TPIT0016 | Dobbin to Fish Creek | Build 15.5 miles of 138 kV transmission line with 959 ACSS |  | Dobbin | Fish Creek | planned | 13TPIT0107 15TPIT0022 16TPIT0016 | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11046 | 2018-06-02 |  | 138 | 15.5 | 0 | 0 | 0 | MONTGOMERY | MONTGOMERY | Tier 1 | 2010-10-04 | 2010-12-20 | 2011-05-05 | 3, 22, 23, 24 | Y | N
Old Project | Change in Service Date. Changed from 3/1/2018 to 9/1/2018 | 13TPIT0045 | Blumenthal | Construct a new 8.4-mile 138 kV transmission line from a tap point on the Kendall CTEC (7147) - Mountain Top (7148)138 kV transmission line to the new Blumenthal substation (7418). | Delayed from initial May 2013 in-service date | Blumenthal | Kendall CTEC/Mountain Top | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2018-09-01 |  | 138 | 8.4 | 0 | 0 | 0 | KENDALL |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | Change in Service Date. Changed from 3/30/2018 to 3/30/2019 | 06TPIT0068 | Hamilton Road to Picacho, reconductor 138 kV line | Reconductor Del Rio 138 kV System | Changed Inservice date | Hamilton Road | Picacho | Conceptual | 301 - 0449 | AEP/TCC | Glen Reed 918-599-2664 | 1544 | 2019-03-30 |  | 138 | 0 | 8.67 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2017 to 3/31/2019 | 08TPIT0132 | Melon Creek to Tatton: Build 69 KV Line | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. | Date Change | Melon Creek | Tatton | Conceptual | 100 - 0100 | AEP/TCC | Glen Reed 918-599-2664 | 2028 | 2019-03-31 |  | 69 | 9 | 0 | 0 | 0 | REFUGIO | ARANSAS | Tier 2 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2016 to 3/31/2019 | 08TPIT0131 | Melon Creek: Install 138/69 KV Auto | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. | Date Change | Melon Creek |  | Conceptual | 100 - 0100 | AEP/TCC | Glen Reed 918-599-2664 | 2021 | 2019-03-31 |  | 138 | 0 | 0 | 50 | 0 | REFUGIO |  | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 4/30/2018 to 4/30/2019 | 06TPIT0084 | Hamilton Road to Del Rio reconductor 138 kV line | Reconductor Del Rio 138 kV System | Changed Inservice date | Hamilton Road | Del Rio | Conceptual | 301 - 0449 | AEP/TCC | Glen Reed 918-599-2664 | 1545 | 2019-04-30 |  | 138 | 0 | 3 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
Old Project | No Change | 14TPIT0008 | Holt - Emma 69 Tap kV line | Upgrade existing line |  | Holt | Emma | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8006-E | 2019-05-01 |  | 69 | 0 | 6.2 | 0 | 0 | ECTOR | ANDREWS | Tier 4 |  |  |  | 1262, 1142 | N | N | 2009-R5
Old Project | No Change | 14TPIT0000 | CSU Graham Rd Substation | Install (3) Breaker ring to include (2) 138 lines and tap to College Station Utilities |  | CSU Graham Rd | CSU Graham Rd | planned |  | BTU/CSU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2019-05-06 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 5/30/2018 to 5/30/2019 | 06TPIT0083 | Del Rio to Buena Vista, reconductor 138 kV line | Reconductor Del Rio 138 kV System | Changed Inservice date | Del Rio | Buena Vista | Conceptual | 301 - 0449 | AEP/TCC | Glen Reed 918-599-2664 | 1546 | 2019-05-30 |  | 138 | 0 | 3 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
Old Project | No Change | 18TPIT0003 | Carrizo Crossing Station | Construct a 69 kV substation at the crossing of the AEP Carrizo – Crystal City 69 kV line and STEC Brundage – Carrizo Springs 69 kV line |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2019-06-01 |  | 69 | 0 | 0 | 0 | 0 | DIMMIT |  | Tier 1 | 2012-04-16 | 2012-08-30 | 2012-09-18 | 8245 | Y | N
Old Project | No Change | 19TPIT0000 | Weser substation | Replace 5.6 MVA with 69-13.09 kV, 20 MVA transformer |  | Weser |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2019-06-15 |  | 69 | 0 | 0 | 0 | 0 | GOLIAD |  | Tier 4 |  |  |  | See Project Title | Y | N
Old Project | Change in Service Date. Changed from 3/31/2017 to 6/30/2019 | 07TPIT0252 | Greta: Install 1-7.2 MVAR 69 kV Cap Bank | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. | Date Change | Greta |  | Conceptual | 100 - 0100 | AEP/TCC | Glen Reed 918-599-2664 | 2045 | 2019-06-30 |  | 69 | 0 | 0 | 0 | 7.2 | REFUGIO |  | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 6/30/2018 to 6/30/2019 | 06TPIT0082 | Buena Vista to Picacho, reconductor 138 kV line | Reconductor Del Rio 138 kV System | Changed Inservice date | Buena Vista | Picacho | Conceptual | 301 - 0449 | AEP/TCC | Glen Reed 918-599-2664 | 1547 | 2019-06-30 |  | 138 | 0 | 3 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
Old Project | Change in Service Date. Changed from 6/30/2018 to 6/30/2019 | 07TPIT0083 | Picacho to CFE, construct new 138 kV line | Convert Amistad to CFE Amistad 12.5 kV distribution to 138 kV line | Changed Inservice date | Picacho | CFE | Conceptual | 301 - 0449 | AEP/ETT | Glen Reed 918-599-2664 | 1548 | 2019-06-30 |  | 138 | 8.8 | 0 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | Y
Old Project | No Change | 07TPIT0012 | Trinity Switch - Richland 138 kV line | Upgrade existing 138 kV line |  | Trinity Switch | Richland | Conceptual | M5014-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5069-E | 2019-12-01 |  | 138 | 0 | 0.5 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2096, 2100 | N | N
Old Project | No Change | 08TPIT0007 | Austin Ranch - Hebron 138 kV line | Upgrade existing 138 kV line |  | Austin Ranch | Hebron | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3002-E | 2019-12-01 |  | 138 | 0 | 0.7 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  | 2376, 2377 | N | N
Old Project | No Change | 07TPIT0001 | Liggett - Trinity Switch 345 kV line | Construct Liggett - Trinity 345 kV line |  | Liggett | Trinity Switch | Conceptual | M5014-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5015-E | 2019-12-01 |  | 345 | 12.8 | 0 | 0 | 0 | DALLAS | TARRANT | Tier 2 |  |  |  | 2095, 2097 | N | N
Old Project | No Change | 07TPIT0002 | Trinity Switch 345/138 kV autotransformer | Create Trinity Switch and install a 600 MVA 345/138 kV autotransformer |  |  |  | Conceptual | M5015-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5014-E | 2019-12-01 |  | 345 | 0 | 0 | 600 | 0 | TARRANT |  | Tier 4 |  |  |  | 2096, 2097 | N | N
Old Project | Change in Service Date. Changed from 12/1/2017 to 12/31/2019 | 12TPIT0025 | Refugio - Tatton: Rebuild Irreparable 69 kV Line | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. | Date Change | Refugio | Tatton | Conceptual | 100 - 0100 | AEP/TCC | Glen Reed 918-599-2664 | 2027 | 2019-12-31 |  | 69 | 0 | 12.6 | 0 | 0 | REFUGIO | ARANSAS | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 5/1/2018 to 12/31/2019 | 10TPIT0027 | West Batesville, Install 138 kV ring bus | West Batesville: Construct bundled 2x795 ACSR 138 kV line, add 138 kV circuit breaker and convert to 4 breaker ring bus | Changed Inservice date | West Batesville |  | Conceptual | 383 - 0560 | AEP/ETT | Glen Reed 918-599-2664 | 2168 | 2019-12-31 |  | 138 | 0 | 0 | 0 | 0 | ZAVALA |  | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | N | N
Old Project | Change in Service Date. Changed from 5/1/2018 to 12/31/2019 | 10TPIT0028 | Escondido to West Batesville, build 138 kV Line | West Batesville: Construct bundled 2x795 ACSR 138 kV line, add 138 kV circuit breaker and convert to 4 breaker ring bus | Changed Inservice date | Escondido | West Batesville | Conceptual | 383 - 0560 | AEP/ETT | Glen Reed 918-599-2664 | 2169 | 2019-12-31 |  | 138 | 46.2 | 0 | 0 | 0 | MAVERICK | ZAVALA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | N | Y
Old Project | No Change | 09TPIT0024 | Electra - KMA Tap 69 kV line | Upgrade existing 69 kV line |  | Electra | KMA Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R185-E | 2020-05-01 |  | 69 | 0 | 9.9 | 0 | 0 | WICHITA | WICHITA | Tier 4 |  |  |  | 1538, 1536 | N | N
Old Project | No Change | 09TPIT0116 | Gatesville Tap - Gatesville TDC 69 kV line | Upgrade existing 69 kV line |  | Gatesville Tap | Gatesville TDC | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R497-WA | 2020-05-01 |  | 69 | 0 | 4.4 | 0 | 0 | MCLENNAN | CORYELL | Tier 4 |  |  |  | 3587, 3583 | N | N
Old Project | No Change | 11TPIT0014 | Muenster - St. Jo (BEC) 69 kV line | Upgrade existing 69 kV line |  | Muenster | St. Jo | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R186B-E | 2020-05-01 |  | 69 | 0 | 7.8 | 0 | 0 | COOKE | COOKE | Tier 4 |  |  |  | 1712, 1716 | N | N
Old Project | No Change | 14TPIT0009 | Odessa North - North Cowden 69 kV line | Upgrade existing line |  | Odessa North | North Cowden | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8008-E | 2020-05-01 |  | 69 | 0 | 12.4 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1259, 1123 | N | N | 2009-R4
Old Project | No Change | 06TPIT0047 | Elkton - Tyler West 138 kV line | Upgrade existing 138 kV line |  | Elkton | Tyler | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R323-E | 2020-05-01 |  | 138 | 0 | 4.98 | 0 | 0 | SMITH | SMITH | Tier 4 |  |  |  | 3106, 3139 | N | N
Old Project | No Change | 06TPIT0143 | Temple Switch - Temple SE 138 kV line | Upgrade existing 138 kV line |  | Temple Switch | Temple SE | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R448-E | 2020-05-01 |  | 138 | 0 | 4.4 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3415, 3612, 3602, 3611 | N | N
Old Project | No Change | 07TPIT0014 | Plano West - Richardson Tap 138 kV line | Upgrade existing 138 kV line |  | Plano West | Richardson Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M364-E | 2020-05-01 |  | 138 | 0 | 1.9 | 0 | 0 | COLLIN | DALLAS | Tier 4 |  |  |  | 2673, 2685 | N | N
Old Project | No Change | 09TPIT0047 | N. Waco - NE. Waco 138 kV line | Upgrade existing 138 kV line |  | N. Waco | NE. Waco | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R477-E | 2020-05-01 |  | 138 | 0 | 1.9 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3551, 3552 | N | N
Old Project | No Change | 09TPIT0118 | Fisher Road - Wichita Falls 138 kV line | Upgrade existing 138 kV line. |  | Fisher Road | Wichita Falls | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R191-E | 2020-05-01 |  | 138 | 0 | 1.45 | 0 | 0 | WICHITA | WICHITA | Tier 4 |  |  |  | 1427, 1448 | N | N
Old Project | No Change | 09TPIT0122 | Shamburger - Tyler NW 138 kV line | Upgrade existing 138 kV line |  | Shamburger | Tyler NW | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6001-E | 2020-05-01 |  | 138 | 0 | 6.3 | 0 | 0 | SMITH | SMITH | Tier 4 |  |  |  | 3104, 3141 | N | N | 2009-E6
Old Project | No Change | 10TPIT0019 | Everman - Cleburne Switch 138 kV line sections | Upgrade existing 138 kV line |  | Everman | Cleburne Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3034-E | 2020-05-01 |  | 138 | 0 | 8.5 | 0 | 0 | TARRANT | JOHNSON | Tier 4 |  |  |  | 2279, 2210, 2209, 2208, 1883 | N | N
Old Project | No Change | 10TPIT0053 | Kaufman South 138 kV capacitors | Install 138 kV capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3064-E | 2020-05-01 |  | 138 | 0 | 0 | 0 | 55.2 | KAUFMAN |  | Tier 4 |  |  |  | 2728 | N | N
Old Project | No Change | 10TPIT0054 | Royse 138/69 kV autotransformer | Install larger autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3065-E | 2020-05-01 |  | 138 | 0 | 0 | 120 | 0 | ROCKWALL |  | Tier 4 |  |  |  | 2462, 2463 | N | N
Old Project | No Change | 10TPIT0091 | Elm Mott - Waco Northcrest 138 kV line upgrade | Upgrade existing 138 kV line |  | Elm Mott | Waco Northcrest | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R714-E | 2020-05-01 |  | 138 | 0 | 3.6 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3407, 3575 | N | N
Old Project | No Change | 11TPIT0033 | Saginaw - American MFG Tap 138 kV line | Upgrade existing 138 kV line |  | Saginaw | American MFG Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5070-E | 2020-05-01 |  | 138 | 0 | 1.37 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2146, 1957 | N | N
Old Project | No Change | 13TPIT0059 | Cedar Crest - Industrial 138 kV line | Upgrade existing line |  | Cedar Crest | Industrial | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4072-E | 2020-05-01 |  | 138 | 0 | 3.2 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2494, 2981, 2976 | N | N | 2009-R23
Old Project | No Change | 13TPIT0061 | Terrell Switch - North Terrell Tap 138 kV line | Upgrade existing line |  | Terrell Switch | North Terrell Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M363-E | 2020-05-01 |  | 138 | 0 | 7.9 | 0 | 0 | KAUFMAN | KAUFMAN | Tier 4 |  |  |  | 2718, 2715, 2721 | Y | N
Old Project | No Change | 13TPIT0112 | North Andrews | Install 138 kV capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8015-E | 2020-05-01 |  | 138 | 0 | 0 | 0 | 36.8 | ANDREWS |  | Tier 4 |  |  |  | 1159 | N | N
Old Project | No Change | 14TPIT0011 | Midland East - Windwood 138 kV line | Upgrade existing line |  | Midland East | Windwood | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8009-E | 2020-05-01 |  | 138 | 0 | 1.7 | 0 | 0 | MIDLAND | MIDLAND | Tier 4 |  |  |  | 1023, 1116 | N | N
Old Project | No Change | 14TPIT0014 | NW Carrollton - Lakepointe (TNMP) 138 kV line (Oncor Electric Delivery's section) | Upgrade existing line |  | NW Carrollton | Lakepointe (TNMP) | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5156-E | 2020-05-01 |  | 138 | 0 | 2.1 | 0 | 0 | DALLAS | DENTON | Tier 4 |  |  |  | 2362, 37010 | N | N
Old Project | No Change | 14TPIT0056 | Northaven - Welch 138 kV line | Upgrade existing line |  | Northaven | Welch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4088-E | 2020-05-01 |  | 138 | 0 | 6 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2657, 2658, 2660, 2661 | N | N
Old Project | No Change | 07TPIT0073 | Venus - Webb 345 kV line | Upgrade existing 345 kV line |  | Venus | Webb | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5098-E | 2020-05-01 |  | 345 | 0 | 11.3 | 0 | 0 | ELLIS | DALLAS | Tier 4 |  |  |  | 1906, 1904 | N | N
Old Project | No Change | 13TPIT0104 | Jack County Auto | Install 345/138 kV, 700 MVA auto at Jack County |  | Jack County | Jack County | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11038 | 2020-06-01 |  | 345 | 0 | 0 | 700 | 0 | JACK |  | Tier 4 |  |  |  | 575, 579 | Y | N
Old Project | No Change | 14TPIT0033 | Muenster to Red River | Add 60 MVA 138/69 kV auto at Munester. Build 11 miles of 795 ACSR line to Red River. |  | Muenster | Red River | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 09033 | 2020-12-01 |  | 69 | 11 | 0 | 60 | 0 | COOKE | COOKE | Tier 2 |  |  |  | 694, 694, 735 | Y | N
Old Project | Change in Service Date. Changed from 12/30/2018 to 12/30/2020 | 15TPIT0008 | Triple R - New Substation | Build a 138-26.18 kV, 40 MVA substation on the GVEC Wilson - Sutherland Springs (T549) 138 kV transmission line |  | Triple R | Wilson/Sutherland Springs | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2020-12-30 |  | 138 | 0 | 0 | 0 | 0 | WILSON |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 08TPIT0097 | Rhome to Roanoke Rebuild | Rebuild existing Rhome to Roanoke |  | Rhome | Roanoke | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 06062 | 2020-12-31 |  | 138 | 0 | 16.6 | 0.0 | 0 | WISE | DENTON | Tier 4 |  |  |  | 602-640 640-1866-1852 | Y | N |  | 602-640 completed 4/19/2012 640-1852-1866 completed 12/31/2012
Old Project | Change in Service Date. Changed from 12/31/2019 to 12/31/2020 | 11TPIT0036 | Caddo - New Substation | Construct a new 69-13.09x26.18-KV, 10 MVA substation |  | Caddo | La Vernia/GVEC Nixon | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2020-12-31 |  | 138 | 0 | 0 | 0 | 0 | WILSON |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | Change in Service Date. Changed from 12/1/2019 to 1/1/2021 | 13TPIT0133 | Devine Switch breaker addition | Adds breakers to Devine Switch to allow closing of normally open Devine Switch to Devine. Creates 3- terminal switching station |  |  |  | Conceptual |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2021-01-01 |  | 69 | 0 | 0 | 0.0 | 0 | Medina |  | Tier 4 |  |  |  | 5857 | Y | N
Old Project | Change in Service Date. Changed from 6/30/2019 to 1/1/2021 | 13TPIT0131 | Oaks to Fashing Rebuild | Rebuild 4/0 ACSR 69 kV to 795 ACSR double circuit 138 kV structures with one side operated at 69 kV. |  | Oaks | Fashing | Conceptual |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2021-01-01 |  | 138 | 38 | 38 | 0 | 0 | ATASCOSA | ATASCOSA | Tier 3 |  |  |  | 5716, 5714, 5710, 5712, 5713 | N | N
Old Project | Change in Service Date. Changed from 2/1/2019 to 2/1/2021 | 13TPIT0125 | CR343 138 kV Substation | Build new load serving station in the 138 kV line between Cross and Hindes. |  |  |  | Conceptual |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2021-02-01 |  | 138 | 0 | 0 | 0.0 | 0 | ATASCOSA |  | Tier 4 |  |  |  | 5897 | N | N
Old Project | Change in Service Date. Changed from 3/1/2019 to 3/1/2021 | 12TPIT0141 | Dinero 138 kV Substation | Build new load serving station in the 138 kV line from Orange Grove to AEP's George West. |  |  |  | Conceptual |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2021-03-01 |  | 138 | 0.5 | 0 | 0.0 | 0 | LIVE OAK |  | Tier 4 |  |  |  | 5670 | Y | N
Old Project | No Change | 10TPIT0009 | Trinity Switch - Hurst 138 kV line | Upgrade existing 138 kV line |  | Trinity Switch | Hurst | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5040-E | 2021-05-01 |  | 138 | 0 | 4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2096, 2115 | N | N
Old Project | No Change | 10TPIT0034 | Leon Switch #2 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R517-E | 2021-05-01 |  | 138 | 0 | 0 | 100 | 0 | EASTLAND |  | Tier 4 |  |  |  | 1624, 1626 | N | N
Old Project | No Change | 11TPIT0027 | East Richardson Switch - Ben Davis Switch (TMPA) 138 kV line | Create a new 138 kV line by reconfiguring existing lines |  | East Richardson Switch | Ben Davis Switch | Conceptual | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375D-E | 2021-05-01 |  | 138 | 0 | 0 | 0 | 0 | COLLIN | DALLAS | Tier 4 |  |  |  | 968, 2690 | N | N
Old Project | No Change | 11TPIT0028 | Allen Switch - West Plano Switch 138 kV line | Create a new 138 kV line by reconfiguring existing lines and adding circuit to existing structures |  | Allen Switch | West Plano Switch | Conceptual | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375C-E | 2021-05-01 |  | 138 | 3.5 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 2510, 2691, 2673 | N | N
Old Project | No Change | 12TPIT0019 | Pleasant Valley second 138/69 kV autotransformer | Install second 138/69 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R555-E | 2021-05-01 |  | 138 | 0 | 0 | 100 | 0 | WICHITA |  | Tier 4 |  |  |  | 1450, 1451 | N | N
Old Project | No Change | 14TPIT0029 | Lake Creek - Robinson 138 kV line | Rebuild 138 kV line |  | Lake Creek | Robinson | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R476 | 2021-05-01 |  | 138 | 0 | 8.3 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3410, 3567 | N | N | 2007-R8
Old Project | No Change | 00TPIT0004 | DeCordova - Benbrook 345 kV line upgrade | Upgrade existing 345 kV line |  | DeCordova | Benbrook | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5034-E | 2021-05-01 |  | 345 | 0 | 27 | 0 | 0 | HOOD | TARRANT | Tier 4 |  |  |  | 1873, 1890 | N | N
Old Project | No Change | 07TPIT0118 | Lavon 345/138 kV Switching Station | Construct 345/138 kV switching station |  |  |  | Conceptual | M375B, M375C | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375A-E | 2021-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  | Tier 4 |  |  |  | 2475, 2476 | N | N
Old Project | No Change | 08TPIT0071 | North Lake 345/138 kV autotransformer | Install a 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3020-E | 2021-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2334, 2333 | N | N
Old Project | No Change | 11TPIT0034 | Sargent Road 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M486-E | 2021-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2946, 2949 | N | N
Old Project | No Change | 11TPIT0097 | Norwood Switch autotransformer | Replace #1 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4070-E | 2021-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2405, 2406 | N | N
Old Project | No Change | 13TPIT0062 | Cedar Hill Switch second 345/138 kV autotransformer | Install autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4071-E | 2021-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2420, 2422, 2421 | N | N
Old Project | Change in Service Date. Changed from 12/1/2013 to 6/1/2021 | 13TPIT0126 | Hindes 138 kV Substation | Build new load serving station in the 138 kV line between Cross and Pearsall. |  |  |  | Conceptual |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2021-06-01 |  | 138 | 0 | 0 | 0.0 | 0 | FRIO |  | Tier 4 |  |  |  | 5899 | Y | N
Old Project | Change in Service Date. Changed from 6/30/2019 to 6/30/2021 | 11TPIT0037 | Santa Clara - New Substation | Build a new 138-26.18 kV 40 MVA substation on the GVEC McQueeney(7606)-Cibolo(7608) 138 kV transmission line |  | Santa Clara | McQueeney/Cibolo | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2021-06-30 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 06TPIT0092 | Wichita Falls Switch - Wichita Falls Basin 69 kV line | Upgrade existing 69 kV line |  | Wichita Falls Switch | Wichita Falls Basin | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R168A-E | 2022-05-01 |  | 69 | 0 | 1 | 0 | 0 | ARCHER | WICHITA | Tier 4 |  |  |  | 1449, 1508 | N | N
Old Project | No Change | 08TPIT0110 | Temple - Little River 69 kV line | Rebuild existing 69 kV line |  | Temple | Little River | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R097-E | 2022-05-01 |  | 69 | 0 | 7.4 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3645, 3644 | N | N
Old Project | No Change | 09TPIT0068 | W. Weatherford - Weatherford 69 kV line | Rebuild existing 69 kV line |  | W. Weatherford | Weatherford | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R515-E | 2022-05-01 |  | 69 | 0 | 7.5 | 0 | 0 | PARKER | PARKER | Tier 4 |  |  |  | 1586, 1585 | N | N
Old Project | No Change | 07TPIT0069 | Sterrett - Sardis 138 kV line | Upgrade existing 138 kV line |  | Sterrett | Sardis | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M361-E | 2022-05-01 |  | 138 | 0 | 1.95 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 2317, 203 | N | N
Old Project | No Change | 11TPIT0048 | Austin Ranch 138 kV capacitors | Install capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3074-E | 2022-05-01 |  | 138 | 0 | 0 | 0 | 55.2 | DENTON |  | Tier 4 |  |  |  | 2378, 2377 | N | N
Old Project | No Change | 14TPIT0010 | Handley - Pantego 138 kV line | Upgrade existing line |  | Handley | Pantego | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5155-E | 2022-05-01 |  | 138 | 0 | 3.8 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1950, 1951, 2247 | N | N
Old Project | Change in Service Date. Changed from 5/1/2020 to 5/1/2022 | 00TPITno07 | Loma Alta - Rio Hondo 345-kV line | Install 345-kV line from Loma Alta to Rio Hondo |  | Loma Alta Substation | Rio Hondo Substation | Conceptual |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2022-05-01 |  | 345 | 35 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 2 |  |  |  |  | N | N
Old Project | No Change | 07TPIT0234 | Collin Switch - NW. Carrollton 345 kV line | Upgrade existing 345 kV line |  | Collin Switch | NW. Carrollton | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3061-E | 2022-05-01 |  | 345 | 0 | 19.3 | 0 | 0 | COLLIN | DALLAS | Tier 4 | 2006-10-01 | 2007-02-01 | N/A | 2372, 2361 | N | N |  | The ERCOT Staff determined this project is not economically justified in their February 2007 study.
Old Project | No Change | 12TPIT0004 | Sulpher Springs - New 138kV Substation | Loop new 138kV substation into the existing 138kV OW Sommers to Kirby line |  | Sulpher Springs | OW Sommers/Kirby | Conceptual |  | CPS | Blake Williams | S-0385 | 2022-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5416 | Y | N |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 11/30/2020 to 11/30/2022 | 12TPIT0006 | Olmos(7613) - New Substation | Build a new 138-13.09 kV 20 MVA substation on the Olmos switching station site |  | Olmos | Olmps Switching Station | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2022-11-30 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | Y | N
Old Project | No Change | 12TPIT0078 | Southeast Nacogdoches - Lufkin Switch 345 kV line | Construct new 345 kV line, add second circuit to existing structures and add 345 kV circuit breakers at existing switching stations |  | Southeast Nacogdoches | Lufkin Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R862 | 2022-12-01 |  | 345 | 8 | 13 | 0 | 0 | NACOGDOCHES | ANGELINA | Tier 2 | 2008-07-01 |  | 2008-09-01 | 3117, 3119 | N | N | 2007-E4
Old Project | No Change | 06TPIT0036 | Ennis Switch - Ennis 138 kV line | Upgrade existing 138 kV line |  | Ennis Switch | Ennis | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M280-E | 2023-05-01 |  | 138 | 0 | 6.32 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 2324, 2326 | N | N
Old Project | No Change | 06TPIT0042 | Lake Wichita Switch - Wichita Falls Switch 69 kV line | Upgrade existing 69 kV line |  | Lake Wichita Switch | Wichitia Falls Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R168-E | 2023-05-01 |  | 138 | 0 | 6.3 | 0 | 0 | ARCHER | WICHITA | Tier 4 |  |  |  | 1447, 1449 | N | N
Old Project | No Change | 07TPIT0115 | Elgin Switch - Taylor 138 kV line | Upgrade existing 138 kV line |  | Elgiin Switch | Taylor | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R026-E | 2023-05-01 |  | 138 | 0 | 11.4 | 0 | 0 | BASTROP | BASTROP | Tier 4 |  |  |  | 3650, 3658 | N | N
Old Project | No Change | 07TPIT0119 | Lavon Switch - Allen Switch 138 kV line | Create a new 138 kV line by reconfiguring existing lines and adding circuit to existing structures |  | Lavon Switch | Allen Switch | Conceptual | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375B-E | 2023-05-01 |  | 138 | 8.9 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 2475, 2477, 2509 | N | N
Old Project | No Change | 07TPIT0122 | Royse - Dalrock 138 kV line | Upgrade existing 138 kV line |  | Royse | Dalrock | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3035-E | 2023-05-01 |  | 138 | 0 | 6.8 | 0 | 0 | ROCKWALL | ROCKWALL | Tier 4 |  |  |  | 2472, 2733, 2735 | N | N
Old Project | No Change | 07TPIT0138 | Oates (GPL) - Garland Bobtown Tap 138 kV line | Upgrade existing 138 kV line |  | Oats (GPL) | Garland Bobtown Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M322-E | 2023-05-01 |  | 138 | 0 | 1.5 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 831, 2739 | N | N
Old Project | No Change | 08TPIT0069 | Lake Creek - East Waco 138 kV line | Upgrade existing 138 kV line |  | Lake Creek | East Waco | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R470-E | 2024-05-01 |  | 138 | 0 | 10.5 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3410, 3452, 3438 | N | N
Old Project | No Change | 08TPIT0111 | Lufkin Switching Station - Texas Foundries Tap 138 kV line | Upgrade existing 138 kV line |  | Lufkin Switching Station | Texas Foundries Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R389-E | 2024-05-01 |  | 138 | 0 | 0.73 | 0 | 0 | ANGELINA | ANGELINA | Tier 4 |  |  |  | 3326, 3327, 3328 | N | N
Old Project | No Change | 09TPIT0043 | Coppell - North Lake 138 kV line | Construct 138 kV line |  | Coppell | North Lake | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M549-E | 2024-05-01 |  | 138 | 4.8 | 0 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2015, 2386 | N | N
Old Project | No Change | 09TPIT0046 | N. Midlothian - Midlothian TXI Tap 138 kV line | Upgrade existing 138 kV line |  | N. Midlothian | Midlothian TXI Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3031-E | 2024-05-01 |  | 138 | 0 | 6.2 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 2310, 2311, 2313 | N | N
Old Project | No Change | 09TPIT0050 | Rowlett - Garland Bobtown Tap 138 kV line | Upgrade existing 138 kV line |  | Rowlett | Garland Bobtown Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3032-E | 2024-05-01 |  | 138 | 0 | 4.1 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2736, 2739 | N | N
Old Project | No Change | 09TPIT0051 | Salado Switch - Cedar Valley Switch (BEC) 138 kV line and switching stations | Establish two new 138 kV switching stations and connect them with a new 138 kV line |  | Saldo Switch | Cedar Valley Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R469-E | 2024-05-01 |  | 138 | 7 | 0 | 0 | 0 | BELL | BELL | Tier 2 |  |  |  | 117, 3640 | N | N
Old Project | No Change | 09TPIT0066 | Boggy Creek 138 kV Switching Station and associated line | Construct 138 kV switching station and add second circuit to a 138 kV line |  | Boggy Creek | Little River | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R488-E | 2024-05-01 |  | 138 | 3.5 | 0 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3424, 3415, 3425, 13645 | N | N
Old Project | No Change | 09TPIT0067 | Bonham Switching Station 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R516-E | 2024-05-01 |  | 138 | 0 | 0 | 100 | 0 | FANNIN |  | Tier 4 |  |  |  | 1760, 1761 | N | N

## CompletedTPIT03012013NoCost
MARCH BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) COMPLETED PROJECTS As Of 03/01/2013.
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional)
06TPIT0167 | MVEC Merett-MVEC Pharr | Rebuild 138kV line from Merett to MVEC Pharr Substations | Clearance extended to 1-14-11 |  |  |  | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org | 984505 | 2010-12-30 | 2011-01-01 | 138 | 0 | 2.2 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8752-8762 | Y | N
09TPIT0022 | Killeen Switch - S. Harker Heights 138 kV line | Upgrade existing 138 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R410-WAC | 2011-01-01 | 2011-01-01 | 138 | 0 | 5.3 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3423, 3633 | Y
11TPIT0127 | Graham 345/138 kV autotransformer | Replace existing autotransformer | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R904A-WAC | 2011-05-01 | 2011-01-01 | 345 | 0 | 0 | 350 | 0 | YOUNG |  | Tier 4 |  |  |  | 1596, 1430 | Y
11TPIT0113 | Oasis - Meadow Ckt.99 | Upgrade 345kV Ckt. 99 Oasis to Meadow to increase thermal ratings. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-12-31 | 2011-01-07 | 345 | 0 | 3.91 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 4 |  |  |  | 43035, 43030 | Y |  |  | 1) Identified by ERCOT as an Economic Project in 2009 5-Year Plan. Needed by summer peak 2011. 2) No transformer capacity to be added.
10TPIT0108 | Dowling Rd Substation Additions | Build new distibution substation in BTU transmission line from BTU South Switch to TAMU Substation | [5 empty] | COCS/BTU | Tony Michalsky 979- 764-3438 tmichalsky@cstx.gov |  | 2011-01-01 | 2011-01-11 | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
08TPIT0032 | Gilleland 345/138kV autotransformer | Install a 672 MVA 345/138kV autotransformer at the new Gilleland switching substation | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-01-01 | 2011-01-11 | 345 | 0 | 0 | 672 | 0 | TRAVIS |  | Tier 4 |  |  |  | The 345kV bus is 7340 and the 138kV bus is 7336 | Y
08TPIT0042 | Seaton to Barclay Rebuild | Rebuild existing Seaton to Barclay with 1033 ACSR | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2010-12-23 | 2011-01-20 | 69 | 0 | 10.2 | 0 | 0 | BELL | FALLS | Tier 4 |  |  |  | 69131 | Y |  |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
09TPIT0119 | Whitesboro SE - Gordonville 138 kV tap line | Construct 138 kV line and convert existing 69 kV line and substations to 138 kV operation. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R546-WAC | 2011-01-01 | 2011-01-25 | 138 | 0.9 | 7.9 | 0 | 0 | GRAYSON | GRAYSON | Tier 4 |  |  |  | 1744, 1725 | Y
08TPIT0020 | Zorn/Clear Springs-Gilleland Creek-Hutto Switch 345-kV line | Construct a 345 kV double circuit (bundled 959 ACSS) line between Zorn/Clear Springs and Hutto Switch and other ONCOR and AE projects. Upgrade the 7.5-mile McNeil (7334)-Gilleland(7336) 795 ACSR 138-kV transmission line to 1433 ACSS/TW. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org | Not yet assigned | 2011-02-01 | 2011-02-01 | 345 | 165 | 7.5 | 0 | 0 | WILLIAMSON | GUADALUPE | Tier 1 | 2001-12-01 | 2001-12-01 | 2002-02-01 | 7042, 7050, 7340, 3696 | Y |  |  | Harris Branch substation replaced with Gilleland Creek substation as an in-line termination point for one of the
09TPIT0098 | Dilley, add 138 kV terminal | Construct 9 miles 795 ACSR 138 kV line from Palo Duro to Dilley | IN-SERVICE |  |  |  | 382 - 0559 | AEP/TCC | Brian Johnson 918-599-2653 | 3098 | 2011-02-17 | 2011-02-11 | 138 | 0 | 0 | 0 | 0 | FRIO | FRIO | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
11TPIT0126 | Cactus tap located on the Ft. Lancaster to West Yates 69 kV line | SouthWest Texas Electric Co-Op distribution station | IN-SERVICE |  |  |  | 491 - 0692 | AEP/TNC | Joe Gilbert 918-599-2653 | 2429 | 2011-02-16 | 2011-02-16 | 69 | 0 | 0 | 0 | 0 | CROCKETT | CROCKETT | Tier 4 |  |  |  |  | Y
07TPIT0055 | Frisco to Kruegerville Rebuild | Rebuild existing Frisco to Kruegerville with1590 or Acss conductor | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-04-08 | 2011-02-16 | 138 | 0 | 11.7 | 0 | 0 | COLLIN | DENTON | Tier 3 | 2009-10-13 | 2009-11-01 | N/A | 662, 1994, 681 | Y
08TPIT0085 | Palo Duro Switching Station | Construct a new Palo Duro switching substation in the 138 kV transmission line, from Pearsall to Batesville, at the point where the line changes from a north/south direction to an east/west direction, ties-in new 138 kV transmission line to AEP Dilley. | Negotiation of site is in progress. Acquiring Right-Of-Way Easements. |  |  |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-01-01 | 2011-02-17 | 138 | 0 | 0 | 0 | 0 | FRIO |  | Tier 4 | 2006-02-01 | 2006-06-29 | 2006-08-01 | 5866 | Y | N
08TPIT0094 | Palo Duro to AEP Dilley SS 138 kV Line | Construct 9 miles 795 ACSR 138 kV line from Palo Duro to AEP Dilley. | Changed responsibility to STEC |  |  |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-01-01 | 2011-02-17 | 138 | 9 | 0 | 0 | 0 | FRIO | FRIO | Tier 4 | 2006-02-01 | 2006-06-29 | 2006-08-01 | 5866-8212 | Y | N
09TPIT0189 | Pearsall to Dilley 69 kV Line | Upgrade 21.8 miles of 69 kV to 795 ACSR conductor from Pearsall to Derby to Dilley. | Upgrade 69 kV line for new generation at Pearsall |  |  |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-01-01 | 2011-02-25 | 69 | 0 | 21.8 | 0 | 0 | FRIO | FRIO | Tier 4 | 2006-02-01 | 2006-06-29 | 2006-08-01 | 5893-5842--5860 | Y | N
10TPIT0076 | Stephenville to Granbury 138KV Conversion | Convert exisitng Stephenville to Granbury 69KV line to 138KV operation | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-01-04 | 2011-02-25 | 138 | 0 | 27.81 | 0 | 0 | HOOD | ERATH | Tier 4 |  |  |  | 306, 307, 309, 306, 305, 304, 303, 299 | Y
10TPIT0050 | Rayburn Substation | Install (3) Breaker ring to include (2) 69 lines and (1) 69/12.5 transformer | [5 empty] | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2011-02-28 | 2011-03-01 | 69 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
11TPIT0088 | La Quinta: Configure station to 3 breaker ring bus | Construct new 138kV La Quinta Substation to directly interconnect 150MW Cedro Hill Wind Farm | Schedule Update |  |  |  | 398 - 0587 | AEP/ETT | Tommy Vannoy 918-599-2653 | 3351 | 2012-03-31 | 2011-03-01 | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB | Tier 4 |  |  |  |  | Y
10TPIT0021 | Krum West Switch - NW Carrollton 345 kV circuit (Oncor Electric Delivery section) | Add second 345 kV circuit on existing structures . |  |  |  |  | C017 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C037-WA | 2011-03-01 | 2011-03-01 | 345 | 37.2 | 0 | 0 | 0 | DENTON | DALLAS | CREZ |  |  |  | 988, 1730, 2361 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
08TPIT0162 | Convert Alta Loma 69/138kV dual voltage substation to a 138kV substation. | Convert Alta Loma 69/138kV dual voltage double tap configuration substation to a 138kVsectionalizing substation looped into Ckt.93 PH Robinson to Hitchcock. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-03-31 | 2011-03-02 | 138 | 0 | 0.1 | 0 | 0 | GALVESTON |  | Tier 4 |  |  |  | 42061, 42062 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
12TPIT0055 | Hill Country to Stonegate - 138 kV 2nd Circuit | Build second 138kV transmission line from Hill Country to Stonegate on existing transmission structures |  | Hill Country | Stonegate |  | S-0580 | CPS | PM: Hector Torres | T-0163 | 2011-03-17 | 2011-03-08 | 138 | 10.01 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5209 5415 | Y | N |  | There are no transformers associated with this project
11TPIT0141 | Ft. Lancaster to Illinois #4, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE |  |  |  | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2437 | 2011-03-31 | 2011-03-09 | 69 | 0 | 17.21 | 0 | 0 | PECOS | CROCKETT | CREZ Modified |  |  |  |  | Y
11TPIT0119 | Texas Substation Conversion | Convert Texas substation from 69kV to 138kV service. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-04-30 | 2011-03-09 | 138 | 0.76 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 41550, 41540 | Y |  |  | No transformer capacity to be added.
11TPIT0148 | Ayers 138 kV terminal equipment | Upgrade terminal equipment on line from Handley to Hemphill | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5169-WAC | 2011-05-01 | 2011-03-11 | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1950, 2167, 2164 | Y
07TPIT0018 | Lewisville Switch (Brazos) - Highland (TNMP) 138 kV line (Oncor portion) | Upgrade existing 138 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5067-WAC | 2011-05-01 | 2011-03-14 | 138 | 0 | 1.6 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | 2010-06-15 | 645, 1970 | Y
06TPIT9999 | Sioux-Gandy 138kV Line | Build New 138kV Line from Sioux-Gandy Substations | Acquiring Right-Of-Way Easements |  |  |  | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org | 789640 | 2011-03-01 | 2011-03-16 | 138 | 4.5 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 2 | 2005-02-01 | 2005-04-20 |  | 8792-8755 | Y | N
10TPIT0123 | Sioux 138 kV substation | Build New 138kV Sioux Substation in the Line from Doedyns-Gandy. | Acquiring Right-Of-Way Easements on Sioux-Gandy T/L |  |  |  | 06TPIT9999 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-03-01 | 2011-03-16 | 138 | 0 | 0 | 0 | 0 | HIDALGO |  | Tier 4 |  |  |  | 8792 | Y | N
11TPIT0160 | Bruni auto upgrade | Upgrade the 18 MVA138/69 kV autotransformer. | [5 empty] | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-04-01 | 2011-03-16 | 138 | 0 | 0 | 37 | 0 | WEBB |  | Tier 4 |  |  |  | 5887, 5888 | Y | N
08TPIT0068 | Collin - Frisco (Brazos) 138 kV line | Upgrade existing 138 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M596-WAC | 2011-05-01 | 2011-03-18 | 138 | 0 | 1.7 | 0 | 0 | COLLIN | DENTON | Tier 4 |  |  | 2010-06-15 | 2370, 681 | Y |  | 2009-R14
11TPIT0137 | Hilltop Lakes Auto | Replace 40 MVA, 138/69 kV auto with 60 MVA auto | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-04-01 | 2011-03-21 | 138 | 0 | 0 | 60 | 0 | MADISON |  | Tier 4 |  |  |  | 47, 48 | Y
11TPIT0093 | Saginaw Switch capacitors | Install 138 kV capacitors | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5160-WAC | 2011-05-01 | 2011-03-29 | 138 | 0 | 0 | 0 | 55.2 | TARRANT |  | Tier 4 |  |  |  | 1957 | Y
11TPIT0116 | FM 237 Yorktown - New Substation | Construct a new 69-13.09x26.18-KV, 7.0 MVA substation | COMPLETED |  |  |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2011-04-11 | 2011-03-31 | 69 | 0 | 0 | 0 | 0 | DEWITT |  | Tier 4 |  |  |  | See Project Title | Y
11TPIT0178 | AGRI Substation Removal | Remove AGRI substation from CNP transmission service | IN-SERVICE | AGRI |  | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | N/A | 2011-03-31 | 69 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 40051 | Y | N
11TPIT0161 | Pt Lavaca to Pt Oconnor | Upgrade miles of 69 kV from 4/0 to 795 ACSR conductor between Pt Lavaca and Pt Oconnor. | [5 empty] | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-04-01 | 2011-04-01 | 69 | 0 | 20.1 | 0 | 0 | CALHOUN | CALHOUN | Tier 4 |  |  |  | 5592-5596 | Y | N
11TPIT0053 | Gresham Road 138 kV Switching Station | Construction switching station to connect a new power plant | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6000-WAC | 2011-06-01 | 2011-04-01 | 138 | 0 | 0 | 0 | 0 | NACOGDOCHES |  | Tier 4 |  |  |  | 3301 | Y
11TPIT0121 | Parker - Comanche Peak - Everman 345 kV line | Connect Parker - Everman 345 kV line into Comanche Peak | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2011-05-01 | 2011-04-01 | 345 | 0 | 0 | 0 | 0 | SOMERVELL |  | Tier 2 | 2009-07-01 | 2010-03-31 |  | 1900 | Y
09TPIT0105 | Rattlesnake Road Switch - Lake Creek 345 kV line | Upgrade existing 345 kV line |  |  |  |  | R499 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R499A-E | 2011-09-01 | 2011-04-04 | 345 | 0 | 1.5 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3399, 3409 | Y
10TPIT0047 | Zenith 345kV Switching Station | Build a new 345 kV Zenith substation. Loop Ckt.99 Singleton - Obrien, Ckt.98 Singleton - T.H. Wharton, Ckt 98 T.H. Wharton - Obrien into the new substation. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 | 2011-04-06 | 345 | 1 | 0 | 0 | 0 | HARRIS |  | Tier 3 | 2007-04-28 | 2007-07-16 | 2007-08-21 | 44900 | Y |  |  | Added to Houston Area Constraint Mitigation Project, Phase II per discussion with ERCOT.
11TPIT0159 | AGRI 69kV Substation | Disconnect customer owned AGRI 69kV substation from CNP service. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-04-30 | 2011-04-20 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 40051 | Y
11TPIT0112 | Hockley - Peters Ckt.58 | Convert Hockley to Peters Ckt. 58 from 69kV to 138kV | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 | 2011-04-20 | 138 | 0 | 28.5 | 0 | 0 | HARRIS | AUSTIN | Tier 4 |  |  |  | 45890, 46250, 46230 | Y |  |  | No transformer capacity to be added. After completion of conversion to 138kV, Ckt. 58 will become Ckt. 65.
10TPIT0044 | Marbach substation removal - Reconfigure 138kV lines at Marbach and Cagnon | Reroute the 138kV lines at Marbach and Cagnon. Due to removal of the Marbach substation. |  |  |  |  | S-0401 | CPS | T: Aaron Finley PM:Hector Torres | T-0129 | 2011-06-01 | 2011-04-21 | 138 | 0.3 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5295 | Y | N |  | There are no transformers associated with this project
11TPIT0051 | Riley, Build 345 kV switch station, cutting in the existing Oklaunion to Bowman 345 kV line | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 | IN-SERVICE |  |  |  | 467 - 0668 | AEP/ETT | Tommy Vannoy 918-599-2653 | 2350 | 2011-05-27 | 2011-04-28 | 345 | 0 | 0 | 0 | 0 | WILBARGER | WILBARGER | CREZ Modified |  |  |  |  | Y
11TPIT0149 | Hemphill 138 kV terminal equipment | Upgrade terminal equipment on line to Randol Mill | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5167-WAC, M5167B-WAC & M5167C-WAC | 2011-05-01 | 2011-04-29 | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2164, 2105 | Y
11TPIT0150 | Hemphill 138 kV terminal equipment | Upgrade terminal equipment on line to Ayers | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5167D-E & M5167E-E | 2011-05-01 | 2011-04-29 | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2164, 2167 | Y
11TPIT0117 | Leakey | Remove a 15.6 MVAR Capacitor bank from the Bandera substation (7439) and add a 15.6 MVAR capacitor bank at the Leakey substation (7426) | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-04-01 | 2011-05-01 | 69 | 0 | 0 | 0 | 0 | BANDERA | REAL | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
14TPIT0019 | Orange Grove Switch to Orange Grove Sub upgrade | Upgrade 0.21 miles of 69 kV circuit between Orange Grove Switch and Orange Grove Sub | [5 empty] | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-06-01 | 2011-05-01 | 69 | 0 | 0.21 | 0 | 0 | JIM WELLS | JIM WELLS | Tier 4 |  |  |  | 5658 - 5662 | Y | N
11TPIT0054 | Abilene South - Leon 138 kV line (Oncor Electric Delivery's section) | Rebuild existing 69 kV line for 138 kV operation. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C042-E | 2011-06-01 | 2011-05-01 | 138 | 0 | 8.4 | 0 | 0 | EASTLAND | EASTLAND | CREZ |  |  |  | 1624 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0128 | Leon Switch | Install 138 kV breaker. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C042-E | 2011-06-01 | 2011-05-01 | 138 | 0 | 0 | 0 | 0 | EASTLAND |  | CREZ |  |  |  | 1624 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0152 | Randol Mill 138 kV terminal equipment | Upgrade terminal equipment on Hemphill - Randol Mill - Handley/Saginaw line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5168-WAC, M5168B-WAC, M5168C-WAC & M5168D-WAC | 2011-05-01 | 2011-05-01 | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2164, 2105, 2103, 2104, 2106 | Y
11TPIT0166 | Alazan to Nelson Sharpe 138 kV line rebuild | Barney Davis to Nelson Sharpe 138 kV line rebuild 1st circuit on a double circuit capable structure | IN-SERVICE |  |  |  | 400 - 0647 | AEP/ETT/TCC | Michael Glueck 918-599-2653 | 3360 | 2011-06-01 | 2011-05-01 | 138 | 0 | 10.1 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y
09TPIT0101 | Oleander, Construct 138/69 kV Substation | Construct a new 138/69 kV Switching Station near East Harrison substation and reconductor the 69 kV line from La Palma to San Benito | IN-SERVICE |  |  |  | 362 - 0537 | AEP/TCC | Rich Haley 918-599-2653 | 3101 | 2011-05-31 | 2011-05-02 | 138 | 0 | 0 | 130 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  | 80023, 80022 | Y
11TPIT0094 | Venus Switch capacitors | Install 138 kV capacitors | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3096-WAC | 2011-05-01 | 2011-05-04 | 138 | 0 | 0 | 0 | 110.4 | ELLIS |  | Tier 4 |  |  |  | 1908 | Y
11TPIT0151 | Mesquite 138 kV terminal equipment | Upgrade terminal equipment on the E Mesquite - Mesquite - Seagoville Switch line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4046-WAC | 2011-05-01 | 2011-05-05 | 138 | 0 | 0 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2771, 2775, 2776 | Y
07TPIT7777 | MVEC Pharr-Alberta Switch | Rebuild 138kV line from Pharr to Alberta Switch Substations | Delay of Start of Construction to 1-17-11 |  |  |  | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-05-01 | 2011-05-06 | 138 | 0 | 1.2 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8759-8762 | Y | N
11TPIT0056 | Cisco, Convert station to 138 kV | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line | IN-SERVICE |  |  |  | 466 - 0666 | AEP/TNC | Dave Goetz 918-599-2653 | 2341 | 2011-06-30 | 2011-05-06 | 138 | 0 | 0 | 0 | 0 | EASTLAND |  | CREZ Modified |  |  |  |  | Y
11TPIT0090 | Benbrook Switch capacitors | Install 138 kV capacitors | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5158-WAC | 2011-05-01 | 2011-05-13 | 138 | 0 | 0 | 0 | 220.8 | TARRANT |  | Tier 4 |  |  |  | 1874, 1875 | Y
11TPIT0091 | Elkton Switch capacitors | Install 138 kV capacitors | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6003-WA | 2011-05-01 | 2011-05-13 | 138 | 0 | 0 | 0 | 110.4 | SMITH |  | Tier 4 |  |  |  | 3106 | Y
10TPIT0141 | Olney to Rice | Rebuild existin Olney to Rice 138 kV line | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-04-29 | 2011-05-16 | 138 | 0 | 17.1 | 0 | 0 | YOUNG | YOUNG | Tier 4 |  |  |  | 787, 1477 | Y |  |  | 2009-R10
11TPIT0132 | Olney 2nd Auto | Add 60 MVA, 138/69 kV auto | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-05-09 | 2011-05-16 | 138 | 0 | 0 | 60 | 0 | YOUNG |  | Tier 4 |  |  |  | 787, 788 | Y
10TPIT0069 | Thomaston: Install 138 kV PST, Add 3-28.8 MVAR Cap Banks, Reterminate 138 kV Line | Upgrade Thomaston substation to 3 breaker ring bus, install 180/200 MVA PST on Thomaston to LCRA Cuero 138 kV line. | IN-SERVICE |  |  |  | 402 - 0653 | AEP/ETT/TCC | Dave Goetz 918-599-2653 | 3264 | 2011-05-31 | 2011-05-19 | 138 | 0 | 0 | 150 | 86.4 | DEWITT |  | Tier 4 |  |  |  |  | Y
11TPIT0124 | Construct Service to Crystal Bay 138kV Substation | Serve substation by looping into Ckt.84 Borden to Dowlap. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 | 2011-05-20 | 138 | 0.2 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 40290 | Y |  |  | No transformer capacity to be added.
11TPIT0005 | Talley Rd - New 138kV Substation | Loop new 138kV substation into future 138kV Medina Lake to CPS line (06TPIT0080) |  | Tally | Tx Research/Medina Lake |  | T-0160 | CPS | PM: Ulrich Skerhut | S-0383 | 2011-06-01 | 2011-05-26 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5422 | Y | N |  | There are no transformers associated with this project
11TPIT0021 | Nassau Bay to Nassau Bay Sw. Rebuild | Rebuild existing 138 kV 4/0 line from Nassau Bay to Nassau Bay Sw. with 1033 double-circuit construction | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-05-03 | 2011-05-30 | 69 | 0 | 1.21 | 0 | 0 | HOOD | HOOD | Tier 4 |  |  |  | 364373451455 | Y
11TPIT0039 | Dresden to LA Heights - 138kV line upgrade | Upgrade the existing Dresden to LA Heights 138kV transmission line |  | Dresden | LA Heights |  | S-0308 | CPS | PM: Bruce Raney | T-0156 | 2011-06-01 | 2011-05-31 | 138 | 0 | 3.29 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5130 5285 5286 | Y | N |  | There are no transformers associated with this project
11TPIT0087 | Putnam, Recofigure Station | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line | IN-SERVICE |  |  |  | 466 - 0666 | AEP/TNC | Dave Goetz 918-599-2653 | 2400 | 2011-05-31 | 2011-05-31 | 138 | 0 | 0 | 0 | 0 | CALLAHAN |  | CREZ Modified |  |  |  |  | Y
11TPIT0102 | Waples to Hood Conversion | Convert existing Waples to Hood line to 138 kV operation | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-05-03 | 2011-05-31 | 138 | 0 | 7.25 | 0 | 0 | HOOD | HOOD | Tier 4 |  |  |  | 466, 373, 455, 451, 364 | Y
11TPIT0135 | Navo Capacitor Bank | Install additional 75 MVAR at Navo sub | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-04-15 | 2011-05-31 | 138 | 0 | 0 | 0 | 75 | DENTON |  | Tier 4 |  |  |  | 662 | Y
10TPIT0115 | Gibbons Creek Substation Upgrade Project | Install new control houses for both 138kV and 345kV systems. Upgrade all relays and SCADA devices and install new cabling for yard equipment. Install high-side load-break switches for autotransformers 1 and 2. | Revised due to coordination with generation plant outage schedule |  |  |  |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T09002 | 2011-05-01 | 2011-05-31 | 345 | 0 | 0 | 0 | 0 | GRIMES | GRIMES | Tier 4 |  |  |  |  | N
11TPIT0035 | McCree 69 kV, install 18.0 MVAR Cap Bank | Install 18 MVAR capacitor bank to support local low voltage problems | [5 empty] | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2011-06-01 | 2011-06-01 | 69 | 0 | 0 | 0 | 18 | DALLAS |  | Tier 4 |  |  |  | 832 | Y
11TPIT0044 | Highway 9 to Valero West 69 kV transmission line upgrades | Upgrade the Upriver to Highway 9 69 kV Loop and add transformation to remove contingency overloads during off-peak maintenance | IN-SERVICE | Highway 9 | Upriver | Under Construction | 399 - 0644 | AEP/ETT/TCC | Michael Glueck 918-599-2653 | 3280 | 2011-06-30 | 2011-06-01 | 69 | 0 | 3.96 | 0 | 0 | NUECES | NUECES | Tier 1 | 2009-03-18 | 2009-10-09 | 2009-12-01 |  | Y | N
05TPIT0068 | Marshall Ford-Buttercup | Upgrade the 9.8-mile Marshall Ford(7356)-Buttercup(7531) 795 ACSR (220-MVA) 138-kV transmission line to bundled 795 ACSR (440MVA). | Complete 6/1/11 |  |  |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-06-01 | 2011-06-01 | 138 | 0 | 9.8 | 0 | 0 | TRAVIS | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
09TPIT0130 | Newman 138 kV, install 24.0 MVAR Cap Bank | Install 24 MVAR capacitor bank to support local low voltage problems | [5 empty] | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2011-05-02 | 2011-06-01 | 138 | 0 | 0 | 0 | 24 | DALLAS |  | Tier 4 |  |  |  | 849 | Y
11TPIT0075 | Kirby to Tuttle - 138 kV Circuit | Construct a 138 kV circuit between Kirby and Tuttle using existing ROW and install new substation terminal equipment |  | Kirby | Tuttle |  |  | CPS | PM: Bruce Raney | T-0206 | 2011-10-01 | 2011-06-01 | 138 | 6.475 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5250 5435 | Y | N |  | There are no transformers associated with this project
11TPIT0080 | Killeen Switch - Killeen South - Killeen Fort Hood West Tap 138 kV line | Upgrade existing 138 kV line |  | Killeen Switch | Killeen Fort Hood West Tap | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R741-E | 2011-06-01 | 2011-06-01 | 138 | 0 | 7 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3423, 3428 | Y | N | 2009-R32
11TPIT0122 | Cedar Hill Switch 138 kV terminal equipment | Upgrade 138 kV terminal equipment used to connect the 345/138 kV autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4083B-WAC | 2011-06-01 | 2011-06-01 | 138 | 0 | 0 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 2421, 2422 | Y | N
11TPIT0145 | Goldsmith Tap - Goldsmith 138 kV Line | Rebuild existing 69 kV line as a double-circuit line with a 138 kV circuit and a 69 kV circuit and convert Goldsmith Substation to 138 kV. |  | Goldsmith Tap | Goldsmith | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8021-WAC | 2011-06-01 | 2011-06-01 | 138 | 3.3 | 3.3 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 11256, 11250, 1141, 1145 | Y | N
11TPIT0067 | Tonkawa Switch | Expand existing switching station |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C859-E | 2011-06-01 | 2011-06-01 | 345 | 0 | 0 | 0 | -100 | MITCHELL |  | CREZ |  |  |  | 11048 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0068 | Tonkawa - Sweetwater East 345 kV line | Construct double-circuit 345 kV line |  | Tonkawa | Sweetwater East | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1007-E | 2011-06-01 | 2011-06-01 | 345 | 63.4 | 0 | 0 | 0 | MITCHELL | NOLAN | CREZ |  |  |  | 11048, 11420 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0069 | Sweetwater East Switch | Construct 345 kV switching station |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C858-E | 2011-06-01 | 2011-06-01 | 345 | 0 | 0 | 0 | -100 | NOLAN |  | CREZ |  |  |  | 11420 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0172 | PH Robinson - Center Ckt. 97 | Upgrade substation equipment to increase thermal ratings. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-06-01 | 2011-06-01 | 345 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 42000, 40240 | Y
12TPIT0040 | Scurry County South Switch (Central A) | Construct 345 kV switching station with 345/138 kV autotransformers and shunt reactor |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1004-E | 2011-06-01 | 2011-06-01 | 345 | 0 | 0 | 1200 | -150 | SCURRY |  | CREZ |  |  |  | 11318 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0041 | Dermott Switch (Central B) | Construct 345 kV switching station with 345/138 kV autotransformers and shunt reactor |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1003-E | 2011-06-01 | 2011-06-01 | 345 | 0 | 0 | 1200 | -150 | SCURRY |  | CREZ |  |  |  | 11305 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0042 | Scurry County South Switch (Central A) - Tonkawa 345 kV line | Construct double-circuit 345 kV line |  | Scurry County South | Tonkawa | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1008-E | 2011-06-01 | 2011-06-01 | 345 | 30.4 | 0 | 0 | 0 | SCURRY | MITCHELL | CREZ |  |  |  | 11318, 11048 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0118 | Cheapside - New Substation | Construct a new 138-13.09KV, 20 MVA x two, redundant backup substation | COMPLETED |  |  |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2011-06-03 | 2011-06-03 | 138 | 0 | 0 | 0 | 0 | GONZALES |  | Tier 4 |  |  |  | See Project Title | Y | N
08TPIT0080 | Abilene South to Tuscola, Rebuild 69 kV line | Re-Build Portions of the Ballinger to Abilene South 69 kV line with 795 ACSR | IN-SERVICE | Abilene South | Tuscola | Under Construction | 499 - 0704 | AEP/ETT | Teresa Trotman 918-599-2653 | 2455 | 2011-06-06 | 2011-06-06 | 69 | 0 | 11.4 | 0 | 0 | TAYLOR | TAYLOR | Tier 1 | 2008-06-20 | 2009-03-19 | 2009-08-06 |  | Y | N
11TPIT0139 | DUNCAN 138kV Substation | Serve DUNCAN substation by looping into Ckt.86 BENDER - BARHIL. | IN-SERVICE | DUNCAN | BENDER/ BARHIL |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-06-30 | 2011-06-06 | 138 | 0.3 | 0 | 0 | 0 | CHAMBERS | CHAMBERS | Tier 4 |  |  |  | 40360, 40150, 40155 | Y | N |  | No autotransformer capacity to be added.
10TPIT0087 | Putnam to Leon, Convert 69 kV line to 138 kV | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line | IN-SERVICE | Putnam | Leon | Under Construction | 466 - 0666 | AEP/ETT/ONCOR | Larry Roberson 918-599-2653 | 2347 | 2011-06-30 | 2011-06-07 | 138 | 0 | 17.38 | 0 | 0 | NUECES | EASTLAND | CREZ Modified | 2008-06-20 | 2009-03-19 | 2009-08-06 |  | Y | Y
11TPIT0146 | Big Brown 345 kV terminal equipment | Upgrade terminal equipment on line to Venus |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R752-WAC | 2011-06-01 | 2011-06-08 | 345 | 0 | 0 | 0 | 0 | FREESTONE | FREESTONE | Tier 4 |  |  |  | 3380, 1906 | Y | N
10TPIT0065 | Dansby Substation | Install (1) Breaker in existing ring bus for a 138 lines to Thompson Creek Substation |  | Dansby | Dansby | completed | 05TPIT0172 11TIPIT0030 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2011-06-11 | 2011-06-11 | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32897 | Y | N
11TPIT0030 | Thompson Creek Substation | Install (3) Breaker ring to include (1) 138 lines, and (1) 138/12.5 transformer |  | Thompson Creek | Thompson Creek | completed | 05TPIT0172 10TIPIT0065 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2011-06-11 | 2011-06-11 | 138 | 0 | 0 | 14 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y | N
11TPIT0125 | Teasley Substation - Add 28 MVA Transformer | Install an additional 138kV circuit breaker and a new 28 MVA tranformer in the existing Teasley Substation to accommodate additional load growth | On schedule |  |  | Complete | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602766 | 2011-06-11 | 2011-06-11 | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 918 | Y | N
12TPIT0092 | OXY USA Collie Field 69kV Tap | This project will tap TNMP's Worsham to IH20 69kV line to serve the new Oxy Collie Filed station |  | Worhsam | IH20 | Completed |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | NTE07410 | 2012-02-28 | 2011-06-20 | 69 | 3.077 | 0 | 0 | 0 | WARD | REEVES | Tier 4 |  |  |  | 38020, 38040, 38041, 38042 | Y | N
05TPIT0172 | Thompson Creek to Dansby 138, New line construction | Build a 1033 ACSR 138 kV line |  | Thompson Creek | Dansby | completed | 10TPIT0065 11TPIT0030 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com | 802 | 2011-06-20 | 2011-06-20 | 138 | 10.2 | 0 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  | 32897, 32863 | Y | N
11TPIT0147 | Venus 345 kV terminal equipment | Upgrade terminal equipment on line to Big Brown |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3103-WAC & M3103B-WAC | 2011-06-01 | 2011-06-20 | 345 | 0 | 0 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 3380, 1906 | Y | N
11TPIT0120 | Pegasus 138 kV Tap and Point of Interconnection | Convert the tap line to Pegasus and South Pegasus substations to 138 kV and connect to the Odesaa - Crane 138 kV line (Oncor portion) | Construction taking more time than expected | Pleasant Farms | Pagasus and South Pegasus | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8010-WAC | 2011-06-01 | 2011-06-23 | 138 | 0 | 11.4 | 0 | 0 | ECTOR | MIDLAND | Tier 4 |  |  |  | 1235, 1234 | Y | N | 2009-R2
12TPIT0066 | Laguna Vista 138 kV tap lines | Construct 138 kV tap lines to convert Laguna Vista Substation to 138 kV service. | Construction taking more time than expected | East Tap and West Tap | Laguna Vista | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R587-WAC | 2011-06-01 | 2011-06-23 | 138 | 10.4 | 10.4 | 0 | 0 | PARKER | PARKER | Tier 4 |  |  |  | 528, 1590, 529 | Y | N
11TPIT0074a | Galveston Area 138kV Circuit Upgrades Phase Two | Upgrade 138 kV Ckt. 63 Webster to Stewart to increase thermal ratings. | IN-SERVICE | Webster | Stewart |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-06-30 | 2011-06-30 | 138 | 0 | 21.85 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 43507, 42861, 43290 | Y | N |  | No transformer capacity to be added. Project is part of the 2009 ERCOT 5-Year Plan. Construction included in cancelled project 11TPIT0071 is now included in 11TPIT0074.
11TPIT0074b | Galveston Area 138kV Circuit Upgrades Phase Two | Upgrade 138kV Ckt. 93 Alta Loma to Hitchcock to West Galveston to increase thermal ratings. | IN-SERVICE | Alta Loma | West Galveston |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-06-30 | 2011-06-30 | 138 | 0 | 15.7 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 42061, 42800, 43400 | Y | N | See project 11TPIT0074a for total project cost estimate | No transformer capacity to be added. Project is part of the 2009 ERCOT 5-Year Plan. Construction included in cancelled project 11TPIT0071 is now included in 11TPIT0074.
11TPIT0074c | Galveston Area 138kV Circuit Upgrades Phase Two | Upgrade 138 kV Ckt. 01 Webster to Tiki Island to Galveston to increase thermal ratings. | IN-SERVICE | Webster | Galveston |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-06-30 | 2011-06-30 | 138 | 0 | 26.38 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 43500, 42862, 43355, 42670 | Y | N | See project 11TPIT0074a for total project cost estimate | No transformer capacity to be added. Project is part of the 2009 ERCOT 5-Year Plan. Construction included in cancelled project 11TPIT0071 is now included in 11TPIT0074.
07TPIT0026 | Booneville to Hearne Southwest Rebuild | Rebuild existing Booneville - Hearne Southwest with 795 | row issues | Booneville | Hearne Southwest | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-09-20 | 2011-07-07 | 69 | 0 | 22.2 | 0 | 0 | ROBERTSON | BRAZOS | Tier 4 |  |  |  | 38, 32870 | Y | N |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0086 | Circuit 978 (Seaholm to Warren) Reconductor | Reconductor the last span of the Ckt 978 (Seaholm to Warren) going into Warren substation with bundled 795 ACSR Drake conductor. | COMPLETE | Seaholm Substation | Warren Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P086 | 2011-08-01 | 2011-08-01 | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9132, 9286 | Y | N
11TPIT0142 | Illinois #4 to Comstock, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE | Illinois #4 | Comstock | Under Construction | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2438 | 2011-08-02 | 2011-08-02 | 69 | 0 | 63.6 | 0 | 0 | CROCKETT | VALVERDE | CREZ Modified |  |  |  |  | Y | Y
11TPIT0177 | TRIBAY Substation Removal | Remove TRIBAY substation from CNP transmission service | IN-SERVICE | TRIBAY |  | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | N/A | 2011-09-22 | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 41600 | Y | N
11TPIT0136 | Bissett to Aspermont | Rebuild Bissett to Aspermont 69 kV line with 795 ACSR | construction delay due to high temps | Bissett | Aspermont | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10030 | 2011-09-15 | 2011-09-27 | 69 | 0 | 21.35 | 0 | 0 | STONEWALL | STONEWALL | Tier 4 |  |  |  | 753, 755, 6156 | Y | N
11TPIT0106 | Pelican 138 kV: Build 4 Breaker ring Bus | Pelican 138 kV Switching Station for ultimate interconnect of Papalote Creek and Cotton Windfarms | IN-SERVICE |  |  | In Service | 486 - 0688 | AEP/ETT/TCC | Tommy Vannoy 918-599-2653 | 3361 | 2011-09-28 | 2011-09-28 | 138 | 0 | 0 | 0 | 0 | SAN PATRICIO |  | Tier 4 |  |  |  |  | Y | N
11TPIT0171 | Hutto Switch shunt reactors | Install shunt reactors on the tertiary of the 345/138 kV autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R755-WAC | 2011-10-01 | 2011-09-30 | 138 | 0 | 0 | 0 | -75 | WILLIAMSON |  | Tier 4 |  |  |  | 3666 | Y | N
10TPIT0022 | Ckt 918 Oak Hill to Brodie Lane Reconductor | Reconductor the last span of the Ckt 918 going into Oak Hill sub with bundled 795 ACSR Drake capable of 2000 Amperes | COMPLETE | Oak Hill Substation | Brodie Lane Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P080 | 2011-10-01 | 2011-10-01 | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9169, 9247 | Y | N
10TPIT0026 | Mueller 138kV substation | Establish new 138kV Mueller substation with a 30MVA transformer and two underground feeders. The substation will cut into existing Ckt 938 (Kingsbery to Wheless Lane). | COMPLETE | Mueller Substation | Mueller Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | 3230_117_2793 3240_117_4793 3230_117_4229 | 2011-10-01 | 2011-10-01 | 138 | 1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9342 | Y | N
11TPIT0169 | Graham 138 kV terminal equipment | Upgrade terminal equipment on 345/138 kV autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R904A-WAC | 2011-12-01 | 2011-10-01 | 138 | 0 | 0 | 382 | 0 | YOUNG |  | Tier 4 |  |  |  | 1601 | Y | N
09TPIT0176 | Bertram-Andice | Close the normally open Bertram (7520)-Andice(7521) 69 kV transmission line. |  | Bertram | Andice |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-09-12 | 2011-10-10 | 69 | 0 | 0 | 0 | 0 | BURNET | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
11TPIT0131 | Hearne Auto | Replace 60 MVA, 138/69 kV auto with 100 MVA auto |  | Hearne |  | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10067 | 2011-10-07 | 2011-10-11 | 138 | 0 | 0 | 100 | 0 | ROBERTSON |  | Tier 4 |  |  |  | 35, 36 | Y | N
11TPIT0143 | Comstock to Rough Canyon, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE | Comstock | Rough Canyon | In-Service | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2439 | 2011-10-12 | 2011-10-12 | 69 | 0 | 21.6 | 0 | 0 | VALVERDE | VALVERDE | CREZ Modified |  |  |  |  | Y | N
10TPIT0078 | Granbury to Glen Rose Rebuild | Rebuild Granbury to Geln Rose with 959ACSS |  | Granbury | Glen Rose | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 07017 | 2011-10-10 | 2011-10-17 | 69 | 0 | 14.2 | 0 | 0 | HOOD | SOMERVELL | Tier 4 |  |  |  | 315307 | Y | N
12TPIT0070 | Ballinger to Winters, Rebuild 69 kV line | Re-Build Portions of the Ballinger to Abilene South 69 kV line with 795 ACSR | IN-SERVICE | Ballinger | Winters | Under Construction | 499 - 0705 | AEP/ETT | Teresa Trotman 918-599-2653 | 2460 | 2011-10-22 | 2011-10-22 | 69 | 0 | 16.7 | 0 | 0 | TAYLOR | TAYLOR | Tier 1 | 2008-06-20 | 2009-03-19 | 2009-08-06 |  | Y | N
11TPIT0130 | Webberville Solar Project | A new 30MW solar plant operated at 138kV level and tapped into an existing Austrop to Decker Ckt 921. | COMPLETE | Webberville Solar Plant | Webberville Tap | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P311 | 2011-11-01 | 2011-11-01 | 138 | 0.91 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9030, 9185, 9289 | Y | N
12TPIT0119 | Forney - Hubbard 138 kV line | Replace terminal equipment |  | Forney | Hubbard | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4040A - WAC | 2011-12-01 | 2011-11-01 | 138 | 0 | 0 | 0 | 0 | KAUFMAN | DALLAS | Tier 4 |  |  |  | 2934, 2438, 2402 | Y | N
11TPIT0099 | Temple Switch circuit breaker | Install 345 kV circuit breaker on line to Salado Switch. |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R739-WAC | 2011-12-01 | 2011-11-01 | 345 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 3414 | Y | N
11TPIT0092 | Handley SES capacitors | Install 138 kV capacitors |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5159-WAC | 2011-09-01 | 2011-11-05 | 138 | 0 | 0 | 0 | 110.4 | TARRANT |  | Tier 4 |  |  |  | 1951 | Y | N
11TPIT0153 | Colorado City 69 kV terminal equipment | Upgrade terminal equipment on line to Morgan Creek |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8026-WAC, R8026B-WAC, R8026C-WAC & R8026D-WAC | 2011-11-01 | 2011-11-09 | 69 | 0 | 0 | 0 | 0 | MITCHELL | MITCHELL | Tier 4 |  |  |  | 1378, 1033 | Y | N
09TPIT0103 | Alamito Creek, add 2nd 138/69 kV auto | Add 2nd 138/69 kV autotransformer at Alamito Creek, and install a NaS Battery at Gonzales | IN-SERVICE |  |  | In-Service | 358 - 0532 | AEP/TNC | Jim Eriksen 918-599-2653 | 1178 | 2011-11-10 | 2011-11-10 | 138 | 0 | 0 | 50 | 0 | PRESIDIO |  | Tier 1 | 2008-03-21 | 2008-06-10 | 2008-07-15 |  | Y | N
11TPIT0103 | Remove Hearn Rd from Lon Hill to Sinton 69 kV Line | Lon Hill to Upriver 69 kV Hairpin into Hearn Road and Upgrade Lon Hill to Hearn Road section | IN-SERVICE | Lon Hill | Sinton | Under Construction | 399 - 0709 | AEP/TCC | Michael Glueck 918-599-2653 | 3279 | 2011-11-11 | 2011-11-11 | 69 | 0 | 0.25 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y | N
11TPIT0104 | Move Hearn Rd to the Lon Hill to Upriver 69 kV line | Lon Hill to Upriver 69 kV Hairpin into Hearn Road and Upgrade Lon Hill to Hearn Road section | IN-SERVICE | Lon Hill & Upriver | Hearn Road | Under Construction | 399 - 0709 | AEP/ETT/TCC | Michael Glueck 918-599-2653 | 3279 | 2011-11-11 | 2011-11-11 | 69 | 0.5 | 0.5 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y | N
11TPIT0163 | Tres Palacious 69 kV Substation | Construct new 69 kV load serving substation in the line between N Clemville and Saltdome. |  |  |  | Under Construction |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-09-01 | 2011-11-11 | 69 | 0 | 0 | 0 | 0 | MATAGORDA |  | Tier 4 |  |  |  | 5553 | Y | N
11TPIT0156 | Bandera Sub 138kv switches | Upgrade 138kv switches and bus |  | Bandera Sub | Bandera Sub | Complete |  | Bandera Electric | David Baker 830-796-6084 | 182768 | 2011-10-30 | 2011-11-11 | 138 | 0 | 0 | 0 | 0 | Bandera |  | Tier 4 | N/A | N/A | N/A |  | N | N |  | Necessary to utilize full rating of the 2-795 circuit
11TPIT0157 | Verde Creek Sub 138kv switches | Upgrade 138kv switches |  | Verde Creek Sub | Verde Creek Sub | Complete |  | Bandera Electric | David Baker 830-796-6084 | 182769 | 2011-10-30 | 2011-11-11 | 138 | 0 | 0 | 0 | 0 | Kerr |  | Tier 4 | N/A | N/A | N/A |  | N | N |  | Necessary to utilize full rating of the 2-795 circuit
11TPIT0138 | Deer Park Area Reconfigurations | Reconfigure Ckt. 84 SOUTH - WABURN and Ckt. 96 CONIAL - Morgan's Point to create new Ckt. 96 SOUTH - Morgan's Point and Ckt. 84 WABURN - CONIAL. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-11-30 | 2011-11-16 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 43250, 41670, 40370, 41100, 40442, 40443, 42241 | Y | N |  | No autotransformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
12TPIT0024 | Kendall Autotransformer Replacement | Replace the existing 345/138 kV 336 MVA autotransformer with an 800 MVA autotransformer at the Kendall Substation (7152). | [5 empty] | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2012-06-01 | 2011-11-17 | 345 | 0 | 0 | 800 | 0 | KENDALL |  | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | CREZ Default project assigned to LCRA TSC
10TPIT0064 | Parkway(7611) - Schertz(7610) Transmission Line | Replace existing 795 "Drake" circuit with 680T19 ACCR composite conductor, new line rating = 1491 amps | COMPLETED | Parkway | Schertz | Complete |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2011-11-17 | 2011-11-18 | 138 | 2.8 | 0 | 0 | 0 | GUADALUPE | GUADALUPE | Tier 4 |  |  |  | See Project Title | ? | ?
11TPIT0042 | Gila to Highway 9 138kV, Re-connect existing Highway 9 to Nueces Bay into Gila, | Expand Nueces Bay 138 kV system for interconnection of 700 MW of new generation | IN-SERVICE | Highway 9 | Gila | Planned | 399 - 0649 | AEP/TCC | Michael Glueck 918-599-2653 | 3255 | 2011-11-18 | 2011-11-18 | 138 | 0 | 3.29 | 0 | 0 | NUECES | NUECES | Tier 1 | 2009-03-17 | 2009-10-09 | 2009-12-01 |  | Y | N |  | Comment: Distribution banks converted to 138kV
11TPIT0058 | Paducah Clare to Paducah City, Rebuild 69 kV line | Rebuild 69 kV line from Matador to Paducah Clare to Paducah City as 69/138 kV double circuit capable with 795 ACSS | IN-SERVICE | Paducah Clare | Paducah City | In-Service | 454 - 0652 | AEP/ETT | Eric Scott 918-599-2653 | 2378 | 2011-11-22 | 2011-11-22 | 69 | 0 | 0.68 | 0 | 0 | COTTLE | COTTLE | Tier 4 | 2010-05-03 |  |  |  | Y | N
11TPIT0165 | Wirtz (7107) - Johnson City (7516) | Rebuild Johnson City 69kV bus to single bus, replacing switches (512 and 542) with breakers (22150 and 22160). Move T-313 from Wirtz breaker (1430) to Wirtz breaker (1690). Close loop Wirtz (1690)-Johnson City(22150)-Mountain Top (1990). |  | Wirtz | Johnson City |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-10-30 | 2011-11-23 | 69 | 0 | 0 | 0 | 0 | BURNET | Blanco | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
12TPIT0089 | Knox to Knox | Rebuild Knox to Knox 69 kV line with 795 ACSR |  | Knox | Knox | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10032 | 2011-12-07 | 2011-11-30 | 69 | 0 | 3.67 | 0 | 0 | HASKELL | KNOX | Tier 4 |  |  |  | 765, 6114 | Y | N
11TPIT0052 | Riley, Build a new Riley to Oklaunion 345 kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | IN-SERVICE | Riley | Oklaunion | Under Construction | 467 - 0668 | AEP/ETT | Paul Hassink 918-599-2653 | 2351 | 2011-11-30 | 2011-11-30 | 345 | 3.5 | 0 | 0 | 0 | WILBARGER | WILBARGER | CREZ Modified |  |  |  |  | Y | N
12TPIT0076 | Oklaunion, Expand 345 kV switch station for the addition of the new Oklaunion to Riley circuit #2 | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 | IN-SERVICE |  |  | Under Construction | 501 - 0708 | AEP/ETT | Paul Hassink 918-599-2653 | 2452 | 2011-11-30 | 2011-11-30 | 345 | 0 | 0 | 0 | 0 | WILBARGER |  | CREZ Modified |  |  |  |  | Y | N
08TPIT0133 | Rocksprings Station: Install 69 KV Ring Bus | Rocksprings : Install 5-69 KV Breaker Ring Bus and 3.6 MVAR Cap Bank | IN-SERVICE (Updated TPIT after it was posted - 2/16 | Rocksprings |  | Under Constuction | 377 - 0552 | AEP/ETT | Eric Scott 918-599-2653 | 3019 | 2011-12-01 | 2011-12-01 | 69 | 0 | 0 | 0 | 3.6 | EDWARDS |  | Tier 4 |  |  |  |  | N | N
09TPIT0214 | Alberta Switch 138kV Substation | Build new 138kV Switching Station |  |  |  | Under Construction | 07TPIT7777 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-12-01 | 2011-12-01 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8759 | Y | N
11TPIT0110a | Alberta Switch-Valverde | Rebuild 4.05 Miles of 138kV line from Alberta Switch to Valverde Substation to AEP Weslaco Switch | Project Speedup due to delay with Alberta Switch-Doedyns | Alberta Switch | Valverde | Planned | 07TPIT7777 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-12-31 | 2011-12-01 | 138 | 0 | 4.05 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8759-8769-8354 | Y | N |  | Divided Project into two projects. Associated with Valverde to AEP Weslaco Switch
10TPIT0103 | Bowman Switch terminal equipment | Replace terminal equipment on line to Fisher Road. |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C032-WA | 2011-12-01 | 2011-12-01 | 345 | 0 | 0 | 0 | 0 | ARCHER |  | CREZ |  |  |  | 1422, 1425 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0104 | Bowman Switch terminal equipment | Replace terminal equipment on line to Graham. |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C070-WA | 2011-12-01 | 2011-12-01 | 345 | 0 | 0 | 0 | 0 | ARCHER |  | CREZ |  |  |  | 1422, 1430 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0061 | Bowman - Riley (Oklaunion) 345 kV line (Oncor Electric Delivery portion) | Construct double-circuit 345 kV line |  | Bowman | Riley | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C073-E | 2011-12-01 | 2011-12-01 | 345 | 85.2 | 0 | 0 | 0 | WILBARGER | ARCHER | CREZ |  |  |  | 1422, 6101 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0062 | Sweetwater East - Central Bluff 345 kV line | Construct double-circuit 345 kV line |  | Sweetwater East | Central Bluff | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C058-E | 2011-12-01 | 2011-12-01 | 345 | 71.6 | 0 | 0 | 0 | NOLAN | NOLAN | CREZ |  |  |  | 11420, 11406 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0063 | Central Bluff Switch | Construct 345 kV switching station with 345/138 kV autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C074-E | 2011-12-01 | 2011-12-01 | 345 | 0 | 0 | 600 | -75 | NOLAN |  | CREZ |  |  |  | 11406 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0064 | Central Bluff - Bluff Creek 345 kV line | Construct double-circuit 345 kV line with one circuit |  | Central Bluff | Bluff Creek | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C075-E | 2011-12-01 | 2011-12-01 | 345 | 19 | 0 | 0 | 0 | NOLAN | TAYLOR | CREZ |  |  |  | 11406, 60040 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0070 | Dermott Switch (Central B) - Scurry County South Switch (Central A) 345 kV line | Construct double-circuit 345 kV line |  | Dermott Switch | Scurry County South Switch | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1009-E | 2011-12-01 | 2011-12-01 | 345 | 65.4 | 0 | 0 | 0 | SCURRY | SCURRY | CREZ |  |  |  | 11305, 11318 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0098 | Bowman Switch | Rebuild switching station |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C009-E | 2011-12-01 | 2011-12-01 | 345 | 0 | 0 | 0 | 0 | ARCHER |  | CREZ |  |  |  | 1422 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0176 | TH Wharton - TH Wharton (tap) Ckt. 81 | Upgrade substation equipment at TH Wharton to increase thermal ratings. | IN-SERVICE |  |  | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-12-31 | 2011-12-03 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 45515, 45511 | Y | N
11TPIT0168 | Elroy | Add Elroy station (7209) to LCRA TSC's Colton (7208) to Wolf Lane (7212) 138 kV transmission line. |  | Elroy | Colton/Wolf Lane | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-03-01 | 2011-12-09 | 138 | 0 | 0 | 0 | 0 | TRAVIS |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
12TPIT0069 | Barney Davis to Alazan 138 kV line rebuild | Barney Davis to Nelson Sharpe 138 kV line rebuild 1st circuit on a double circuit capable structure | IN-SERVICE | Barney Davis | Alazan | Under Construction | 400 - 0647 | AEP/ETT/TCC | Michael Glueck 918-599-2653 | 3332 | 2011-12-09 | 2011-12-09 | 138 | 0 | 12.24 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y | N
12TPIT0032 | Fort Mason to Pitsburg | Rebuild and convert the capacity of the existing transmission line (approximately 31 miles) between the LCRA TSC Fort Mason (76390) and Pitsburg (7120) stations. The new transmission line will consist of 1x795 ACSR Drake conductor to provide a thermal rating of 220 MVA. |  | Fort Mason | Pitsburg | Under construction |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-12-01 | 2011-12-14 | 138 | 0 | 31 | 0 | 0 | MASON | LLANO | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N
11TPIT0155 | Pearsall Capacitor Bank | Install 60 MVAR Capacitor and a new 138 kV circuit breaker at the Pearsall Substation. Replace Existing Substation Equipment at Pearsall to remove MLSE on the Leon Creek to Pearsall and the Medina Base to Pearsall 138kV transmission lines. | [5 empty] | CPS | S: Juan Salinas | S-0605 | 2011-12-15 | 2011-12-15 | 138 | 0 | 0 | 0 | 60 | BEXAR | BEXAR | Tier 4 |  |  |  | 5335 5260 5305 | Y | N |  | There are no transformers associated with this project
11TPIT0144 | Rough Canyon to Hamilton Road, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE | Rough Canyon | Hamilton Road | Planned | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2440 | 2011-12-20 | 2011-12-20 | 69 | 0 | 12.4 | 0 | 0 | VALVERDE | VALVERDE | CREZ Modified |  |  |  |  | Y | N
12TPIT0117 | Temple Switch shunt reactors | Install shunt reactors 345/138 kV autotransformer tertiary |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R756-WAC | 2011-12-01 | 2011-12-28 | 138 | 0 | 0 | 0 | -37.5 | BELL |  | Tier 4 |  |  |  | 3415 | Y | N
11TPIT0060 | Lamesa - Ackerly Vealmoor 69 kV line | Rebuild existing 69 kV line |  | Lamesa | Ackerly Vealmoor | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8005-WAC | 2011-12-01 | 2011-12-29 | 69 | 0 | 21.5 | 0 | 0 | DAWSON | HOWARD | Tier 4 |  |  | 2009-07-21 | 1164, 1364, 1362, 1363, 1356 | Y | N | 2009-R3 | ERCOT BOD approved this project as part of the RMR exit strategy for Permian Basin generation. Ackerly Vealmoor - Sparenburg section was completed in 5/2011, and Sparenburg - Lamesa section will be completed in 12/2011.
10TPIT0090 | Copperas Cove - Killeen Clark Road Tap - Killeen Fort Hood West 138 kV line upgrade | Upgrade existing 138 kV line |  | Copperas Cove | Killeen Fort Hood West | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R717-WAC | 2011-12-01 | 2011-12-29 | 138 | 0 | 5 | 0 | 0 | CORYELL | BELL | Tier 4 |  |  |  | 3630, 3620, 3629 | Y | N
12TPIT0122 | Killeen Switch Shunt Reactors | Install shunt reactors on the tertiary of the 345/138 kV autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R757-WAC | 2012-01-01 | 2011-12-29 | 138 | 0 | 0 | 0 | -75.0 | BELL |  | Tier 4 |  |  |  | 3423 | Y | N
12TPIT0091 | Garvey Road 345 kV Switching Station | Construct new switching station |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R905-WAC | 2011-12-01 | 2011-12-29 | 345 | 0 | 0 | 0 | 0 | ARCHER | ARCHER | Tier 4 |  |  |  | 1702 | Y | N
10TPIT0037 | Bell County East - TNP One 345 kV line and Bell County East Switching Station (Oncor Electric Delivery part of project) | Install 345 kV switching station and construct a double-circuit 345 kV line |  | Bell County East | TNP One | Completed | R704A, R705 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R494-WAC | 2011-12-01 | 2011-12-30 | 345 | 82.6 | 0 | 0 | 0 | ROBERTSON | BELL | Tier 1 | 2006-11-30 |  | 2007-07-01 | 39950, 3687 | Y | N |  | Bell County East Switching Station was completed in 5/2011.
11TPIT0175 | Rocksprings - PEC Rocksprings: Constrcut 69 kV line | Rocksprings : Install 5-69 KV Breaker Ring Bus and 3.6 MVAR Cap Bank | IN-SERVICE (Updated TPIT after it was posted - 2/16 | Rocksprings | PEC Rocksprings | Under Construction | 377 - 0552 | AEP/ETT | Eric Scott 918-599-2653 | 3203 | 2011-12-31 | 2011-12-31 | 69 | 0 | 0 | 0 | 0 | EDWARDS | EDWARDS | Tier 4 |  |  |  |  | Y | N
09TPIT0031 | Circuit 972 (McNeil to Howard Lane) Reconductor | Reconductor the last span of the Ckt 972 (McNeil to Howard Lane) going into McNeil substation with bundled 795 ACSR Drake conductor. | COMPLETE | McNeil Substation | Howard Lane Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P085 | 2012-01-01 | 2012-01-01 | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9079, 9217 | Y | N
11TPIT0158 | Mason Creek Sub 138kv breakers | Add 138kv breakers |  | Mason Creek Sub | Mason Creek Sub | Complete |  | Bandera Electric | David Baker 830-796-6084 | 201491 | 2011-12-01 | 2012-01-12 | 138 | 0 | 0 | 0 | 0 | Bandera |  | Tier 4 | N/A | N/A | N/A |  | N | N |  | System reliability & Maintenance
10TPIT0088 | Ft. Lancaster to Illinois #4, Convert 69 KV to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE | Ft. Lancaster | Illinois #4 | Planned | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2363 | 2012-01-19 | 2012-01-19 | 138 | 0 | 17.21 | 0 | 0 | PECOS | CROCKETT | CREZ Modified |  |  |  |  | Y | N
10TPIT0089 | Illinois #4 to Hamilton Rd., Convert 69 kV to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE | Illinois #4 | Hamilton Road | Planned | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2364 | 2012-01-19 | 2012-01-19 | 138 | 0 | 97.63 | 0 | 0 | CROCKETT | VALVERDE | CREZ Modified |  |  |  |  | Y | Y
12TPIT0034 | Illinois #4, Build new three breaker ring bus & add 138/69 kV auto | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE | Illinois #4 |  | Under Construction | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2365 | 2012-01-19 | 2012-01-19 | 138 | 0 | 0 | 83 | 0 | CROCKETT |  | CREZ Modified |  |  |  |  | Y | N
12TPIT0064 | Rough Canyon, Convert station to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE |  |  | Planned | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2433 | 2012-01-19 | 2012-01-19 | 138 | 0 | 0 | 0 | 0 | VALVERDE |  | CREZ Modified |  |  |  |  | Y | N
12TPIT0065 | Comstock, Convert station to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE |  |  | Planned | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2401 | 2012-01-19 | 2012-01-19 | 138 | 0 | 0 | 0 | 0 | VALVERDE |  | CREZ Modified |  |  |  |  | Y | N
10TPIT0039 | East Bell County - TNP One 345 kV Line Project | Expansion of 345 kV Switchyard at TNP One associated with East Bell County TNP One 345 kV Line Project |  | TNP One | TNP One | Completed | 10TPIT0037 | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2011-12-11 | 2012-01-20 | 345 | 0 | 0 | 0 | 0 | ROBERTSON | ROBERTSON | Tier 4 | 2006-11-30 | 2007-01-02 |  | 39950 | Y | N | See Oncor Electric Delivery Entry for this project, 10TPIT0037
11TPIT0154 | Montell: Construct 69 kV Substation Including Motor Operated Switches with Interrupters | Add new 69 kV Montell Substation for STEC distribution interconnection | IN-SERVICE |  |  | Under Constuction | 498 - 0703 | AEP/TCC | Kenneth 'Rich' Haley 918-599-2653 | 3419 | 2012-01-23 | 2012-01-23 | 69 | 0 | 0 | 0 | 0.0 | UVALDE |  | Tier 4 |  |  |  | 8230 | N | N |  | $2,272,000 (AEP) $200,000 (STEC) MODELING TO BE ADDED TO CASES WITH APR 2011 TPIT UPDATES
11TPIT0089 | Cottonwood Road 69 kV Switch | Construct new switching station |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R588-WAC | 2011-12-01 | 2012-01-30 | 69 | 0 | 0 | 0 | 0 | ARCHER |  | Tier 4 |  |  |  | 1605 | Y | N
09TPIT0054 | LA Heights - 138kV Breaker Installations | Install line breakers between LA Heights bus A & B. | Delayed due to Budget Constraints |  |  |  | T-0156 | CPS | PM: Bruce Raney | S-0308 | 2012-02-01 | 2012-02-01 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5285 5286 | Y | N |  | This is a line terminal addition, there are no additional tranformer capacity or transmission circuit miles associated with this project
11TPIT0164 | McNeil 138kV Bus Upgrade | Upgrade the pin cap and bus support insulators for fault duty requirements. A minor topology change will be made within the station. | COMPLETE | McNeil Substation | McNeil Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | 1461 | 2012-03-01 | 2012-02-01 | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9076, 9077, 9079 | N | N
14TPIT0018 | Upgrade North Alvin-Hastings | This project will rebuild North Alvin to Hastings transmission line |  | North Alvin | Hastings | Completed |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE07113 | 2012-05-31 | 2012-02-01 | 138 | 0 | 1.93 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 39010, 39015 | Y | N
12TPIT0095a | South Lane - West Columbia Ckts. 04 & 60 | Upgrade 138kV Ckt.60 South Lane - TXGULF to increase thermal ratings. | IN-SERVICE | South Lane | TXGULF | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-07-31 | 2012-02-03 | 138 | 0 | 10.52 | 0 | 0 | WHARTON | WHARTON | Tier 3 | 2011-02-02 | 2011-02-24 | N/A | 43190, 43012, 43340 | Y | N |  | Project is part of the 2011 ERCOT 5-Year Plan.
11TPIT0086 | Bruni 138kV Station: Install breaker | Construct new 138kV La Quinta Substation to directly interconnect 150MW Cedro Hill Wind Farm | IN-SERVICE |  |  | Under Constuction | 398 - 0587 | AEP/TCC | Tommy Vannoy 918-599-2653 | 3354 | 2012-02-06 | 2012-02-06 | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB | Tier 4 |  |  |  |  | Y | N
11TPIT0140 | Convert Kirby Substation into a double tap substation | Reconfigure Kirby substation. Kirby will loop through Ckt.37 (existing) and tap from Ckt.90 HOC to Garrott (new). | IN-SERVICE | Kirby | HO Clarke/ Garrott | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-06-30 | 2012-02-08 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47320, 47321, 47322 | Y | N |  | No autotransformer capacity to be added.
11TPIT0041 | Gila 138kV: Construct new 138 kV, 6 breaker Ring Bus | Expand Nueces Bay 138 kV system for interconnection of 700 MW of new generation | IN-SERVICE |  |  | Under Construction | 399 - 0650 | AEP/ETT/TCC | Michael Glueck 918-599-2653 | 3242 | 2012-02-10 | 2012-02-10 | 138 | 0 | 0 | 0 | 57.6 | NUECES |  | Tier 1 | 2009-03-16 | 2009-10-09 | 2009-12-01 |  | Y | N
08TPIT0092 | North Victoria to Victoria: Reconductor 69 kV Line | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. | IN-SERVICE | North Victoria | Victoria Power Plant | Planned | 389 - 0567 | AEP/TCC | Dave Goetz 918-599-2653 | 15 | 2012-02-15 | 2012-02-15 | 69 | 0 | 3.1 | 0 | 0 | VICTORIA | VICTORIA | Tier 4 |  |  |  |  | Y | N
12TPIT0086 | Hamilton Road, expand station | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE |  |  | Under Construction | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2368 | 2012-02-16 | 2012-02-16 | 138 | 0 | 0 | 0 | 0 | VALVERDE |  | CREZ Modified |  |  |  |  | Y | N
05TPIT0079 | Port Aransas: add 3 breaker 69 kv bus and 1-14.4 MVAR 69 kV cap bank | Add 3 breaker 69 kV ring bus on high side and install 1-14.4 MVAR capacitor bank at Port Aransas substation | IN-SERVICE |  |  | Under Construction | 029 - 0123 | AEP/TCC/ETT/LCRA | Michael Glueck 918-599-2653 | 1136 | 2012-02-17 | 2012-02-17 | 69 | 0 | 0 | 0 | 14.4 | ARANSAS |  | Tier 4 |  |  |  |  | Y | N
10TPIT0045 | Mauermann Rd - New 138kV Substation | Loop new 138kV substation into the existing VH Braunig to Toyota line | Delayed due to resource allocation | VH Braunig | Toyota | Planned | T-0087 | CPS | PM: Hector Torres | S-0399 | 2012-02-28 | 2012-02-22 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5297 | Y | N |  | There are no transformers associated with this project
12TPIT0105 | Elroy 138kV Unit Transformer | Establish one 30MVA unit transformer at the LCRA owned 138kV Elroy substation | COMPLETE | Elroy Substation | Elroy Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | 3230_117_2943 3230_117_4943 | 2012-01-01 | 2012-02-23 | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9198 | Y | N |  | Will add to the base case in this TPIT updates.
10TPIT0080 | Olney to South Bend Switch Rebuild | Rebuild Olney to South Bend Switch with 959ACSS |  | Olney | South Bend Switch | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 08011 | 2012-12-15 | 2012-02-28 | 69 | 0 | 24 | 0.0 | 0 | YOUNG | YOUNG | Tier 4 |  |  |  | 788, 795 | Y | N
11TPIT0167 | Lyssy: Construct 138 kV Facilities | Construct Lyssy 138 kV Substation |  | Kenedy Switch Station | Pleasanton | Planned | 497 - 0702 | AEP/TCC/ STEC | Kenneth Haley 918-599-2653 | 3413 | 2012-02-28 | 2012-02-28 | 138 | 0 | 0 | 0 | 0 | KARNES |  | Tier 4 |  |  |  | 8193 | Y | N |  | $3,719,200 (AEP) $200,000 (STEC)
12TPIT0101 | Knippa 69 kV Substation Upgrade | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW | IN-SERVICE | Uvalde | Sabinal | Under Constuction | 291 - 0046 | AEP/TCC | Terry Weeks (AEP) 918-599-2653 | 1523 | 2012-02-29 | 2012-02-29 | 69 | 0 | 0 | 0 | 0 | UVALDE | MEDINA | Tier 1 |  |  |  |  | Y | N
12TPIT0063 | Rebuild Heights-Lamarque 69kV line | This project will rebuild the 69 kV path from Heights to LaMarque. This includes lines 69-H1, 69-H2, and 69-J. Total length of line is approximately 2.8 miles. This project also will add to the system hardening efforts taken after Hurricane Ike in September of 2008. |  | Heights | LaMarque | Completed |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE07610 | 2012-03-01 | 2012-03-01 | 69 | 0 | 2.8 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 38770, 39280, 39310, 39340 | N | N
06TPIT0112 | Lakeway second circuit from LCRA tap to the substation. | Construct 0.88 mile long 138kV circuit from Lakeway substation to the LCRA tap between Marshall Ford and Bee Creek substation. | COMPLETE | Lakeway Substation | Lakeway Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | 3230_117_4255 | 2012-03-01 | 2012-03-01 | 138 | 0.88 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 7349, 9235 | Y | N
10TPIT0018 | Austin Ranch - Colony 138 kV line | Upgrade existing 138 kV line |  | Austin Ranch | Colony | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3004-WAC | 2012-05-01 | 2012-03-01 | 138 | 0 | 4.6 | 0 | 0 | DENTON | COLLIN | Tier 4 |  |  |  | 2518, 2378, 12518 | Y | N | 2009-R16
10TPIT0122 | Formosa: Interconnect New Generation at Formosa Substation | Interconnect Generation at Formosa Substation | IN-SERVICE | Formosa |  | Planned | 437 - 0645 | AEP/TCC | Dave Goetz 918-599-2653 | 3333 | 2012-03-01 | 2012-03-01 | 138 | 0 | 0 | 0 | 0 | CALHOUN | CALHOUN | Tier 4 |  |  |  |  | Y | N |  | Project schedule date delayed based on customer's input.
11TPIT0129 | Pilot Grove - New Substation | Construct a new 138-26.18KV, 40 MVA x two, redundant backup substation | COMPLETED | Pilot Grove | Sweet Home/Yoakum | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-03-06 | 2012-03-06 | 138 | 0 | 0 | 0 | 0 | LAVACA |  | Tier 4 |  |  |  | See Project Title | Y | N
12TPIT0133 | PH Robinson Autotransformer A3 | Install temporary 600MVA Autotransformer A3 at PH Robinson | IN-SERVICE |  |  | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-03-31 | 2012-03-18 | 345 | 0 | 0 | 600 | 0 | GALVESTON |  | Tier 4 |  |  |  | 42000, 42010, 49049 | Y | N |  | EPRI sponsored autotransformer project
10TPIT0011 | Olney to Lake Kemp Switch Rebuild | Rebuild existing Olney to Lake Kemp Switch 69kv line |  | Olney | Lake Kemp Switch | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 05007 | 2012-03-20 | 2012-03-21 | 69 | 0 | 29 | 0 | 0 | YOUNG | BAYLOR | Tier 3 | 2011-11-11 | 2011-12-27 | N/A | 788781784782 | Y | N
11TPIT0096 | Elm Mott Switch circuit breaker | Install 345 kV circuit breaker on line to Tradinghouse |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R737-WAC | 2012-05-01 | 2012-04-01 | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3406 | Y | N
11TPIT0072b | Garrott - Midtown - Polk Ckt. 90 | Upgrade 138 kV underground Ckt. 90 Midtown to Polk by building additional underground cable parallel to existing cable. | IN-SERVICE | Midtown | Polk | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-04-30 | 2012-04-03 | 138 | 0 | 1.04 | 0 | 0 | HARRIS | HARRIS | Tier 3 | 2009-07-01 | 2009-07-01 | N/A | 47705, 47730 | Y | N | See project 11TPIT0072a for total project cost estimate | No transformer capacity to be added.
12TPIT0103 | Las Pulgas: Construct 138 kV Tap Station for WF Interconnect | Construct a 138 kV tap substation for the Magic Valley WF Interconnect, cut the Raymondville to Rio Hondo 138 kV line into the tap station | *Added "Terminal From" information *IN-SERVICE *Updated Cost & Sched | Las Pulgas |  | INSV | 490 - 0691 | AEP/TCC | Teresa Trotman 918-599-2653 | 3371 | 2012-04-30 | 2012-04-10 | 138 | 0 | 0 | 0 | 0 | WILLACY |  | Tier 4 |  |  |  | 80309 | Y | N
12TPIT0116 | Scarsdale 138kV Substation | Build new 138kV Scarsdale customer-owned substation. Loop through Ckt.92 PH Robinson to Garden Villas. | IN-SERVICE | Scarscale | El Dorado/ South Houston | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-04-30 | 2012-04-20 | 138 | 0.9 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 43610, 42652, 43173 | Y | N
10TPIT0084 | Magruder: Add 1-14.4 MVAR 69 kV Cap Bank | Add capacitors in Victoria area at the McGruder Victoria plant and Lone Tree | IN-SERVICE | Magruder |  | Planned | 389 - 0667 | AEP/ETT | Dave Goetz 918-599-2653 | 3374 | 2012-05-31 | 2012-04-23 | 69 | 0 | 0 | 0 | 14.4 | VICTORIA |  | Tier 4 | 0 | 0 |  |  | Y | N
06TPIT0057 | Magruder: Add 138/69 kV, 187 MVA, auto, 3 breaker 138 kV ringbus, 1 69 kV lowside breaker | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. | IN-SERVICE | Magruder |  | Planned | 389 - 0567 | AEP/ETT/TCC | Dave Goetz 918-599-2653 | 3375 | 2012-05-31 | 2012-04-23 | 138 | 0 | 0 | 187 | 0 | VICTORIA |  | Tier 4 |  |  |  |  | Y | N
11TPIT0072a | Garrott - Midtown - Polk Ckt. 90 | Upgrade 138 kV underground Ckt. 90 Garrott to Midtown by building additional underground cable parallel to existing cable. | IN-SERVICE | Garrott | Midtown | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-04-30 | 2012-04-26 | 138 | 0 | 1.47 | 0 | 0 | HARRIS | HARRIS | Tier 3 | 2009-07-01 | 2009-07-01 | N/A | 47660, 47705 | Y | N |  | No transformer capacity to be added.
11TPIT0057 | Matador to Paducah Clare, Rebuild 69 kV line | Rebuild 69 kV line from Matador to Paducah Clare to Paducah City as 69/138 kV double circuit capable with 795 ACSS | IN-SERVICE | Matador | Paducah Clare | Under Construction | 454 - 0652 | AEP/ETT | Eric Scott 918-599-2653 | 2328 | 2012-04-30 | 2012-04-30 | 69 | 0 | 31.2 | 0 | 0 | MOTLEY | COTTLE | Tier 3 | 2010-05-01 | 2010-06-01 | N/A |  | Y | N
12TPIT0099 | Knippa to Sabinal 69 kV line, transfer to new 138/69 double circuit line | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW | IN-SERVICE | Knippa | Sabinal | IN-SERVICE | 291 - 0046 | AEP/TCC | Terry Weeks (AEP) 918-599-2664 | 1521 | 2012-04-30 | 2012-04-30 | 69 | 0 | 8.5 | 0 | 0 | UVALDE | MEDINA | Tier 4 |  |  |  |  | Y | N
12TPIT0047a | Zenith - Kluge and Zenith - Addicks: Reconfigure and Upgrade Circuits 09, 21, & 76. | Reconfigure circuits to form Zenith to Gertie tap to Cy Fair tap to Kluge Ckt.09. | IN-SERVICE | ZENITH | KLUGE | COMPLETE | 12TPIT0046 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-05-31 | 2012-04-30 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 2 | 2009-02-06 | 2009-09-01 | N/A | 44910, 45801, 45711, 45952 | Y | N |  | Part of the 2012 Northwest Houston Reliability Project
12TPIT0047b | Zenith - Kluge and Zenith - Addicks: Reconfigure and Upgrade Circuits 09, 21, & 76. | Reconfigure circuits to form Zenith to Gertie tap to Satsuma tap to Addicks Ckt.76. Upgrade portion of Ckt.76 to increase thermal ratings. | IN-SERVICE | ZENITH | ADDICKS | COMPLETE | 12TPIT0046 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-05-31 | 2012-04-30 | 138 | 0 | 1.49 | 0 | 0 | HARRIS | HARRIS | Tier 2 | 2009-02-06 | 2009-09-01 | N/A | 44910, 45802, 46302, 45610 | Y | N | Cost included in main project | Part of the 2012 Northwest Houston Reliability Project
12TPIT0047c | Zenith - Kluge and Zenith - Addicks: Reconfigure and Upgrade Circuits 09, 21, & 76. | Reconfigure circuits to form Camron to Cy Fair tap to Kluge Ckt.21. Upgrade portion of Ckt.21 to increase thermal ratings. | IN-SERVICE | CAMRON | KLUGE | COMPLETE | 12TPIT0046 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-05-31 | 2012-04-30 | 138 | 0 | 4.62 | 0 | 0 | HARRIS | HARRIS | Tier 2 | 2009-02-06 | 2009-09-01 | N/A | 45700, 45712, 45952 | Y | N | Cost included in main project | Part of the 2012 Northwest Houston Reliability Project
12TPIT0166 | Aldine Cap Bank | Install 7.2MVAR capacitor bank at Aldine substation. | IN-SERVICE |  |  | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-05-31 | 2012-04-30 | 138 | 0 | 0 | 0 | 7.2 | HARRIS |  | Tier 4 |  |  |  | 45640 | Y | N
12TPIT0046 | Zenith 138kV | Expand Zenith substation with addition of 345/138kV 800MVA Autotransformer. Build a new 138kV double circuit line from Zenith to Gertie corner. | IN-SERVICE | ZENITH | Gertie | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-05-31 | 2012-04-30 | 345 | 10 | 0 | 800 | 0 | HARRIS | HARRIS | Tier 2 | 2009-02-06 | 2009-09-01 | N/A | 44900, 44910, 45801, 45802 | Y | N |  | Part of the 2012 Northwest Houston Reliability Project
08TPIT0034 | McNeil to Summit Reconductor | The proposal of adding the 2nd ckt from McNeil to Summit in not feasible due to right of way issues. New proposal calls for the upgrading of the original circuit to 3000Amp. | COMPLETE | McNeil Substation | Summit Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P351 PLAN_117_P372 PLAN_117_P373 | 2012-05-01 | 2012-05-01 | 138 | 2 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9079, 9279 | Y
09TPIT0120 | Sun Switch - Golden - Sacroc 138 kV line | Rebuild 138 kV line |  | Sun Switch | Sacroc | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R807-E | 2012-05-01 | 2012-05-01 | 138 | 0 | 12.8 | 0 | 0 | SCURRY | SCURRY | Tier 4 |  |  |  | 1064, 1067, 1311 | Y | N
10TPIT0024 | Stoney Ridge 138kV substation (original title is Linda Vista substation) | Establish new 138kV Stoney Ridge substation and install (2) 30MVA transformers. The substation will cut into Ckt 962 (Garfield to Onion Ck). | COMPLETE | Stoney Ridge Substation | Stoney Ridge Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | 3230_117_2894 3230_117_4894 | 2012-05-01 | 2012-05-01 | 138 | 0.1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9237 | Y | N
12TPIT0118 | Elkton - Tyler Bullard Rd - S Tyler 138 kV line | Upgrade existing 138 kV line |  | Elkton | S Tyler | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6008-WAC | 2012-05-01 | 2012-05-01 | 138 | 0 | 2.8 | 0 | 0 | SMITH | SMITH | Tier 4 |  |  |  | 3106, 3219,3218 | Y | N
12TPIT0161 | East Mesquite Switch terminal equipment | Upgrade terminal equipment at East Mesquite Switch in the East Mesquite Switch - Seagoville Switch 138 kV line |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4096A, B &C -WAC | 2012-05-01 | 2012-05-01 | 138 | 0 | 0 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 2756 | Y | N
12TPIT0179 | Lake Hubbard capacitors | Install 138 kV capacitors |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4100-WAC | 2012-05-01 | 2012-05-01 | 138 | 0 | 0 | 0 | 36.8 | DALLAS |  | Tier 4 |  |  |  | 2401, 2402 | Y | N
12TPIT0207 | Handley - Hurst 138 kV line | Upgrade existing 138 kV line |  | Handley | Hurst | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2012-05-01 | 2012-05-01 | 138 | 0 | 18.7 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1950, 2110, 2109, 1951 | Y | N
10TPIT0109 | Burwick Switching Station | Construct new switching station to connect a new wind farm |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R583-WAC | 2012-05-01 | 2012-05-01 | 345 | 0 | 0 | 0 | 0 | JACK |  | Tier 4 |  |  |  | 1456 | Y | N
12TPIT0067 | Anna Switch 345/138 kV autotransformer replacement | Replace #1 autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3085-WAC | 2012-05-01 | 2012-05-01 | 345 | 0 | 0 | 600 | 0 | COLLIN |  | Tier 4 |  |  |  | 2373, 2374 | Y | N
12TPIT0106 | Southeast Nacogdoches 345/138 kV autotransformer | Replace existing 345/138 kV autotransformer with larger autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6007-WAC | 2012-05-01 | 2012-05-01 | 345 | 0 | 0 | 600 | 0 | NACOGDOCHES |  | Tier 2 | 2010-11-01 | 2010-12-01 |  | 3119, 3120 | Y | N
07TPIT0251 | Victoria Power Plant: Install 1-28.8 MVAR 69 kV Cap Bank | Add capacitors in Victoria area at the McGruder Victoria plant and Lone Tree | IN-SERVICE | Victoria Power Plant |  | Planned | 389 - 0667 | AEP/TCC | Dave Goetz 918-599-2653 | 2243 | 2012-03-01 | 2012-05-04 | 69 | 0 | 0 | 0 | 28.8 | VICTORIA |  | Tier 4 |  |  |  |  | Y | N
12TPIT0173 | Austin to Kirby Rebuild - 138 kV Transmission Line | Remove the existing bifrucation line between Austin2 and Kirby2 and rebuild with a single 138 kV transmission line |  | Austin | Kirby |  |  | CPS | T: Adam Marin | T-0182 | 2012-05-04 | 2012-05-04 | 138 | 0 | 2.75 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5005 5006 5249 5250 | Y | N |  | There are no transformers associated with this project
09TPIT0132 | Bonnie Brae Substation Construction | Construct new 50MVA, 69kV to 13.2kV substation adjacent to DME's 69kV Hickory to North Lakes transmission line 1/4 mile south of US 380 | On schedule |  |  | Complete | 07TPIT0097 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602099 | 2012-05-15 | 2012-05-12 | 69 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 905 | Y | N
12TPIT0163 | Line Ratings Project - Ball Park to Deely and Deely to Laredo - 138kV substation equipment upgrade | Upgrade substation equipment at Deely and Laredo to remove existing MLSE on the Deely to Laredo and the Ball Park to Laredo 138kV line |  | Deely | Ball Park/Laredo |  |  | CPS | Blake Williams | S-0700 | 2012-05-31 | 2012-05-17 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5011 5110 | Y | N |  | There are no transformers associated with this project
12TPIT0177 | Wirtz Autotransformer Replacement | Replace the existing T-1 autotransformer (comprised of three single phase units) at the Wirtz Substation with a three phase 40 MVA 138/69-kV autotransformer (7104 - 7107 -7110) | [5 empty] | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2012-06-01 | 2012-05-18 | 138 | 0 | 0 | 40 | 0 | BURNET |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
10TPIT0079 | Morris Sheppard to Oran Rebuild | Rebuild Morris Sheppard to Oran with 959ACSS | row issues | Morris Sheppard | Oran | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 07018 | 2012-05-15 | 2012-05-21 | 69 | 0 | 18.4 | 0 | 0 | PALO PINTO | PALO PINTO | Tier 4 |  |  |  | 343785 | Y | N
12TPIT0096 | Pearsall auto upgrade | Upgrade the 50 MVA138/69 kV autotransformer. |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-10-01 | 2012-05-21 | 138 | 0 | 0 | 200 | 0 | FRIO |  | Tier 4 |  |  |  | 5893, 5895 | Y | N
12TPIT0100 | Uvalde to Knippa 69 kV line, tranfer to new 138/69 double circuit line | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW | IN-SERVICE | Uvalde | Knippa | IN-SERVICE | 291 - 0046 | AEP/TCC | Terry Weeks AEP) 918-599-2664 | 1520 | 2012-05-31 | 2012-05-31 | 69 | 0 | 4.5 | 0 | 0 | UVALDE | MEDINA | Tier 4 |  |  |  |  | Y | N
12TPIT0113 | Mont - New Substation | Construct a new 138-26.18KV, 12/16/20 MVA on LCRA Hallettsville to Sweet Home 138 Transmission line | COMPLETED | Mont | Hallestville/Sweet Home | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-05-31 | 2012-05-31 | 138 | 0 | 0 | 0 | 0 | LAVACA |  | Tier 4 |  |  |  | See Project Title | N | N
12TPIT0018 | Bonham Switch 69 kV capacitors | Install 69 kV capacitors | Construction delays |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R556-WAC | 2012-06-18 | 2012-06-01 | 69 | 0 | 0 | 0.0 | 18.4 | FANNIN |  | Tier 4 |  |  |  | 1761 | Y | N
12TPIT0120 | Seymour 69 kV capacitors | Install 69 kV capacitors | Construction delays |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R599-WAC | 2012-06-27 | 2012-06-01 | 69 | 0 | 0 | 0.0 | 9.2 | BAYLOR |  | Tier 4 |  |  |  | 1532 | Y | N
08TPIT0107 | Leon - Flat Creek 138 kV line | Rebuild existing 138 kV line | Construction delays | Leon | Flat Creek | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R520A-E | 2012-06-28 | 2012-06-01 | 138 | 0 | 19.5 | 0.0 | 0 | EASTLAND | ERATH | Tier 4 |  |  |  | 1624, 1640 | Y | N
10TPIT0032 | Arco (TMPA) - Krugerville 138 kV line | Rebuild existing 138 kV line | Construction delays | Arco (TMPA) | Krugerville | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5129-WAC | 2012-06-29 | 2012-06-01 | 138 | 0 | 5.6 | 0.0 | 0 | DENTON | DENTON | Tier 4 |  |  | 2010-06-15 | 1994, 1993 | Y | N
11TPIT0031 | Celina SE 138 kV capacitors | Install 138 kV capacitors | Construction delays |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3066-WAC | 2012-05-21 | 2012-06-01 | 138 | 0 | 0 | 0.0 | 110.4 | COLLIN |  | Tier 4 |  |  |  | 2350 | Y | N
11TPIT0065 | Ector County North Switch (West B) - Moss 138 kV line | Construct 138 kV line with one circuit in place. |  | Ector County North Switch | Moss | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C043-E | 2012-06-01 | 2012-06-01 | 138 | 20.1 | 0 | 0.0 | 0 | ECTOR | ECTOR | CREZ |  |  |  | 11140, 1019 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0066 | Ector County North Switch (West B) | Construct 138 kV switching station |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C016-E | 2012-06-01 | 2012-06-01 | 138 | 0 | 0 | 0.0 | 0 | ECTOR |  | CREZ |  |  |  | 11140 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0100 | Moss Switch | Install 138 kV circuit breakers |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C005-E | 2012-06-01 | 2012-06-01 | 138 | 0 | 0 | 0.0 | 0 | ECTOR |  | CREZ |  |  |  | 1019 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0072 | Ferguson to Wirtz | Upgrade the 4.0 mile Ferguson (7126) -Wirtz (7104) 138kV transmission lines to 1433.6 ACSS/TW (2000 Amps) |  | Ferguson | Wirtz | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2012-06-01 | 2012-06-01 | 138 | 0 | 4 | 0 | 0 | BURNET | LLANO | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
12TPIT0107 | AMD to Pedernales New Circuit | First part of the project is to merge Circuit 1014 (Burleson to Pedernales) and Circuit 1017 (AMD to Burleson) into single 138kV circuit bypassing Burleson sub. Second part of the project is to relocate the Ckt 923 termination to the MB2. | COMPLETE | AMD Substation | Pedernales Substation | Planned |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com |  | 2012-06-01 | 2012-06-01 | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9151, 9118 | Y | N
12TPIT0125 | Westside MLSE Upgrade - 138 kV Substation Equipment Upgrade | Replace Existing Substation Equipment at Westside to remove MLSE on the Cagnon to Westside and SWRI to Westside 138kV transmission line |  | Cagnon | Westside |  |  | CPS | Blake Williams | S-0524 | 2012-06-01 | 2012-06-01 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5490 5419 5310 5150 5054 | Y | N |  | There are no transformers associated with this project
12TPIT0131 | DEPOT 138kV Substation | Construct service to new 138kV DEPOT customer-owned substation. Loop through Ckt.84 Channelview - Jacintoport | IN-SERVICE | DEPOT | Channelview/EPOTH | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-06-30 | 2012-06-01 | 138 | 0.1 | 0 | 0.0 | 0 | HARRIS |  | Tier 4 |  |  |  | 40410 | Y | N
12TPIT0193 | Graham Switch 138 kV series reactor | Install 9-ohm series reactor on line to Barton Switch |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R911-WAC | 2012-06-27 | 2012-06-01 | 138 | 0 | 0 | 0.0 | 0 | YOUNG |  | Tier 4 |  |  |  | 1596 | Y | N | 2007- E7d
13TPIT0068 | Reconfigure Helotes to Bandera - 138kV Circuit | Reconfigure Helotes - Bandera to Helotes - Grissom 138 kV circuit |  | Helotes | Grissom | Planned |  | CPS | Ballard, Cathleen | T-0203 | 2012-06-08 | 2012-06-01 | 138 | 0.5 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 2 |  |  |  | 5200 5020 5185 | Y | N |  | There are no transformers associated with this project
10TPIT0041 | Temple Switch - Salado Switch 345 kV line | Upgrade existing 345 kV line |  | Temple Switch | Salado Switch | Completed | R494 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R705-WAC | 2012-06-18 | 2012-06-01 | 345 | 0 | 15.2 | 0.0 | 0 | BELL | BELL | Tier 1 | 2006-11-01 |  | 2007-07-01 | 3414, 3699 | Y | N
11TPIT0047 | Twin Buttes - Brown 345 kV line (Oncor Electric Delivery section) | Add second 345 kV circuit |  | Twin Buttes | Brown | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C038-E | 2012-06-01 | 2012-06-01 | 345 | 0.2 | 0 | 0.0 | 0 | BROWN | BROWN | CREZ |  |  |  | 76009 | Y | N | 2007-E7f | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0043 | Bluff Creek - Brown 345 kV line | Construct double-circuit 345 kV line with one circuit |  | Bluff Creek | Brown | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C076-E | 2012-06-01 | 2012-06-01 | 345 | 86.1 | 0 | 0.0 | 0 | TAYLOR | BROWN | CREZ |  |  |  | 60040, 1444 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0044 | Central Bluff - Brown 345 kV line | Construct double-circuit 345 kV line with one circuit |  | Central Bluff | Brown | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C075-E & C076-E | 2012-06-01 | 2012-06-01 | 345 | 96.1 | 0 | 0.0 | 0 | NOLAN | BROWN | CREZ |  |  |  | 11406, 11425, 1444 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0045 | Brown Switch | Construct 345 kV switching station with shunt reactors |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C022-E | 2012-06-01 | 2012-06-01 | 345 | 0 | 0 | 0.0 | -250 | BROWN |  | CREZ |  |  |  | 1444 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0124 | Skyline to Marion - 345 kV Substation Equipment Upgrade | Replace Metering CT at Skyline and ensure a 1800 A rating and remove the existing MLSE on Skyline to Marion 345kV transmission line |  | Skyline | Marion |  |  | CPS | Blake Williams | S-0467 | 2012-06-01 | 2012-06-01 | 345 | 0 | 0 | 0 | 0 | BEXAR | GUADALUPE | Tier 4 |  |  |  | 5371 7044 | Y | N |  | There are no transformers associated with this project
12TPIT0144 | Rayburn to Nursery Rebuild | Rebuild 4/0 ACSR 69 kV to 795 ACSR. |  | Rayburn | Nursery | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-06-10 | 2012-06-10 | 69 | 0 | 3.4 | 0.0 | 0 | VICTORIA | VICTORIA | Tier 4 |  |  |  | 5500, 5504 | Y | N
12TPIT0127 | Barstow Oncor POI | Create Tap for Oncor's new Barstow station; install 10 MVAR Capacitor Bank |  |  |  | Completed |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE087AA | 2012-06-01 | 2012-06-11 | 69 | 0 | 0 | 0.0 | 10 | Ward |  | Tier 4 |  |  |  | 38150, 1086 | Y | N
10TPIT0051 | Alamito Creek to Gonzales, Replace existing 69kV line with new 69kV line | Replace Alamito Creek to Gonzales line with 795 ACSR | IN-SERVICE | Alamito Creek | Gonzales | Under Construction | 438 - 0701 | AEP/ETT | Jim Eriksen 918-599-2653 | 2170 | 2012-06-12 | 2012-06-12 | 69 | 60 | 0 | 0 | 0 | PRESIDIO | PRESIDIO | Tier 1 | 2008-03-21 | 2008-06-10 | 2008-07-15 |  | Y | N
12TPIT0139 | Gonzales, add 3.0 Mvar reactor and add 69 kV line | Replace Alamito Creek to Gonzales line with 795 ACSR | IN-SERVICE | Gonzales | 0 | Under Construction | 438 - 0701 | AEP/ETT | Jim Eriksen 918-599-2653 | 2451 | 2012-06-15 | 2012-06-15 | 69 | 0 | 0 | 0 | -3 | PRESIDIO |  | Tier 4 |  |  |  |  | Y | N
12TPIT0146 | Bonnieview Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-06-15 | 2012-06-15 | 69 | 0 | 0 | 0.0 | 9.6 | REFUGIO |  | Tier 4 |  |  |  | 5614 | Y | N
12TPIT0155 | Kenedy Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-06-15 | 2012-06-15 | 69 | 0 | 0 | 0.0 | 9.6 | KARNES |  | Tier 4 | 2011-12-16 | 2012-04-25 | N/A | 5722 | Y | N
11TPIT0115 | Reagor Springs to Purdon Rebuild | Rebuild existing Reagor Springs to Purdon 69 kV line to serve new load at Emmett. |  | Reagor Springs | Purdon | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10020 | 2012-06-15 | 2012-06-18 | 69 | 0 | 28.55 | 0.0 | 0 | ELLIS | NAVARRO | Tier 4 |  |  |  | 204, 210, 193, 194, 198 | Y | N |  | Load-serving project, necessitated by a large load addition at Emmett.
10TPIT0086 | East Abilene to Putnam, Add 138 kV to existing 69 kV line | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line | IN-SERVICE | East Abilene | Putnam | Planned | 466 - 0666 | AEP/ETT | Larry Roberson 918-599-2653 | 2346 | 2012-06-19 | 2012-06-19 | 138 | 0 | 32 | 0 | 0 | NUECES | CALLAHAN | CREZ Modified |  |  |  |  | Y | N
11TPIT0016 | GPLTemp-Shiloh 69kV line and Shiloh 138kV substation rebuild and install a 138 kV/69 kV autotransformer (75 MVA) | Line upgrade and substation rebuild with installing a 138 kV/69 kV autotransformer (75 MVA) at Shiloh substation |  |  |  | Completed |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-06-20 | 2012-06-20 | 69 | 0 | 2 | 75.0 | 0 | DALLAS |  | Tier 4 |  |  |  | 808, 830, 854 | Y | N
12TPIT0136 | STEC Sioux - El Gato: Construct 138 kV Line | Construct El Gato 138 kV partial ringbus substation and build a new 138 kV transmission line from STEC Sioux to El Gato | IN-SERVICE | El Gato | Sioux | Under Construction | 255 - 0488 | AEP/TCC/STEC | Frank Pritzlaff (AEP) 918-599-2653 | 1328 | 2012-06-20 | 2012-06-20 | 138 | 5.43 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 2 | 2005-02-11 | 2005-04-20 | Unknown | 85005, 8792 | Y | N |  | $9,305,100 (AEP) $500,000 (STEC)
12TPIT0114 | Lost Creek - New Substation | Construct a new 69/138-4.16-KV, 12/16/20 MVA x two, redundant backup substation | COMPLETED | Lost Creek | FM237/Cuero Hydro | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-06-15 | 2012-06-26 | 69 | 0 | 0 | 0.0 | 0 | DEWITT |  | Tier 4 |  |  |  | See Project Title | N | N
13TPIT0044 | Hill Country - Install Fourth 345/138 kV Autotransformer | Install 600 MVA autotransformer at Hill Country | [5 empty] | CPS | Blake Williams |  | 2012-06-28 | 2012-06-28 | 345 | 0 | 0 | 600.0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5211 5210 | Y | N |  | There is no transmission line additions associated with this project
12TPIT0082 | Hotwells - New 138kV Substation | Loop new 138kV substation into existing 138kV Ball Park to Deely line |  | Hotwells | Ball Park/Deely |  | T-0168 | CPS | PM: Hector Torres | S-0615 | 2012-06-29 | 2012-06-29 | 138 | 0.1 | 0 | 0.0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5227 5255 5110 | Y | N |  | There are no transformers associated with this project
12TPIT0195 | 1360 East Midland Substation | Transfer 1360 East Midland Substation into ERCOT | New | Oncor Stanton East Substation | Oncor Midland East Substation | Planned |  | SU | Dwight Yarbrough (956) 279-6902 dyarbrough@sharyland.com |  | 2012-10-01 | 2012-06-29 | 138 | 0 | 0 | 0 | 0 | MIDLAND |  | Tier 4 |  |  | N/A |  | N | N
12TPIT0211 | Wink - Loving 138 kV line | Increase line rating |  | Wink | Loving | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2012-07-01 | 2012-07-01 | 138 | 0 | 16.59 | 0 | 0 | WINKLER | LOING | Tier 4 |  |  |  | 1092, 1074 | Y | N
14TPIT0013 | Norwood - East Levee 138 kV line | Upgrade existing line and retire a section of the West Dallas Tap - East Levee 138 kV line |  | Norwood | East Levee | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4073-WAC | 2012-06-01 | 2012-07-01 | 138 | 0 | 6.6 | 0.0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2481, 2405 | Y | N
11TPIT0101 | Reno to Rhome Rebuild | Rebuild existing Reno to Rhome 138 kV Line |  | Reno | Rhome | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 09010 | 2012-10-14 | 2012-07-02 | 138 | 0 | 13.85 | 0.0 | 0 | PARKER | WISE | Tier 4 |  |  |  | 541, 572, 576 | Y | N
11TPIT0081 | Plastipak-Shiloh 138 kV line | Line upgrade |  | Switch 7512 at Plastipak | Switch 8702 at Shiloh | Completed |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-07-11 | 2012-07-11 | 138 | 0 | 1.5 | 0.0 | 0 | DALLAS |  | Tier 4 |  |  |  | 808, 830 | Y | N
09TPIT0125 | East Abilene, Build new 138 kV switch station, terminate new 138 kV Putnam line | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line | IN-SERVICE | East Abilene | 0 | Planned | 479 - 0681 | AEP/ETT | Larry Roberson 918-599-2653 | 2272 | 2012-07-12 | 2012-07-12 | 138 | 0 | 0 | 0 | 0 | EASTLAND |  | CREZ Modified |  |  |  |  | Y | N
13TPIT0014 | East Bridgeport Capacitor Bank | Install 15mvar capacitor bank at East Bridgeport |  | East Bridgeport |  | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 08053 | 2012-07-11 | 2012-07-13 | 138 | 0 | 0 | 0.0 | 15 | WISE |  | Tier 4 |  |  |  | 601 | Y | N
12TPIT0110 | Hollmig | Cut in the new Hollmig (7145) substation on the LCRA TSC Fredericksburg-Kendall 138 kV transmission line |  | Hollmig | Fredricksburg/Kendall | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2012-07-01 | 2012-07-17 | 138 | 0 | 0 | 0.0 | 0 | GILLESPIE |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
07TPIT0042 | 2nd Lewisville Auto | Install (2nd) 345/138 kV autotransformer at Lewisville station |  | Lewisville |  | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 02032 | 2012-06-28 | 2012-07-17 | 345 | 0 | 0 | 700.0 | 0 | DENTON |  | Tier 4 |  |  |  | 646, 645 | Y | N | 2009-R17
12TPIT0134 | St Jo to Capps Corner | Install additional poles and modify existing structures to raise normal operating temperature to 75° C |  | St Jo | Capps Corner | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11035 | 2012-07-06 | 2012-07-18 | 138 | 0 | 8.6 | 0.0 | 0 | MONTAGUE | MONTAGUE | Tier 4 |  |  |  | 750, 754 | Y | N
12TPIT0147 | Salt Dome Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-08-01 | 2012-08-01 | 69 | 0 | 0 | 0.0 | 9.6 | MATAGORDA |  | Tier 4 |  |  |  | 5551 | Y | N
12TPIT0151 | Hillje Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-12-01 | 2012-08-01 | 69 | 0 | 0 | 0.0 | 9.6 | WHARTON |  | Tier 4 |  |  |  | 5532 | Y | N
12TPIT0154 | Tilden Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-07-01 | 2012-08-01 | 69 | 0 | 0 | 0.0 | 9.6 | MCMULLEN |  | Tier 4 |  |  |  | 5700 | Y | N
12TPIT0094 | De-energization of Crosby - Mont Belvieu Ckt. 43 | De-energize Ckt. 43 Crosby - Mont Belvieu. Remove autotransformers from Crosby and Mont Belvieu. Move Highlands tap from Ckt. 43 to Ckt. 66 Haney - Baytown. | IN-SERVICE | CROSBY | MONT BELVIEU | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-07-31 | 2012-08-13 | 138 | 0 | 0 | -158.0 | 0 | HARRIS | CHAMBERS | Tier 4 |  |  |  | 40391, 49010, 40380, 40812, 41112, 49023, 41111 | Y | N
12TPIT0164 | Lindenau - New Substation | Construct a new 138-26.18KV, 18/24/30 MVA on LCRA Cheapside to Cuero Hydro 138 Transmission line |  | Lindenau | Cheapside/Cuero Hydro | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-08-24 | 2012-08-24 | 138 | 0 | 0 | 0.0 | 0 | DEWITT |  | Tier 4 |  |  |  | See Project Title | Y | N
13TPIT0078 | Kendall Autotransformer Addition | Replace the existing 345-138 kV 478MVA autotransformer with an 672 MVA autotransformer at the Kendall substation (7150). | [5 empty] | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2012-08-01 | 2012-08-24 | 345 | 0 | 0 | 672.0 | 0 | KENDALL |  | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | CREZ Default project assigned to LCRA TSC
12TPIT0206 | Dewitt County Capacitor Bank Additions | Install one 7.8 MVAr cap bank at the Lost Creek substation (78188) and one 7.8 MVAr cap bank at the Nordheim West substation (78576) |  |  |  | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2012-08-31 | 2012-08-31 | 69 | 0 | 0 | 0.0 | 15.6 | DEWITT |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
12TPIT 0219 | Odessa North - Cowden North 69 kV line | Increase line rating |  | Odessa North | Cowden North | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2012-09-01 | 2012-09-01 | 69 | 0 | 12.36 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1123, 1259 | Y | N
12TPIT0213 | Odessa North - Holt Switch 69 kV line | Upgrade terminal equipment |  | Odessa North | Holt Switch | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | WAC | 2012-09-01 | 2012-09-01 | 69 | 0 | 0 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1123, 1142 | Y | N
12TPIT0210 | Lakepointe - Jones St 138 kV line | Increase rating of line |  | Lakepointe | Jones St | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2012-09-01 | 2012-09-01 | 138 | 0 | 5.02 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  | 37010, 1972 | Y | N
12TPIT0212 | Moss - Westover 138 kV line | Upgrade terminal equipment |  | Moss | Westover | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2012-09-01 | 2012-09-01 | 138 | 0 | 0 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1019, 1129 | Y | N
12TPIT0216 | Judkins Substation switches | Upgrade switches |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2012-09-01 | 2012-09-01 | 138 | 0 | 0 | 0 | 0 | ECTOR |  | Tier 4 |  |  |  | 1102 | Y | N
12TPIT0073 | Nordheim West - New Substation (Formerly FM 239) | Construct a new 69/138-26.18-KV, 12/16/20 MVA substation |  | Nordheim West | Nordheim/Yorktown | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-09-10 | 2012-09-10 | 69 | 0 | 0 | 0.0 | 0 | DEWITT |  | Tier 4 |  |  |  | See Project Title | Y | N
12TPIT0102 | Lone Tree: Construct 69 kV Station | Lone Tree Station: Construct New Distribution Substation in the Victoria to Leary Lane 69 kV transmission line. | IN-SERVICE | Lone Tree |  | Under Construction | 555 - 0496 | AEP/TCC | Dave Goetz 918-599-2664 | 2555 | 2012-10-30 | 2012-09-14 | 69 | 0 | 0 | 0 | 0 | VICTORIA |  | Tier 4 |  |  |  | 88179 | Y | N
12TPIT0188 | Mayo: Construct 138 kV Station | Mayo Sub-Construct new distribution station on Gila to Whitepoint 138kV line. | IN-SERVICE | Gila | Whitepoint | Under Construction | 562-0730 | AEP/TCC | Frank Pritzlaff 918-599-2664 | 3440 | 2012-09-14 | 2012-09-14 | 138 | 0 | 0 | 0 | 0 | SAN PATRICIO |  | Tier 4 |  |  |  | 80258 | N | N
12TPIT0148 | Olivia Capacitor | Add 4.8 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-10-01 | 2012-10-01 | 69 | 0 | 0 | 0.0 | 4.8 | CALHOUN |  | Tier 4 |  |  |  | 5576 | Y | N
12TPIT0152 | Louise Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-09-01 | 2012-10-01 | 69 | 0 | 0 | 0.0 | 9.6 | WHARTON |  | Tier 4 |  |  |  | 5528 | Y | N
12TPIT0176 | Odlaw | Construct the new Odlaw (7425) substation on the LCRA TSC 138 kV transmission line T-464 from AEP Hamilton Road (8255) - Uvalde (8234) |  | Odlaw | Hamilton Road/Uvalde | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2012-10-01 | 2012-10-01 | 138 | 0 | 0 | 0.0 | 0 | KINNEY |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N | Generation Interconnection -Coordinate with AEP
13TPIT0101 | Winchester Terminal Equipment Upgrade | Upgrade three switches and jumpers to 2000 A at the Winchester Substation (7306). |  | Winchester | Winchester | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2012-09-17 | 2012-10-01 | 138 | 0 | 0 | 0.0 | 0 | FAYETTE |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
12TPIT0214 | Odessa North 138/69 kV autotransformer | Increase rating of autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | WAC | 2012-09-01 | 2012-10-09 | 138 | 0 | 0 | 99 | 0 | ECTOR |  | Tier 4 |  |  |  | 1123, 1122 | Y | N
12TPIT0104 | Rio Hondo: Add 138 kV double breaker terminal for WF Interconnect | Construct a 138 kV double breakered terminal at Rio Hondo for the Los Vientos WF Interconnect | IN-SERVICE | Rio Hondo |  | Under Construction | 487 - 0689 | AEP/TCC | Rich Haley 918-599-2664 | 3365 | 2012-10-24 | 2012-10-24 | 138 | 0 | 0 | 0 | 0 | CAMERON |  | Tier 4 |  |  |  | 8319 | Y | N |  | Backfeed anticipated in Oct, 2012
12TPIT0108 | Wolfgang: Build new Switch Tap | Interconnect Mozart Wind Farm at Wolfgang to connect Mozart to the Jayton to Rotan 69 kV line | IN-SERVICE | Jayton | Rotan | Planned | 493 - 695 | AEP/TNC | Dave Goetz 918-599-2664 | 2441 | 2012-10-30 | 2012-10-30 | 69 | 0 | 0 | 0 | 0 | KENT | FISHER | Tier 4 |  |  |  |  | Y | N
12TPIT0087 | Wilson Substation | Add T2, 138kV-13.09x26.18 dual kV, 40 MVA PWT w/associated bus, structures, panels, etc | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-10-18 | 2012-10-30 | 138 | 0 | 0 | 0.0 | 0 | WILSON |  | Tier 4 |  |  |  | See Project Title | N | N
12TPIT0153 | Cotulla Capacitor | Add 9.6 MVAR capacitor |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-01-01 | 2012-11-01 | 69 | 0 | 0 | 0.0 | 9.6 | LA SALLE |  | Tier 4 |  |  |  | 5876 | Y | N
13TPIT0185 | Fashing Capacitor | Add two 9.6 MVAR capacitors |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-02-01 | 2012-11-01 | 69 | 0 | 0 | 0.0 | 19.2 | ATASCOSA |  | Tier 2 | 2011-12-16 | 2012-04-25 | N/A | 5716 | Y | N
09TPIT0121 | Sun Switch - Sacroc 138 kV line | Rebuild 138 kV line |  | Sun Switch | Sacroc | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R812-WAC | 2012-12-01 | 2012-11-01 | 138 | 0 | 1.8 | 0.0 | 0 | SCURRY | SCURRY | Tier 4 |  |  |  | 1064, 1311 | Y | N
12TPIT0159 | Windthorst 138 kV Switching Station | Build new switching station |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R911-WAC | 2012-12-01 | 2012-11-01 | 138 | 0 | 0 | 0.0 | 0 | ARCHER |  | Tier 4 |  |  |  | 1475 | Y | N
12TPIT0189 | Orlando: Build new Tap | Interconnect Blue Summit Wind Farm at Orlando to connect Blue Summit to the Lake Pauline to Vernon Main 138 kV line | IN-SERVICE | Lake Pauline | Vernon Main | Planned | 506 - 0717 | AEP/ETT | Dave Goetz 918-599-2664 | 2512 | 2012-11-01 | 2012-11-01 | 138 | 0 | 0 | 0 | 0 | WILBARGER |  | Tier 4 |  |  |  |  | Y | N
12TPIT0208 | Goldsmith Gulf Substation Conversion | Convert service to substation to 138 kV |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8049-WAC | 2012-11-01 | 2012-11-01 | 138 | 0 | 0 | 0 | 0 | ECTOR |  | Tier 4 |  |  |  | 1260 | Y | N
12TPIT0215 | Odessa North 138/69 kV autotransformer | Replace existing autotransformer with a larger autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8110-E | 2012-11-01 | 2012-11-01 | 138 | 0 | 0 | 125 | 0 | ECTOR |  | Tier 4 |  |  |  | 1123, 1122 | Y | N
14TPIT0037 | Mount Enterprise Switching Station and 345 kV line | Reconfigure switching station and 345 kV lines from Martin Lake and Trinidad |  | Martin Lake | Mount Enterprise | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6006-WAC | 2012-12-01 | 2012-11-01 | 345 | 0 | 1.2 | 0.0 | 0 | GREGG |  | Tier 2 | 2010-11-01 | 2010-12-01 |  | 3116 | Y | N
12TPIT0187 | La Quinta: Add 138 kV breaker terminal for WF interconnect | Construct a 138 kV breaker terminal at La Quinta for the Whitetail WF Interconnect | IN-SERVICE | LaQuinta |  | Under Construction | 574-0751 | AEP/ETT | Kenneth 'Rich' Haley 918-599-2664 | 3456 | 2012-11-07 | 2012-11-07 | 138 | 0 | 0 | 0 | 0 | WEBB | 0 | TIER 4 | 0 | 0 | 0 | 80439 | Y | N | 0 | 0
15TPIT0014 | Wink-Cochise-Pecos 69kV rebuild | Rebuild the Oncor Wink - TNMP Wink and TNMP Wink - Cochise - Pecos 69 kV lines with 795 ACSR conductor. Upgrade terminal equipment at Cochise station. |  | Wink | Pecos | Completed |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE09711 | 2012-12-01 | 2012-11-09 | 69 | 0 | 33.12 | 0.0 | 0 | Reeves | Winkler | Tier 3 | 2011-07-08 | 2011-08-24 | N/A | 1075, 37921, 37922, 38160, 38090 | Y | N |  | Rebuild of all three line sections was completed in May 2012. Terminal equipment upgrades at Cochise were completed in Nov 2012.
12TPIT0168 | WINFRE 138kV Substation | Construct service to new 138kV WINFRE customer-owned substation. Loop through Ckt. 86 Cities - Brine. | IN-SERVICE | WINFRE | CITIES/ BRINE | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-11-30 | 2012-11-12 | 138 | 0 | 0 | 0.0 | 0 | CHAMBERS | CHAMBERS | Tier 4 |  |  |  | 40340, 40764, 40220 | Y | N
12TPIT0201 | Highlands - West rebuild | Rebuild Highlands - West 138 kV transmission line with 795 ACSS conductor. |  | Highlands | West | Completed |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE08312 | 2012-11-01 | 2012-11-15 | 138 | 0 | 1.6 | 0.0 | 0 | Denton | Denton | Tier 4 |  |  |  | 37050, 37060 | Y | N
12TPIT0186 | Musquiz: Build new Switch Tap | Construct new Musquiz station along the Barrilla Junction to Permian Basin 138 kV line | IN-SERVICE | Barrilla Junction | Permian Basin | Under Construction | 509 - 0723 | AEP/TNC | Michael Tallon 918-599-2664 | 2503 | 2012-11-16 | 2012-11-16 | 138 | 0 | 0 | 0 | 0 | REEVES |  | Tier 4 |  |  |  |  | Y | N
09TPIT0060 | Buda-Turnersville | Replace under-rated limiting line terminal equipment at Buda to increase Buda (7498)-Turnersville (7500) to the conductor's rating. |  | Buda | Turnersville | Planned |  | PEC | Tony Perez (830) 868-5158 |  | 2012-12-16 | 2012-11-19 | 138 | 0 | 0 | 0.0 | 0 | HAYS | HAYS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
12TPIT0028 | Twin Buttes to Big Hill | Construct a new double circuit capable 345 kV transmission line (approximately 31 miles) between the existing LCRA TSC Twin Buttes (76009) and new Big Hill station (76003). The new transmission line will consist of Cumberland conductor to provide a thermal rating of 2988 MVA. |  | Twin Buttes | Big Hill | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2012-11-01 | 2012-11-26 | 345 | 31 | 0 | 0.0 | 0 | TOM GREEN | SCHLEICHER | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N
12TPIT0130 | Oates Substation Conversion | Convert Oates substation from double-tap to 138kV loop service Ckt. 08. | IN-SERVICE | Oates | Anbush/Greens Bayou | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 | 2012-11-29 | 138 | 0 | 0.1 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 41191, 41192 | Y | N
12TPIT0162 | Line Ratings Project - Grandview substation equipment upgrade | Upgrade substation equipment at Grandview and Laredo to remove existing MLSE on the Grandview to Highlands and Grandview to Tenth St. 138kV line |  | Grandview | Highland Hills/Tenth St | Planned |  | CPS | Dieckrow, Robert | S-0704 | 2012-10-01 | 2012-11-29 | 138 | 0 | 0 | 0.0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5175 5205 5420 | Y | N |  | There are no transformers associated with this project
12TPIT0165 | Fairbanks - White Oak Ckt. 81 | Upgrade 138kV Ckt. 81 Fairbanks to Deihl to increase thermal ratings. | IN-SERVICE | Fairbanks | Deihl | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-11-30 | 2012-11-29 | 138 | 0 | 3.59 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 45760, 45730 | Y | N
12TPIT0165a | Fairbanks - White Oak Ckt. 81 | Upgrade 138kV Ckt. 81 Deihl to White Oak to increase thermal ratings. | IN-SERVICE | Deihl | White Oak | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-11-30 | 2012-11-29 | 138 | 0 | 4.05 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 45730, 46610 | Y | N | Cost included in main project
12TPIT0169 | Bellaire - Ulrich Ckt. 35 | Upgrade 138kV Ckt. 35 Bellaire to Ulrich to increase thermal ratings. | IN-SERVICE | Bellaire | Ulrich | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 | 2012-11-29 | 138 | 0 | 3.39 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47011, 47441 | Y | N
12TPIT0203 | Musquiz: Build 138 kV point of delivery for Patriot Resources | Build 138 kV point of delivery from AEP's Musquiz tap to serve customer load. |  | Musquiz | Wolf Bone Tap | Completed | 12TPIT0186 | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE08812 | 2012-11-01 | 2012-11-30 | 138 | 0 | 0 | 0.0 | 0 | Pecos |  | Tier 4 |  |  |  | 6673, 38300 | Y | N
13TPIT0172 | Highlands Switching Station upgrade | Upgrade the Highlands 138 kV Switching Station to 3000 Amp. |  | Highlands |  | Completed |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE08412 | 2012-11-01 | 2012-11-30 | 138 | 0 | 0 | 0.0 | 0 | Denton |  | Tier 4 |  |  |  | 37050 | Y | N
12TPIT0121 | Oran 138/69 kV autotransformer | Install second 138/69 kV autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R598-WAC | 2012-12-01 | 2012-12-01 | 138 | 0 | 0 | 50.0 | 0 | PALO PINTO |  | Tier 4 |  |  |  | 1571, 1572 | Y | N
12TPIT0167 | Crockett - Hardy Ckt. 91 | Upgrade 138kV Ckt. 91 Crockett - Northside tap to increase thermal ratings. | IN-SERVICE | Crockett | Northside | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 | 2012-12-01 | 138 | 0 | 2.53 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47570, 47711 | Y | N
12TPIT0218 | Moss - Odessa EHV 138 kV line | Increase line rating |  | Moss | Odessa EHV | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2012-12-01 | 2012-12-01 | 138 | 0 | 14.2 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1019, 1027 | Y | N
13TPIT0079 | Alvin-North Alvin rebuild | Rebuild Alvin to North Alvin 138 kV transmission line with 795 ACSS conductor. Upgrade terminal equipment at Alvin Substation. |  | Alvin | North Alvin | Completed |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE07211 | 2012-12-31 | 2012-12-01 | 138 | 0 | 2.08 | 0.0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 39015, 39030 | Y | N |  | Line rebuild completed on June 1, 2012. Terminal equipment upgrades at Alvin Substation completed on Dec1, 2012.
10TPIT0125 | Killeen Switch | Install circuit breakers and second 345/138 kV autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C006-WA | 2012-12-01 | 2012-12-01 | 345 | 0 | 0 | 600.0 | 0 | BELL |  | CREZ |  |  |  | 3422, 3423 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. The autotransformer was placed in service in 12/2010.
11TPIT0059 | Odessa EHV Switch | Expand existing switching station |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1010-E | 2012-12-01 | 2012-12-01 | 345 | 0 | 0 | 0.0 | 0 | ECTOR |  | CREZ |  |  |  | 11028 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0036 | Brown - Newton 345 kV line | Construct double-circuit 345 kV line with one circuit |  | Brown | Newton | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C048-E | 2012-12-01 | 2012-12-01 | 345 | 96 | 0 | 0.0 | 0 | BROWN | LAMPASAS | CREZ |  |  |  | 1444, 3690 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0037 | Newton - Killeen Switch 345 kV line | Construct double-circuit 345 kV line with one circuit. |  | Newton | Killeen Switch | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C049-E & C006B-E | 2012-12-01 | 2012-12-01 | 345 | 27.9 | 0 | 0.0 | 0 | LAMPASAS | BELL | CREZ |  |  |  | 3690, 3422 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0038 | Brown - Killeen Switch 345 kV line | Add 345 kV circuit to the structures of the Brown - Newton - Killeen Switch line |  | Brown | Killeen Switch | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C048-E & C049-E | 2012-12-01 | 2012-12-01 | 345 | 126.5 | 0 | 0.0 | 0 | BROWN | BELL | CREZ |  |  |  | 1444, 3691, 3422 | Y | Y | 2007-E7f | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. Cost estimate is included in the estimate for Brown - Newton - Killeen Switch 345 kV line.
12TPIT0039 | Newton Relay Booster Station | Construct a relay booster station |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C023-E | 2012-12-01 | 2012-12-01 | 345 | 0 | 0 | 0.0 | 0 | LAMPASAS |  | CREZ |  |  |  |  | N | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0095b | South Lane - West Columbia Ckts. 04 & 60 | Upgrade 138kV Ckt.04 TXGULF - West Columbia to increase thermal ratings. | IN-SERVICE | TXGULF | West Columbia | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 | 2012-12-05 | 138 | 0 | 27.53 | 0.0 | 0 | WHARTON | BRAZORIA | Tier 3 | 2011-02-02 | 2011-02-24 | N/A | 43340, 43011, 43120, 43380 | Y | N | See project 12TPIT0095b for total project cost estimate | Project is part of the 2011 ERCOT 5-Year Plan.
12TPIT0095c | South Lane - West Columbia Ckts. 04 & 60 | Upgrade substation equipment at South Lane and TXGULF to increase thermal ratings. | IN-SERVICE | South Lane | TXGULF | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 | 2012-12-05 | 138 | 0 | 0 | 0.0 | 0 | WHARTON | WHARTON | Tier 3 | 2011-02-02 | 2011-02-24 | N/A | 43190, 43012, 43340 | Y | N | See project 12TPIT0095b for total project cost estimate | Project is part of the 2011 ERCOT 5-Year Plan.
12TPIT0095d | South Lane - West Columbia Ckts. 04 & 60 | Upgrade substation equipment at TXGULF and West Columbia to increase thermal ratings. | IN-SERVICE | TXGULF | West Columbia | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 | 2012-12-05 | 138 | 0 | 0 | 0.0 | 0 | WHARTON | BRAZORIA | Tier 3 | 2011-02-02 | 2011-02-24 | N/A | 43340, 43011, 43120, 43380 | Y | N | See project 12TPIT0095b for total project cost estimate | Project is part of the 2011 ERCOT 5-Year Plan.
10TPIT0073 | Buda-Rutherford | Replace under-rated limiting line terminal equipment at Buda to increase Buda (7498)-Rutherford (7509) to the conductor's rating. |  | Buda | Rutherford | Planned |  | PEC | Tony Perez (830) 868-5158 |  | 2012-12-16 | 2012-12-06 | 138 | 0 | 0 | 0.0 | 0 | HAYS |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
14TPIT0030 | Bellaire - HO Clarke Ckt. 09 | Upgrade substation equipment to increase thermal ratings. | IN-SERVICE | Bellaire | HO Clarke | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 | 2012-12-12 | 138 | 0 | 0 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47010, 47050, 47150 | Y | N
12TPIT0209 | Lewisville Switch - Jones St 138 kV line | Increase rating of line |  | Lewisville Switch | Jones St | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2012-12-01 | 2012-12-19 | 138 | 0 | 0.3 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  | 645, 1972 | Y | N
11TPIT0026 | Cagnon - Install a Third 345kV Autotransformer | Install one 600 MVA autotransformer. | COMPLETE |  |  |  |  | CPS | Blake Williams |  | 2012-12-12 | 2012-12-19 | 345 | 0 | 0 | 600.0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5055 5056 | Y | N |  | There are no transmission line additions associated with this project
10TPIT0012 | Barclay to Silver City Rebuild | Rebuild existing Barclay to Silver City 69kv line |  | Barclay | Silver City | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 05009 | 2012-12-21 | 2012-12-20 | 69 | 0 | 17 | 0.0 | 0 | FALLS | MILAM | Tier 4 |  |  |  | 69,65 | Y | N
08TPIT0018 | Uvalde to Castroville, build 138 kV line, double circuit capable | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW | IN-SERVICE | Uvalde | Castroville | IN-SERVICE | 291 - 0046 | AEP/ETT | Terry Weeks (AEP) 918-599-2664 Hector Torres (CPS) 210-353-2404 | 1522 | 2012-12-20 | 2012-12-20 | 138 | 77.5 | 0 | 0 | 0 | UVALDE | MEDINA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 5430, 8234 | Y | N | $50,000,000 (AEP) $10,500,000 (CPS)
10TPIT0074 | Buttercup-Whitestone | Replace under-rated limiting line terminal equipment at Buttercup and Whitestone to increase Buttercup (7531)-Whitestone (7529) to the conductor's rating. |  | Buttercup | Whitestone | Planned |  | PEC | Tony Perez (830) 868-5158 |  | 2012-12-01 | 2012-12-28 | 138 | 0 | 0 | 0.0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
12TPIT0129 | Industrial Substation Conversion | Convert Industrial substation from double-tap to 138kV loop service Ckt. 84. | IN-SERVICE | Industrial | Haden/Port | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 | 2012-12-31 | 138 | 0 | 0.1 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 40841, 40842 | Y | N
12TPIT0178 | LaMarque 69kV Substation Removal | Convert LaMarque Sub from 69kV to 138kV and remove 69kV facilities | IN-SERVICE | EXTER | HASTINGS | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 | 2012-12-31 | 138 | 0.1 | 0 | 0.0 | 0 | HARRIS | BRAZORIA | Tier 4 |  |  |  | 42600, 42860, 42820 | Y | N
12TPIT0158 | Permian Basin terminal equipment | Upgrade terminal equipment at Permian Basin in the Permian Basin - Wickett 69 kV line |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8052-WAC | 2013-05-01 | 2013-01-01 | 69 | 0 | 0 | 0.0 | 0 | WARD |  | Tier 4 |  |  |  | 1015 | Y | N
13TPIT0071 | Bullick Hollow 138kV Substation | Establish a new substation with (2) 50MVA unit transformers to serve the Water Treatment Plant | COMPLETE | Bullick Hollow Substation | Bullick Hollow Substation | Under Construction |  | AUSTIN ENERGY | Biju Mathew (512) 322-6737 Biju.Mathew@austinenergy.com | PLAN_117_P070 PLAN_117_P355 | 2013-01-01 | 2013-01-01 | 138 | 0 | 0 | 0.0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9161, 9162 | Y | N |  | Will add idev file to the cases
14TPIT0058m | Mont Belvieu Area Upgrades | Install first 73.3MVAR capacitor bank at Mont Belvieu substation. | IN-SERVICE | Mont Belvieu |  | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 | 2013-01-13 | 138 | 0 | 0 | 0.0 | 73.3 | CHAMBERS |  | Tier 4 | 2012-02-03 | 2012-03-05 | N/A | 41111 | Y | N
12TPIT0132 | BARNES 138kV Substation | Construct service to new 138kV BARNES customer-owned substation. Loop through Ckt.88 SRB - ROHMAS | IN-SERVICE | BARNES | SR Bertron/ ROHMAS | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-01-30 | 2013-01-15 | 138 | 0.1 | 0.4 | 0.0 | 0 | HARRIS |  | Tier 4 |  |  |  | 41355 | Y | N
12TPIT0202 | West Substation upgrade | Upgrade the 138 kV portion of the West substation to 3000 Amp. |  | West |  | Completed |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE03612 | 2013-01-23 | 2013-01-15 | 138 | 0 | 0 | 0.0 | 0 | Denton |  | Tier 4 |  |  |  | 37060 | Y | N
11TPIT0040 | Uvalde 138 kV Substation Upgrade | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW | IN-SERVICE | Uvalde |  | IN-SERVICE | 291 - 0046 | AEP/TCC | Terry Weeks (AEP) 918-599-2664 | 1525 | 2013-01-20 | 2013-01-20 | 138 | 0 | 0 | 0 | 0 | UVALDE |  | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
12TPIT0137 | New Barksdale: Construct new 69 kV Substation including box bay structure interconnection | Add new 69 kV New Barksdale Substation for PEC distribution interconnection | IN-SERVICE | New Barksdale |  | IN-SERVICE | 4690671 | AEP/ETT | Eric Scott 918-599-2664 | 3343 | 2013-01-24 | 2013-01-24 | 69 | 0 | 0 | 0 | 0 | EDWARDS | EDWARDS | Tier 4 |  |  |  | 8365 | Y | N | 8365
12TPIT0170 | Hardy - Airline - White Oak Ckt. 21 | Upgrade 138kV Ckt. 21 Hardy to White Oak to increase thermal ratings. | IN-SERVICE | Airline | White Oak | COMPLETE |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 | 2013-01-24 | 138 | 0 | 3.03 | 0.0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 45630, 46610 | Y | N
07TPIT0024 | Lytle: Add 138/69 kV Auto | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | IN-SERVICE | Lytle |  | IN-SERVICE | 028 - 0028 | AEP/ETT | Terry Weeks (AEP) 918-599-2664 | 3373 | 2013-01-13 | 2013-01-25 | 138 | 0 | 0 | 93 | 0 | MEDINA |  | Tier 4 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 8962, 8622 | Y | N
07TPIT0027 | CPS Lytle to ETT Lytle: Build 138 kV Line and CPS Lytle Substation Upgrades | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | IN-SERVICE | CPS Lytle | ETT Lytle | IN-SERVICE | 028 - 0028 | AEP/ETT/CPS | Terry Weeks (AEP) 918-599-2664 Hector Torres (CPS) 210-353-2404 | 21 | 2013-01-13 | 2013-01-25 | 138 | 4 | 0 | 0 | 0 | BEXAR | MEDINA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 5290, 8962 | Y | N | $3,889,600 (AEP) $4,500,000 (CPS) | There are no transformers associated with this project
12TPIT0068 | South Bend Switch to Morris Sheppard Rebuild | Rebuild South Bend Switch to Morris Sheppard 69 kV line |  | South Bend Switch | Morris Sheppard | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 09008 | 2013-01-31 | 2013-01-28 | 138 | 0 | 18.2 | 0.0 | 0 | YOUNG | PALO PINTO | Tier 4 |  |  |  | 795, 343 | Y | N
13TPIT0118 | EL Campo: Add 138kV bay and breaker | EL Campo add 138kV bay: Add 138kV breaker and associated protection to accomodate LCRA's upgrade of the EL Campo-Altair 69kV line to 138kV. | IN-SERVICE | EL Campo |  | IN-SERVICE | 560 - 0728 | AEP/TCC | Glen Reed 918-599-2664 | 3434 | 2013-01-30 | 2013-01-30 | 138 | 0 | 0 | 0 | 0 | WHARTON |  | Tier 4 |  |  |  | 8102 | N | N |  | No topology changes
12TPIT0115 | Bullick Hollow Substation (7535) | Construct a new 4 breaker ring-bus to serve load at Austin Energy's WTP#4. New substation will be constructed approximately 3.7 miles north of Marshall Ford Substation on T-325. |  | Bullick Hollow | Marshall Ford/Balcones | Under Construction | 13TPIT0071 (AE) | PEC | Tony Perez (830) 868-5158 |  | 2013-01-21 | 2013-01-31 | 138 | 0 | 2.3 | 0.0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
13TPIT0178 | Skywest | Cut in the new Skywest (71210) substation on the LCRA TSC Midkiff (1210) - Sprayberry (1329) 138kV transmission line. |  | Skywest | Midkiff/Sprayberry | Planned | 13TPIT0166 (SU) | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-03-01 | 2013-02-01 | 138 | 0 | 0 | 0.0 | 0 | MIDLAND |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N

## CancelledTPIT03012013NoCost
MARCH BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) CANCELLED PROJECTS As Of 03/01/2013
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) (only in completed tab) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location of Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional)
15TPIT0038 | Venus Switch terminal equipment | Upgrade terminal equipment | Studies indicate timing of project should be changed |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R912-E | 2015-05-01 |  | 138 | 0 | 0 | 0 | 0 | ELLIS |  | Tier 4 |  |  |  | 1909 | Y | N
16TPIT0014 | Fort Stockton to Sanderson rebuild | Rebuild the Fort Stockton to Sanderson 69 kV line. |  | Fort Stockton | Sanderson | Conceptual |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE075AA | 2016-08-31 |  | 69 | 0 | 0 | 0 | 0 | Pecos | TERRELL | Tier 3 |  |  |  |  | N | N
12TPIT0015 | Barney Davis to Laguna, Construct 138 kV transmission line | Construct new 138 kV line and add tranformation at Laguna to remove contingency overloads during off-peak maintenance | Cancelled | Barney Davis | Laguna | Planned | 400 - 0648 | AEP/ETT | Michael Glueck 918-599-2664 | 3302 | 2014-12-31 |  | 138 | 4.2 | 0 | 0 | 0 | NUECES | NUECES | Tier 1 | 2009-03-26 | 2009-10-09 | 2009-12-01 |  | Y | N
12TPIT0014 | Laguna: Add 138/69 kV Auto | Construct new 138 kV line and add tranformation at Laguna to remove contingency overloads during off-peak maintenance | Cancelled | Laguna |  | Planned | 400 - 0648 | AEP/ETT/TCC | Michael Glueck 918-599-2664 | 3307 | 2014-12-31 |  | 138 | 0 | 0 | 240 | 0 | NUECES |  | Tier 1 | 2009-03-24 | 2009-10-09 | 2009-12-01 |  | Y | N
13TPIT0179 | McCarty Lane Terminal Equipment Upgrade | Upgrade the jumper continuous ratings to minimum 2000 Amps on Zorn - McCarty Lane line at the McCarty Lane (7182) substation. |  | McCarty Lane |  | Planned |  | LCRA TSC | Brad Woods (512) 578-4104 brad.woods@lcra.org |  | 2013-05-01 |  | 138 | 0 | 0 | 0.0 | 0 | HAYS |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
10TPIT0083 | Mustang Capacitor Bank | Install 100mvar capacitors at future Mustang substation |  | Mustang |  | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 08052 | 2015-06-01 |  | 138 | 0 | 0 | 0 | 100 | DENTON |  | Tier 4 |  |  |  | 654 | Y | N

## TPIT5YearPlanProjects
Project Number | Project Name | Proposed in-service year | Status of Project | Associated TPIT ERCOT Project Number(s) | Notes

## TransmissionOwnerProjContacts
TRANSMISSION OWNER | TPIT DISTRIBUTION | Primary Contact | Primary Email Address | Primary Phone | Secondary Contacts | Secondary Email Addresses | Secondary PHONE
AEP | Primary & Secondary | Bob Healey | bhealey@aep.com | Bob Healey: 918 599 2249 | Glen Reed; David Kidd; Brad Myers; Sugam Patel; Mabel See; Mike Forcum; Doug Lee; Daniel Lyons; Bob Lager; Mina Turner | gareed@aep.com; dekidd@aep.com; rlbentz@aep.com; naward@aep.com; smdsouza@aep.com; camatthes@aep.com; blmyers@aep.com; pcbelkin@aep.com ; msee@aep.com; mlforcum@aep.com; dnlyons@aep.com; dlee@aep.com; rjlager@aep.com; myturner@aep.com | David Kidd: 918 599 2637 Glen Reed: 918 599 2664 Brad Myers: 918 599 2690
AUSTIN ENERGY | Primary & Secondary | Biju Mathew | biju.mathew@austinenergy.com; | Biju: 512 322 6737 | Armke, James; Mathew, Biju; Ebrahimian, Reza; Hunt, Dandy; Ron Krautz; Brion Ryan | James.Armke@austinenergy.com; biju.mathew@austinenergy.com; reza.ebrahimian@austinenergy.com; dandy.hunt@austinenergy.com; ron.krautz@austinenergy.com; Ryan, Brion <Brion.Ryan@austinenergy.com> | James:512 322 6705 Biju:512 322 6381 Reza:512 322 6740 Dandy:512 322 6748 Ron:512 322 6835 Brion: 512-322-6879
Bandera Electric | Primary | David Baker | d.baker@banderaelectric.com | David: 830-796-6084 | Brian Bartos | b.bartos@banderaelectric.com | Brian: 830 796 6074
BPUB | Primary | Ramon Sanz | rsanz@brownsville-pub.com; | Ramon: 956 983 6203 | James McCann | jmccann@brownsville-pub.com; | James: 956 983 6204
BEPC (BRAZOS ELECTRIC) | Primary & Secondary | Dwight Beckman | dbeckman@brazoselectric.com | Dwight: 254 750 6373 | David Albers | dalbers@brazoselectric.com | David: 254 750 6358
BTU | Primary & Secondary | James Tanneberger | jtanneberger@btutilities.com | James: 979 821 5763 | Shawndra Green | sgreen@btutilities.com | Shawndra: 979 821 5744
CNP | Primary & Secondary | Wayne Kemper | wayne.kemper@centerpointenergy.com | Wayne: 713 207 2192 | Wesley Woitt; Cody Mann; Roy Palacios | wesley.woitt@centerpointenergy.com; Roy.Palacios@centerpointenergy.com cody.mann@centerpointenergy.com; | Wesley Woitt: 713-207-2760 Cody Mann: 713-207-3149
COCS | Primary | Tony Michalsky | tmichalsky@cstx.gov; | Tony: 979 764 3438 | Timothy Crabb; Stacy Engelmann | tcrabb@cstx.gov; sengelmann@cstx.gov; | Timothy Crabb 979 764 3439 Stacy Engelmann 979 764 3681
CPS | Primary & Secondary | Basileo Rocha, Mario De La Garza | bdrocha@cpsenergy.com; MADelagarza1@CPSEnergy.com | Basileo: 210 353 4933 | Kenneth Bowen Blake Williams | kbowen@cpsenergy.com; bawilliams@cpsenergy.com; | Kenneth: 210 353 4142 Blake: 210 353 3557
CTT (Cross Texas Transmission) | Primary & Secondary | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310 | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310
DENTON | Primary & Secondary | Chuck Sears | Chuck.Sears@cityofdenton.com; | Chuck: 940 349 7111 | Brent Heath | brent.heath@cityofdenton.com; | Brent: 940 349 7180
GARLAND | Primary & Secondary | Danh Huynh | Dhuynh@garlandpower-light.org | Danh: 972 205 3826 | Grubbs, David; Fred Sherman; Steve Zaragoza | Dgrubbs@garlandpower-light.org; FredS@gplops.org; stevez@gplops.org | David: 972 205 2664 Fred: 972 205 3184 Steve: 972-205-3098
Golden Spread EC | Primary & Secondary | Chris Koenig | ckoenig@gsec.coop | Chris: 806 349 5201 | Shane McMinn, Mark Reinart | smcminn@gsec.coop; mreinart@gsec.coop | Shane: 806 379 7766 Mark: 806 349 6562
LCRA TSC; PEC; SBEC; GVEC; City of Georgetown; BBEC,CTEC, NBU | Primary & Secondary | Brad Woods | brad.woods@lcra.org | Brad: 512 578 4104 | Sergio Garza, Christina Doerr, Ken Chui | sergio.garza@lcra.org; christina.doerr@lcra.org; ken.chui@lcra.org | Sergio: 512 578 4149 Christina: 512 578 4514 Ken: 512 578 4510
Lone Star | Primary & Secondary | Don Le | don.le@lonestar-transmission.com | Don - 512-236-3144 | Matt Gomes | Matthew.Gomes@LONESTAR-TRANSMISSION.COM | Matt - 512-236-3133
Oncor | Primary & Secondary | Mike Juricek | Michael.Juricek@oncor.com; | Mike: 214 743 6671 | Jim Painter | jpainte1@oncor.com | Jim: 214 743 6779
Sharyland Utilities | Primary & Secondary | Mark Caskey | mcaskey@sharyland.com | Mark: 214 978 8243 | Michael Glass, Dwight Yarbrough, Miguel Alvarado | mglass@sharyland.com; dyarbrough@sharyland.com; malvarado@sharyland.com | Michael: (956) 687-5600, Dwight: (432) 684-0321, Miguel: (214) 855-6103
STEC | Primary & Secondary | Doug Evans | devans@stec.org | Doug: 361 485 6459 | Dotty DiSanto Loretta Gallaga | dottyd@stec.org; lgallaga@stec.org; | Dotty: 361 645 6146 Loretta: 956 377 7120
TMPA | Primary & Secondary | Ahmad Saboor | asaboor@texasmpa.org | Ahmad: 936 873 1104 | Frank Owens | fowens@texasmpa.org; | Frank: 936 873 1120
TNMP | Primary & Secondary | Dustin Ballay | dustin.ballay@tnmp.com | Dustin: 281 910 1030 | Anthony, Hudson Aars, Alton | Anthony.Hudson@tnmp.com; Alton.Aars@tnmp.com; | Anthony: 281 581 4712 Dustin:281 581 4730 Alton:972 420 4189
Wind Energy Texas Transmission (WETT) | Primary | Julius Horvath | julius.horvath@windenergyoftexas.com | Julius: 512 279 7377; cell: 512 496 9186 | Christina Eckhoff | christina.eckhoff@windenergyoftexas.com | Christina: Christina: 512 279 7371