## Slide 1
Proposed 2022 Ancillary Service Methodology And Preliminary Quantities
WMWG
October 25, 2021
ERCOT Staff

## Slide 2: Stakeholder Discussion Timeline
August 11, 2021 – PDCWG (Current Methodology)
August 23, 2021 – WMWG (Current Methodology)
September 08, 2021 – PDCWG (Proposed Methodology)
September 22, 2021 – WMWG (Proposed Methodology)
October 13, 2021 – PDCWG (Proposed Methodology)
October 21, 2020 – OWG (Proposed Methodology)
October 25, 2021 – WMWG (Proposed Methodology)
November 03, 2021 - WMS
November 04, 2021 - ROS
November 17, 2021 - TAC
December 14, 2021 - BoD

## Slide 3: Discussion Scope
ERCOT is not recommending any changes to the methodology used for computing Regulation Service requirements for 2022.
ERCOT is recommending one change in the methodology used for computing Responsive Reserve Service (RRS) requirements for 2022.
ERCOT is recommending changes in the methodology used for computing Non-Spinning Reserve Service (Non-Spin) requirements for 2022 that will account for the highest net load forecast error within an operating hour and intra-day changes in thermal resource availabilities due to forced outages.
The Ancillary Service (A/S) quantities for 2022 contained in this presentation are based on the methodology that was approved in December 2020.
  The quantities for 2022 reflect moving forward the historic data on which these are based, unless otherwise noted.
  Spreadsheets that contain the associated quantities for January through September of 2022 have been posted on the meeting page for this meeting.
ERCOT is seeking stakeholder feedback on these proposed changes for the 2022 A/S Methodology.

## Slide 4: Regulation Service Methodology
ERCOT is not proposing any change to the methodology used to compute the minimum Regulation Service requirements for 2022.
  In the current methodology, the increased Regulation need due to future increases in wind and solar installed capacities are accounted for through wind and solar adjustment tables.
  ERCOT will continue to monitor the variations in intra-hour net load ramps and will tune ERCOT’s Generation Applications in EMS as necessary to meet established frequency control related performance criteria.
The preliminary Regulation quantities for January 2022 through September 2022 in subsequent slides have been computed using current methodology (2020 and 2021 five-minute net load variability), updated Wind Adjustment tables and the updated Solar Adjustment tables.

## Slide 5: Wind Adjustment Tables - 2022
Wind Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind capacity.
Notes: Avg Reg Up adjustment for wind is 1.57 MW. Average reduction in adjustment is about 1.5 MW
Avg Reg Down adjustment for wind is 1.44 MW. Average reduction in adjustment is about 0.6 MW

## Slide 6: Solar Adjustment Tables – 2022
With the implementation of SCR811, the solar adjustment tables track the incremental MWs of Regulation needed to account for the “remaining variability” that is unable to be covered by the predictable nature of solar alone. As a result, the largest impact of the solar adjustment is during periods wherein solar irradiance is highly variable.
Reg-Up
Reg-Down
Max: 20 MW
Mean: 4 MW
Mean (Day Time hours): 6.7 MW
Max: 19 MW
Mean: 4 MW
Mean (Day Time hours): 7.1 MW

## Slide 7: Regulation Up March
Notes: Trends between blue and red are fairly similar.
Largest change in Reg Up is 309 MW in HE17. Daily Average increase is ~91 MW.
Largest change in Reg Down is 248 MW in HE10. Daily Average increase is ~83 MW.

## Slide 8: Regulation Up June
Notes: Trends between blue and red are fairly similar.
Largest change in Reg Up is 147 MW in HE20. Daily Average increase is ~52 MW.
Largest change in Reg Down is 125 MW in HE17. Daily Average increase is ~35 MW.

## Slide 9: Average Regulation Comparison
Notes: Reg Up
On an average blue and red are fairly similar. Largest increase is 91 MW in Mar
Reg Do
On an average blue and red are fairly similar. Largest increase is 94 MW in May

## Slide 10: Responsive Reserve Service (RRS) Methodology
ERCOT is proposing one change to the methodology used to compute the minimum RRS requirements for 2022.
  A floor of 2800 MW will be applied to RRS quantities during the peak. During the peak hour, this additional RRS will help maintain a larger operating margin and operate with reduced risk.
The preliminary RRS quantities for January 2022 through September 2022 in subsequent slides have been computed using 2020 and 2021 system inertia conditions and updated RRS table.
  The RRS table tracks RRS requirements for different inertia conditions. This table was updated in 2020 to use a minimum RRS-PFR limit of 1420 MW.

## Slide 11: Impact of additional RRS on Physical Responsive Capability (PRC)
Since July 12, 2021, ERCOT has been procuring 2,800 MW of RRS over the peak hours.
  The additional RRS has directly impacted ERCOT’s PRC during the peak hours.
  This change has helped increase ERCOT’s operating margin during hours with higher net load.

## Slide 12: Seasonal trend in Physical Responsive Capability (PRC)
Net load and PRC data for all hours between January 1, 2019 and September 30, 2021* was also analyzed.
  Peak hours during Summer and Fall seasons are more vulnerable to lower PRC.
  The proposed change in RRS methodology for 2022 will raise the RRS quantities during peak hours between May and October.
*Excludes Feb 14 – Feb 28, 2021

## Slide 13: RRS May
Notes: Trends between blue and red are fairly similar.
Max Change between blue and red/gray in HE11-14 is 222 MW. Max Change between red and gray in HE15-22 is 17 MW.
On an average increase between blue and gray of 145 MW

## Slide 14: RRS July
Notes: Trends between blue and red are fairly similar.
Max Change between blue and gray in HE1-2 & HE23-24 is 52 MW.
On an average increase blue and gray of 9 MW

## Slide 15: Hourly Average RRS Comparison
Notes: On an average blue and red/gray are fairly similar.
On an average largest increase between blue and gray is 172 MW in June

## Slide 16: Non-Spinning Reserve Service Methodology
ERCOT is proposing the following changes to the methodology used to compute minimum Non-Spin requirements in 2022
  Update the hourly net load forecast uncertainty calculation to use
    the 6 Hours-Ahead net load forecast, and
    the highest 5-min net load within the hour
  Change percentile coverage to vary between 85th and 95th . The applicable coverage for any hour will continue to be based on risk of net load up ramp in the hour
  Build a table that tracks historical intra-day variations in thermal resource availabilities due to Forced Outages and use it to incrementally increase Non-Spin quantities.
ERCOT will continue the practice of monitoring the weather near Real Time and may procure up to an additional 1,000 MW of Non-Spin for Operating Hours that are identified as having an increased potential of high forecast variability that may cause a higher net load during these hours.
The preliminary Non-Spin quantities for January 2022 through September 2022 in subsequent slides have been computed using current methodology (2019, 2020 and 2021 Net load and Net load Forecast), updated Wind Over-Forecast Error Adjustment table and the updated Solar Over-Forecast Error Adjustment table.

## Slide 17: Drivers for the methodology changes
3 Hours Ahead vs. 6 Hours Ahead: On tighter days in Summer months generally units with 6 hours+ lead times tend to be available for RUC; these lead time tend to double during winter when units available for RUC are typically “cold”. Since forecast uncertainties tend to be a bit higher further away from the operating hours, using 6-hours ahead forecast errors allows to better reflect this risk in the computed Non-Spin quantities.
Hourly Average vs. Max 5-min Net load: Intra-hour net load patterns due to load/wind/solar can be vastly different even with same hourly average values. By using the highest 5-min net load within the hour, the largest net load forecast error for the hour will be used in determining Non-Spin quantities.
75th to 95th vs. 85th to 95th Percentile Coverage: This change better reflects the risk associated with net load forecast uncertainties during off peak hours in the Non-Spin methodology.
Intra-day Forced Outage table: This table will help account for increased capacity needs following forced outages of thermal resources within an operating day.

## Slide 18: Adequacy of historic Non-Spin quantities
Non-Spin quantities between January 1, 2020 and July 31, 2021* weren’t sufficient to cover the 6 hours ahead risk up to 40% of the time.
  ~7% of these instances were related to peak conditions
  ~3% of these instances real time headroom was less than 4,500 MW
  peak hours with insufficiency reduced significantly since July 12, 2021.
  3HA/6HA Non-Spin Sufficiency = Non-Spin Plan – 3HA/6HA NLFE – Intra-day forced outage change
  Real Time Headroom = Total Online HSL + Offline Non-Spin – Actual Load
  *Excludes Feb 14 – Feb 28, 2021

## Slide 19: Trend in historic Headroom
6 hours ahead, 3 hours head and real time Headroom between January 1, 2020 and July 31, 2021* was also analyzed. There were several instances where the real time headroom was lower than the 6 hour ahead headroom.
  ~23% off these instances real time headroom was lower than 6 hour ahead headroom by an amount greater than 1430 MW.
  ~5% off these instances were related to peak conditions
  3HA/6HA Headroom = Total Online HSL + Offline Non-Spin – Active Load Forecast
  Real Time Headroom = Total Online HSL + Offline Non-Spin – Actual Load
  *Excludes Feb 14 – Feb 28, 2021

## Slide 20: Proposed Intra-Day Forced Outage Table 2022
The proposed Intra-Day Forced Outage table has been built using 75th percentile of the maximum accumulated forced outage in a 6-hour block for each month in 2018, 2019, 2020.
  For the purposes of building this table, a conservative 75th percentile coverage is recommended due to the observation that the extreme forced outages tend to not occur at the same time as the highest net load forecast error.

## Slide 21: Wind Over-Forecast Error Adjustment Table 2022
Wind Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind capacity.
Max: 39 MW per 1000 MW additional Wind capacity
Mean: 31 MW per 1000 MW additional Wind capacity

## Slide 22: Solar Over-Forecast Error Adjustment Table 2022
Solar Over-Forecast Error Adjustment Table track estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
Max: 56 MW per 1000 MW additional solar capacity
Mean: 13 MW per 1000 MW additional solar capacity
Mean (Day time): 23 MW per 1000 MW additional solar capacity

## Slide 23: Non-Spin January
Notes: Max change between red and purple in He15-18 is 2878 MW.
Largest value 4520 MW in HE15-18.
On an average increase of 2135 MW
The dark blue 2022 (6500 Method): Non-Spin = 6500 – (Reg-Up + RRS-PFR-Gen/ESR)

## Slide 24: Non-Spin May
Notes: Max change between red and purple in HE15-19 is 2513 MW.
Largest value 4994 MW in HE13-14.
On an average increase of 2339 MW
The dark blue 2022 (6500 Method): Non-Spin = 6500 – (Reg-Up + RRS-PFR-Gen/ESR)

## Slide 25: Non-Spin June
Notes: Max change between red and purple in HE1-2,23-24 is 2896 MW.
Largest value 4839 MW in HE13-14.
On an average increase of 2367 MW
The dark blue 2022 (6500 Method): Non-Spin = 6500 – (Reg-Up + RRS-PFR-Gen/ESR)

## Slide 26: Hourly Average Non-Spin Comparison
Notes: On an average largest increase between red and purple is 2367 MW in June
The dark blue 2022 (6500 Method): Non-Spin = 6500 – (Reg-Up + RRS-PFR-Gen/ESR)
The orange 2021 (Intra Year Posting) has the following three trends
  2021 NSRS between Jan 1 and Jul 12: Based on Dec 2020 Posting
  2021 NSRS between Jul 12 and Aug 31: Non-Spin = 6500 – (Reg Up + RRS)
  2021 NSRS between Sep 1 and Dec 31 : Non-Spin = 6500 – (Reg Up + RRS-PFR-Gen/ESR)

## Slide 27
Discussion

## Slide 28: Projected Increase in IRR Capacity

## Slide 29: Solar Adjustment Tables - 2022
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity.
Notes: Avg Reg Up adjustment for wind is 3.9 MW. Average reduction in adjustment is about 0.8 MW
Avg Reg Down adjustment for wind is 4.15 MW. Average reduction in adjustment is about 0.9 MW

## Slide 30: Regulation January
Notes: Trends between blue and red are fairly similar.
Largest change in Reg Up is 209 MW in HE17. Daily Average increase is ~39 MW.
Largest change in Reg Down is 194 MW in HE10. Daily Average increase is ~47 MW.

## Slide 31: RRS January
Chart: 
| a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
2021 (Dec Posting) | 3053 | 3053 | 2959 | 2880 | 2880 | 2959
2022 (Dec-2020 Methodology) | 3053 | 3053 | 2959 | 2959 | 2959 | 2959
2022 (2800 MW floor peak hours) | 3053 | 3053 | 2959 | 2959 | 2959 | 2959
2021 (July 12 Posting) | 3053 | 3053 | 2959 | 2880 | 2880 | 2959
Notes: Trends between blue and red are fairly similar.
Max Change between blue and red/gray in HE11-18 is 79 MW. No Change between red and gray
On an average decrease between blue and red/gray of 26 MW

## Slide 32: Trends in 6HA Net Load Forecast Error
As years progress, an increase in magnitude of the 6 Hours-Ahead net load forecast error can be observed.

## Slide 33: Intra-Day Forced Outage Rate
For 2018, 2019 and 2020, the heat maps below show the 75th percentile of the maximum accumulated forced outage on thermal units (excluding IRR and PUN) since midnight for every hour in each month.