## Slide 1
Proposed 2022 Ancillary Service Methodology And Preliminary Quantities
WMS
November 03, 2021
ERCOT Staff

## Slide 2: Stakeholder Discussion Timeline
August 11, 2021 – PDCWG (Current Methodology)
August 23, 2021 – WMWG (Current Methodology)
September 08, 2021 – PDCWG (Proposed Methodology)
September 22, 2021 – WMWG (Proposed Methodology)
October 13, 2021 – PDCWG (Proposed Methodology)
October 21, 2020 – OWG (Proposed Methodology)
October 25, 2021 – WMWG (Proposed Methodology)
November 03, 2021 - WMS
November 04, 2021 - ROS
November 17, 2021 - TAC
December 14, 2021 - BoD

## Slide 3: Discussion Scope
Following is a summary of the proposed changes in the methodologies for determining Ancillary Service (A/S) quantities for 2022.
  ERCOT is not recommending any changes to the methodology used for computing Regulation Service requirements for 2022.
  ERCOT is recommending one change in the methodology used for computing Responsive Reserve Service (RRS) requirements for 2022.
  NERC’s preliminary 2022 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows a reduction in ERCOT’s IFRO. This is primarily because of an update in the IFRO methodology that as approved as a part of the Project 2017-01, Modifications to BAL-003. In order to align with ERCOT’s new IFRO, ERCOT is proposing to change the minimum RRS-PFR limit for 2022 to 1,240 MW.
  ERCOT is recommending changes in the methodology used for computing Non-Spinning Reserve Service (Non-Spin) requirements for 2022 that will account for the highest 6 hours ahead net load forecast error within an operating hour and intra-day changes in thermal resource availabilities due to forced outages.
  The Ancillary Service (A/S) quantities for 2022 contained in this presentation are based on the methodology that was approved in December 2020. The quantities for 2022 reflect moving forward the historic data on which these are based, unless otherwise noted.
A redline version of the draft methodology and spreadsheets that contain the associated quantities for January through September of 2022 have been posted on the meeting page for this meeting.

## Slide 4: Regulation Service Methodology
ERCOT is not proposing any change to the methodology used to compute the minimum Regulation Service requirements for 2022.
The preliminary Regulation quantities for January 2022 through September 2022 in subsequent slides have been computed using current methodology (2020 and 2021 five-minute net load variability), updated Wind Adjustment tables and the updated Solar Adjustment tables.
  Wind and Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind and solar capacity, respectively.

## Slide 5: Regulation Up March
Notes: Trends between blue and red are fairly similar.
Largest change in Reg Up is 309 MW in HE17. Daily Average increase is ~91 MW.
Largest change in Reg Down is 248 MW in HE10. Daily Average increase is ~83 MW.

## Slide 6: Regulation Up June
Notes: Trends between blue and red are fairly similar.
Largest change in Reg Up is 147 MW in HE20. Daily Average increase is ~52 MW.
Largest change in Reg Down is 125 MW in HE17. Daily Average increase is ~35 MW.

## Slide 7: Average Regulation Comparison
Notes: Reg Up
On an average blue and red are fairly similar. Largest increase is 91 MW in Mar
Reg Do
On an average blue and red are fairly similar. Largest increase is 94 MW in May

## Slide 8: Responsive Reserve Service (RRS) Methodology
ERCOT is proposing one change to the methodology used to compute the minimum RRS requirements for 2022.
  A floor of 2800 MW will be applied to RRS quantities during the peak. During the peak hour, this additional RRS will help maintain a larger operating margin and operate with reduced risk.
NERC’s preliminary 2022 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows a reduction in ERCOT’s IFRO. This is primarily because of an update in the IFRO methodology that as approved as a part of the Project 2017-01, Modifications to BAL-003. In order to align with ERCOT’s new IFRO, ERCOT is proposing to change the minimum RRS-PFR limit for 2022 to 1,240 MW.
The preliminary RRS quantities for January 2022 through September 2022 in subsequent slides have been computed using 2020 and 2021 system inertia conditions and updated RRS table.
  The RRS table tracks RRS requirements for different inertia conditions. This table has been updated in 2022 to use a minimum RRS-PFR limit of 1,240 MW.

## Slide 9: RRS Table - 2022
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
*RRS Curr IFRO (MW) | 3352 | 3303 | 3255 | 3210 | 3170 | 3092 | 3053 | 3002 | 2959 | 2880 | 2783 | 2712
**RRS Upd IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3088 | 3015 | 2982 | 2936 | 2898 | 2825 | 2732 | 2668
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2658 | 2605 | 2566 | 2521 | 2469 | 2429 | 2383 | 2344 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2618 | 2571 | 2538 | 2498 | 2450 | 2416 | 2375 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,420 MW.
**RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,240 MW.
***Red font in table above identifies study scenario where RRS needed < 2300 MW. RRS requirement during these is based on the applicable floor.
****Generation mix (CCs, Gas, SC, Coal, Steam) providing 1150 MW of PFR has been aligned with actual historic system operations.
Inertia < 250 GW·s: 30% Coal + 70% Rest. Inertia ≥ 250 GW·s: 15% Coal + 85% Rest
Notes: RRS quantity for 2022 decrease between 8 MW (310 GW.s case) and 82 MW (170 GW.s case)

## Slide 10: RRS March
Notes: Trends between orange-pattern and red are fairly similar.
Max Change between blue and orange in HE7-10 is 168 MW.
Max Change between blue and orange-pattern in HE1-2 & HE23-24 & HE7-10 is 86 MW.
No Change between orange-pattern and red.
On an average increase between blue and red of 47 MW

## Slide 11: RRS May
Notes: Trends between orange-pattern and red are fairly similar.
Max Change between blue and orange in HE11-14 is 222 MW.
Max Change between blue and orange-pattern in HE11-14 is 167 MW.
Max Change between orange-pattern and red in HE15-22 is 68 MW.
On an average increase between blue and red of 99 MW

## Slide 12: RRS July
Notes: Trends between orange-pattern and red are fairly similar.
Max Change between blue and orange in HE1-2 & HE23-24 is 52 MW.
Max Change between blue and orange-pattern in HE1-2 & HE23-24 is 29 MW.
Max Change between orange-pattern and red in HE15-22 is 500 MW.
No change in average monthly quantities

## Slide 13: Hourly Average RRS Comparison
Notes: Trends between orange-pattern and red are mostly similar.
On an average largest increase between blue and red is 145 MW in June

## Slide 14: Non-Spinning Reserve Service Methodology
ERCOT is proposing the following changes to the methodology used to compute minimum Non-Spin requirements in 2022
  Update the hourly net load forecast uncertainty calculation to use
    the 6 Hours-Ahead net load forecast, and
    the highest 5-min net load within the hour
  Change percentile coverage to vary between 85th and 95th . The applicable coverage for any hour will continue to be based on risk of net load up ramp in the hour.
  Build a table that tracks historical intra-day variations in thermal resource availabilities due to Forced Outages and use it to incrementally increase Non-Spin quantities.
ERCOT will continue the practice of monitoring the weather near Real Time and may procure up to an additional 1,000 MW of Non-Spin for Operating Hours that are identified as having an increased potential of high forecast variability that may cause a higher net load during these hours.
The preliminary Non-Spin quantities for January 2022 through September 2022 in subsequent slides have been computed using current methodology (2019, 2020 and 2021 Net load and Net load Forecast), updated Wind Over-Forecast Error Adjustment table and the updated Solar Over-Forecast Error Adjustment table.
  Wind and Solar Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind and solar capacity, respectively.

## Slide 15: Drivers for the methodology changes
3 Hours Ahead vs. 6 Hours Ahead: On tighter days in generally units with 6 hours+ lead times tend to be available for RUC. Since forecast uncertainties tend to be a bit higher further away from the operating hours, using 6-hours ahead forecast errors allows to better reflect this risk in the computed Non-Spin quantities.
Hourly Average vs. Max 5-min Net load: Intra-hour net load patterns due to load/wind/solar can be vastly different even with same hourly average values. By using the highest 5-min net load within the hour, the largest net load forecast error for the hour will be used in determining Non-Spin quantities.
75th to 95th vs. 85th to 95th Percentile Coverage: This change better reflects the risk associated with net load forecast uncertainties during off peak hours in the Non-Spin methodology.
Intra-day Forced Outage table: This table will help account for increased capacity needs following forced outages of thermal resources within an operating day.

## Slide 16: Proposed Intra-Day Forced Outage Table 2022
The proposed Intra-Day Forced Outage table has been built using 75th percentile of the maximum accumulated forced outage in a 6-hour block for each month in 2018, 2019, 2020.
  A conservative 75th percentile coverage is recommended due to the observation that the extreme forced outages tend to not occur at the same time as the highest net load forecast error.

## Slide 17: Non-Spin January
Notes: Max change between red and purple in He15-18 is 2878 MW.
Largest value 4520 MW in HE15-18.
On an average increase of 2135 MW
The dark blue 2022 (6500 Method): Non-Spin = 6500 – (Reg-Up + RRS-PFR-Gen/ESR)

## Slide 18: Non-Spin May
Notes: Max change between red and purple in HE15-19 is 2513 MW.
Largest value 4994 MW in HE13-14.
On an average increase of 2339 MW
The dark blue 2022 (6500 Method): Non-Spin = 6500 – (Reg-Up + RRS-PFR-Gen/ESR)

## Slide 19: Non-Spin June
Notes: Max change between red and purple in HE1-2,23-24 is 2896 MW.
Largest value 4839 MW in HE13-14.
On an average increase of 2367 MW
The dark blue 2022 (6500 Method): Non-Spin = 6500 – (Reg-Up + RRS-PFR-Gen/ESR)

## Slide 20: Hourly Average Non-Spin Comparison
Notes: On an average largest increase between red and purple is 2367 MW in June
The dark blue 2022 (6500 Method): Non-Spin = 6500 – (Reg-Up + RRS-PFR-Gen/ESR)
The orange 2021 (Intra Year Posting) has the following three trends
  2021 NSRS between Jan 1 and Jul 12: Based on Dec 2020 Posting
  2021 NSRS between Jul 12 and Aug 31: Non-Spin = 6500 – (Reg Up + RRS)
  2021 NSRS between Sep 1 and Dec 31 : Non-Spin = 6500 – (Reg Up + RRS-PFR-Gen/ESR)

## Slide 21: Summary
Following is a summary of the proposed Ancillary Service Methodology for 2022.
  ERCOT is not recommending any changes to the methodology used for computing Regulation Service requirements.
  ERCOT is recommending one change in the methodology used for computing Responsive Reserve Service (RRS) requirements.
  ERCOT is also proposing to change the minimum RRS-PFR limit for 2022 to 1,240 MW based on updates to NERC’s BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for OY2022.
  ERCOT is recommending changes in the methodology used for computing Non-Spinning Reserve Service (Non-Spin) requirements that will account for the highest 6 hours ahead net load forecast error within an operating hour and intra-day changes in thermal resource availabilities due to forced outages.

## Slide 22
Discussion

## Slide 23: Projected Increase in IRR Capacity

## Slide 24: Wind Adjustment Tables - 2022
Wind Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind capacity.
Notes: Avg Reg Up adjustment for wind is 1.57 MW. Average reduction in adjustment is about 1.5 MW
Avg Reg Down adjustment for wind is 1.44 MW. Average reduction in adjustment is about 0.6 MW

## Slide 25: Solar Adjustment Tables – 2022
With the implementation of SCR811, the solar adjustment tables track the incremental MWs of Regulation needed to account for the “remaining variability” that is unable to be covered by the predictable nature of solar alone. As a result, the largest impact of the solar adjustment is during periods wherein solar irradiance is highly variable.
Reg-Up
Reg-Down
Max: 20 MW
Mean: 4 MW
Mean (Day Time hours): 6.7 MW
Max: 19 MW
Mean: 4 MW
Mean (Day Time hours): 7.1 MW

## Slide 26: Solar Adjustment Tables - 2022
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity.
Notes: Avg Reg Up adjustment for wind is 3.9 MW. Average reduction in adjustment is about 0.8 MW
Avg Reg Down adjustment for wind is 4.15 MW. Average reduction in adjustment is about 0.9 MW

## Slide 27: Wind Over-Forecast Error Adjustment Table 2022
Wind Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind capacity.
Max: 39 MW per 1000 MW additional Wind capacity
Mean: 31 MW per 1000 MW additional Wind capacity

## Slide 28: Solar Over-Forecast Error Adjustment Table 2022
Solar Over-Forecast Error Adjustment Table track estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
Max: 56 MW per 1000 MW additional solar capacity
Mean: 13 MW per 1000 MW additional solar capacity
Mean (Day time): 23 MW per 1000 MW additional solar capacity