| PGRR Number | 097 | PGRR Title | Related to NPRR1098, Direct Current Tie (DC Tie) Reactive Power Capability Requirements |
| --- | --- | --- | --- |

| Date | November 1, 2021 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Collin Martin |
| E-Mail Address | collin.martin@oncor.com |
| Company | Oncor Electric Delivery Company LLC |
| Phone Number | 817-215-6174 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU) |

Comments

Oncor submits these comments to Planning Guide Revision Request 097, Direct Current Tie (DC Tie) Reactive Power Capability Requirements, to ensure the requirements proposed by this Planning Guide Revision Request (PGRR) are appropriately split between facility owners and facility operators, similar to existing modeling requirements that apply to Resource Entities (REs) as facility owners.

Most DC Ties in ERCOT are owned by the same entity that performs the Direct Current Tie Operator (DCTO) role.  However, in one instance the DCTO is a different entity from the DC Tie owner.  Oncor believes it is appropriate to assign the proposed reactive power and modeling requirements to DC Tie owners to address this particular situation.  In general, the relationship of DC Tie owners to DCTOs is similar to the RE to Qualified Scheduling Entity (QSE) relationship, and asset-based reliability requirements such as dynamic model development should be assigned to the owning entity.

Revised Cover Page Language

| Revision Description | This Planning Guide Revision Request (PGRR) clarifies the responsibilities of Direct Current Tie owners relative to the develop of dynamics models and aligns the Planning Guide with the revisions proposed in NPRR1098. |
| --- | --- |

Revised Proposed Guide Language

6.2	Dynamics Model Development

(1)	To adequately simulate dynamic and transient events in the ERCOT System, it is necessary to establish and maintain dynamics data and simulation-ready study cases representing the dynamic capability and frequency characteristics of machines and equipment connected to the ERCOT System.

(2)	Dynamics data is the network data and mathematical models required in accordance with the Reliability and Operations Subcommittee (ROS)-approved Dynamics Working Group Procedure Manual for simulation of dynamic and transient events in the ERCOT System.

(3)	For Resource Entities, dynamics data includes the data needed to represent the dynamic and transient response of Resource Entity-owned devices and/or Loads including but not limited to generating units, plants, and other equipment when connected to the ERCOT System including the data for any privately owned transmission system or collection system used to connect the Resource to the ERCOT System.

(4)	For Transmission Service Providers (TSPs) and owners of Direct Current Tie Facilities, dynamics data needed to represent the dynamic and transient capability of TSP-owned and DC Tie Facility owners’ devices including but not limited to Load shedding relays, protective relays, FACTS devices (e.g., SVC, STATCOMs), Direct Current Ties (DC Ties), variable-frequency transformers, automatically switched shunts, and transformers with automatic load tap changers.

(5)	The owner of the generator Facility or dynamic device shall provide appropriate dynamics data to ERCOT, including the data for a planned Facility, in accordance with the Dynamics Working Group Procedure Manual.  The dynamic data shall include the following:

(a)	A model with parameters that accurately represent the dynamics of the device and that is compatible with the current version of the planning and operations model software as described in the Dynamics Working Group Procedure Manual.  If a user written model is provided:

(i)	The data shall also include a model manual containing a technical description of the model characteristics, including descriptions for all model parameters and variables, a list of which parameters are commonly tuned for site-specific settings, and a description of procedures and considerations for using the model in dynamic simulations, including steady state representation and limitations for model adequacy and usability in the planning model software; and

(ii)	The user-written model shall allow the user to determine the allocation of machine identifiers (bus numbers, bus names, machine IDs etc.) without restriction.

(b)	Verification reports that support the model data based on documented field settings shall be provided as specified in the Dynamics Working Group Procedure Manual for Generation Resources, Energy Storage Resources (ESRs), and for Transmission Elements represented by a dynamic model.  The reports shall demonstrate that the model parameters which are commonly tuned match site-specific settings implemented in the field.  For new Generation Resources and ESRs, these reports shall be provided as required in paragraph (4)(e) in Section 5.7.1, Generation Resource and Settlement Only Generator Data Requirements.  For existing Generation Resources and ESRs, these reports shall be provided as required in paragraph (4)(f) of Section 5.7.1.  For Transmission Elements represented by a dynamic model, these reports shall be provided no later than two years following energization of new equipment and updated a minimum of every ten years.

[PGRR085: Replace paragraph (b) above upon system implementation of PGRR082:] (b) Verification reports that support the model data based on documented field settings shall be provided as specified in the Dynamics Working Group Procedure Manual for Generation Resources, Energy Storage Resources (ESRs), and for Transmission Elements represented by a dynamic model. The reports shall demonstrate that the model parameters which are commonly tuned match site-specific settings implemented in the field. For new Generation Resources and ESRs, these reports shall be provided as required in paragraph (2) of Section 5.5, Generator Commissioning and Continuing Operations. For existing Generation Resources and ESRs, these reports shall be provided as required in paragraph (3) of Section 5.5. For Transmission Elements represented by a dynamic model, these reports shall be provided no later than two years following energization of new equipment and updated a minimum of every ten years.

(c)	Results of model quality tests and associated simulation files that demonstrate acceptable performance of the models in the planning model software as described in the Dynamics Working Group Procedure Manual.  These shall be provided whenever a new or updated dynamic model is provided to ERCOT representing a Generation Resource, ESR, or Transmission Element.  The purpose of these tests is to ensure the quality of the provided dynamic data and models for use in numerous system studies and ensure consistency across planning software platforms.  Therefore, the Facility owner shall also assess sufficient sensitivities, including but not limited to Voltage Set Point at the Point of Interconnection (POI), real power output, and Reactive Power output to ensure acceptable model performance over the entire range of operating conditions.  An explanation shall be provided for review if model responses do not match.

(i)	All site-specific dynamic models required to represent the Facility shall be included in the model quality tests.  These tests can be performed in a simple test system without requiring ERCOT System information.

(ii)	For Intermittent Renewable Resource (IRR) equipment aggregated together to form an IRR in accordance with paragraph (12) of Protocol Section 3.10.7.2, Modeling of Resources and Transmission Loads, the dynamic model shall represent the aggregated IRR.

(iii)	Results for the following model quality tests shall be provided to demonstrate acceptable model performance.  Additional details about each test, including the set up and description of desirable response, are included in the Dynamics Working Group Procedure Manual.

(A)	Flat start test: A no-disturbance test shall be performed to demonstrate appropriate model initialization and the Facility’s dynamic response under a no-disturbance condition.

(B)	Small voltage disturbance test: A voltage step increase and decrease shall be applied to the POI to demonstrate the Facility’s dynamic response.

(C)	Large voltage disturbance test:

(1)	For IRRs, ESRs, and inverter-based transmission equipment, the high and low Voltage Ride-Through (VRT) profiles as described in Nodal Operating Guide Section 2.9.1, Additional Voltage Ride-Through Requirements for Intermittent Renewable Resources, shall be applied to the POI to demonstrate the Facility’s dynamic response.

(2)	For Resources other than IRRs, ESRs, and inverter-based equipment, a fault shall be applied to the POI to demonstrate the Facility’s dynamic response.

(D)	Small frequency disturbance test: A frequency step increase and decrease shall be applied to the POI to demonstrate the Facility’s dynamic response.

(E)	System strength test: The model for IRRs and inverter-based Resources shall be tested under a few equivalent short circuit ratios, as described in the Dynamics Working Group Procedure Manual.  This tests the robustness of the model to varying system conditions.

(d)	Inverter-Based Resources (IBRs) shall provide results of the unit model validation to demonstrate that the PSCAD model, as described in the Dynamics Working Group Procedure Manual, accurately represents the dynamic responses of all inverter-based dynamic devices within the Facility.  This validation is not intended to be site-specific; rather it is intended to be a hardware type test, where models representing different inverter hardware are benchmarked for accuracy.  Validation results for a specific model of inverter can be submitted for multiple uses of that model of inverter.

(i)	The validation results shall be included when submitting a PSCAD model to ERCOT.

(ii)	Results for the following unit model validation tests shall be provided to demonstrate model accuracy.  Additional details about each test are included in the Dynamics Working Group Procedure Manual.

(A)	Step change in voltage;

(B)	Large voltage disturbance (VRT tests);

(C)	System strength test;

(D)	Phase angle jump test; and

(E)	Subsynchronous test.

(6)	Dynamics data for a planned Facility will be updated by the Facility owner upon completion of the design for the Facility.

(7)	Updated dynamics data for an existing Facility shall be provided to ERCOT when field tests, inspections, or other information demonstrates that the dynamics data should be changed to accurately represent the dynamic characteristics of the Facility.

(8)	Dynamics Data is considered Protected Information pursuant to Protocol Section 1.3, Confidentiality.

(9)	Dynamics data shall be provided with the legal authority to provide the information to all TSPs.  If any of the information is considered Protected Information, the Facility owner shall indicate as such.

6.2.3	Dynamics Data Requirements for Transmission and/or Distribution Service Providers and DC Tie Facility Owners

(1)	The owner of under-frequency Load shedding equipment shall provide necessary data to model under frequency Load shedding relays for their portion of the ERCOT System as described in the Dynamics Working Group Procedure Manual.

(2)	The owner of under voltage Load shedding equipment shall provide necessary data to model under voltage Load shedding relays for their portion of the ERCOT System as described in the Dynamics Working Group Procedure Manual.

(3)	When requested by ERCOT or a Transmission and/or Distribution Service Provider (TDSP), the owner of protective relays, control systems, and Remedial Action Schemes (RASs) shall provide dynamics data needed to simulate their action.

(4)	The DWG shall document appropriate Load model data as described in the Dynamics Working Group Procedure Manual for use in dynamic simulations.

(5)	The owner of a dynamic element connected to the transmission system shall provide the dynamic data needed to simulate the action of the device in dynamic simulations to ERCOT and the TDSP to which the element is connected.

(6)	The owner of a dynamic element connected to the transmission system shall verify the dynamic models through comparison with operational data of actual events or test results within five years of energization and a minimum of every ten years thereafter.  Industry accepted testing techniques shall be used for testing, measuring and calculating the modeling parameters.  The owner of the dynamic element shall document and retain results for the model verification effort.  Documentation shall include the operational data used to verify the modeling parameters.