## Slide 1: Weatherization Rule
Phase I

## Slide 2
§25.55. Weather Emergency Preparedness.
(a) Application. This section applies to the Electric Reliability Council of Texas, Inc. (ERCOT) and to generation entities and transmission service providers (TSPs) in the ERCOT power region. A generation resource with an ERCOT-approved notice of suspension of operations for the 2021-2022 winter weather season is not required to be in compliance under this section until it is returned to service.

## Slide 3
(b) Definitions. In this section, the following definitions apply unless the context indicates otherwise.
Cold weather critical component - Any component that is susceptible to freezing or icing, the occurrence of which is likely to significantly hinder the ability of a resource or transmission system to function as intended and, for a generation entity, to lead to a trip, derate, or failure to start of a resource. For a TSP, cold weather critical component is limited to any transmission-voltage component within the fence surrounding a TSP's high-voltage switching station or substation.
Energy storage resource - An energy storage system registered with ERCOT for the purpose of providing energy or ancillary services to the ERCOT grid and associated facilities controlled by the generation entity that are behind the system's point o f interconnection, necessary for the operation o f the system, and not part of a manufacturing process that is separate from the generation of electricity.
Generation entity - An ERCOT-registered resource entity acting on behalf of an ERCOT-registered generation resource or energy storage resource.
Generation resource - A generator capable of providing energy or ancillary services to the ERCOT grid and that is registered with ERCOT as a generation resource, as well as associated facilities controlled by the generation entity that are behind the generator's point of interconnection, necessary for the operation of the generator, and not part of a manufacturing process that is separate from the generation of electricity.
Inspection - Activities that ERCOT engages in to determine whether a generation entity is in compliance with all or parts ofparagraph (c)(1) ofthis section or whether a TSP is in compliance with all or parts of paragraph (f)(1) of this section. An inspection may include site visits; assessments of procedures; interviews; and review of information provided by a generation entity or TSP in response to a request by ERCOT, including review of evaluations conducted by the generation entity or TSP or its contractor.
Resource - A generation resource or energy storage resource.
Weather emergency - A situation resulting from weather conditions that produces significant risk for a TSP that firm load must be shed or a situation for which ERCOT provides advance notice to market participants involving weather-related risks to the ERCOT power region.
Weather emergency preparation measures - Measures that a generation entity or TSP takes to support the function of a facility during a weather emergency.

## Slide 4
(c) Weather emergency preparedness reliability standards for a generation entity.
By December 1,2021, a generation entity must complete the following winter weather emergency preparation measures for each resource under its control.
  (A) Use best efforts to implement weather emergency preparation measures intended to ensure the sustained operation of all cold weather critical components during winter weather conditions, including weatherization, onsite fuel security, staffing plans, operational readiness, and structural preparations; secure sufficient chemicals, auxiliary fuels, and other materials; and personnel required to operate the resource;

## Slide 5
(B) Install adequate wind breaks for resources susceptible to outages or derates caused by wind; enclose sensors for cold weather critical components; inspect thermal insulation for damage or degradation and repair damaged or degraded insulation; confirm the operability of instrument air moisture prevention systems; conduct maintenance of freeze protection components for all applicable equipment, including fuel delivery systems controlled by the generation entity, the failure of which could cause an outage or derate, and establish a schedule for testing of such freeze protection components on a monthly basis from November through March; and install monitoring systems for cold weather critical components, including circuitry providing freeze protection or preventing instrument air moisture;

## Slide 6
(C) Use best efforts to address cold weather critical component failures that occurred because of winter weather conditions in the period between November 30,2020, and March 1,2021;
(D) Provide training on winter weather preparations and operations to relevant operational personnel; and
(E) Determine minimum design temperature or minimum experienced operating temperature, and other operating limitations based on temperature, precipitation, humidity, wind speed, and wind direction.