## Slide 1
ERCOT Frequency Control Report
October 2021
ERCOT
Operations Planning
PDCWG | November 12th, 2021

## Slide 2: Summary of October 2021
CPS1: 170.98%
Current CPS1 12-Month Rolling Average: 169.37%
1 BAAL Exceedance(s)
5 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2021 RMS1 Statistics
  Mean: 16.44 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz
Energy Statistics
  Total Energy: 32,664,264 MWh
  Wind Energy: 8,604,573 MWh
  Percent Energy from Wind: 26.34%
  Solar Energy: 1,414,241 MWh
  Percent Energy from Solar: 4.33%
Minimum System Inertia
  Mean: 181,905 MW*s
  Max: 245,061 MW*s on Oct 4th
  Min: 134,760 MW*s on Oct 29th
Notes: 2018 BAAL-003 FRM Performance: -843.17
  Mean: 16.44 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz
Mean: 181,905 MW*s
Max: 245,061 MW*s on Oct 4th
Min: 134,760 MW*s on Oct 29th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Oct-21 CPS1 (%): 170.98
Notes: 1. 83.5% @ 10/14/2021 HE 19:00
Expected Generation Deviation
Expected gen dev remained negative for the entire hour. The largest expected gen dev was -2507 MW @ 18:15 with contribution from solar and wind.
IRR Ramps
Between 18:00 to 19:00 solar ramped down by 3900 MW and wind ramped down by 1000 MW.
Regulation: Regulation up was exhausted for the most part of this hour. A 300 MW SCED manual offset was applied.
2. 88.7% @ 10/27/2021 HE 2:00
Expected Generation Deviation
Expected gen dev remained negative for half of the hour. The largest expected gen dev was -2125 MW @ 1:17 with contribution from wind and combine cycles.
IRR Ramps
Between 1:03 to 1:18 wind ramped down by 450 MW.
DC Ties
Between 1:00 to 1:20 DC Tie ramped up by 215 MW.
Regulation: Regulation up was exhausted during the ramp intervals. A 200 MW SCED manual offset was applied.
3. 41.3% @ 10/27/2021 HE 19:00
Expected Generation Deviation
Expected gen dev remained negative for the entire hour. The largest expected gen dev was -3600MW @ 18:30 with contribution from solar and wind.
IRR Ramps
Between 18:32 to 19:00 solar ramped down by 700 MW and wind ramped down by 2800 MW. Steel mill load ramped up by 290 MW during the IRR ramps.
Regulation: Regulation up was exhausted during these IRR ramp intervals. A 200 MW SCED manual offset was applied.
4. 61.1% @ 10/28/2021 HE 19:00
Expected Generation Deviation
Expected gen dev remained negative for the entire hour.. The largest expected gen dev was -3685 MW @ 18:32 with contribution from solar and wind.
IRR Ramps
Between 18:00to 19:00 solar ramped down by 2200 MW and wind ramped down by 3200 MW.
Regulation: Regulation up was exhausted for the entire hour. A 300 MW SCED manual offset was applied.
5. 84.0% @ 10/29/2021 HE 19:00
Expected Generation Deviation
Expected gen dev remained negative for the entire hour. The largest expected gen dev was -2818 MW @ 18:08 with contribution from solar and wind.
IRR Ramps
Between 18:00to 19:00 solar ramped down by 3100 MW and wind ramped down by 4600 MW.
Regulation: Regulation up was exhausted for most part of the hour. A 250 MW and a 400 MW SCED manual offset were applied.

## Slide 5: BAAL Exceedances & Violations
There is 1 BAAL exceedance(s) in October
Notes: Occurred on 10/1/2021

## Slide 6: 15-Minute Average CPS1%
Oct-21 CPS1 (%): 170.98

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 169.37%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 16.44 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: 16Mhz on avg

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 32,664,264MWh

## Slide 22: Total Energy from Wind Generation
Notes: 8,604,573 MWh

## Slide 23: % Energy from Wind Generation
Notes: 26.34%

## Slide 24: Total Energy From Solar Generation
Notes: 1,414,241 MWh

## Slide 25: % Energy from Solar Generation
Notes: 4.33%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 134,760 MW*s on 10/29/2021
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 181,905 MW*s
Max: 245,061 MW*s on Oct 4th
Min: 134,760 MW*s on Oct 29th

## Slide 28: Questions?
Thank you!