## Slide 1
Review of Advanced Action Notices during October 2021
Dan Woodfin
Sr. Director, System Operations
WMWG
November 15, 2021

## Slide 2: Advanced Action Notices (AANs)
Issued October 7 for October 11
Issued October 18 for October 20-22
Issued October 20 for October 25

## Slide 3: Process
Issue AAN when potential shortage is seen in AAN planning assessment
Where feasible, wait 24 hours including 8 Business hours prior to issuing Outage Schedule Adjustments (OSAs) to allow:
  Self-adjustment of Outages based on market conditions
  Notification that Resources cannot be considered for an OSA
May issue OSAs once this waiting period is over
Issue AAN
Post Planning Assessment
(Prelim OAE)
< 1 hour
Update Planning Assessment (OAE)
>24 hrs and 8 Bus. Hrs
Issue Outage Schedule Adjustments if needed

## Slide 4: Planning Assessments
Based on:
  High Load forecast
  Lowest wind and solar forecasts
  Estimated forced outages and derates
  Emergency DC Tie imports
  Some price responsive demand and SODG
Maintain ability to cover load plus Ancillary Services from generation (which cover intraday forecast errors, etc.)
Goal is to retain availability of sufficient generation to operate conservatively
Updated as inputs change through Operating Day-1; but within Operating Day, use AS sufficiency
For this set of AANs, generally used 6500 MW of required AS from gen, 820 MW tie import capacity and 1500 MW for combo of price sensitive demand and DG
Moved a lot of transmission outages that would have affected generation availability and DC Tie outages

## Slide 5: AAN for 10/11
Planning Assessment Posted | AAN Worst Time | Load | Wind | Solar | Forced Outages | Shortage (-) /Actual Avail Capacity
10/7/2021 13:00 | 10/11/2021 19:00 | 56569 | 2490 | 1283 | 12075 | -2600
10/8/2021 13:00 | 10/11/2021 19:00 | 58302 | 4753 | 1257 | 11027 | -94
10/9/2021 13:00 | 10/11/2021 19:00 | 56022 | 6553 | 1271 | 10218 | >0
Actual | 10/11/2021 19:00 | 53867 | 11496 | 2219 | ~8800 | NA
No Outage Schedule Adjustments issued
  1737 MW of voluntary adjustments of planned outages
  Weather model forecasts evolved to decrease likelihood of low wind generation
Did not recalculate the sum of actual available capacity at this time

## Slide 6: AAN for 10/20-22
Planning Assessment Posted | AAN Worst Time | Load | Wind | Solar | Forced Outages | Shortage (-) /Actual Avail Capacity
10/18/2021 13:00 | 10/21/2021 18:00 | 53906 | 1599 | 2262 | 12545 | -3450
10/19/2021 13:00 | 10/21/2021 18:00 | 55774 | 2212 | 2103 | 12434 | -4500
10/20/2021 13:30 | 10/20/2021 19:00 | 53584 | 1690 | 575 | 10834 | -2750
Actual | 10/20/2021 18:25 | 52390 | 2947 | 1537 | 10484 | 5124
Few upcoming Planned Outages by time AAN was issued
No Outage Schedule Adjustments issued
  643 MW of voluntary adjustments of planned outages
  Weather model forecasts evolved to incrementally decrease load and solar but increase wind
Actual is at time of lowest PRC

## Slide 7: AAN for 10/25
Planning Assessment Posted | AAN Worst Time | Load | Wind | Solar | Forced Outages | Shortage (-) /Actual Avail Capacity
10/20/2021 15:45 | 10/25/2021 18:00 | 61580 | 3049 | 3217 | 10996 | -7000
10/21/2021 15:30 | 10/25/2021 18:00 | 59877 | 2201 | 3430 | 11336 | -5600
10/22/2021 15:30 | 10/25/2021 18:00 | 62865 | 4110 | 3561 | 10941 | -3950
10/23/2021 15:45 | 10/25/2021 17:00 | 61518 | 3529 | 5516 | 11207 | -1100
Actual for Monday | 10/25/2021 16:26 | 61495 | 5131 | 6213 | 9359 | 6796
Actual for Sunday | 10/24/2021 18:37 | 53456 | 4177 | 673 | 10767 | 4359
1615 MW of Outage Schedule Adjustments issued to 10 units
  1139 MW of voluntary adjustments of planned outages
  Weather model evolved to result in low point in wind generation to occur Sunday rather than Monday
OSAs were needed for Sunday
  Available Reserve Capacity would have been 2744 MW without the OSAs (4359 – 1615)
Actual is at time of lowest PRC

## Slide 8: Improvements
Now that this has been used a few times, want to collect improvement ideas
  External process
  Internal process
Some initial ideas on next two slides

## Slide 9: Improvement Ideas for Feedback - External
AAN Planning assessment will be posted hourly on a continuous basis once NPRR 1108 Phase 2 is implemented
Only a few Resources notified ERCOT that they could not be considered for an OSA
Some Entities did not adjust their Outage schedules during the 24-hour waiting period, but then wanted to adjust on their own (not receive OSA treatment) after being issued OSAs
  ERCOT will do hotline/MIS posting to indicate time units are subject to OSAs
Need better process for allowing Resources with ongoing Outages to communicate their ability to restore their Outage if they receive OSA treatment during the 24-hour waiting period
OSAs will apply to planned derates for the portion of the unit that is derated
Change energy offer curve in section 3.1.6.9.(g) ii (currently $4500)

## Slide 10: Improvement Ideas for Feedback - Internal
Tradeoff between issuing early to allow for more feasibility of outage adjustments and waiting for more accurate weather forecasts
  Timing of outage starts
  Day of week
  Magnitude of shortage relative to MW of upcoming outages
Future level of forced outages assumptions
  Used current level of FOs at time of planning assessment to estimate future level
  This is appropriate if FOs were random, but FOs may be lower if planning assessment is done on a lower load, higher wind day
Send OSA notifications to a general mailbox, not individual Client Svcs Reps
Chart: 
Future Forced Outages | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000
Currently Known Forced Outages | 12000 | 11900 | 11700 | 11200 | 11150 | 9950 | 9700

## Slide 11
Questions