## Slide 1
Proposed 2022 Ancillary Service Methodology And Preliminary Quantities
TAC
November 29, 2021
ERCOT Staff

## Slide 2: Stakeholder Discussion Timeline
August 11, 2021 – PDCWG (Current Methodology)
August 23, 2021 – WMWG (Current Methodology)
September 08, 2021 – PDCWG (Proposed Methodology)
September 22, 2021 – WMWG (Proposed Methodology)
October 13, 2021 – PDCWG (Proposed Methodology)
October 21, 2020 – OWG (Proposed Methodology)
October 25, 2021 – WMWG (Proposed Methodology)
November 03, 2021 – WMS (Not noted for a vote in time; not endorsed)
November 04, 2021 – ROS (Not noted for a vote in time; endorsed)
November 29, 2021 - TAC
December 14, 2021 - BoD

## Slide 3: Discussion Scope
Following is a summary of the proposed changes in the methodologies for determining Ancillary Service (A/S) quantities for 2022.
  ERCOT is not recommending any changes to the methodology used for computing Regulation Service requirements for 2022.
  ERCOT is recommending one change in the methodology used for computing Responsive Reserve Service (RRS) requirements for 2022.
  ERCOT is also proposing to change the minimum RRS-PFR limit for 2022 to 1,240 MW based on updates to NERC’s BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for OY2022.
  ERCOT is recommending changes in the methodology used for computing Non-Spinning Reserve Service (Non-Spin) requirements for 2022 that will account for the highest 6 hours ahead net load forecast error within an operating hour and intra-day changes in thermal resource availabilities due to forced outages.
  The Ancillary Service (A/S) quantities for 2022 contained in this presentation are based on the methodology that was approved in December 2020. The quantities for 2022 reflect moving forward the historic data on which these are based, unless otherwise noted.
A redline version of the draft methodology and spreadsheets that contain the associated quantities for January through October of 2022 have been posted on the meeting page for this meeting.

## Slide 4: Regulation Service Methodology
ERCOT is not proposing any change to the methodology used to compute the minimum Regulation Service requirements for 2022.
The preliminary Regulation quantities for January 2022 through October 2022 in subsequent slides have been computed using current methodology (2020 and 2021 five-minute net load variability), updated Wind Adjustment tables and the updated Solar Adjustment tables.
  Wind and Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind and solar capacity, respectively.

## Slide 5: Average Regulation Comparison
Notes: Reg Up
On an average blue and red are fairly similar. Largest increase is 91 MW in Mar
Reg Do
On an average blue and red are fairly similar. Largest increase is 94 MW in May

## Slide 6: Responsive Reserve Service (RRS) Methodology
ERCOT is proposing one change to the methodology used to compute the minimum RRS requirements for 2022.
  A floor of 2800 MW will be applied to RRS quantities during the peak. During the peak hour, this additional RRS will help maintain a larger operating margin and operate more conservatively.
ERCOT is proposing to change the minimum RRS-PFR limit for 2022 to 1,240 MW to align with ERCOT’s updated IFRO for OY2022. NERC’s preliminary 2022 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows a reduction in ERCOT’s IFRO. This is primarily because of an update in the IFRO methodology that as approved as a part of the Project 2017-01, Modifications to BAL-003.
The preliminary RRS quantities for January 2022 through October 2022 in subsequent slides have been computed using 2020 and 2021 system inertia conditions and updated RRS table.
  The RRS table tracks RRS requirements for different inertia conditions. This table has been updated in 2022 to use a minimum RRS-PFR limit of 1,240 MW.
Notes: RRS quantity for 2022 decrease between 8 MW (310 GW.s case) and 82 MW (170 GW.s case)

## Slide 7: Hourly Average RRS Comparison
Notes: On an average RRS quantities between 2021 and 2022 are fairly similar; largest increase between blue and purple is 145 MW in June
May – milder 2021 has influenced increase
Jun – floor during peak hours

## Slide 8: Non-Spinning Reserve Service Methodology
ERCOT is proposing the following changes to the methodology used to compute minimum Non-Spin requirements in 2022
  Update the hourly net load forecast uncertainty calculation to use
    the 6 Hours-Ahead net load forecast, and
    the highest 5-min net load within the hour
  Change percentile coverage to vary between 85th and 95th . The applicable coverage for any hour will continue to be based on risk of net load up ramp in the hour.
  Include an adjustment to account for intra-day forced outages of thermal resources.
The preliminary Non-Spin quantities for January 2022 through October 2022 in subsequent slides have been computed using current methodology (2019, 2020 and 2021 Net load and Net load Forecast), updated Wind Over-Forecast Error Adjustment table and the updated Solar Over-Forecast Error Adjustment table.
  Wind and Solar Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind and solar capacity, respectively.

## Slide 9: Forecast Variability Process
In 2022, ERCOT is proposing to continue the practice of monitoring the weather near Real Time and may procure up to an additional 1,000 MW of Non-Spin for specific Operating Hours.
The approach for determining the additional increase will be updated such that the additional Non-Spin may be procured for Operating Hours that are
  identified as having an increased potential of high forecast variability,
  there is a risk that the actual net load during these Operating Hours could be higher than forecast (after making appropriate forecast model selection) AND
  the expected available capacity and expected reserves including the posted minimum Non-Spin requirements during these Operating Hours is not sufficient to cover the projected net load forecast uncertainty risk.
If the above proposed approach was used during the nine Operating Days since July 6, 2021 wherein additional Non-Spin quantities were procured due to high forecast variability and risk of net load under-forecast, projected available capacity and expected reserves were identified as being sufficient in eight of these days and additional Non-Spin quantities would not have been procured.

## Slide 10: Proposed Intra-Day Forced Outage Table 2022
The proposed Intra-Day Forced Outage table has been built using 75th percentile of the maximum hourly accumulated forced outage in every 6-hour block for each month in 2018, 2019, 2020.
  A conservative 75th percentile coverage is recommended due to the observation that the extreme forced outages tend to not occur at the same time as the highest net load forecast error.
Notes: Max 1129 MW
Average 730 MW
Min 392 MW

## Slide 11: Non-Spin January
Notes: Max change between red and purple in HE15-18 is 2878 MW.
Largest value 4520 MW in HE15-18.
On an average increase of 2135 MW
The “6500 Method”: Non-Spin = 6500 – (Reg-Up + RRS-PFR-Gen/ESR)
The 2021 (Intra Year Posting) has the following three trends
  2021 NSRS between Jan 1 and Jul 12: Based on Dec 2020 Posting
  2021 NSRS between Jul 12 and Aug 31: Non-Spin = 6500 – (Reg Up + RRS)
  2021 NSRS between Sep 1 and Dec 31 : Non-Spin = 6500 – (Reg Up + RRS-PFR-Gen/ESR)

## Slide 12: Non-Spin June
Notes: Max change between red and purple in HE1-2,23-24 is 2896 MW.
Largest value 4839 MW in HE13-14.
On an average increase of 2367 MW
The “6500 Method”: Non-Spin = 6500 – (Reg-Up + RRS-PFR-Gen/ESR)
The 2021 (Intra Year Posting) has the following three trends
  2021 NSRS between Jan 1 and Jul 12: Based on Dec 2020 Posting
  2021 NSRS between Jul 12 and Aug 31: Non-Spin = 6500 – (Reg Up + RRS)
  2021 NSRS between Sep 1 and Dec 31 : Non-Spin = 6500 – (Reg Up + RRS-PFR-Gen/ESR)

## Slide 13: Hourly Average Non-Spin Comparison
Notes: Between Jan – Jun 2022, on an average, as can be expected, there is an increase (2200 MW+) in Non-Spin quantities in comparison to 2021.
Between Jul – Dec 2022, on an average the quantities are similar and/or mostly lower in comparison to 2021.
On an average largest increase between blue and purple is 3030 MW in May.
On an average largest increase between red and purple is 2367 MW in June.
The “6500 Method”: Non-Spin = 6500 – (Reg-Up + RRS-PFR-Gen/ESR)
The 2021 (Intra Year Posting) has the following three trends
  2021 NSRS between Jan 1 and Jul 12: Based on Dec 2020 Posting
  2021 NSRS between Jul 12 and Aug 31: Non-Spin = 6500 – (Reg Up + RRS)
  2021 NSRS between Sep 1 and Dec 31 : Non-Spin = 6500 – (Reg Up + RRS-PFR-Gen/ESR)

## Slide 14: Summary
Following is a summary of the proposed Ancillary Service Methodology for 2022.
  ERCOT is not recommending any changes to the methodology used for computing Regulation Service requirements.
  ERCOT is recommending one change in the methodology used for computing Responsive Reserve Service (RRS) requirements.
  ERCOT is also proposing to change the minimum RRS-PFR limit for 2022 to 1,240 MW based on updates to NERC’s BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for OY2022.
  ERCOT is recommending changes in the methodology used for computing Non-Spinning Reserve Service (Non-Spin) requirements that will account for the highest 6 hours ahead net load forecast error within an operating hour and intra-day changes in thermal resource availabilities due to forced outages.
ERCOT is seeking TAC’s endorsement for the proposed 2022 Ancillary Service Methodology.

## Slide 15
Discussion