## Slide 1
Lower Rio Grande Valley (LRGV) System Enhancement Regional Planning Group Project
Shun Hsien (Fred) Huang
Manager, Regional Planning
Technical Advisory Committee Meeting
ERCOT Public
November 17, 2021

## Slide 2: Overview
ERCOT submitted the Lower Rio Grande Valley (LRGV) System Enhancement project for Regional Planning Group review
  The project was submitted as a Tier 1 project that was estimated to cost $1.28 Billion
  Primarily addresses reliability needs
  Improves system resiliency under high-impact weather conditions
  Mitigates stability constraints and subsynchronous resonance (SSR) vulnerability
  Provides operational flexibility
  Provides long-term transmission capability for future load and generation development

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review indicated reliability planning criteria violations under normal system condition and multiple high-impact weather scenarios
System improvement is needed to meet reliability planning criteria
Base Case | Reliability Need Year
All in service (Base Case, Normal System Condition) | 2027
Outage of two conventional plants in LRGV | Current
Outage of one 345-kV import circuit | Current
Outage of two 345-kV import circuits | Current
Very Low Wind/Solar Conditions | Current

## Slide 5: Consideration of Ultra-High-Voltage (UHV) AC Circuit
345-kV circuits
  Require series compensation to effectively improve transfer capability, however, the SSR vulnerability to both synchronous generators and inverter-based resources must be assessed
  All three existing 345-kV LRGV import circuits are series compensated
500-kV circuits
  Improve power transfer capability but also require more right-of-way and higher cost
Low impedance 345-kV circuit (recommended option in this project)
  Provide sufficient transfer capability without series compensation
  Require less right-of-way and cost compared to a 500-kV circuit

## Slide 6: Comparison of Project Options
ERCOT developed two short-listed options
Option 2 is the preferred option
Items | System Improvement | 
 | Option 1 | Option 2
Estimated new 345-kV right of way (miles) | 357 | 351
Estimated cost ($Billion) | $1.34 | $1.28
LRGV load serving capability (BAU) | > 2040 | > 2040
Improve system resilience and operation flexibility | Yes | Yes
Improve stability constraints | Yes | Yes (Superior to Opt. 1)
Reduce SSR vulnerability | Yes | Yes (Superior to Opt. 1)
Reduce the impact of hurricane | Yes | Yes (Superior to Opt. 1)
Future load and generation integration | Yes | Yes

## Slide 7: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for the preferred Option 2 and found no adverse SSR impacts to the existing and planned generation resources in the LRGV area
  A detailed SSR assessment is recommended due to historical SSR challenges in the LRGV area
  TSPs that owns the affected series capacitors will coordinate with ERCOT to perform and complete a detailed SSR assessment and SSR Mitigation, if required, prior to energization of the preferred Option 2

## Slide 8: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 2 did not cause new or additional congestion
  Four potential renewable resources located inside the LRGV area were identified and are not expected to have a material impact on the project need
  The load scaling did not have a material impact on the project need

## Slide 9: ERCOT Recommendation:
Based on the review, ERCOT will recommend the Board endorse Option 2 to address the reliability need in the LRGV area
TSPs expect to implement the upgrades by 2027
Estimated Capital Cost: $1.28 Billion
ERCOT will recommend that the Board designate Option 2 as critical to the reliability of the ERCOT System pursuant to PUCT Substantive Rule 25.101(b)(3)(D)

## Slide 10: ERCOT Recommendation: Option 2
Construct a new 345-kV New Substation 1 approximately 69.2 miles east of existing Cenizo 345-kV substation
Construct a new 345-kV New Substation 2 tapped into the existing 345-kV line from Lon Hill to North Edinburg approximately 48 miles east of New Substation 1
Build a new double-circuit 345-kV line from existing San Miguel substation to New Substation 1 (approximately 132.8 miles, normal and emergency ratings of at least 1,784 MVA)
Build a new double-circuit 345-kV line from New Substation 1 to existing Del Sol substation (approximately 54.2 miles, normal and emergency ratings of at least 1,784 MVA)
Build a new double-circuit 345-kV line from New Substation 1 to existing Cenizo 345 kV substation (approximately 69.2 miles, normal and emergency ratings of at least 1,784 MVA)
Build a new double-circuit 345-kV line between New Substation 1 and New Substation 2 (approximately 48 miles, normal and emergency ratings of at least 1,784 MVA)
Build a new double-circuit 345-kV line from existing Ajo substation to New Substation 2 (approximately 11 miles, normal and emergency ratings of at least 1,784 MVA)
Construct a new Frontera 345-kV substation at the existing Frontera 138-kV substation
Build a new double-circuit 345-kV line from existing Del Sol substation to new Frontera substation (approximately 36.5 miles, normal and emergency ratings of at least 1,784 MVA)
Install two new 345/138-kV transformers at the Frontera substation (normal and emergency ratings of at least 743 MVA)

## Slide 11: Option 2

## Slide 12: Option 1