## Slide 1
Generic Transmission Constraint (GTC) Modeling Error Impacting the Day-Ahead Market (DAM) and Potential Price Correction - Analysis of Settlement Impacts
Alfredo Moreno
Manager, Forward Markets
TAC
November 29, 2021

## Slide 2: Background
On October 13, 2021, ERCOT discovered an error related to the modeling of the NE_LOBO GTC in the DAM.
The NE_LOBO GTC definition (interface constraint) consists of the following transmission equipment:
The constraint represents a stability limit associated with South Texas wind farms connecting along the North Edinburg – Lobo 345 kV line.
Line/Autotransformer Acronym | From Station (Acronym) | To Station (Acronym) | Voltage Rating (kV) | Line/Auto Rating (MVA)
1_345_138_H | Lobo 345 kV (LOBO) | Lobo 138 kV (LOBO) | 345/138 | 675
2_345_138_H | Lobo 345 kV (LOBO) | Lobo 138 kV (LOBO) | 345/138 | 675
LOBO_FOWLRTN1 | Lobo (LOBO) | Fowlerton (FOWLRTON) | 345 | 1329
NEDIN_POMELO1 | Pomelo (POMELO) | North Edinburg (NEDIN) | 345 | 1322*
* Line is dynamically rated. Listed rating is static nominal rating.

## Slide 3: Background- Communication
On October 13, 2021, ERCOT implemented a corrected definition for the NE_LOBO GTC in the DAM as a manual workaround; the corrected definition was effective as of OD October 14, 2021.
ERCOT determined that DAM prices for OD October 13, 2021, were impacted by the incorrect GTC definition and corrected prices for that OD prior to prices becoming final. ERCOT posted price correction data for OD October 13, 2021, on October 14, 2021.
ERCOT also determined that the NE_LOBO GTC was incorrectly modeled in the DAM model load impacting ODs October 7 to 12, 2021. ERCOT issued a public notice on October 15, 2021, that DAM prices were under investigation for those ODs due to the incorrect GTC definition.

## Slide 4: Background- Communication
ERCOT subsequently determined that the NE_LOBO GTC was also incorrectly modeled in a DAM model load that impacted ODs September 30 to October 6, 2021. Accordingly, ERCOT issued a public notice on October 22, 2021, that DAM prices were also under investigation for ODs September 30 to October 6, 2021, due to the incorrect GTC definition
Upon completion of the investigation into prices, ERCOT issued Market Notice W-C102921-01 on October 29, 2021, which informed Market Participants that ERCOT would seek correction of DAM prices for September 30, 2021, and October 6 to 12, 2021
Real-Time Market prices were not impacted by this error

## Slide 5: Input Error
ERCOT’s investigation determined that a defect existed in the Common Information Model (CIM) Importer introduced by the CIM version 16 (CIM16) upgrade project
The CIM Importer translates the ERCOT Network Operations Model to a readable format consumed by the Market Management System (MMS)
The CIM upgrade project was the first CIM upgrade project undertaken by ERCOT since Nodal Go-Live
The modified class changes in CIM16 led to the CIM Importer interpreting the transformer (mw flow) direction incorrectly for the NE_LOBO GTC
On October 13, 2021, ERCOT implemented a manual workaround to address the modeling error, starting with OD October 14, 2021
On October 28, 2021, ERCOT deployed an off-cycle release to fix the defect (account for the class changes)

## Slide 6: Impacts to the DAM
For the impacted ODs, ERCOT reran DAM cases in a study environment with the corrected NE_LOBO GTC definition to determine price and settlement impacts
After reviewing the cases for the thirteen impacted ODs:
  On four ODs, prices were not impacted by the modeling error because the NE_LOBO was not binding in the Production case or re-run case.
  One OD, prices were impacted by the modeling error but did not meet the “significant” threshold in Protocol Section 4.5.3 (6)(b) for seeking correction of prices by the ERCOT Board
ERCOT found that there were 8 ODs that met the “significant” criteria threshold in Protocol 4.5.3 (6)(b) and are eligible for consideration of a price correction by the ERCOT Board

## Slide 7: “Significance” criteria for price correction
Per Protocol Section 4.5.3(6)(b), ERCOT must seek correction of DAM prices by the ERCOT Board for an OD if the absolute value impact of the price correction on any single Counter-Party (CP) -- based on the sum of all original DAM Settlement Statement amounts of MPs assigned to the CP for the OD -- is greater than either:
    (i) 2% and also greater than $20,000; or
    (ii) 20% and also greater than $2,000.

## Slide 8: Estimated Settlement Impacts
OD | Change in Statement Charges Due to ERCOT | 
9/30/2021 | ($33.86) | 0.3%
10/6/2021 | ($14.58) | 0.1%
10/7/2021 | ($54.74) | 0.4%
10/8/2021 | $19.84 | 0.1%
10/9/2021 | $76.59 | 0.4%
10/10/2021 | $344.36 | 1.4%
10/11/2021 | ($19.11) | 0.1%
10/12/2021 | $375.30 | 1.6%
All Settlement amounts are changes in statement amounts due to ERCOT in $ thousands. Negative amounts are reduced charges to Market Participants; positive amounts are increased charges.
The % amount is the absolute value of the % of impact to the previously settled statement amounts due to ERCOT.

## Slide 9: DAM Settlement Impacts
 | Energy Purchases |  | Energy Sales |  | PTP Purchases |  | CRR Settlements |  | AS Payments |  | Make-whole Payment | 
9/30/2021 | (201.9) | 0.6% | 196.0 | 0.6% | 33.4 | 1.2% | (25.4) | 0.9% | 29.5 | 1.2% | (0.0) | 0.0%
10/6/2021 | (20.4) | 0.1% | 21.0 | 0.1% | 5.2 | 0.2% | (12.8) | 0.6% | 19.2 | 0.6% | 0.0 | 0.0%
10/7/2021 | 49.9 | 0.1% | (44.6) | 0.1% | (22.0) | 0.6% | 8.1 | 0.2% | 6.4 | 0.2% | 2.1 | 14.7%
10/8/2021 | (54.1) | 0.1% | 46.3 | 0.1% | (22.9) | 0.4% | 33.9 | 0.4% | (23.0) | 0.5% | 0.4 | 43.0%
10/9/2021 | (147.6) | 0.4% | 137.7 | 0.4% | 165.8 | 2.1% | (124.9) | 1.1% | 14.4 | 0.4% | (0.2) | 4.0%
10/10/2021 | (349.7) | 1.0% | 340.0 | 1.1% | 586.8 | 5.9% | (315.5) | 2.8% | (15.0) | 0.4% | 0.0 | 0.0%
10/11/2021 | (377.0) | 0.8% | 365.0 | 0.8% | 142.6 | 3.0% | (28.6) | 0.5% | 40.8 | 1.0% | (0.1) | 0.6%
10/12/2021 | 61.1 | 0.2% | (47.3) | 0.2% | 451.0 | 4.2% | (154.0) | 1.2% | (49.5) | 1.4% | (5.9) | 13.7%
All Settlement amounts are net amounts due to/from ERCOT in $ thousands. Negative amounts are increased payments to Market Participants; positive amounts are increased charges.
The % amount is the absolute value of the % of impact to the previously settled net amount due to/from ERCOT.

## Slide 10: Settlement Impacts to Counter-Parties
OD | Absolute Value Impact to Counter-Party |  | 
 | Maximum Amount ($Thousand) | Maximum Percentage Criteria in Protocol Section 4.5.3(6)(b)(i)* | Maximum Percentage Criteria in Protocol Section 4.5.3(6)(b)(ii)**
9/30/2021 | 27.9 | 369.6% | 560.0%
10/6/2021 | 5.9 | NA | 117.9%
10/7/2021 | 16.1 | NA | 225.1%
10/8/2021 | 27.6 | 3.0% | 33.0%
10/9/2021 | 38.9 | 876.1% | 2638.3%
10/10/2021 | 94.6 | 1409.2% | 1409.2%
10/11/2021 | 25.0 | 280.3% | 280.3%
10/12/2021 | 66.3 | 137.3% | 209.1%
* The maximum of percentage change to any single Counter-Party with an impact of more than $20,000 (set as NA when no single counter party has impact more than $ 20,000).
** The maximum of percentage change to any single Counter party with impact more than $2,000 (set as NA when no single counter party has impact more than $ 2,000)
OD 10/1/2021 was also evaluated for Settlement impacts and did not meet the criteria for Board review. The maximum impact to any individual Counter Party on OD 10/1/2021 was $623.

## Slide 11: Next Steps
ERCOT will request that the ERCOT Board review and approve the correction of DAM prices for ODs September 30, 2021, and October 6 to 12, 2021, at the next ERCOT Board meeting, which is currently scheduled for Dec 9 & 10, 2021.