## Slide 1
ERCOT Frequency Control Report
November 2021
ERCOT
Operations Planning
PDCWG | December 8th, 2021

## Slide 2: Summary of November 2021
CPS1: 172.59%
Current CPS1 12-Month Rolling Average: 169.32%
1 BAAL Exceedance(s)
0 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2021 RMS1 Statistics
  Mean: 16.37 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz
Energy Statistics
  Total Energy: 27,968,176 MWh
  Wind Energy: 8,537,442 MWh
  Percent Energy from Wind: 30.53%
  Solar Energy: 1,182,376 MWh
  Percent Energy from Solar: 4.23%
Minimum System Inertia
  Mean: 149,710 MW*s
  Max: 212,412 MW*s on Nov 4th
  Min: 128,780 MW*s on Nov 17th
Notes: Mean: 149,710 MW*s
Max: 212,412 MW*s on Nov 4th
Min: 128,780 MW*s on Nov 17th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Nov-21 CPS1 (%): 172.59

## Slide 5: BAAL Exceedances & Violations
There is 1 BAAL exceedance(s) in November
Notes: Occurred on 11/17/2021 due to a frequency event

## Slide 6: 15-Minute Average CPS1%
Nov-21 CPS1 (%): 172.59

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 169.32%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 16.37 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: 16Mhz on avg

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 27,968,176MWh

## Slide 22: Total Energy from Wind Generation
Notes: 8,537,442 MWh

## Slide 23: % Energy from Wind Generation
Notes: 30.53%

## Slide 24: Total Energy From Solar Generation
Notes: 1,182,376 MWh

## Slide 25: % Energy from Solar Generation
Notes: 4.23%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 128,780 MW*s on 11/4/2021
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 149,710 MW*s
Max: 212,412 MW*s on Nov 4th
Min: 128,780 MW*s on Nov 17th

## Slide 28: Questions?
Thank you!