## Slide 1
Regulation Bias Analysis Post SCR-773
Nov 2021
ERCOT
Operations Planning
PDCWG | Dec 8th, 2021

## Slide 2
Discussion Points
Current GTBD Parameters & References
Metric to measure Regulation bias and performance
Regulation Deployed comparison for last three months.
Total Regulation (net) Deployed Comparison
Regulation Deployed 15-minute interval comparison by each hour for 2018, 2019, and 2020 months
Regulation Exhaustion Rate
Regulation bias for consecutive 5-min SCED intervals
Time Error & Contributing Factors
Summary

## Slide 3: Current GTBD Parameters
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 – K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 – 10:05 AM – K6 Changed from 0 to 0.5
2/12/19 – 2:15 PM – K6 changed from 0.5 to 1.0
3/12/19 – 2:10 PM – PWRR Threshold from 10 to 15 MW/min
3/19/19 – 2:15 PM – PWRR Threshold from 15 to 20 MW/min
4/01/19 – 10:00 AM – K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 – 1:15 PM – Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – 1:10 PM – K5 changed from 0.4 to 0.5, Max Integral ACE feedback changed from 160 to 200, PWRR Threshold changed from 25 to 30
6/17/20 – 10 AM - PWRR Calculation method changed from Direct to Interpolated
9/1/20 – 11 AM - Max Integral ACE Feedback changed from 200 to 250
9/3/20 – 3 PM - Max Integral ACE Feedback changed from 250 to 300
9/4/20 – 3 PM - Max Integral ACE Feedback changed from 300 to 250
6/1/21 – 10:00 AM – K8 Changed from 0 to 0.5, PSRR Threshold changed to 10
6/2/21 – 10:00 AM – PSRR Threshold changed from 10 to 20
6/3/21 – 10:00 AM – K8 Changed from 0.5 to 0.75
6/4/21 – 10:00 AM – K8 Changed from 0.75 to 1
9/2/21 – 10:00 AM – PSRR Threshold changed to 30

## Slide 4: Projected Wind Ramp Rate MAE

## Slide 5: Projected Wind Ramp Rate Error

## Slide 6: Projected Solar Ramp Rate MAE

## Slide 7: Projected Solar Ramp Rate Error

## Slide 8: References

## Slide 9
Metrics to Measure SCR-773 Performance
Trend and monitor the regulation deployed by hour.
Set target of 50 MW for total regulation deployed by hour for peak hours.
Set target of 85% for the number of intervals where regulation deployment was both up and down for peak hours.
Track the Regulation exhaustion rate for all hours (not to exceed 5%).
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5 minute intervals for peak hours.

## Slide 10: Total Regulation Deployed Comparison
Total regulation deployed for the last three months.

## Slide 11: Total Regulation Deployed Comparison - Monthly

## Slide 12: Metric 1: Regulation Deployed Comparisons
Trend and monitor the regulation deployed by hour.

## Slide 13: Regulation Deployed Comparison

## Slide 14: Regulation Deployed Comparison

## Slide 15: Regulation Deployed Comparison

## Slide 16: Metric 2: Total Regulation Deployed Comparisons
Set target of 50MW for total regulation deployed by hour for peak hours.

## Slide 17: Total Regulation Deployed Comparison

## Slide 18: Metric 3: 15-min Intervals Where Both REGUP/REGDN Were Deployed
Set target of 85% for the number of intervals where regulation deployment was both up and down.

## Slide 19: “Zero” Crossing Regulation

## Slide 20: “Zero” Crossing Regulation

## Slide 21: Metric 4: Regulation Exhaustion Rate
Track the regulation exhaustion rate for all hours (not to exceed 5%.)

## Slide 22: Regulation Exhaustion Rate

## Slide 23: Regulation Exhaustion Rate

## Slide 24: Metric 5: Stats on REGUP Bias for Consecutive 5-min Intervals
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5-minute intervals for peak hours.

## Slide 25: Regulation Bias for Consecutive SCED Intervals

## Slide 26: Regulation Bias for Consecutive SCED Intervals

## Slide 27: Time Error and Contributing Factors
Accumulated Time Error, Load and Wind Ramp, PWRR Error, Start-Up/Shut-Down Hours, STLF Error, and Expected Generation Deviation.

## Slide 28: Time Error Accumulation

## Slide 29: Load Profile

## Slide 30: Net Load Profile

## Slide 31: Load Ramp

## Slide 32: Wind Profile

## Slide 33: Start-Up & Shut-Down Hours

## Slide 34: Short-Term Load Forecast Error
Notes: Forecast – Actual
+ve Error => Over forecasted load
-ve Error +> Under forecasted load

## Slide 35: STLF Error Chart
Notes: Error = Forecast – Actual
Min,Max, 10th, 90th percentile
15 minute intervals
Max Positive Forecast Error:
11/14/2021 5:30 -> 375 MW
Max Negative Forecast Error:
11/27/2021 11:45-> -367 MW

## Slide 36: Expected Generation Deviation

## Slide 37: Expected Generation Deviation

## Slide 38: Expected Generation Deviation

## Slide 39: Questions?
Thank you!