## 1) General Information
CenterPoint Energy Distribution Loss Factor for |  |  |  |  | 2022
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses, which was updated on September 1, 2016. See following
protocol link: http://www.ercot.com/mktrules/nprotocols/current
According to this protocol, ERCOT will calculate Distribution Loss Factors for each Settlement Interval of the Operating Day for
settlement purposes. Distribution Loss Factors will be calculated from the data provided by Distribution Service Providers using
the following equation
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load (15 minute basis)
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
| AAL value for use in 2022 = |  | 11,048 MWH
AAL value for use in 2021 = 10,968 MWH
AAL value for use in 2020 = 10,740 MWH
AAL value for use in 2019 = 10,708 MWH
AAL value for use in 2018 = 10,190 MWH
AAL value for use in 2017 = 9,898 MWH
AAL value for use in 2016 = 9,940 MWH
AAL value for use in 2015 = 9,741 MWH
AAL value for use in 2014 = 9,290 MWH
AAL value for use in 2013 = 9,304 MWH
AAL value for use in 2012 = 9,463 MWH
AAL value for use in 2011 = 9,034 MWH
AAL value for use in 2010 = 8,785 MWH
Customer Coding for CenterPoint Energy:
Distribution customers that take service at secondary voltage are coded "D"
Distribution customers that take service at primary voltage are coded "E"
CenterPoint Energy customers taking service at transmission level voltages have no distribution losses associated with their energy
delivery. Therefore, each transmission ESI-ID account has been coded with a "T", and their losses are determined by ERCOT rules for
transmission customers.
For "D" Secondary Customers
F1 = |  | 0.0205
F2 = |  | -0.0068
F3 = |  | 0.025
AAL for ERCOT (15 mins) = 10,708 |  | 11048
For "E" Primary Customers
F1 = |  | 0.01522
F2 = |  | -0.0062
F3 = |  | 0.0035
AAL for ERCOT (15 mins) = 10,708 |  | 11048
Assumptions
1. Assume AAL for CNP corresponds to AAL for ERCOT
2. However, the peak for CNP is proportionately greater than the peak for ERCOT relative to AAL.
Ratio of Peak to AAL
|  | CNP | ERCOT
|  | 2.0005 | 1.6697
Ratio of Peak to AAL for CNP is not proportional to ERCOT
| 2019 for use in 2020 |  | 2020 for use in 2021 |  | 2021 for use in 2022
| 15 mins | 1 hour | 15 mins | 1 hour | 15 mins | 1 hour
CNP Peak | 3917.75 | 15671 | 3952 | 15808 | 3835 | 15340
CNP AAL | 1954.75 | 7819 | 1945 | 7780 | 1917 | 7668
ERCOT Peak | 18686 | 74744 | 18598 | 74392 | 18446.5 | 73786
ERCOT AAL | 10740 | 42960 | 10968 | 43872 | 11048 | 44192
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % losses (and DLF) above AAL are
increased an amount that is consistent with this higher loading at peak, so that when ERCOT hits peak, % losses will correspond to CNP peak.
Methodology upon which the calculation of loss factor was made:
Over the years, CenterPoint Energy has developed system loss equations for each part of the system. Equations for distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses
were utilized to calculate the total losses on the CenterPoint Energy distribution system for various load levels. See Tab 3 - Loss Equations.
|  | Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
The constants (A & B) for each of the equations were updated in 2018 for use as follows:
1. Substation Transformer Losses - The A B constants for substation transformers were updated for | [7 empty] | 2022
The current substation transformer database was used to determine the total "No-load" losses for all transformers on the system.
This database contains test data for every substation transformer.
| The total no-load losses are |  | 18.826 | MW.
Also, the database provided the total "Load" losses for the transformers on the system at rated trf load.
| This value is | 64.53 | MW at | 18.826 | MW load level.
| This results in a total of |  | 83.356 | MW of substation transformer losses at approximately |  |  |  | 18835 | MVA at CNP (Sub Trf nameplate rating)
The constants in the system loss equations were adjusted to match this result. See Tab 3.
2. Primary Conductor Losses (No change in the A B constants for primary conductor)
The primary conductor losses for 2007 were considered to be similar to the losses in 2006, but the constant for the system loss
equation was increased 2.5% due to the increased loading on our circuits which is a result of our revised design criteria.
The design criteria allows higher loadings due to an increase in switching operations under contingency conditions from
2 pairs of switching operations to 4 pairs of switching operations.
| For | 2022 | there is no further change in the system loss equations.
3. Distribution Transformer Losses - The A B constants for distribution transformers were updated for | [7 empty] | 2022
An inventory of the distribution transformers was downloaded from the GIS system. For every size transformer
the "No-load" losses and "Load" losses were determined by various test reports. This information was entered
for each size of transformer to determine the total "No-load" losses and the total "Load" losses for the distribution transformers.
Additionally, a TLM (Transformer Load Maintenance) Program was used to calculate no-load and load losses.
Since the no-load losses used in the TLM program were based on older/higher values from 1985 and the GIS spreadsheet
used more current test values from 2000-2005, the results of the two programs were averaged together to get
a balanced result for "no-load" losses for a distribution system that has both old and new transformers.
The "load losses" from both methods were very close, so the load losses from GIS were used.
See Tab 3 for the updated A B constants for distribution transformers.
4. Secondary Conductor Losses - No change in the A B constants for secondary conductor for | [6 empty] | 2022
The constant in the system loss equation for secondary losses is same as used in previous years.
5. AAL for ERCOT
| The AAL for ERCOT was updated based on information from ERCOT. The new value is | [5 empty] | 11048 | MWH for 15 minutes.
DLF Coefficients (F1, F2 and F3)
For both primary and secondary customers, the F1, F2 and F3 coefficients were selected to provide a curve fit with the loss equations that were
developed above. F1 impacts the right side of the curve, F2 impacts the middle/entire curve, and F3 impacts the left side of the curve. These
coefficents were adjusted to get a curve fit in the most critical areas. See spreadsheet and graphs in Tab 2 - Loss Analysis.
The F1, F2, and F3 coefficients for D secondary customers and E primary metered customers for 2017 are shown above.
Overall results:
For "E" Primary Customers |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 for use in 2022
|  | DLF at AAL | 1.274% | 1.286% | 1.3% | 1.27% | 1.286% | 1.252%
|  | DLF at ERCOT Peak | 2.154% | 2.107% | 2.155% | 2.157% | 2.18% | 2.131%
For "D" Secondary Customers |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 for use in 2022
|  | DLF at AAL | 3.805% | 3.791% | 3.816% | 3.838% | 3.837% | 3.87%
|  | DLF at ERCOT Peak | 4.256% | 4.213% | 4.259% | 4.289% | 4.303% | 4.24%
Questions:
If you have any questions, please call Robert Pitcel at 713-207-7621 or Brian Clowe 713-207-6287.
or email Robert Pitcel at robert.pitcel@centerpointenergy.com or Brian Clowe at brian.clowe@centerpointenergy.com

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 2) Loss Analysis
|  | CenterPoint Energy Distribution Loss Factor | [12 empty] | No Scaling | With Scaling | Using F1, F2 & F3 Coefficients |  | No Scaling | With Scaling
ERCOT | ERCOT |  | CNP | CNP |  | PELCAR | Primary | Total | Total |  |  |  | Secondary | [5 empty] | Total |  | Adjustment for % Losses |  | 2008 | 2008
Load (15 min) | Load (1 hr) |  | Load (15 min) | Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | Total Losses | DLF | DLF | Primary Loss % | Primary Loss % | Sec | Pri | Primary MW Losses | Sec MW Losses
|  |  |  | (MW) | (MW) | (MW) | (MW) |  |  | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | Secondary | Primary
SIEL | [15 empty] | 0% |  |  |  | 0%
|  |  |  | 50 | 18.5694 | 31.4306 | 0.0011256 | 18.5706 | 37.14% | 31.4294 | 156.7244 | -125.295 | 0.0055646 | 175.3005 | 350.6% | 350.6%
|  |  |  | 135 | 18.5721 | 116.4279 | 0.015445 | 18.5876 | 13.77% | 116.4124 | 156.7294 | -40.317 | 0.00057616 | 175.3176 | 129.9% | 129.9%
|  |  |  | 500 | 18.6121 | 481.3879 | 0.26404 | 18.8761 | 3.775% | 481.1239 | 156.8167 | 324.3071 | 0.03728 | 175.7301 | 35.15% | 35.15%
1440.7929 | 5763.1716 |  | 250 | 1000 | 18.7414 | 981.2586 | 1.0971 | 19.8385 | 1.984% | 980.1615 | 157.1088 | 823.0527 | 0.24012 | 177.1874 | 17.72% | 17.72%
3457.903 | 13831.6119 | 1 | 600 | 2400 | 19.5621 | 2380.4379 | 6.4563 | 26.0185 | 1.084% | 2373.9815 | 158.9813 | 2215.0002 | 1.7391 | 186.7388 | 7.781% | 7.781% | 7.949% | 0.9746% | 1.084% | 1.084% |  |  | 26.0185 | 186.7388
4034.2201 | 16136.8805 | 2 | 700 | 2800 | 19.9207 | 2780.0793 | 8.8062 | 28.7269 | 1.026% | 2771.2731 | 159.8001 | 2611.473 | 2.4173 | 190.9443 | 6.819% | 6.819% | 6.915% | 0.8943% | 1.026% | 1.026% |  |  | 28.7269 | 190.9443
4610.5373 | 18442.1492 | 3 | 800 | 3200 | 20.3346 | 3179.6654 | 11.5195 | 31.8541 | 0.9954% | 3168.1459 | 160.7442 | 3007.4017 | 3.2059 | 195.8042 | 6.119% | 6.119% | 6.166% | 0.8538% | 0.9954% | 0.9954% |  |  | 31.8541 | 195.8042
5186.8545 | 20747.4178 | 4 | 900 | 3600 | 20.8035 | 3579.1965 | 14.5963 | 35.3998 | 0.9833% | 3564.6002 | 161.8133 | 3402.7868 | 4.1043 | 201.3174 | 5.592% | 5.592% | 5.607% | 0.8401% | 0.9833% | 0.9833% |  |  | 35.3998 | 201.3174
5763.1716 | 23052.6865 | 5 | 1000 | 4000 | 21.3277 | 3978.6723 | 18.0364 | 39.364 | 0.9841% | 3960.636 | 163.007 | 3797.629 | 5.112 | 207.483 | 5.187% | 5.187% | 5.182% | 0.8449% | 0.9841% | 0.9841% |  |  | 39.364 | 207.483
6339.4888 | 25357.9551 | 6 | 1100 | 4400 | 21.907 | 4378.093 | 21.8395 | 43.7465 | 0.9942% | 4356.2535 | 164.3249 | 4191.9286 | 6.2287 | 214.3 | 4.87% | 4.87% | 4.853% | 0.8633% | 0.9942% | 0.9942% |  |  | 43.7465 | 214.3
6915.8059 | 27663.2238 | 7 | 1200 | 4800 | 22.5415 | 4777.4585 | 26.0056 | 48.5471 | 1.011% | 4751.4529 | 165.7665 | 4585.6864 | 7.4538 | 221.7674 | 4.62% | 4.62% | 4.597% | 0.8919% | 1.011% | 1.011% |  |  | 48.5471 | 221.7674
7492.1231 | 29968.4924 | 8 | 1300 | 5200 | 23.2312 | 5176.7688 | 30.5344 | 53.7656 | 1.034% | 5146.2344 | 167.3316 | 4978.9028 | 8.7869 | 229.8841 | 4.421% | 4.421% | 4.397% | 0.9282% | 1.034% | 1.034% |  |  | 53.7656 | 229.8841
8068.4403 | 32273.7611 | 9 | 1400 | 5600 | 23.976 | 5576.024 | 35.426 | 59.402 | 1.061% | 5540.598 | 169.0196 | 5371.5784 | 10.2275 | 238.6491 | 4.262% | 4.262% | 4.24% | 0.9708% | 1.061% | 1.061% |  |  | 59.402 | 238.6491
8644.7574 | 34579.0297 | 10 | 1500 | 6000 | 24.776 | 5975.224 | 40.68 | 65.456 | 1.091% | 5934.544 | 170.8303 | 5763.7137 | 11.7753 | 248.0616 | 4.134% | 4.134% | 4.119% | 1.018% | 1.091% | 1.091% |  |  | 65.456 | 248.0616
9221.0746 | 36884.2984 | 11 | 1600 | 6400 | 25.6312 | 6374.3688 | 46.2964 | 71.9276 | 1.124% | 6328.0724 | 172.7631 | 6155.3093 | 13.4297 | 258.1204 | 4.033% | 4.033% | 4.026% | 1.07% | 1.124% | 1.124% |  |  | 71.9276 | 258.1204
9797.3918 | 39189.567 | 12 | 1700 | 6800 | 26.5416 | 6773.4584 | 52.2749 | 78.8165 | 1.159% | 6721.1835 | 174.8178 | 6546.3658 | 15.1903 | 268.8246 | 3.953% | 3.953% | 3.957% | 1.124% | 1.159% | 1.159% |  |  | 78.8165 | 268.8246
10373.7089 | 41494.8357 | 13 | 1800 | 7200 | 27.5071 | 7172.4929 | 58.6155 | 86.1226 | 1.196% | 7113.8774 | 176.9938 | 6936.8836 | 17.0567 | 280.1732 | 3.891% | 3.891% | 3.907% | 1.182% | 1.196% | 1.196% |  |  | 86.1226 | 280.1732
10950.0261 | 43800.1043 | 14 | 1900 | 7600 | 28.5278 | 7571.4722 | 65.318 | 93.8458 | 1.235% | 7506.1542 | 179.2909 | 7326.8633 | 19.0284 | 292.1652 | 3.844% | 3.844% | 3.874% | 1.242% | 1.235% | 1.235% | 0 | 0 | 93.8458 | 292.1652
11526.3432 | 46105.373 | 15 | 2000 | 8000 | 29.6037 | 7970.3963 | 72.3823 | 101.986 | 1.275% | 7898.014 | 181.7086 | 7716.3054 | 21.105 | 304.7996 | 3.81% | 3.832% | 3.855% | 1.303% | 1.275% | 1.299% | 1 | 1 | 103.9193 | 306.5681
12102.6604 | 48410.6416 | 16 | 2100 | 8400 | 30.7347 | 8369.2653 | 79.8081 | 110.5429 | 1.316% | 8289.4571 | 184.2466 | 8105.2105 | 23.2861 | 318.0755 | 3.787% | 3.831% | 3.848% | 1.367% | 1.316% | 1.364% | 2 | 2 | 114.6029 | 321.7892
12678.9776 | 50715.9103 | 17 | 2200 | 8800 | 31.921 | 8768.079 | 87.5954 | 119.5164 | 1.358% | 8680.4836 | 186.9044 | 8493.5792 | 25.5711 | 331.9918 | 3.773% | 3.839% | 3.851% | 1.432% | 1.358% | 1.431% | 3 | 3 | 125.8964 | 337.8276
13255.2947 | 53021.1789 | 18 | 2300 | 9200 | 33.1624 | 9166.8376 | 95.744 | 128.9064 | 1.401% | 9071.0936 | 189.6817 | 8881.412 | 27.9596 | 346.5476 | 3.767% | 3.855% | 3.863% | 1.498% | 1.401% | 1.498% | 4 | 4 | 137.7997 | 354.6824
13831.6119 | 55326.4476 | 19 | 2400 | 9600 | 34.459 | 9565.541 | 104.2537 | 138.7127 | 1.445% | 9461.2873 | 192.578 | 9268.7093 | 30.4513 | 361.742 | 3.768% | 3.879% | 3.883% | 1.565% | 1.445% | 1.566% | 5 | 5 | 150.3127 | 372.3525
14407.9291 | 57631.7162 | 20 | 2500 | 10000 | 35.8107 | 9964.1893 | 113.1244 | 148.9351 | 1.489% | 9851.0649 | 195.593 | 9655.4719 | 33.0456 | 377.5738 | 3.776% | 3.908% | 3.91% | 1.633% | 1.489% | 1.634% | 6 | 6 | 163.4351 | 390.8369
14984.2462 | 59936.9849 | 21 | 2600 | 10400 | 37.2176 | 10362.7824 | 122.356 | 159.5736 | 1.534% | 10240.4264 | 198.7263 | 10041.7001 | 35.7422 | 394.0422 | 3.789% | 3.944% | 3.944% | 1.702% | 1.534% | 1.704% | 7 | 7 | 177.1669 | 410.1348
15560.5634 | 62242.2535 | 22 | 2700 | 10800 | 38.6797 | 10761.3203 | 131.9482 | 170.6279 | 1.58% | 10629.3721 | 201.9775 | 10427.3945 | 38.5406 | 411.1461 | 3.807% | 3.984% | 3.982% | 1.772% | 1.58% | 1.773% | 8 | 8 | 191.5079 | 430.245
16136.8805 | 64547.5222 | 23 | 2800 | 11200 | 40.197 | 11159.803 | 141.901 | 182.098 | 1.626% | 11017.902 | 205.3462 | 10812.5558 | 41.4404 | 428.8846 | 3.829% | 4.028% | 4.026% | 1.843% | 1.626% | 1.843% | 9 | 9 | 206.458 | 451.1667
16713.1977 | 66852.7908 | 24 | 2900 | 11600 | 41.7694 | 11558.2306 | 152.2142 | 193.9836 | 1.672% | 11406.0164 | 208.8321 | 11197.1843 | 44.4411 | 447.2568 | 3.856% | 4.077% | 4.074% | 1.914% | 1.672% | 1.914% | 10 | 10 | 222.0169 | 472.8989
17289.5149 | 69158.0595 | 25 | 3000 | 12000 | 43.397 | 11956.603 | 162.8876 | 206.2846 | 1.719% | 11793.7154 | 212.4347 | 11581.2807 | 47.5423 | 466.2617 | 3.886% | 4.129% | 4.126% | 1.985% | 1.719% | 1.985% | 11 | 11 | 238.1846 | 495.4406
17865.832 | 71463.3281 | 26 | 3100 | 12400 | 45.0798 | 12354.9202 | 173.9211 | 219.0009 | 1.766% | 12180.9991 | 216.1536 | 11964.8454 | 50.7436 | 485.8982 | 3.919% | 4.184% | 4.181% | 2.058% | 1.766% | 2.056% | 12 | 12 | 254.9609 | 518.7908
18442.1492 | 73768.5968 | 27 | 3200 | 12800 | 46.8178 | 12753.1822 | 185.3146 | 232.1324 | 1.814% | 12567.8676 | 219.9885 | 12347.8791 | 54.0446 | 506.1655 | 3.954% | 4.242% | 4.24% | 2.13% | 1.814% | 2.128% | 13 | 13 | 272.3457 | 542.9486
19018.4664 | 76073.8654 | 28 | 3300 | 13200 | 48.6109 | 13151.3891 | 197.0678 | 245.6787 | 1.861% | 12954.3213 | 223.9391 | 12730.3822 | 57.4447 | 527.0625 | 3.993% | 4.302% | 4.301% | 2.203% | 1.861% | 2.2% | 14 | 14 | 290.3387 | 567.913
19594.7835 | 78379.1341 | 29 | 3400 | 13600 | 50.4592 | 13549.5408 | 209.1807 | 259.6399 | 1.909% | 13340.3601 | 228.0048 | 13112.3553 | 60.9437 | 548.5884 | 4.034% | 4.365% | 4.365% | 2.277% | 1.909% | 2.272% | 15 | 15 | 308.9399 | 593.6831
20171.1007 | 80684.4027 | 30 | 3500 | 14000 | 52.3627 | 13947.6373 | 221.653 | 274.0158 | 1.957% | 13725.9842 | 232.1853 | 13493.7989 | 64.541 | 570.7421 | 4.077% | 4.43% | 4.432% | 2.351% | 1.957% | 2.344% | 16 | 16 | 328.1491 | 620.2579
20747.4178 | 82989.6714 | 31 | 3600 | 14400 | 54.3214 | 14345.6786 | 234.4847 | 288.8061 | 2.006% | 14111.1939 | 236.4803 | 13874.7136 | 68.2363 | 593.5227 | 4.122% | 4.497% | 4.501% | 2.425% | 2.006% | 2.416% | 17 | 17 | 347.9661 | 647.6363
21323.735 | 85294.94 | 32 | 3700 | 14800 | 56.3352 | 14743.6648 | 247.6756 | 304.0109 | 2.054% | 14495.9891 | 240.8893 | 14255.0999 | 72.0291 | 616.9292 | 4.168% | 4.566% | 4.572% | 2.499% | 2.054% | 2.489% | 18 | 18 | 368.3909 | 675.8176
21900.0522 | 87600.2087 | 33 | 3800 | 15200 | 58.4042 | 15141.5958 | 261.2256 | 319.6298 | 2.103% | 14880.3702 | 245.412 | 14634.9582 | 75.919 | 640.9607 | 4.217% | 4.637% | 4.645% | 2.574% | 2.103% | 2.562% | 19 | 19 | 389.4231 | 704.8007
22476.3693 | 89905.4773 | 34 | 3900 | 15600 | 60.5284 | 15539.4716 | 275.1344 | 335.6628 | 2.152% | 15264.3372 | 250.048 | 15014.2892 | 79.9055 | 665.6163 | 4.267% | 4.709% | 4.719% | 2.648% | 2.152% | 2.635% | 20 | 20 | 411.0628 | 734.5847
23052.6865 | 92210.746 | 35 | 4000 | 16000 | 62.7078 | 15937.2922 | 289.402 | 352.1097 | 2.201% | 15647.8903 | 254.7969 | 15393.0934 | 83.9883 | 690.8949 | 4.318% | 4.782% | 4.796% | 2.724% | 2.201% | 2.708% | 21 | 21 | 433.3097 | 765.1686
24061.2415 | 96244.9661 |  | 4175 | 16700 | 66.6544 | 16633.3456 | 315.233 | 381.8873 | 2.287% | 16318.1127 | 263.378 | 16054.7347 | 91.3637 | 736.629 | 4.411% | 4.897% | 4.933% | 2.855% | 2.287% | 2.818% | 22 | 22
[21 empty] | 23 | 23
15 min | ERCOT |  | 15 min | CNP | [12 empty] | Secondary | Primary | CNP
11048 | 44192 | AAL | 1917 | 7668 | 29.6749 | 7638.3251 | 66.4766 | 96.1515 | 1.254% | 7571.8485 | 184.2248 | 7387.6237 | 19.3454 | 299.7216 | 3.909% |  | 3.87% | 1.252% | At ERCOT AAL
18446.5 | 73786 | Peak | 3850.75 | 15403 | 62.8989 | 15340 | 268.1162 | 331.0152 | 2.149% | 15071.8838 | 249.7472 | 14822.1366 | 77.8733 | 658.6357 | 4.276% |  | 4.24% | 2.131% | At ERCOT Peak
| 1.6697 |  |  | 2.0087
15402.8989
AAL for CNP ( | 7638.3251 | MW) is measured at the Dist Fdr Bkr (PELCAR, Column G) so this value is increased | [6 empty] | 29.6749 | MW (Cell F50 ) for the high side of the sub trfs
Peak for CNP ( | 15340 | MW) is measured at the Dist Fdr Bkr (PELCAR, Column G) so this value is increased 60 MW (Cell F51) for the high side of the sub trfs | [12 empty] | Secondary (adjusted) |  | Primary (Adjusted)
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % Losses above AAL are scaled proportionately.
(When ERCOT is at peak, CNP is 4.5 intervals below peak, so % losses at ERCOT peak are scaled up to match % losses at CNP peak.) | [14 empty] | ERCOT Peak | 4.242% | ERCOT Peak | 2.128%
[15 empty] | CNP Peak | 4.242% | CNP Peak | 2.127%
[15 empty] | Scaling for % Losses |  |  | 2021
[15 empty] | Secondary | Primary |  | For Secondary Distribution Customers "D"
|  |  |  | Substation Transformers |  | Primary Conductor |  |  |  | Distribution Transformers |  | Secondary Conductor |  |  | 0.42% | 0.3625% |  | For Primary Distribution Customers "E"
|  |  |  | B Constant | A Constant | B Constant | A Constant |  |  | B Constant | A Constant | B Constant | A Constant |  |  |  | Primary Constants
|  | 2021 Values ----> |  | 18.826 | 1.819e-07 | 0 | 1.1394e-06 |  |  | 164.118 | 3.8579e-07 | 0 | 3.5446e-07 | <----2021 Values
|  | 2020 Values ----> |  | 18.728 | 1.8618e-07 | 0 | 1.1394e-06 |  |  | 162.105 | 3.8581e-07 | 0 | 3.5446e-07 | <----2020 Values
|  | 2019 Values ----> |  | 18.008 | 1.8612e-07 | 0 | 1.1394e-06 |  |  | 159.986 | 3.9124e-07 | 0 | 3.5446e-07 | <----2019 Values
|  | 2018 Values ----> |  | 18.569 | 1.7242e-07 | 0 | 1.1394e-06 |  |  | 156.724 | 4.0053e-07 | 0 | 3.5446e-07 | <----2018 Values |  |  | F1 = | 0.01522 | right
|  | 2017 Values ----> |  | 18.268 | 1.7762e-07 | 0 | 1.1394e-06 |  |  | 152.212 | 4.0973e-07 | 0 | 3.5446e-07 | <--- 2017 Values |  |  | F2 = | -0.0062 | middle
|  | 2016 Values ----> |  | 20.6354 | 1.8059e-07 | 0 | 1.1394e-06 |  |  | 149.175 | 4.2041e-07 | 0 | 3.5446e-07 | <--- 2016 Values |  |  | F3 = | 0.0035 | left
|  | 2015 Values ----> |  | 20.867 | 1.7797e-07 | 0 | 1.1394e-06 |  |  | 145.39 | 4.3561e-07 | 0 | 3.5446e-07 | <--- 2015 Values
|  | 2014 Values ----> |  | 19.863 | 1.893e-07 | 0 | 1.1394e-06 |  |  | 142.346 | 4.4856e-07 | 0 | 3.5446e-07 | <--- 2014 Values
|  | 2013 Values ----> |  | 19.473 | 1.9548e-07 | 0 | 1.1394e-06 |  |  | 137.751 | 4.7391e-07 | 0 | 3.5446e-07 | <--- 2013 Values |  |  |  | Secondary Constants
|  | 2012 Values ----> |  | 21.1118 | 1.8286e-07 | 0 | 1.1394e-06 |  |  | 133.986 | 5.0407e-07 | 0 | 3.5446e-07 | <--- 2012 Values
|  | 2009 Values ----> |  | 20.312 | 1.9194e-07 | 0 | 1.1394e-06 |  |  | 130.794 | 5.041e-07 | 0 | 3.5446e-07 | <--- 2009 Values
|  | 2008 Values ----> |  | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2008 Values |  |  | F1 = | 0.0205 | right
|  | 2007 Values ----> |  | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2007 Values |  |  | F2 = | -0.0068 | middle
[17 empty] | F3 = | 0.025 | left
|  |  |  | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | <--- 1995 |  | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | <--- 1995
|  |  |  | 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2001 |  | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2001
|  |  |  | 20.2955 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2004/2006 |  | 133.2966 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2004/2006
|  |  |  | 2.866% increase in Sub Trf nameplate MVA from 2001 to 2004 | [5 empty] | 15.9% 1ncrease in distribution trf nameplate KVA from 2001 to 2004
|  |  | 2007 Start Values ----> | 18.586 | 2.13e-07 | 0 | 1.1116e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <---2007 Start Value
|  |  |  | New values as per updated |  | Add 2.5 % to 2006 values due |  |  |  | New values as per updated
|  |  | 2007 Adjustments ----> | substation trf review. |  | to increased loading on circuits |  |  |  | distribution trf review.
|  |  |  | Decrease from 2006 values. |  | as per revised Design Criteria |  |  |  | Decrease from 2006 values. |  | No change to 2006 values.
[11 empty] | AAL for ERCOT (15 mins) = 10,740 |  |  | DLF = F1 * (SIEL/AAL) + F2 + F3 / (SIEL/AAL)
(See graphs below)
Primary Constants
F1 = | 0.01522 | right
F2 = | -0.0062 | middle
F3 = | 0.0035 | left
Secondary Constants
F1 = | 0.0205 | right
F2 = | -0.0068 | middle
F3 = | 0.025 | left

## 3) Loss Equations
System Loss Equations For CenterPoint Energy
| Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
Substation Transformers
Calculations/Formulas
83.356 | = | A * (TRF name plate*TRF name plate) + (No load losses+1%)
| A = | 1.819e-07
| B = | 18.826
Variables
| 2021 | for use in | 2022
Total No Load Losses for Substation Transformers +1% [MW]: |  |  |  | 18.826
Total Load Losses at Trf base name plate rating +1% [MW]: |  |  |  | 64.53
Total Losses [MW]: |  |  |  | 83.356
Trf base name plate rating [MVA]: |  |  |  | 18835
Distribution Transformers
Calculations/Formulas
251.756 | = | A * (Distribution Input*Distribution Input) + No load losses
| A = | 3.8579e-07
| B = | 164.118
Variables
| 2021 | for use in | 2022
Total No-Load Loss Average For Distribution Transformer[MW]: |  |  |  | 164.118
Total Load Losses at input to Distribution Transformers [MW]: |  |  |  | 87.638
Total Losses [MW]: |  |  |  | 251.756
Distribution Input [MW]: |  |  |  | 15072
Conductors
Primary Conductor
| A = | 1.1394e-06
| B = | 0
Secondary Conductor
| A = | 3.5446e-07
| B = | 0

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified