## 1996 Load Responsibility
Utility | 4CP Average | GSU Losses | Net Generation | Loss Adjustment Factor | Load at Delivery Point | VAMO Loss Allocation | Load Responsibility | Load Ratio Share | Utility | June 19, 1996 @1700 | July 22, 1996 @1700 | August 5, 1996 @1700 | September 10, 1996 @1800 | 4CP Average
| (A) | (B) | (C=A-B) | (D) | (E=C/(1+D)) | (F) | (G=E*(1+F)) |  |  | (KW) | (KW) | (KW) | (KW) | (KW)
Brazos | 1061825 | 2062.9 | 1059762.1 | 3.519% | 1023732.2346 | 3.62% | 1060788.5182 | 2.327% | Brazos | 1107900 | 1117600 | 1108700 | 913100 | 1061825
BPM | 7725 | 0 | 7725 | 0% | 7725 | 5.202% | 8126.8205 | 0.01783% | BPM | 4800 | 5400 | 10300 | 10400 | 7725
Bryan | 200500 | 0 | 200500 | 2.301% | 195989.8538 | 2.474% | 200837.7227 | 0.4406% | Bryan | 205800 | 209300 | 207600 | 179300 | 200500
COA | 1714221.25 | 1762.6781 | 1712458.5719 | 1.985% | 1679131.107 | 2.181% | 1715749.6483 | 3.764% | COA | 1777995 | 1776943 | 1788587 | 1513360 | 1714221.25
College Station | 117560 | 0 | 117560 | 0.08621% | 117458.7425 | 3.552% | 121631.0985 | 0.2668% | College Station | 119600 | 119520 | 119880 | 111240 | 117560
CPL | 3791252.5 | 6933.8867 | 3784318.6132 | 4.278% | 3629080.0077 | 3.184% | 3744615.7306 | 8.214% | CPL | 3927085 | 3880383 | 3967544 | 3389998 | 3791252.5
CPS | 3190250 | 5886.1706 | 3184363.8294 | 1.287% | 3143913.6537 | 1.269% | 3183819.7553 | 6.984% | CPS | 3356000 | 3232000 | 3309000 | 2864000 | 3190250
Denton | 209475 | 0 | 209475 | 2.2% | 204964.9462 | 2.474% | 210034.8168 | 0.4607% | Denton | 215200 | 218200 | 216800 | 187700 | 209475
Garland | 430150 | 0 | 430150 | 2.291% | 420514.7536 | 2.474% | 430916.3146 | 0.9453% | Garland | 441900 | 453300 | 441200 | 384200 | 430150
Granbury | 14450 | 0 | 14450 | 0% | 14450 | 5.314% | 15217.8744 | 0.03338% | Granbury | 15300 | 15000 | 15000 | 12500 | 14450
Greenville | 90875 | 0 | 90875 | 2.072% | 89030.406 | 2.474% | 91232.6003 | 0.2001% | Greenville | 95100 | 97200 | 92400 | 78800 | 90875
HLP | 11900154 | 41577.6432 | 11858576.3568 | 1.085% | 11731336.7366 | 1.054% | 11855008.0377 | 26.01% | HLP | 11640756 | 11943860 | 12598000 | 11418000 | 11900154
Hunt Collins | 10557.5 | 0 | 10557.5 | 0% | 10557.5 | 6.979% | 11294.2867 | 0.02478% | Hunt Collins | 10860 | 11820 | 10890 | 8660 | 10557.5
LCRA | 2009832.75 | 2957.3281 | 2006875.4219 | 2.944% | 1949480.507 | 2.213% | 1992617.0171 | 4.371% | LCRA | 2094182 | 2076376 | 2104269 | 1764504 | 2009832.75
PUB | 161000 | 0 | 161000 | 0.2483% | 160601.2384 | 4.374% | 167626.2988 | 0.3677% | PUB | 168000 | 165000 | 159000 | 152000 | 161000
Rayburn | 42500 | 0 | 42500 | 0% | 42500 | 3.012% | 43780 | 0.09604% | Rayburn | 43000 | 42000 | 42000 | 43000 | 42500
SESCO | 99250 | 0 | 99250 | 0.5447% | 98712.3155 | 5.788% | 104425.4348 | 0.2291% | SESCO | 118000 | 93000 | 93000 | 93000 | 99250
STECMEC | 278273.5 | 0 | 278273.5 | 5.189% | 264545.0352 | 4.204% | 275665.8181 | 0.6047% | STECMEC | 294931 | 288304 | 295176 | 234683 | 278273.5
TexLa | 111871.75 | 11596 | 100275.75 | 0% | 100275.75 | 6.924% | 107218.3642 | 0.2352% | TexLa | 110554 | 122517 | 118397 | 96019 | 111871.75
TNP | 582280 | 434.25 | 581845.75 | 0.6409% | 578140.1632 | 2.196% | 590833.3543 | 1.296% | TNP | 629928 | 510824 | 612684 | 575684 | 582280
TUEC | 18506010 | 56175.5918 | 18449834.4082 | 2.081% | 18073674.0233 | 1.968% | 18429310.8954 | 40.43% | TUEC | 19212392 | 19332678 | 19135150 | 16343820 | 18506010
Weatherford | 25000 | 0 | 25000 | 0% | 25000 | 7.566% | 26891.5132 | 0.05899% | Weatherford | 25000 | 25000 | 25000 | 25000 | 25000
WTU | 1191133.65 | 2705.7559 | 1188427.8941 | 2.373% | 1160884.4145 | 3.23% | 1198376.2094 | 2.629% | WTU | 1241731.6 | 1262252 | 1244126 | 1016425 | 1191133.65
TOTAL | 45746146.9 | 132092.2045 | 45614054.6955 |  | 44721698.3886 |  | 45586018.1298 | 100% | TOTAL | 46856014.6 | 46998477 | 47714703 | 41415393 | 45746146.9
Changes since the 12/19/96 ERCOT filing of Postage Stamp Billing Determinants
1. As approved by the ERCOT ESC in a motion on 12/11/96,
a loss adjustment factor based on metered data was used by TMPA cities.
2. As per Docket 15840 "Order Relating to Transmission Rate Issues",
(a) TexLa load responsibility is reduced by 11,596 kW for load transfered to SPP, and
(b) a metered load correction of 11,122 kW was deducted for WTU and credited to TexLa.

## LOAD RESP REC
June 19, 1996 @1700 | Receiving Utility | Load Responsibility | Control Area Load | COA | CPL | CPSB | HLP | LCRA | PUB | STECMEC | TMPP | TNP | TUEC | WTU | Total Adjustment
|  | (A+B) | (A) | [11 empty] | (B)
BEPC | Brazos | 1107900 | 2074000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1003100 | 0 | 37000 | 0 | -966100
BPM | BPM | 4800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4800 | 0 | 0 | 0 | 4800
BRYAN | Bryan | 205800 | [8 empty] | 205800 |  |  |  | 205800
COA | COA | 1777995 | 1781215 | -4255 | 0 | 0 | 0 | 1035 | 0 | 0 | 0 | 0 | 0 | 0 | -3220
COLLEGE STA | College Station | 119600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119600 | 0 | 119600
CPL | CPL | 3927085 | 3917000 | 0 | -6894 | 0 | 0 | 3227 | 0 | 13752 | 0 | 0 | 0 | 0 | 10085
CPS | CPS | 3356000 | 3356000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DENTON | Denton | 215200 | [8 empty] | 215200 |  |  |  | 215200
GARLAND | Garland | 441900 | [8 empty] | 441900 |  |  |  | 441900
GRANBURY | Granbury | 15300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15300 | 0 | 0 | 0 | 15300
GREENVILLE | Greenville | 95100 | [8 empty] | 95100 |  |  |  | 95100
HLP | HLP | 11640756 | 12241000 | 0 | 0 | 0 | -600244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -600244
HUNT COLLIN | Hunt Collins | 10860 | 0 | 0 | 0 | 0 | 0 | 10860 | 0 | 0 | 0 | 0 | 0 | 0 | 10860
LCRA | LCRA | 2094182 | 2060700 | 4255 | 1938 | 0 | 0 | -15122 | 0 | 4373 | 0 | 0 | 13324 | 24714 | 33482
PUB | PUB | 168000 | 168000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAYBURN | Rayburn | 43000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43000 | 0 | 43000
SESCO | SESCO | 118000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118000 | 0 | 118000
STECMEC | STECMEC | 294931 | 308100 | 0 | 4956 | 0 | 0 | 0 | 0 | -18125 | 0 | 0 | 0 | 0 | -13169
TEXLA | TexLa | 110554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110554 | 110554
TNP | TNP | 629928 | 0 | 0 | 0 | 0 | 600244 | 0 | 0 | 0 | 0 | 0 | 29684 | 0 | 629928
TUEC | TUEC | 19212392 | 19573000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -360608 | 0 | -360608
WEATHERFORD | Weatherford | 25000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 0 | 0 | 0 | 25000
WTU | WTU | 1241731.6 | 1377000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -135268 | -135268
TOTAL |  | 46856014.6 | 46856015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July 22, 1996 @1700 | Receiving Utility | Load Responsibility | Control Area Load | COA | CPL | CPSB | HLP | LCRA | PUB | STECMEC | TMPP | TNP | TUEC | WTU | Total Adjustment
|  | (A+B) | (A) | [11 empty] | (B)
BEPC | Brazos | 1117600 | 2141000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1023400 | 0 | 0 | 0 | -1023400
BPM | BPM | 5400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5400 | 0 | 0 | 0 | 5400
BRYAN | Bryan | 209300 | [8 empty] | 209300 |  |  |  | 209300
COA | COA | 1776943 | 1780227 | -4334 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | -3284
COLLEGE STA | College Station | 119520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119520 | 0 | 119520
CPL | CPL | 3880383 | 3871000 | 0 | -6567 | 0 | 0 | 3170 | 0 | 12780 | 0 | 0 | 0 | 0 | 9383
CPS | CPS | 3232000 | 3232000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DENTON | Denton | 218200 | [8 empty] | 218200 |  |  |  | 218200
GARLAND | Garland | 453300 | [8 empty] | 453300 |  |  |  | 453300
GRANBURY | Granbury | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 0 | 0 | 0 | 15000
GREENVILLE | Greenville | 97200 | [8 empty] | 97200 |  |  |  | 97200
HLP | HLP | 11943860 | 12425000 | 0 | 0 | 0 | -481140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -481140
HUNT COLLIN | Hunt Collins | 11820 | 0 | 0 | 0 | 0 | 0 | 11820 | 0 | 0 | 0 | 0 | 0 | 0 | 11820
LCRA | LCRA | 2076376 | 2044600 | 4334 | 1845 | 0 | 0 | -16040 | 0 | 4288 | 0 | 0 | 13118 | 24231 | 31776
PUB | PUB | 165000 | 165000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAYBURN | Rayburn | 42000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42000 | 0 | 42000
SESCO | SESCO | 93000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93000 | 0 | 93000
STECMEC | STECMEC | 288304 | 300650 | 0 | 4722 | 0 | 0 | 0 | 0 | -17068 | 0 | 0 | 0 | 0 | -12346
TEXLA | TexLa | 122517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122517 | 122517
TNP | TNP | 510824 | 0 | 0 | 0 | 0 | 481140 | 0 | 0 | 0 | 0 | 0 | 29684 | 0 | 510824
TUEC | TUEC | 19332678 | 19630000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -297322 | 0 | -297322
WEATHERFORD | Weatherford | 25000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 0 | 0 | 0 | 25000
WTU | WTU | 1262252 | 1409000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -146748 | -146748
TOTAL |  | 46998477 | 46998477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August 5, 1996 @1700 | Receiving Utility | Load Responsibility | Control Area Load | COA | CPL | CPSB | HLP | LCRA | PUB | STECMEC | TMPP | TNP | TUEC | WTU | Total Adjustment
|  | (A+B) | (A) | [11 empty] | (B)
BEPC | Brazos | 1108700 | 2117000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1008300 | 0 | 0 | 0 | -1008300
BPM | BPM | 10300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10300 | 0 | 0 | 0 | 10300
BRYAN | Bryan | 207600 | [8 empty] | 207600 |  |  |  | 207600
COA | COA | 1788587 | 1792163 | -4569 | 0 | 0 | 0 | 993 | 0 | 0 | 0 | 0 | 0 | 0 | -3576
COLLEGE STA | College Station | 119880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119880 | 0 | 119880
CPL | CPL | 3967544 | 3957000 | 0 | -7212 | 0 | 0 | 3284 | 0 | 14472 | 0 | 0 | 0 | 0 | 10544
CPS | CPS | 3309000 | 3309000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DENTON | Denton | 216800 | [8 empty] | 216800 |  |  |  | 216800
GARLAND | Garland | 441200 | [8 empty] | 441200 |  |  |  | 441200
GRANBURY | Granbury | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 0 | 0 | 0 | 15000
GREENVILLE | Greenville | 92400 | [8 empty] | 92400 |  |  |  | 92400
HLP | HLP | 12598000 | 12547000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51000 | 0 | 0 | 51000
HUNT COLLIN | Hunt Collins | 10890 | 0 | 0 | 0 | 0 | 0 | 10890 | 0 | 0 | 0 | 0 | 0 | 0 | 10890
LCRA | LCRA | 2104269 | 2072100 | 4569 | 1914 | 0 | 0 | -15167 | 0 | 4090 | 0 | 0 | 13286 | 23477 | 32169
PUB | PUB | 159000 | 159000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAYBURN | Rayburn | 42000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42000 | 0 | 42000
SESCO | SESCO | 93000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93000 | 0 | 93000
STECMEC | STECMEC | 295176 | 308440 | 0 | 5298 | 0 | 0 | 0 | 0 | -18562 | 0 | 0 | 0 | 0 | -13264
TEXLA | TexLa | 118397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118397 | 118397
TNP | TNP | 612684 | 634000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -51000 | 29684 | 0 | -21316
TUEC | TUEC | 19135150 | 19433000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -297850 | 0 | -297850
WEATHERFORD | Weatherford | 25000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 0 | 0 | 0 | 25000
WTU | WTU | 1244126 | 1386000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -141874 | -141874
TOTAL |  | 47714703 | 47714703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September 10, 1996 @1800 | Receiving Utility | Load Responsibility | Control Area Load | COA | CPL | CPSB | HLP | LCRA | PUB | STECMEC | TMPP | TNP | TUEC | WTU | Total Adjustment
|  | (A+B) | (A) | [11 empty] | (B)
BEPC | Brazos | 913100 | 1771000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -877900 | 0 | 20000 | 0 | -857900
BPM | BPM | 10400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10400 | 0 | 0 | 0 | 10400
BRYAN | Bryan | 179300 | [8 empty] | 179300 |  |  |  | 179300
COA | COA | 1513360 | 1516193 | -3705 | 0 | 0 | 0 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | -2833
COLLEGE STA | College Station | 111240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111240 | 0 | 111240
CPL | CPL | 3389998 | 3382000 | 0 | -5444 | 0 | 0 | 2570 | 0 | 10872 | 0 | 0 | 0 | 0 | 7998
CPS | CPS | 2864000 | 2864000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DENTON | Denton | 187700 | [8 empty] | 187700 |  |  |  | 187700
GARLAND | Garland | 384200 | [8 empty] | 384200 |  |  |  | 384200
GRANBURY | Granbury | 12500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12500 | 0 | 0 | 0 | 12500
GREENVILLE | Greenville | 78800 | [8 empty] | 78800 |  |  |  | 78800
HLP | HLP | 11418000 | 11380000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38000 | 0 | 0 | 38000
HUNT COLLIN | Hunt Collins | 8660 | 0 | 0 | 0 | 0 | 0 | 8660 | 0 | 0 | 0 | 0 | 0 | 0 | 8660
LCRA | LCRA | 1764504 | 1739900 | 3705 | 1490 | 0 | 0 | -12102 | 0 | 3699 | 0 | 0 | 10256 | 17556 | 24604
PUB | PUB | 152000 | 152000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAYBURN | Rayburn | 43000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43000 | 0 | 43000
SESCO | SESCO | 93000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93000 | 0 | 93000
STECMEC | STECMEC | 234683 | 245300 | 0 | 3954 | 0 | 0 | 0 | 0 | -14571 | 0 | 0 | 0 | 0 | -10617
TEXLA | TexLa | 96019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96019 | 96019
TNP | TNP | 575684 | 584000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -38000 | 29684 | 0 | -8316
TUEC | TUEC | 16343820 | 16651000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -307180 | 0 | -307180
WEATHERFORD | Weatherford | 25000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 0 | 0 | 0 | 25000
WTU | WTU | 1016425 | 1130000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -113575 | -113575
TOTAL |  | 41415393 | 41415393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## CONTROL AREA REC
June 19, 1996 @1700 | Receiving Control Area | Control Area Load | Generation | COA | CPL | CPSB | HLP | LCRA | PUB | STECMEC | TMPP | TNP | TUEC | WTU | SPP | Total Purchases | Inadvertent
|  | (A+B+C) | (A) | [12 empty] | (B) | (C)
BEPC | TMPP | 2074000 | 1800000 | 97000 | 0 | 0 | 0 | 0 | 0 | 0 | -75000 | 0 | 250000 | 0 | 0 | 272000 | 2000
BPM
BRYAN
COA | COA | 1781215 | 1666215 | -502000 | 0 | 0 | 50000 | 570000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118000 | -3000
COLLEGE STA
CPL | CPL | 3917000 | 3661000 | 100000 | -181000 | 0 | 77000 | 0 | 15000 | 0 | 0 | 0 | 75000 | 164000 | 0 | 250000 | 6000
CPS | CPS | 3356000 | 2962000 | 0 | 0 | 0 | 400000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | -6000
DENTON
GARLAND
GRANBURY
GREENVILLE
HLP | HLP | 12271000 | 13092000 | 0 | 0 | 0 | -807000 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -806000 | -15000
HUNT COLLIN
LCRA | LCRA | 2060700 | 2662700 | 75000 | 0 | 0 | 0 | -678000 | 0 | 0 | 5000 | 0 | 0 | 0 | 0 | -598000 | -4000
PUB | PUB | 168000 | 36000 | 0 | 28000 | 0 | 50000 | 0 | -15000 | 0 | 0 | 0 | 68000 | 0 | 0 | 131000 | 1000
RAYBURN
SESCO
STECMEC | STECMEC | 308100 | 247100 | 30000 | 30000 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62000 | -1000
TEXLA
TNP
TUEC | TUEC | 19573000 | 19952000 | 200000 | 43000 | 0 | 30000 | 85000 | 0 | 0 | 43000 | 0 | -793000 | 0 | 0 | -392000 | 13000
WEATHERFORD
WTU | WTU | 1377000 | 742000 | 0 | 0 | 0 | 200000 | 20000 | 0 | 0 | 27000 | 0 | 400000 | -164000 | 146000 | 629000 | 6000
TOTAL |  | 46886015 | 46821015 | 0 | -80000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146000 | 66000 | -1000
July 22, 1996 @1700 | Receiving Control Area | Control Area Load | Generation | COA | CPL | CPSB | HLP | LCRA | PUB | STECMEC | TMPP | TNP | TUEC | WTU | SPP | Total Purchases | Inadvertent
|  | (A+B+C) | (A) | [12 empty] | (B) | (C)
BEPC | TMPP | 2141000 | 1792000 | 148000 | 0 | 0 | 0 | 0 | 0 | 0 | -70000 | 0 | 275000 | 0 | 0 | 353000 | -4000
BPM
BRYAN
COA | COA | 1780227 | 1263227 | -348000 | 0 | 0 | 300000 | 566000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 518000 | -1000
COLLEGE STA
CPL | CPL | 3871000 | 3652000 | 100000 | -680000 | 0 | 250000 | 0 | 25000 | 0 | 0 | 0 | 250000 | 283000 | 0 | 228000 | -9000
CPS | CPS | 3232000 | 3402000 | 0 | 0 | -170000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -170000 | 0
DENTON
GARLAND
GRANBURY
GREENVILLE
HLP | HLP | 12455000 | 12877000 | 0 | 0 | 170000 | -583000 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -412000 | -10000
HUNT COLLIN
LCRA | LCRA | 2044600 | 2645600 | 0 | 0 | 0 | 3000 | -672000 | 0 | 0 | 0 | 0 | 70000 | 0 | 0 | -599000 | -2000
PUB | PUB | 165000 | 50000 | 0 | 27000 | 0 | 0 | 0 | -25000 | 0 | 0 | 0 | 45000 | 68000 | 0 | 115000 | 0
RAYBURN
SESCO
STECMEC | STECMEC | 300650 | 226650 | 0 | 25000 | 0 | 0 | 4000 | 0 | 0 | 0 | 0 | 45000 | 0 | 0 | 74000 | 0
TEXLA
TNP
TUEC | TUEC | 19630000 | 20122000 | 0 | 22000 | 0 | 30000 | 81000 | 0 | 0 | 42000 | 0 | -685000 | 0 | 0 | -510000 | 18000
WEATHERFORD
WTU | WTU | 1409000 | 1466000 | 100000 | 0 | 0 | 0 | 20000 | 0 | 0 | 28000 | 0 | 0 | -533000 | 315000 | -70000 | 13000
TOTAL |  | 47028477 | 47496477 | 0 | -606000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -182000 | 315000 | -473000 | 5000
August 5, 1996 @1700 | Receiving Control Area | Control Area Load | Generation | COA | CPL | CPSB | HLP | LCRA | PUB | STECMEC | TMPP | TNP | TUEC | WTU | SPP | Total Purchases | Inadvertent
|  | (A+B+C) | (A) | [12 empty] | (B) | (C)
BEPC | TMPP | 2117000 | 1921000 | 50000 | 25000 | 0 | 0 | 0 | 0 | 0 | -76000 | 0 | 150000 | 0 | 0 | 149000 | 47000
BPM
BRYAN
COA | COA | 1792163 | 1623163 | -400000 | 0 | 0 | 0 | 564000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164000 | 5000
COLLEGE STA
CPL | CPL | 3957000 | 3998000 | 250000 | -346000 | 0 | 0 | 0 | 5000 | 0 | 0 | 0 | 0 | 52000 | 0 | -39000 | -2000
CPS | CPS | 3309000 | 3263000 | 0 | 0 | 0 | 46000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46000 | 0
DENTON
GARLAND
GRANBURY
GREENVILLE
HLP | HLP | 12565000 | 12857000 | 0 | 0 | 0 | -398000 | 6000 | 0 | 0 | 0 | 0 | 150000 | 0 | 0 | -242000 | -50000
HUNT COLLIN
LCRA | LCRA | 2072100 | 2519100 | 100000 | 0 | 0 | 121000 | -665000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -444000 | -3000
PUB | PUB | 159000 | 27000 | 0 | 27000 | 0 | 0 | 0 | -5000 | 0 | 0 | 0 | 45000 | 68000 | 0 | 135000 | -3000
RAYBURN
SESCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STECMEC | STECMEC | 308440 | 255440 | 0 | 20000 | 0 | 30000 | 4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54000 | -1000
TEXLA
TNP | TNP | 634000 | 611000 | 0 | 0 | 0 | 51000 | 0 | 0 | 0 | 0 | -30000 | 0 | 0 | 0 | 21000 | 2000
TUEC | TUEC | 19433000 | 19481000 | 0 | 22000 | 0 | 150000 | 71000 | 0 | 0 | 48000 | 30000 | -345000 | 0 | 0 | -24000 | -24000
WEATHERFORD
WTU | WTU | 1386000 | 1369000 | 0 | 197000 | 0 | 0 | 20000 | 0 | 0 | 28000 | 0 | 0 | -302000 | 61000 | 4000 | 13000
TOTAL |  | 47732703 | 47924703 | 0 | -55000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -182000 | 61000 | -176000 | -16000
September 10, 1996 @1800 | Receiving Control Area | Control Area Load | Generation | COA | CPL | CPSB | HLP | LCRA | PUB | STECMEC | TMPP | TNP | TUEC | WTU | SPP | Total Purchases | Inadvertent
|  | (A+B+C) | (A) | [12 empty] | (B) | (C)
BEPC | TMPP | 1771000 | 1588000 | 34000 | 0 | 0 | 200000 | 25000 | 0 | 0 | -76000 | 0 | 0 | 0 | 0 | 183000 | 0
BPM
BRYAN
COA | COA | 1516193 | 842193 | -139000 | 0 | 50000 | 50000 | 615000 | 0 | 0 | 0 | 0 | 100000 | 0 | 0 | 676000 | -2000
COLLEGE STA
CPL | CPL | 3382000 | 3413000 | 100000 | -558000 | 0 | 285000 | 0 | 0 | 0 | 0 | 0 | 0 | 173000 | 0 | 0 | -31000
CPS | CPS | 2864000 | 3065000 | 0 | 0 | -201000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -201000 | 0
DENTON
GARLAND
GRANBURY
GREENVILLE
HLP | HLP | 11380000 | 11593000 | 0 | 0 | 151000 | -613000 | 43000 | 0 | 0 | 0 | 0 | 200000 | 0 | 0 | -219000 | 6000
HUNT COLLIN
LCRA | LCRA | 1739900 | 2581900 | 5000 | 0 | 0 | 1000 | -853000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -847000 | 5000
PUB | PUB | 152000 | 43000 | 0 | 26000 | 0 | 0 | 15000 | 0 | 0 | 0 | 0 | 0 | 68000 | 0 | 109000 | 0
RAYBURN
SESCO
STECMEC | STECMEC | 245300 | 209300 | 0 | 20000 | 0 | 0 | 64000 | 0 | -50000 | 0 | 0 | 0 | 0 | 0 | 34000 | 2000
TEXLA
TNP | TNP | 584000 | 538000 | 0 | 0 | 0 | 77000 |  | 0 | 0 | 0 | -30000 | 0 | 0 | 0 | 47000 | -1000
TUEC | TUEC | 16651000 | 16742000 | 0 | 22000 | 0 | 0 | 71000 | 0 | 50000 | 49000 | 30000 | -300000 | 0 | 0 | -78000 | -13000
WEATHERFORD
WTU | WTU | 1130000 | 1239000 | 0 | 0 | 0 | 0 | 20000 | 0 | 0 | 27000 | 0 | 0 | -423000 | 232000 | -144000 | 35000
TOTAL |  | 41415393 | 41854393 | 0 | -490000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -182000 | 232000 | -440000 | 1000

## ERCOT READINGS
1996 ERCOT Coincident Peak MW
|  | COA | CSWS | CPS | HLP | LCRA | PUB | STEC | TMPP | TUE | TNP | Total
1996-06-01 | Wed 19-Jun 17:00 | 1815 | 5294 | 3356 | 12273 | 2065 | 168 | 293 | 2148 | 19382 | - | 46794
1996-07-01 | Mon 22-Jul 17:00 | 1841 | 5280 | 3232 | 12628 | 2049 | 165 | 287 | 2215 | 19465 | - | 47162
1996-08-01 | Mon 5-Aug 17:00 | 1824 | 5343 | 3309 | 12553 | 2077 | 159 | 295 | 2190 | 19268 | 665 | 47683
1996-09-01 | Tue 10-Sep 18:00 | 1547 | 4512 | 2864 | 11520 | 1744 | 152 | 232 | 1846 | 16435 | 615 | 41467

## GSU&ADJ&VAMO
UTILITY | GSU MW | ZONE | LOSS MW | LOAD MW | ADJUSTMENT | EVENT | LOSS MW | LOAD MW | VAMO
BEPC | 2.0629 | BEPC (1) | 36.1 | 1025.725 | 3.519% | BEPC | 38.01 | 1050.08 | 3.62%
BPM | 0 | BPM | 0 |  | 0% | BPM | 0.4 | 7.69 | 5.202%
BRYAN | 0 | BRYAN (1) | 4.51 | 195.9835 | 2.301% | TMPA | 24.32 | 983.21 | 2.474%
COA | 1.7627 | COA | 33.96 | 1711 | 1.985% | COA | 38.12 | 1747.98 | 2.181%
COLLEGE STA | 0 | COLSTA | 0.1 | 116 | 0.08621% | COLLEGE STA | 4.22 | 118.8 | 3.552%
CPL | 6.9339 | CPL&MVEC | 155.71 | 3640.1 | 4.278% | CPL/CPL&IBWC | 121.2 | 3807 | 3.184%
CPS | 5.8862 | CPS | 40.45 | 3143.9 | 1.287% | CPS | 40.42 | 3184.4 | 1.269%
DENTON | 0 | DENTON (1) | 4.51 | 204.9625 | 2.2% | TMPA | 24.32 | 983.21 | 2.474%
GARLAND | 0 | GARLAND (1) | 9.635 | 420.504 | 2.291% | TMPA | 24.32 | 983.21 | 2.474%
GRANBURY | 0 | N/A | 0 |  | 0% | GRANBURY | 0.77 | 14.49 | 5.314%
GREENVILLE | 0 | GREENVILLE (1) | 1.845 | 89.05 | 2.072% | TMPA | 24.32 | 983.21 | 2.474%
HLP | 41.5776 | HLP | 130.3 | 12013.5 | 1.085% | HLP | 128.02 | 12143.85 | 1.054%
HUNT COLLIN | 0 | N/A | 0 |  | 0% | HUNT COLLIN | 0.79 | 11.32 | 6.979%
LCRA | 2.9573 | LCRA | 57.79 | 1962.9 | 2.944% | LCRA | 44.96 | 2031.89 | 2.213%
PUB | 0 | COB | 0.4 | 161.1 | 0.2483% | COB | 7.06 | 161.4 | 4.374%
RAYBURN | 0 | N/A | 0 |  | 0% | RAYBURN/DENISON | 1.28 | 42.5 | 3.012%
SESCO | 0 | SESCO | 1.31 | 240.5 | 0.5447% | SESCO/CPL&LCRA | 5.5 | 95.03 | 5.788%
STECMEC | 0 | STEC&MEC&MIGUEL | 14.38 | 277.1 | 5.189% | STECMEC LOAD | 11.67 | 277.61 | 4.204%
TEXLA (2) | 11.596 | WTEXLA | 0 | 68.5 | 0% | TEXLA/DENISON&WTU | 4.78 | 69.04 | 6.924%
TNP | 0.43425 | TNP/HLP | 4.32 | 674 | 0.6409% | TNP/HLP&LEWIS&SS | 15.55 | 708.26 | 2.196%
TUEC | 56.1756 | TUEC&FEC&LEWIS | 382.95 | 18399.9 | 2.081% | TUEC/LOAD&WHSL&SANDOW | 371.04 | 18856.47 | 1.968%
WEATHERFORD | 0 | N/A | 0 |  | 0% | WEATHERFORD | 1.89 | 24.98 | 7.566%
WTU | 2.7058 | WTU&BEPC&TNP&RGEC | 30.27 | 1275.8 | 2.373% | WTU | 35.53 | 1100.14 | 3.23%
(1) As approved by the ERCOT ESC in a motion on 12/11/96, a Loss Adjustment factor
based on metered data was used.
(2) As per Docket 15840 "Order Relating to Transmission Rate Issues", TexLa is load responsibility
is reduced by 11,596 kW for load transfered to SPP

## VAMO MATRIX
1996 S1 VAMO
LOSS ALLOCATION(MW)
EVENT | TU ELE | HLP | CPS | WTU | LCRA | CPL | COA | BEPC | TMPA | STEC | MIGUEL | COB | TNP | SESCO | FEC | TNP | COLSTA | WTEXLA | WTUTNP | BEPCWTU | RGEC | MVEC | MEC | TOTAL
TNP - Lewisville | 0.5 | 0.05 | 0.01 | 0.01 | 0.03 | 0.06 | 0.01 | 0.05 | 0.02 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77
TNP | 1.29 | 7.82 | 0.22 | 0.11 | 0.49 | 0.97 | 0.22 | 0.14 | 0.02 | 0.11 | 0 | 0 | 3.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.78
TNP - SS 01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TUE LOAD | 273.74 | 9.99 | 2.93 | 14 | 9.88 | 21.65 | 3.3 | 15.09 | 2.4 | 0.75 | 0.04 | 0 | 0.9 | 0.74 | 0.11 | 0.13 | 0.01 | 0 | 0.01 | 0.08 | 0 | 0 | 0.26 | 356
TUE TO TNP WHSAL | 9.18 | 0.2 | 0.06 | 0.33 | 0.2 | 0.52 | 0.05 | 0.49 | 0.08 | 0.02 | 0 | 0 | 0.02 | 0.01 | 0.02 | 3.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 14.8
DNDAM TO RAYBURN | 1.21 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0.02 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28
TUE TO COLSTA WH | 2.25 | 0.29 | 0.07 | 0.11 | 0.18 | 0.34 | 0.06 | 0.42 | 0.45 | 0.02 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 4.22
SANDOW TO ALCOA | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24
CPL TO SESCO | 0.61 | 0.13 | 0.07 | 0.02 | 0.1 | 0.51 | 0.02 | 0.03 | 0 | 0.04 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.59
LCRA TO SESCO | 2.19 | 0.31 | 0.06 | 0.08 | 0.5 | 0.28 | 0.17 | 0.12 | 0.01 | 0.02 | 0 | 0 | 0 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.91
HLP LOAD | 9.65 | 99.14 | 1.85 | 0.91 | 4.81 | 7.53 | 1.92 | 1.23 | 0.19 | 0.73 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 128.02
CPS LOAD | 2.37 | 1.73 | 21.45 | 0.4 | 2.56 | 9.44 | 1.1 | 0.28 | 0.07 | 0.66 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 40.42
CPL Gen-CPL Load | 5.04 | 3.39 | 7.84 | 1.96 | 4.7 | 86.62 | 0.9 | 0.51 | 0.07 | 4.36 | 0.14 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 1.26 | 117.8
IBWC to CPL Load | 0.22 | 0.05 | 0.14 | 0.13 | 0.07 | 2.65 | 0.01 | 0.02 | 0 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.03 | 3.4
WTU Gen to WTU L | 19.09 | 0.29 | 0.43 | 8.59 | 1.15 | 4.78 | 0.09 | 0.6 | 0.02 | 0.09 | 0.01 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0.1 | 0.12 | 0.06 | 0 | 0.07 | 35.53
Denison D-Texla | 1.24 | 0.01 | 0 | 0.01 | 0.01 | 0.02 | 0 | 0.04 | 0.01 | 0 | 0 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.45
WTU Gen-Texla | 2.32 | 0.04 | 0.03 | 0.27 | 0.07 | 0.27 | 0.01 | 0.11 | 0.01 | 0.01 | 0 | 0 | 0 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.33
LCRA-96S1 | 6.85 | 1.42 | 1.52 | 1.07 | 23.02 | 4.62 | 5.52 | 0.57 | 0.06 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 44.96
HUNT COLLIN-96S1 | 0.53 | 0.05 | 0.01 | 0.01 | 0.08 | 0.05 | 0.03 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79
COA LOAD | 5.1 | 2.15 | 1.33 | 0.26 | 6.12 | 2.86 | 19.22 | 0.66 | 0.11 | 0.29 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 38.12
COA WEATHERFORD | 0.87 | 0.08 | 0.02 | 0.04 | 0.14 | 0.12 | 0.3 | 0.3 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.89
BPM | 0.16 | 0.03 | 0.01 | 0.01 | 0.04 | 0.03 | 0.09 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4
GRANBURY LOAD | 0.32 | 0.03 | 0.01 | 0.01 | 0.02 | 0.04 | 0 | 0.21 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77
BRAZOS LOAD | 20.72 | 1.13 | 0.54 | 0.86 | 1.44 | 2.75 | 0.49 | 8.6 | 1.09 | 0.27 | 0.03 | 0 | 0 | 0 | 0 | 0.02 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0.05 | 38.01
TMPA LOAD | 11.13 | 1.17 | 0.27 | 0.31 | 0.76 | 1.28 | 0.23 | 2.44 | 6.56 | 0.08 | 0 | 0 | 0 | 0.01 | 0 | 0.03 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0.01 | 24.32
STECMEC LOAD | 0.38 | 0.46 | 1.34 | 0.11 | 1.08 | 4 | 0.15 | 0.07 | 0.01 | 2.11 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.88 | 11.67
COB LOAD | 1.75 | 0.34 | 0.24 | 0.28 | 0.34 | 3.09 | 0.07 | 0.2 | 0.01 | 0.12 | 0 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0.01 | 7.06
TOTALS | 378.94 | 130.3 | 40.45 | 29.9 | 57.79 | 154.45 | 33.96 | 32.25 | 11.32 | 10.04 | 0.33 | 0.4 | 4.32 | 1.31 | 0.15 | 3.86 | 0.1 | 0 | 0.11 | 0.2 | 0.06 | 1.26 | 4.01 | 895.53 | 382.95
LOAD | 18024.6 | 12013.5 | 3143.9 | 1221.7 | 1962.9 | 3481.5 | 1711 | 1065 | 971.9 | 215 | 0 | 161.1 | 674 | 240.5 | 12.5 | 362.8 | 116 | 68.5 | 27.9 | 23.8 | 2.4 | 158.6 | 62.1 | 45721.2 | 18399.9
ZONE LOSS FACTOR | 2.102% | 1.085% | 1.287% | 2.447% | 2.944% | 4.436% | 1.985% | 3.028% | 1.165% | 4.67% | #DIV/0! | 0.2483% | 0.6409% | 0.5447% | 1.2% | 1.064% | 0.08621% | 0% | 0.3943% | 0.8403% | 2.5% | 0.7945% | 6.457% | 1.959%
LOSS ALLOCATION (% OF EVENT LOAD)
EVENT | LOAD | TU ELE | HLP | CPS | WTU | LCRA | CPL | COA | BEPC | TMPA | STEC | MIGUEL | COB | TNP | SESCO | FEC | TNP | COLSTA | WTEXLA | WTUTNP | BEPCWTU | RGEC | MVEC | MEC | TOTAL
TNP - Lewisville | 29.99 | 1.68 | 0.15 | 0.04 | 0.05 | 0.12 | 0.2 | 0.04 | 0.17 | 0.06 | 0.01 | 0 | 0 | 0.02 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.56
TNP | 622.27 | 0.21 | 1.26 | 0.03 | 0.02 | 0.08 | 0.16 | 0.03 | 0.02 | 0 | 0.02 | 0 | 0 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.38
TNP - SS 01 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TUE LOAD | 18091.65 | 1.51 | 0.06 | 0.02 | 0.08 | 0.05 | 0.12 | 0.02 | 0.08 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.97
TUE TO TNP WHSAL | 339.82 | 2.7 | 0.06 | 0.02 | 0.1 | 0.06 | 0.15 | 0.01 | 0.14 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.35
DNDAM TO RAYBURN | 42.5 | 2.85 | 0.01 | 0 | 0.01 | 0.01 | 0.02 | 0 | 0.05 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
TUE TO COLSTA WH | 118.8 | 1.89 | 0.25 | 0.06 | 0.09 | 0.15 | 0.28 | 0.05 | 0.35 | 0.38 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 3.56
SANDOW TO ALCOA | 425 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06
CPL TO SESCO | 21.94 | 2.76 | 0.58 | 0.33 | 0.11 | 0.44 | 2.32 | 0.1 | 0.14 | 0.02 | 0.17 | 0.01 | 0 | 0 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 7.23
LCRA TO SESCO | 73.09 | 2.99 | 0.43 | 0.08 | 0.11 | 0.69 | 0.38 | 0.24 | 0.16 | 0.01 | 0.02 | 0 | 0 | 0 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.35
HLP LOAD | 12143.85 | 0.08 | 0.82 | 0.02 | 0.01 | 0.04 | 0.06 | 0.02 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05
CPS LOAD | 3184.4 | 0.07 | 0.05 | 0.67 | 0.01 | 0.08 | 0.3 | 0.03 | 0.01 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1.27
CPL Gen-CPL Load | 3768 | 0.13 | 0.09 | 0.21 | 0.05 | 0.12 | 2.3 | 0.02 | 0.01 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 3.13
IBWC to CPL Load | 39 | 0.56 | 0.13 | 0.35 | 0.34 | 0.18 | 6.8 | 0.03 | 0.05 | 0 | 0.14 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.08 | 8.72
WTU Gen to WTU L | 1100.14 | 1.74 | 0.03 | 0.04 | 0.78 | 0.1 | 0.43 | 0.01 | 0.05 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0 | 0.01 | 3.23
Denison D-Texla | 27.5 | 4.49 | 0.03 | 0.01 | 0.02 | 0.04 | 0.06 | 0.01 | 0.13 | 0.03 | 0 | 0 | 0 | 0 | 0.45 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 5.29
WTU Gen-Texla | 41.54 | 5.59 | 0.09 | 0.07 | 0.66 | 0.17 | 0.65 | 0.02 | 0.26 | 0.02 | 0.02 | 0 | 0 | 0 | 0.45 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0.01 | 8.01
LCRA-96S1 | 2031.89 | 0.34 | 0.07 | 0.07 | 0.05 | 1.13 | 0.23 | 0.27 | 0.03 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.21
HUNT COLLIN-96S1 | 11.32 | 4.67 | 0.41 | 0.08 | 0.13 | 0.71 | 0.44 | 0.24 | 0.22 | 0.04 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.97
COA LOAD | 1747.98 | 0.29 | 0.12 | 0.08 | 0.01 | 0.35 | 0.16 | 1.1 | 0.04 | 0.01 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.18
COA WEATHERFORD | 24.98 | 3.49 | 0.32 | 0.1 | 0.17 | 0.57 | 0.47 | 1.19 | 1.22 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 7.58
BPM | 7.69 | 2.07 | 0.33 | 0.1 | 0.13 | 0.54 | 0.42 | 1.19 | 0.38 | 0.03 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 5.24
GRANBURY LOAD | 14.49 | 2.23 | 0.18 | 0.05 | 0.08 | 0.17 | 0.25 | 0.03 | 1.47 | 0.83 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 5.32
BRAZOS LOAD | 1050.08 | 1.97 | 0.11 | 0.05 | 0.08 | 0.14 | 0.26 | 0.05 | 0.82 | 0.1 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 3.62
TMPA LOAD | 983.21 | 1.13 | 0.12 | 0.03 | 0.03 | 0.08 | 0.13 | 0.02 | 0.25 | 0.67 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47
STECMEC LOAD | 277.61 | 0.14 | 0.16 | 0.48 | 0.04 | 0.39 | 1.44 | 0.05 | 0.03 | 0 | 0.76 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 4.2
COB LOAD | 161.4 | 1.08 | 0.21 | 0.15 | 0.17 | 0.21 | 1.91 | 0.04 | 0.12 | 0.01 | 0.07 | 0 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.01 | 4.37

## GSU LOSS
|  | UNIT STEP UP TRNASFORMER LOSSES |  |  |  |  | Internal
XLS | UTILITY | 1996-06-19 | 1996-07-22 | 1996-08-05 | 1996-09-10 | Average | Generation
GLCS | COLLEGE STATION
GLNBEC | BEPC | 2.2591 | 2.1982 | 1.8252 | 1.9691 | 2.0629 |  | 1.717%
GLNCOA | COA | 2.3697 | 1.6428 | 2.2674 | 0.77072 | 1.7627 |  | 1.467%
GLNCPS | CPS | 5.2388 | 6.4826 | 6.245 | 5.5783 | 5.8862 |  | 4.898%
GLNCSW | CPL | 6.7413 | 6.7071 | 7.8279 | 6.4592 | 6.9339 |  | 5.77%
GLNCSW | WTU | 1.772 | 3.443 | 2.8661 | 2.7419 | 2.7058 |  | 2.252%
GLNGB | CITY OF GRANBURY
GLNHC | HUNT COLLINS
GLNHLP | HLP | 38.7864 | 43.287 | 44.3494 | 39.8879 | 41.5776 |  | 34.6%
GLNLCRA | LCRA | 3.0185 | 3.0758 | 2.7879 | 2.9471 | 2.9573 |  | 2.461%
GLNPUB | PUB
GLNSTEC | STEC (2) | -0.33 | -0.33 | -0.33 | -0.33 | -0.33
GLNTNP | TNP (1) | -0.216 | -0.047 | 1 | 1 | 0.43425 |  | 0.3614%
GLNTU | TU | 59.0495 | 59.5169 | 58.0234 | 48.1125 | 56.1756 |  | 46.75%
LNTMPA | TMPA
|  | ----------- | ----------- | ----------- | ----------- | -----------
|  | 118.6895 | 125.9764 | 126.8622 | 109.1367 | 120.1662 |  | 100.3%
2026-07-29
46232.8222
(1) In June and July, HLP metering of TNP One accounts for GSU losses, but not the 345 kV transmission line losses.
Since 345 kV line losses are transmission losses, they show up as additional load, instead of a reduction of generation.
(2) STECMEC generation is highside metered, however, the San Miguel is metered on the outgoing lines, and autotransformer
losses are not represented in the reported 4CP load. To correct for unmetered losses, a credit (negative deduct) is allocated to
STECMEC to balance the loss adjustment factor.

## BEPC
bepc step up losses(mw)
| june |  | july | aug | sept
ntex1 | 0.0398 |  | 0.0398 | 0.0788 | 0.0398 | 0.0398 | 0 | 0 | 0.039 | 0
ntex2 | 0.0392 |  | 0.0392 | 0.0742 | 0.0392 | 0.0392 | 0 | 0 | 0.035 | 0
ntex3 | 0.1649 |  | 0.1899 | 0.2089 | 0.0329 | 0.0329 | 0.132 | 0.157 | 0.176 | 0
mil1 | 0.3262 |  | 0.3262 | 0.3112 | 0.3182 | 0.0612 | 0.265 | 0.265 | 0.25 | 0.257
mil2 | 0.5084 |  | 0.5384 | 0.5154 | 0.4934 | 0.0874 | 0.421 | 0.451 | 0.428 | 0.406
mil3 | 0.67265 |  | 0.57665 | 0.13165 | 0.54865 | 0.03965 | 0.633 | 0.537 | 0.092 | 0.509
mil4 | 0.254 |  | 0.25 | 0.25 | 0.246 | 0.041 | 0.213 | 0.209 | 0.209 | 0.205
mil5 | 0.254 |  | 0.238 | 0.255 | 0.251 | 0.041 | 0.213 | 0.197 | 0.214 | 0.21
| 2.2591 |  | 2.1982 | 1.8252 | 1.9691

## COA
Calculation of GSU Losses for COA
1996-06-19
Generator |  | MVA | R (in p.u on 100 MVA) | Losses (KW)
Decker 1 |  | 331.8 | 0.00059 | 649.5383
Decker 2 |  | 398.8 | 0.00049 | 779.3031
Decker GT1 |  | 50 | 0.00196 | 49
Decker GT2 |  | 43 | 0.00196 | 36.2404
Holly 1 |  | 89.1 | 0.00281 | 223.0806
Holly 2 |  | 42.6 | 0.00226 | 41.0136
Holly 3 |  | 141.9 | 0.00122 | 245.6544
Holly 4 |  | 167.7 | 0.00123 | 345.9165
| Total GSU Losses (KW) |  |  | 2369.7468
1996-07-22
Generator |  | MVA | R (in p.u on 100 MVA) | Losses (KW)
Decker 1 |  | 0 | 0.00059 | 0
Decker 2 |  | 396.2 | 0.00049 | 769.1748
Decker GT1 |  | 50 | 0.00196 | 49
Decker GT2 |  | 90.6 | 0.00196 | 160.8839
Holly 1 |  | 59.9 | 0.00281 | 100.8231
Holly 2 |  | 0 | 0.00226 | 0
Holly 3 |  | 143.6 | 0.00122 | 251.5757
Holly 4 |  | 159.1 | 0.00123 | 311.3476
| Total GSU Losses (KW) |  |  | 1642.805
1996-08-05
Generator |  | MVA | R (in p.u on 100 MVA) | Losses (KW)
Decker 1 |  | 326.5 | 0.00059 | 628.9533
Decker 2 |  | 404 | 0.00049 | 799.7584
Decker GT1 |  | 50 | 0.00196 | 49
Decker GT2 |  | 50 | 0.00196 | 49
Decker GT3 |  | 50.6 | 0.00196 | 50.1831
Holly 1 |  | 68.8 | 0.00281 | 133.0097
Holly 2 |  | 0 | 0.00226 | 0
Holly 3 |  | 147.4 | 0.00122 | 265.0665
Holly 4 |  | 154.2 | 0.00123 | 292.465
| Total GSU Losses (KW) |  |  | 2267.4358
1996-09-10
Generator |  | MVA | R (in p.u on 100 MVA) | Losses (KW)
Decker 1 |  | 0 | 0.00059 | 0
Decker 2 |  | 332.3 | 0.00049 | 541.0741
Decker GT1 |  | 0 | 0.00196 | 0
Decker GT2 |  | 0 | 0.00196 | 0
Holly 1 |  | 0 | 0.00281 | 0
Holly 2 |  | 0 | 0.00226 | 0
Holly 3 |  | 137.2 | 0.00122 | 229.6508
Holly 4 |  | 0 | 0.00123 | 0
| Total GSU Losses (KW) |  |  | 770.725

## CPS
Transformer Data
| No Load | Full Load
| Loss | Loss | Test | High Side | Low Side
Generator | (Watts) | (Watts) | MVA | kV | kV
MRP3
LCP3
LCP4
WBT1 | 107140 | 363500 | 85 | 138 | 13.2
WBT2 | 132200 | 494200 | 130 | 138 | 13.2
WBT3 | 123819 | 477446 | 130 | 138 | 13.2
WBT4 | 157600 | 725000 | 210 | 138 | 17.2
VHB1 | 151689 | 789403 | 265 | 138 | 19
VHB2 | 160876 | 769657 | 296 | 138 | 20.9
VHB3 | 248840 | 1461818 | 490 | 138 | 20.9
OWS1 | 261605 | 1437000 | 496 | 138 | 20.9
OWS2 | 285645 | 886656 | 485 | 138 | 22.8
JTD1 | 224866 | 1471686 | 507 | 138 | 22.8
JTD2 | 250182 | 888570 | 485 | 138 | 22.8
JKS1 | 293616 | 842074 | 650 | 345 | 24
STP1
STP2
| June 19, 1996 @ 17:00 |  |  |  | July 22, 1996 @ 17:00 |  |  | August 5, 1996 @ 17:00 |  |  | September 10, 1996 @ 18:00
| Generation |  | GSU Loss |  | Generation |  | GSU Loss | Generation |  | GSU Loss | Generation |  | GSU Loss
| MW | MVAR | Watts |  | MW | MVAR | MW | MW | MVAR | MW | MW | MVAR | MW
MRP3
LCP3
LCP4
WBT1
WBT2 | [7 empty] | 53 |  | 214342.4734
WBT3
WBT4 | [7 empty] | 134 |  | 452795.0113
VHB1 | 60 |  | 192156.7935 |  | 211 |  | 652151.9543 | 211 |  | 652151.9543
VHB2 | 200 |  | 512253.374 |  | 181 |  | 448662.8537 | 185 |  | 461523.2656
VHB3 | 390 |  | 1174881.307 |  | 376 |  | 1109589.6109 | 390 |  | 1174881.307 | 389 |  | 1170138.4655
OWS1 |  |  |  |  | 342 |  | 944801.4913 |  |  |  | 365 |  | 1039783.3502
OWS2 | 340 |  | 721387.092 |  | 334 |  | 706143.6576 | 326 |  | 686241.2506 | 357 |  | 766050.6565
JTD1 | 370 |  | 1008661.3596 |  | 360 |  | 966866.5742 | 362 |  | 975133.9263 | 364 |  | 983447.0809
JTD2 | 379 |  | 792790.4956 |  | 384 |  | 807201.7807 | 377 |  | 787078.867 | 376 |  | 784234.3852
JKS1 | 522 |  | 836696.9274 |  | 527 |  | 847150.6034 | 524 |  | 840866.4393 | 521 |  | 834618.1506
STP | 701 |  |  |  | 687 |  |  | 701 |  |  | 693
Total | 2962 |  | 5238827.3491 |  | 3402 |  | 6482568.5261 | 3263 |  | 6245014.4948 | 3065 |  | 5578272.0889

## CSW
CSW 1996 ESTIMATED LOSSES FOR GENERATOR STEP UP TRANSFORMER
|  |  | Unit | 6/19/96 | 7/22/96 | 8/5/96 | 9/10/96 | Cap | Joint |  |  | 6/19/96 | 7/22/96 | 8/5/96 | 9/10/96
Co | Bus# | Power Station | No | 1700 | 1700 | 1700 | 1800 | MW | Unit | kV | Rpu | 1700 | 1700 | 1700 | 1800 | Average | Master | CC | Rohms | I/phase | Losses MW
CPL | 8032 | Amistad Hydro | 1 | 21 | 0 | 0 | 0 | 58 |  | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 878.5765 | 0
CPL | 8048 | Falcon Hydro | 1 | 5 | 0 | 6 | 0 | 39.5 |  | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 9 | 0 | 209.1849 | 0
CPL | 8139 | Ennis Joslin | 1 | 209 | 156 | 226 | 164 | 249 |  | 22 | 0.001 | 0.43681 | 0.24336 | 0.51076 | 0.26896 | 0.36497 | 4 | 13 | 0.00484 | 5484.8276 | 0.43681
CPL | 8161 | Coleto Creek | 1 | 608 | 624 | 617 | 621 | 632 |  | 24 | 0.0003 | 1.109 | 1.1681 | 1.1421 | 1.1569 | 1.144 | 5 | 7 | 0.001728 | 14626.2068 | 1.109
CPL | 8168 | Victoria | 4 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [5 empty] | 6 | 51 | 0 | 0 | 0
CPL | 8173 | Victoria | 5 | 127 | 109 | 131 | 0 | 174 |  | 22 | 0.001 | 0.16129 | 0.11881 | 0.17161 | 0 | 0.11293 | 7 | 52 | 0.00484 | 3332.8856 | 0.16129
CPL | 8174 | Victoria | 6 | 244 | 152 | 225 | 204 | 258 |  | 22 | 0.001 | 0.59536 | 0.23104 | 0.50625 | 0.41616 | 0.4372 | 8 | 53 | 0.00484 | 6403.3393 | 0.59536
CPL | 8262 | Eagle Pass Hydro | 1 | 7 | 5 | 5 | 7 | 6 |  | 13.8 | 0.0601 | 0.029449 | 0.015025 | 0.015025 | 0.029449 | 0.022237 | 9 | 8 | 0.11445 | 292.8588 | 0.029449
CPL | 8285 | Laredo | 1 | 31 | 28 | 28 | 25 | 34 |  | 13.8 | 0.0113 | 0.10859 | 0.088592 | 0.088592 | 0.070625 | 0.0891 | 10 | 14 | 0.02152 | 1296.9463 | 0.10859
CPL | 8287 | Laredo | 2 | 28 | 27 | 29 | 20 | 32 |  | 13.8 | 0.0094 | 0.073696 | 0.068526 | 0.079054 | 0.0376 | 0.064719 | 11 | 15 | 0.017901 | 1171.4353 | 0.073696
CPL | 8288 | Laredo | 3 | 99 | 98 | 99 | 100 | 111 |  | 13.8 | 0.0028 | 0.27443 | 0.26891 | 0.27443 | 0.28 | 0.27444 | 12 | 16 | 0.0053323 | 4141.8606 | 0.27443
CPL | 8305 | La Palma | 4 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [5 empty] | 13 | 17 | 0 | 0 | 0
CPL | 8306 | La Palma | 5 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [5 empty] | 14 | 18 | 0 | 0 | 0
CPL | 8308 | La Palma | 6 | 157 | 148 | 150 | 148 | 158 |  | 18 | 0.0018 | 0.44368 | 0.39427 | 0.405 | 0.39427 | 0.40931 | 15 | 19 | 0.005832 | 5035.7773 | 0.44368
CPL | 8307 | La Palma | 7 | 0 | 0 | 49 | 0 | 47 |  | 22 | 0.0043 | 0 | 0 | 0.10324 | 0 | 0.025811 | 16 | 20 | 0.020812 | 0 | 0
CPL | 8388 | J. L. Bates | 1 | 66 | 62 | 67 | 0 | 72 |  | 13.8 | 0.0041 | 0.1786 | 0.1576 | 0.18405 | 0 | 0.13006 | 17 | 3 | 0.007808 | 2761.2404 | 0.1786
CPL | 8393 | J. L. Bates | 2 | 107 | 99 | 104 | 101 | 110 |  | 13.8 | 0.0034 | 0.38927 | 0.33323 | 0.36774 | 0.34683 | 0.35927 | 18 | 4 | 0.006475 | 4476.5564 | 0.38927
CPL | 8437 | Nueces Bay | 5 | 32 | 0 | 0 | 0 | 34 |  | 13.8 | 0.0114 | 0.11674 | 0 | 0 | 0 | 0.029184 | 19 | 25 | 0.02171 | 1338.7832 | 0.11674
CPL | 8438 | Nueces Bay | 6 | 162 | 159 | 156 | 158 | 161 |  | 20 | 0.002 | 0.52488 | 0.50562 | 0.48672 | 0.49928 | 0.50413 | 20 | 26 | 0.008 | 4676.5372 | 0.52488
CPL | 8442 | Nueces Bay | 7 | 0 | 351 | 352 | 340 | 368 |  | 22 | 0.001 | 0 | 1.232 | 1.239 | 1.156 | 0.90676 | 21 | 27 | 0.00484 | 0 | 0
CPL | 8444 | Lon C. Hill | 1 | 42 | 0 | 31 | 0 | 72 |  | 13.8 | 0.004 | 0.07056 | 0 | 0.03844 | 0 | 0.02725 | 22 | 21 | 0.0076176 | 1757.153 | 0.07056
CPL | 8445 | Lon C. Hill | 2 | 24 | 0 | 18 | 0 | 73 |  | 13.8 | 0.0054 | 0.031104 | 0 | 0.017496 | 0 | 0.01215 | 23 | 22 | 0.010284 | 1004.0874 | 0.031104
CPL | 8446 | Lon C. Hill | 3 | 143 | 103 | 135 | 0 | 157 |  | 18 | 0.0018 | 0.36808 | 0.19096 | 0.32805 | 0 | 0.22177 | 24 | 23 | 0.005832 | 4586.7271 | 0.36808
CPL | 8447 | Lon C. Hill | 4 | 235 | 203 | 227 | 232 | 248 |  | 22 | 0.001 | 0.55225 | 0.41209 | 0.51529 | 0.53824 | 0.50447 | 25 | 24 | 0.00484 | 6167.1506 | 0.55225
CPL | 8459 | Barney M. Davis | 1 | 306 | 309 | 321 | 311 | 339 |  | 24 | 0.0007 | 0.65545 | 0.66837 | 0.72129 | 0.67705 | 0.68054 | 26 | 5 | 0.004032 | 7361.2159 | 0.65545
CPL | 8460 | Barney M. Davis | 2 | 322 | 319 | 325 | 313 | 356 |  | 22 | 0.0006 | 0.6221 | 0.61057 | 0.63375 | 0.58781 | 0.61356 | 27 | 6 | 0.002904 | 8450.3085 | 0.6221
HLP | 5911 | South Texas Proj | 1 |  |  |  |  | 315 | Yes | 25 | 0 | [5 empty] | 28 | 55 | 0 | 0 | 0
HLP | 5912 | South Texas Proj | 2 |  |  |  |  | 315 | Yes | 25 | 0 | [5 empty] | 29 | 56 | 0 | 0 | 0
WTU | 6698 | Denison Dam | 1 |  |  |  |  | 40 | Yes | 12 | 0.006 | [5 empty] | 30 | 57 | 0.00864 | 0 | 0
WTU | 6698 | Denison Dam | 2 |  |  |  |  | 40 | Yes | 12 | 0.006 | [5 empty] | 31 | 58 | 0.00864 | 0 | 0
WTU | 6061 | Vernon Plant | 1 | 0 | 0 | 0 | 0 | 9 |  | 69 | 0 | [5 empty] | 32 | 46 | 0 | 0 | 0
WTU | 6061 | Vernon Plant | 2 | 0 | 0 | 0 | 0 |  |  | 69 | 0 | [5 empty] | 33 | 47 | 0 | 0 | 0
WTU | 6061 | Vernon Plant | 3 | 0 | 0 | 0 | 0 |  |  | 69 | 0 | [5 empty] | 34 | 48 | 0 | 0 | 0
WTU | 6061 | Vernon Plant | 4 | 0 | 0 | 0 | 0 |  |  | 69 | 0 | [5 empty] | 35 | 49 | 0 | 0 | 0
WTU | 6061 | Vernon Plant | 7 | 0 | 0 | 0 | 0 |  |  | 69 | 0 | [5 empty] | 36 | 50 | 0 | 0 | 0
WTU | 6282 | Abilene Plant | 4 | 12 | 0 | 0 | 0 | 12 |  | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1 | 0 | 100.4087 | 0
WTU | 6628 | Fort Stockton | 2 | 0 | 0 | 0 | 0 | 5 |  | 69 | 0 | [5 empty] | 38 | 12 | 0 | 0 | 0
WTU | 6677 | Renewable | 1 |  |  |  |  | 1 |  | 69 | 0 | [5 empty] | 39 | 59 | 0 | 0 | 0
WTU | 6684 | Presidio | 1 | 0 | 0 | 0 | 0 |  |  | 69 | 0 | [5 empty] | 40 | 36 | 0 | 0 | 0
WTU | 6684 | Presidio | 5 | 0 | 0 | 0 | 0 | 1 |  | 69 | 0 | [5 empty] | 41 | 37 | 0 | 0 | 0
WTU | 6684 | Presidio | 6 | 0 | 0 | 0 | 0 | 1 |  | 69 | 0 | [5 empty] | 42 | 38 | 0 | 0 | 0
WTU | 6750 | Lake Pauline | 1 | 0 | 0 | 0 | 0 | 19 |  | 13.8 | 0.00766 | [5 empty] | 43 | 34 | 0.014588 | 0 | 0
WTU | 6751 | Lake Pauline | 2 | 0 | 0 | 0 | 0 | 27 |  | 13.8 | 0 | [5 empty] | 44 | 35 | 0 | 0 | 0
WTU | 6752 | OklaunioN | 1 | 0 | 665 | 665 | 666 | 666 | Yes | 24 | 0.00028 | 0 | 1.2382 | 1.2382 | 1.242 | 0.9296 | 45 | 29 | 0.0016128 | 0 | 0
WTU | 6753 | Paint Creek | 1 | 8 | 0 | 11 | 0 | 33 |  | 13.8 | 0.00375 | 0.0024 | 0 | 0.0045375 | 0 | 0.0017344 | 46 | 30 | 0.0071415 | 334.6958 | 0.0024
WTU | 6754 | Paint Creek | 2 | 9 | 0 | 9 | 0 | 33 |  | 13.8 | 0.00384 | 0.0031104 | 0 | 0.0031104 | 0 | 0.0015552 | 47 | 31 | 0.0073129 | 376.5328 | 0.0031104
WTU | 6755 | Paint Creek | 3 | 14 | 46 | 15 | 0 | 54 |  | 13.8 | 0.0086 | 0.016856 | 0.18198 | 0.01935 | 0 | 0.054545 | 48 | 32 | 0.016378 | 585.7177 | 0.016856
WTU | 6756 | Paint Creek | 4 | 68 | 96 | 75 | 73 | 117 |  | 14.4 | 0.00337 | 0.15583 | 0.31058 | 0.18956 | 0.17959 | 0.20889 | 49 | 33 | 0.006988 | 2726.3763 | 0.15583
WTU | 6757 | Fort Phantom | 1 | 146 | 147 | 134 | 0 | 158 |  | 14.4 | 0.00163 | 0.34745 | 0.35223 | 0.29268 | 0 | 0.24809 | 50 | 10 | 0.00338 | 5853.6902 | 0.34745
WTU | 6758 | Fort Phantom | 2 | 190 | 190 | 154 | 177 | 204 |  | 20 | 0.0011 | 0.3971 | 0.3971 | 0.26088 | 0.34462 | 0.34992 | 51 | 11 | 0.0044 | 5484.8276 | 0.3971
WTU | 6759 | Oak Creek | 1 | 78 | 78 | 80 | 79 | 87 |  | 13.8 | 0.00416 | 0.25309 | 0.25309 | 0.26624 | 0.25963 | 0.25801 | 52 | 28 | 0.0079223 | 3263.2841 | 0.25309
WTU | 6762 | San Angelo | 1 | 21 | 22 | 21 | 23 | 22 |  | 14.4 | 0.01477 | 0.065136 | 0.071487 | 0.065136 | 0.078133 | 0.069973 | 53 | 43 | 0.030627 | 841.9691 | 0.065136
WTU | 6763 | San Angelo | 2 | 100 | 99 | 81 | 100 | 103 |  | 14.4 | 0.00361 | 0.361 | 0.35382 | 0.23685 | 0.361 | 0.32817 | 54 | 44 | 0.0074857 | 4009.3769 | 0.361
WTU | 6764 | Rio Pecos | 4 | 2 | 2 | 2 | 2 | 3 |  | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 39 | 0 | 274.9287 | 0
WTU | 6765 | Rio Pecos | 5 | 27 | 29 | 29 | 27 | 36 |  | 13.8 | 0.00676 | 0.04928 | 0.056852 | 0.056852 | 0.04928 | 0.053066 | 57 | 40 | 0.012874 | 1129.5984 | 0.04928
WTU | 6766 | Rio Pecos | 6 | 67 | 92 | 93 | 92 | 98 |  | 14.4 | 0.00269 | 0.12075 | 0.22768 | 0.23266 | 0.22768 | 0.20219 | 58 | 41 | 0.005578 | 2686.2825 | 0.12075
|  | Total |  | 2874 | 3638 | 3821 | 3198 |  |  |  |  | 8.5133 | 10.1502 | 10.694 | 9.2011 | 9.6396 | 60 | 54 |  |  | 8.5133
12/06/96
[11 empty] | CPL | 6.7413 | 6.7071 | 7.8279 | 6.4592
[11 empty] | WTU | 1.772 | 3.443 | 2.8661 | 2.7419

## HLP
1995 GSU Losses |  |  |  | 1996 GSU Losses
| MW | MVAR |  | MW | MVAR
June | 45.4 | 1400 |  | 38.7864 | 1157.7117
July | 45.4 | 1400 |  | 43.287 | 1274.32
August | 44.4 | 1350 |  | 44.3494 | 1337.5895
September | 40 | 1200 |  | 39.8879 | 1166.7403
1996 GSU Losses
MAIN TRANSFORMER LOSSES
|  | 6-8-95 |  | 7-28-95 |  | 8-21-95 |  | 9-5-95
|  | Total Loss in Trf |  | Total Loss in Trf |  | Total Loss in Trf |  | Total Loss in Trf
Plant | Unit | MW | MVAR | MW | MVAR | MW | MVAR | MW | MVAR
Cedar Bayou | 1 | 2.3739 | 59.5154 | 2.8686 | 74.6296 | 2.8646 | 73.4749 | 0.42446 | 0.064791
Cedar Bayou | 2 | 1.0834 | 52.1168 | 0.94945 | 43.6063 | 1.2859 | 64.2115 | 1.0737 | 51.1057
Cedar Bayou | 3 | 1.3967 | 70.4138 | 1.4282 | 72.8702 | 1.4731 | 76.3673 | 1.4288 | 72.9812
Deepwater | 7A | 0.2375 | 4.8945 | 0.24021 | 4.9832 | 0.083594 | 0 | 0.086426 | 0.013051
Deepwater | 7B | 0.24232 | 4.8948 | 0.24517 | 4.9835 | 0.084709 | 0 | 0.087578 | 0.013584
Deepwater | 7C | 0.23637 | 4.8951 | 0.23915 | 4.9838 | 0.08278 | 0 | 0.08557 | 0.013561
Greens Bayou | 5 |  |  | 1.4929 | 34.7156 | 1.6132 | 37.6489 | 1.3992 | 32.202
Greens Bayou | 73 |  |  | 0.36815 | 9.7943
Greens Bayou | 74 |  |  | 0 | 0
Greens Bayou | 81 |  |  | 0.33181 | 6.6998 |  |  | 0.11122 | 0.03258
Greens Bayou | 82 |  |  | 0 | 0 |  |  | 0 | 0
Greens Bayou | 83
Greens Bayou | 84
H O Clarke | G1
H O Clarke | G2
H O Clarke | G3
H O Clarke | G4
H O Clarke | G5
H O Clarke | G6
Limestone | 1 | 1.7155 | 55.8292 | 1.7176 | 55.9321 | 1.7168 | 55.8292 | 1.7111 | 55.6293
Limestone | 2 | 1.7139 | 57.886 | 1.7192 | 58.1507 | 1.6946 | 56.8563 | 1.7328 | 58.8513
P H Robinson | 1 | 1.0241 | 46.6569 | 1.0156 | 46.1372 | 1.0355 | 47.541 | 0.98742 | 44.7134
P H Robinson | 2 | 0.33619 | 0 | 1.5962 | 42.4117 | 1.6342 | 43.9272 | 1.4988 | 39.1944
P H Robinson | 3 | 0.82945 | 25.1376 | 1.3708 | 48.4788 | 1.5073 | 54.6812 | 1.2825 | 45.1426
P H Robinson | 4 | 1.3956 | 68.9275 | 0.69274 | 23.3814 | 1.3867 | 68.2786 | 1.2935 | 62.3924
S R Bertron | 1A | 0.24212 | 4.2183 | 0.27657 | 5.408 | 0.2646 | 5.0516 | 0.11961 | 0
S R Bertron | 1B | 0.24171 | 4.2253 | 0.27629 | 5.4169 | 0.26434 | 5.0599 | 0.11875 | 0
S R Bertron | 1C | 0.24479 | 4.2495 | 0.27924 | 5.448 | 0.26714 | 5.089 | 0.12223 | 0
S R Bertron | 2A | 0.23211 | 4.7002 | 0.23899 | 4.9357 | 0.25326 | 5.414 | 0.22418 | 4.4524
S R Bertron | 2B | 0.23676 | 4.7005 | 0.24381 | 4.936 | 0.25853 | 5.4143 | 0.22869 | 4.4527
S R Bertron | 2C | 0.23093 | 4.7008 | 0.2378 | 4.9362 | 0.25217 | 5.4146 | 0.22308 | 4.453
S R Bertron | 3A | 0.12968 | 0 |  |  | 0.12375 | 0 | 0.27272 | 5.7226
S R Bertron | 3B | 0.1257 | 0 |  |  | 0.11996 | 0 | 0.27135 | 5.723
S R Bertron | 3C | 0.12282 | 0 |  |  | 0.11719 | 0 | 0.26742 | 5.7118
S R Bertron | 4A | 0.33585 | 6.6902 | 0.34592 | 7.0136 | 0.39735 | 8.6071 | 0.3685 | 7.7284
S R Bertron | 4B | 0.33516 | 6.6904 | 0.34524 | 7.0138 | 0.39669 | 8.6072 | 0.36783 | 7.7286
S R Bertron | 4C | 0.33534 | 6.6904 | 0.34541 | 7.0138 | 0.39686 | 8.6072 | 0.368 | 7.7286
S R Bertron | G1
S R Bertron | G2
San Jacinto | G1 | 0.36359 | 4.4434 | 0.36874 | 4.5288 | 0.36959 | 4.5431
San Jacinto | G2 | 0.38884 | 4.8628 | 0.36874 | 4.5288 | 0.36653 | 4.4921 | 0.35583 | 4.3144
South Texas | 1A | 1.1884 | 48.0846 | 1.1877 | 48.0403 | 1.1939 | 48.5838 | 1.1837 | 47.8184
South Texas | 1B | 1.6933 | 49.9505 | 1.6922 | 49.9044 | 1.6991 | 50.4692 | 1.6863 | 49.6739
South Texas | 2A | 1.6897 | 50.4929 | 1.6907 | 50.5324 | 1.6669 | 49.8401 | 1.6907 | 50.5324
South Texas | 2B | 1.6876 | 50.493 | 1.6885 | 50.5325 | 1.6646 | 49.8402 | 1.6885 | 50.5325
T H Wharton | 2A | 1.0275 | 21.2296 | 1.0763 | 22.2963 | 1.0419 | 22.4011 | 0.88887 | 19.1195
T H Wharton | 2B | 0.93615 | 22.8119 | 0.97962 | 23.9582 | 0.95056 | 24.0702 | 0.81485 | 20.5436
T H Wharton | 2C | 0.95525 | 22.9609 | 0.99964 | 24.1147 | 0.97002 | 24.2274 | 0.83146 | 20.6778
T H Wharton | G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T H Wharton | 31 | 0.30963 | 5.8304 | 0.30972 | 5.8328 | 0.30669 | 5.7307 | 0.307 | 5.7531
T H Wharton | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T H Wharton | 33 | 0.20797 | 3.1661 | 0.19486 | 2.8191 | 0.20364 | 3.0595 | 0.1931 | 2.777
T H Wharton | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T H Wharton | 41 | 0.29971 | 5.7621 | 0.30147 | 5.8099 | 0.29627 | 5.6482 | 0.30257 | 5.8316
T H Wharton | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T H Wharton | 43 | 0.2201 | 3.8336 | 0.21995 | 3.8289 | 0.33884 | 7.4664 | 0.22127 | 3.8758
T H Wharton | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T H Wharton | 51
T H Wharton | 52
T H Wharton | 53 |  |  | 0.23135 | 4.8942
T H Wharton | 54 |  |  | 0 | 0
T H Wharton | 55 |  |  | 0.34921 | 10.0977
T H Wharton | 56 |  |  | 0 | 0
T H Wharton | ST3 | 0.39053 | 9.9168 | 0.38688 | 9.7946 | 0.3737 | 9.3055 | 0.37647 | 9.4278
T H Wharton | ST4 | 0.42258 | 10.7281 | 0.39344 | 9.7756 | 0.48072 | 12.5434 | 0.39322 | 9.7483
W A Parish | 1A | 0.12535 | 0 | 0.14321 | 0.17728 | 0.55587 | 12.9922 | 1.1202 | 0
W A Parish | 1B | 0.13836 | 0 | 0.14088 | 0 | 0.54708 | 12.9925 | 0.13214 | 0
W A Parish | 1C | 0.14723 | 0 | 0.14985 | 0 | 0.57149 | 12.9915 | 0.14061 | 0
W A Parish | 2A | 0.49822 | 11.0471 | 0.57202 | 13.3235 | 0.55842 | 12.9308 | 0.49892 | 11.0002
W A Parish | 2B | 0.49397 | 11.0471 | 0.56779 | 13.3235 | 0.55413 | 12.9308 | 0.49486 | 11.0002
W A Parish | 2C | 0.48565 | 11.1397 | 0.55839 | 13.4351 | 0.54492 | 13.0391 | 0.48657 | 11.0924
W A Parish | 3 | 0.67658 | 19.3836 | 0.7669 | 23.2799 | 0.7742 | 23.6259 | 0.67867 | 19.4278
W A Parish | 4 | 1.748 | 53.7858 | 1.7745 | 54.8555 | 1.2781 | 34.8515 | 1.7793 | 54.4472
W A Parish | 5 | 1.758 | 64.0979 | 1.7204 | 62.4256 | 1.7727 | 64.9842 | 1.7404 | 62.4567
W A Parish | 6 | 3.4002 | 58.292 | 3.3067 | 55.4259 | 3.3231 | 57.3417 | 3.3855 | 58.7187
W A Parish | 7 | 1.6784 | 80.5993 | 1.7254 | 83.4465 | 1.7736 | 82.996 | 1.7511 | 83.0927
W A Parish | 8 | 1.6385 | 78.3618 | 1.6155 | 76.9684 | 1.617 | 74.1877 | 1.6066 | 74.7879
W A Parish | G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Webster | 3 | 0.81065 | 25.5733 | 0.93322 | 30.7016 | 0.96083 | 31.5331 | 0.9727 | 32.0982
Webster | G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40.778 | 1225.9273 | 45.2788 | 1342.5323 | 46.3291 | 1405.6989 | 41.877 | 1234.799
|  | 1.1884 | 48.0846 | 1.1877 | 48.0403 | 1.1939 | 48.5838 | 1.1837 | 47.8184
|  | 1.6897 | 50.4929 | 1.6907 | 50.5324 | 1.6669 | 49.8401 | 1.6907 | 50.5324
Multiplier | 0.692 | 38.7864 | 1157.7117 | 43.287 | 1274.32 | 44.3494 | 1337.5895 | 39.8879 | 1166.7403
|  | MW | MVAR | MW | MVAR | MW | MVAR | MW | MVAR
|  | 6-8-95 |  | 7-28-95 |  | 8-21-95 |  | 9-5-95
|  | 0.93941 | 0 | 0.60992 | 0 | 0.65327 | 0 | 0.6827 | 0
|  | 39.7258 | 1157.7117 | 43.8969 | 1274.32 | 45.0026 | 1337.5895 | 40.5706 | 1166.7403

## LCRA
UNIT | STEPUP XFMR TEST REPORT DATA | [6 empty] | LOW | HIGH | NO LOAD | FULL LOAD | UNIT LOADING |  | XFMR LOSSES
NAME | BASE | LOW | HIGH | NO LOAD | FULL LOAD | IMPD | IM | SIDE | SIDE | LOSS | LOSS | UNIT | UNIT | LOSS | LOSS
| RATING | SIDE | SIDE | LOSS | LOSS | (%) | (%) | AMPS | AMPS | (MVAR) | (MVAR) | (MW) | (MVAR) | (MW) | (MVAR)
| MVA | KV | KV | (WATTS) | (WATTS)
FPP1 | 600 | 22.8 | 345 | 345230 | 1310500 | 13.95 | 0.617 | 15193.4281 | 1004.0874 | 3.6859 | 83.6897
FPP2 | 600 | 22.8 | 345 | 320967 | 1345107 | 13.67 | 0.427 | 15193.4281 | 1004.0874 | 2.5418 | 82.009
FPP3 | 445 | 26.6 | 345 | 242750 | 703840 | 10.96 | 0.378 | 9658.6793 | 744.6982 | 1.6645 | 48.7669
GID1 | 160 | 17.2 | 138 | 119500 | 595000 | 12.8 | 0.4 | 5370.7002 | 669.3916 | 0.62874 | 20.4714
GID2 | 160 | 17.2 | 138 | 119500 | 595000 | 12.9 | 0.4 | 5370.7002 | 669.3916 | 0.62874 | 20.6314
GID3 | 380 | 20.9 | 138 | 181375 | 1045266 | 11.17 | 0.43 | 10497.2776 | 1589.8051 | 1.6239 | 42.4331
FERG | 480 | 22.8 | 138 | 206336 | 1403494 | 12.19 | 0.14 | 12154.7425 | 2008.1748 | 0.63954 | 58.4952
| JUNE |  |  |  | JULY | SIDE: AUGUST; UNIT: SEPTEMBER
| Loading |  | XFMR |  | Loading | IM: XFMR; SIDE: Loading; LOSS: XFMR; UNIT: Loading; LOSS: XFMR
| UNIT | UNIT | LOSS |  | UNIT | UNIT | LOSS |  | UNIT | UNIT | LOSS |  | UNIT | UNIT | LOSS
| (MW) | (MVAR) | (kW) |  | (MW) | (MVAR) | (kW) |  | (MW) | (MVAR) | (kW) |  | (MW) | (MVAR) | (kW)
FPP1
FPP2
FPP3
GID1 | 142 |  | 588.1555 |  | 135 | IM: 543.0889; SIDE: 132; LOSS: 524.4719; UNIT: 137; LOSS: 555.7326
GID2 | 142 |  | 588.1555 |  | 131 | IM: 518.3592; SIDE: 130; LOSS: 512.293; UNIT: 138; LOSS: 562.1242
GID3 | 309 |  | 872.5318 |  | 299 | IM: 828.5206; SIDE: 294; LOSS: 807.0579; UNIT: 295; LOSS: 811.3215
FERG | 354 |  | 969.7052 |  | 401 | IM: 1185.8639; SIDE: 348; LOSS: 944.0475; UNIT: 365; LOSS: 1017.8833
|  |  | 3018.5479 |  |  | IM: 3075.8326; LOSS: 2787.8703; LOSS: 2947.0616
| 1/2 FPP 1&2 |  | 0 |  | 1/2 FPP 1&2 | IM: 0; SIDE: 1/2 FPP 1&2; LOSS: 0; UNIT: 1/2 FPP 1&2; LOSS: 0
| Total for LCRA |  | 3018.5479 |  | Total for LCRA | IM: 3075.8326; SIDE: Total for LCRA; LOSS: 2787.8703; UNIT: Total for LCRA; LOSS: 2947.0616

## TNP1
| STEPUP AND AUX LOAD XFMR TEST REPORT DATA | [6 empty] | UNIT LOADING |  | LOSSES | UNIT
UNIT | BASE | LOW | HIGH | NO LOAD | FULL LOAD | IMPED | IM | UNIT | UNIT | TOTAL | NET
NAME | RATING | SIDE | SIDE | LOSS | LOSS | (%) | (%) | (MW) | (MVAR) | LOSS | TOTAL
| MVA | KV | KV | (WATTS) | (WATTS) |  |  |  |  | (MW) | (MW)
TNPONE#1 | 200 | 18 | 345 | 118100 | 633231 | 12.84 | 0.147 | 168.6 | N/A | 0.5 | 149.7
TNPONE#1 | 24 | 4.3 | 18 | 17840 | 87502 | 5.77 | 0.267 | 18.4 | N/A
TNPONE#2 | 200 | 18 | 345 | 119699 | 633799 | 12.67 | 0.151 | 165.2 | N/A | 0.5 | 147.1
TNPONE#2 | 24 | 4.3 | 18 | 17880 | 88528 | 5.51 | 0.106 | 17.6 | N/A
TNPSTUP | 15 | 4.3 | 345 | 49436 | 48429 | 7.83 | 0.189 | 0 | N/A
NOTES: | (1) TNPONE#1 and TNPONE#2 gross outputs metered at generator terminals
(2) Aux load metering for TNPONE#1 and TNPONE#2 is on low side of Aux XFMR.
(3) TNPONE#2 and TNPONE#2 does not have MVARH metering.
(4) During unit outages, aux load of outaged unit is carried on startup xfmr fed from
345 KV switchyard bus
Date: Fri, 6 Dec 1996 17:52:20 -0600 (CST)
X-Sender: tnpar3@pop.flash.net
To: phassink@ionet.net
From: Jack McCartney <tnpar3@tnpe.com>
Subject: Revised TNP One Generation Numbers | [8 empty] | 345 kV line losses | -0.216
Cc: Kdonohoo@ercot-iso.com, jack-henry@eng.hlp.com
Based on our telephone discussions concerning TNP One generation numbers for
the June,96 and July, 96 CP's, TNP is agreeable to use the metered numbers
provided by HL&P and adjust them to take into account the 345 KV
transmission losses on the TNP One - Twin Oak double circuit line. The TNP
One metered number for June, 96 is 296,676 KW and the metered number for
July, 1996 is 138,132 KW. These are the same numbers submitted by TNP on
November 6th. Subsequently, these numbers were revised to make them reflect
generation at the TNP One 345 KV bus by subtracting out the GSU losses and
the Auxiliary transformer losses. These were the numbers I sent you on
December 2nd. The earlier TNP One generation CP numbers reported for June,
96 and July, 96 were taken from HL&P metering at the Twin Oak Switching
Station bus and did not include the TNP One - Twin Oak 345 KV transmission
line losses. The equivalent resistance of the double circuit 345 KV line
from TNP One - Twin Oak is 0.309465 ohms. Based on a flow of 296,676 KW, the
equivalent transmission line loss is calculated to be 216 KW and results in
a net generation number of 296,905 KW for the June, 96 CP TNP One
generation. A similar calculation for July based on a flow of 138,132 KW
results in a calculated transmission loss of 47 KW and results in a net
generation number of 138,179 KW. I used a nominal operating voltage of 355
KV in calculating the line losses. Let me know if you have any questions on
the above or wish to discuss. I will be in the office on Monday.

## TNP2
| STEPUP AND AUX LOAD XFMR TEST REPORT DATA | [6 empty] | UNIT LOADING |  | LOSSES | UNIT
UNIT | BASE | LOW | HIGH | NO LOAD | FULL LOAD | IMPED | IM | UNIT | UNIT | TOTAL | NET
NAME | RATING | SIDE | SIDE | LOSS | LOSS | (%) | (%) | (MW) | (MVAR) | LOSS | TOTAL
| MVA | KV | KV | (WATTS) | (WATTS) |  |  |  |  | (MW) | (MW)
TNPONE#1 | 200 | 18 | 345 | 118100 | 633231 | 12.84 | 0.147 | 0 | N/A
TNPONE#1 | 24 | 4.3 | 18 | 17840 | 87502 | 5.77 | 0.267 | 0 | N/A
TNPONE#2 | 200 | 18 | 345 | 119699 | 633799 | 12.67 | 0.151 | 165.8 | N/A | 0.6 | 138.6
TNPONE#2 | 24 | 4.3 | 18 | 17880 | 88528 | 5.51 | 0.106 | 16.8 | N/A
TNPSTUP | 15 | 4.3 | 345 | 49436 | 48429 | 7.83 | 0.189 | 9.8 | N/A
NOTES: | (1) TNPONE#1 and TNPONE#2 gross outputs metered at generator terminals
(2) Aux load metering for TNPONE#1 and TNPONE#2 is on low side of Aux Xfmr.
(3) TNPONE#2 and TNPONE#2 does not have MVARH metering.
(4) During unit outages, aux load of outaged unit is carried on startup xfmr fed from
345 KV switchyard bus
Date: Fri, 6 Dec 1996 17:52:20 -0600 (CST)
X-Sender: tnpar3@pop.flash.net
To: phassink@ionet.net
From: Jack McCartney <tnpar3@tnpe.com>
Subject: Revised TNP One Generation Numbers | [8 empty] | 345 kV line losses | -0.047
Cc: Kdonohoo@ercot-iso.com, jack-henry@eng.hlp.com
Based on our telephone discussions concerning TNP One generation numbers for
the June,96 and July, 96 CP's, TNP is agreeable to use the metered numbers
provided by HL&P and adjust them to take into account the 345 KV
transmission losses on the TNP One - Twin Oak double circuit line. The TNP
One metered number for June, 96 is 296,676 KW and the metered number for
July, 1996 is 138,132 KW. These are the same numbers submitted by TNP on
November 6th. Subsequently, these numbers were revised to make them reflect
generation at the TNP One 345 KV bus by subtracting out the GSU losses and
the Auxiliary transformer losses. These were the numbers I sent you on
December 2nd. The earlier TNP One generation CP numbers reported for June,
96 and July, 96 were taken from HL&P metering at the Twin Oak Switching
Station bus and did not include the TNP One - Twin Oak 345 KV transmission
line losses. The equivalent resistance of the double circuit 345 KV line
from TNP One - Twin Oak is 0.309465 ohms. Based on a flow of 296,676 KW, the
equivalent transmission line loss is calculated to be 216 KW and results in
a net generation number of 296,905 KW for the June, 96 CP TNP One
generation. A similar calculation for July based on a flow of 138,132 KW
results in a calculated transmission loss of 47 KW and results in a net
generation number of 138,179 KW. I used a nominal operating voltage of 355
KV in calculating the line losses. Let me know if you have any questions on
the above or wish to discuss. I will be in the office on Monday.

## TNP3
| STEPUP AND AUX LOAD XFMR TEST REPORT DATA | [6 empty] | UNIT LOADING |  | LOSSES | UNIT
UNIT | BASE | LOW | HIGH | NO LOAD | FULL LOAD | IMPED | IM | UNIT | UNIT | TOTAL | NET
NAME | RATING | SIDE | SIDE | LOSS | LOSS | (%) | (%) | (MW) | (MVAR) | LOSS | TOTAL
| MVA | KV | KV | (WATTS) | (WATTS) |  |  |  |  | (MW) | (MW)
TNPONE#1 | 200 | 18 | 345 | 118100 | 633231 | 12.84 | 0.147 | 166.6 | N/A | 0.5 | 147.5
TNPONE#1 | 24 | 4.3 | 18 | 17840 | 87502 | 5.77 | 0.267 | 18.6 | N/A
TNPONE#2 | 200 | 18 | 345 | 119699 | 633799 | 12.67 | 0.151 | 159.8 | N/A | 0.5 | 142.5
TNPONE#2 | 24 | 4.3 | 18 | 17880 | 88528 | 5.51 | 0.106 | 16.8 | N/A
TNPSTUP | 15 | 4.3 | 345 | 49436 | 48429 | 7.83 | 0.189 | 0 | N/A
1
NOTES: | (1) TNPONE#1 and TNPONE#2 gross outputs metered at generator terminals
(2) Aux load metering for TNPONE#1 and TNPONE#2 is on low side of Aux XFMR.
(3) TNPONE#2 and TNPONE#2 does not have MVARH metering.
(4) During unit outages, aux load of outaged unit is carried on startup xfmr fed from
345 KV switchyard bus

## TNP4
| STEPUP AND AUX LOAD XFMR TEST REPORT DATA | [6 empty] | UNIT LOADING |  | LOSSES | UNIT
UNIT | BASE | LOW | HIGH | NO LOAD | FULL LOAD | IMPED | IM | UNIT | UNIT | TOTAL | NET
NAME | RATING | SIDE | SIDE | LOSS | LOSS | (%) | (%) | (MW) | (MVAR) | LOSS | TOTAL
| MVA | KV | KV | (WATTS) | (WATTS) |  |  |  |  | (MW) | (MW)
TNPONE#1 | 200 | 18 | 345 | 118100 | 633231 | 12.84 | 0.147 | 168 | N/A | 0.5 | 147.5
TNPONE#1 | 24 | 4.3 | 18 | 17840 | 87502 | 5.77 | 0.267 | 20 | N/A
TNPONE#2 | 200 | 18 | 345 | 119699 | 633799 | 12.67 | 0.151 | 159.6 | N/A | 0.5 | 142.5
TNPONE#2 | 24 | 4.3 | 18 | 17880 | 88528 | 5.51 | 0.106 | 16.6 | N/A
TNPSTUP | 15 | 4.3 | 345 | 49436 | 48429 | 7.83 | 0.189 | 0 | N/A
1
NOTES: | (1) TNPONE#1 and TNPONE#2 gross outputs metered at generator terminals
(2) Aux load metering for TNPONE#1 and TNPONE#2 is on low side of Aux XFMR.
(3) TNPONE#2 and TNPONE#2 does not have MVARH metering.
(4) During unit outages, aux load of outaged unit is carried on startup xfmr fed from
345 KV switchyard bus

## TU1
UNIT MAIN LOSSES 1700 HOURS 06/19/96
| STEPUP XFMR TEST DATA |  |  |  | GENERATOR OUTPUT |  |  |  | XFMR LOSSES
| BASE | LOW | NO LOAD | FULL LOAD | TERMINAL | REAL | REACTIVE
UNIT | RATING | SIDE | LOSS | LOSS | VOLTAGE | POWER | POWER | CURRENT | NO LOAD | AT LOAD | TOTAL
| MVA | kV | kW | kW | kV | MW | MVAR | A | kW | kW | kW
BBRN 1 | 600 | 17.1 | 410.646 | 1485.975 | 18 | 578 | 27 | 18559.5749 | 455.0094 | 1247.2644 | 1702.2738
BBRN 2 | 600 | 17.1 | 374.761 | 1423.391 | 18 | 572 | -86 | 18553.1158 | 415.2476 | 1193.9026 | 1609.1503
COLL 1 | 180 | 17.1 | 196 | 765.6 | 18 | 122 | 101 | 5080.1194 | 217.1745 | 534.9562 | 752.1307
CMPK 1 | 1300 | 20.9 | 783.84 | 2435.73 | 22 | 1091 | 334 | 29942.9784 | 868.5208 | 1693.3482 | 2561.8689
CMPK 2 | 1300 | 20.9 | 844.19 | 2375.73 | 22 | 1102 | 409 | 30847.5881 | 935.3906 | 1752.9383 | 2688.3289
DEC 1 | 825 | 22.8 | 341 | 2744.3 | 24 | 742 | 375 | 19999.8409 | 377.8393 | 2515.1722 | 2893.0115
DEC CT A | 51 | 13.5 | 58.283 | 63.93 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT B | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT C | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT D | 51 | 13.5 | 62 | 64 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
EGMT 1 | 112 | 15 | 215.8 | 520 | 15.5 | 106 | 52 | 4397.8363 | 230.4264 | 541.1893 | 771.6157
EGMT 2 | 210 | 19 | 254.75 | 839.85 | 20 | 166 | 76 | 5270.3574 | 282.2715 | 572.8906 | 855.1621
EGMT 3 | 390 | 19 | 216.627 | 1268.339 | 20 | 340 | 154 | 10774.8163 | 240.0299 | 1048.466 | 1288.4959
GRAM 1 | 280 | 19 | 159.362 | 1027.459 | 20 | 214 | -1 | 6177.7153 | 176.5784 | 541.6674 | 718.2458
GRAM 2 | 400 | 21 | 262.2 | 1131.5 | 22 | 376 | 45 | 9937.8579 | 287.766 | 924.017 | 1211.783
HAND 1 | 50 | 12.47 | 154.44 | 143.29 | 13 | 0 | 0 | 0 | 0 | 0 | 0
HAND 2 | 75 | 12.47 | 113 | 270.15 | 13 | 72 | 2 | 3198.8657 | 122.8096 | 229.2602 | 352.0698
HAND 3 | 460 | 18.1 | 288.67 | 1577.048 | 19 | 343 | 165 | 11565.9417 | 318.0912 | 979.8727 | 1297.9639
HAND 4 | 500 | 24.7 | 199.596 | 1392.607 | 26 | 434 | 180 | 10433.3141 | 221.159 | 1109.8091 | 1330.9681
HAND 5 | 500 | 24.7 | 189.401 | 1409.23 | 26 | 427 | 139 | 9971.6066 | 209.8626 | 1025.8581 | 1235.7207
LCRK 1 | 100 | 13.2 | 165 | 195 | 13.8 | 83 | 52 | 4097.675 | 180.3409 | 171.1507 | 351.4916
LCRK 2 | 250 | 19 | 170.445 | 718.294 | 20 | 150 | 96 | 5141.0116 | 188.8587 | 328.9636 | 517.8223
LKHB 1 | 615 | 22 | 355.88 | 1550.208 | 24 | 0 | 0 | 0 | 0 | 0 | 0
LKHB 2 | 580 | 20.9 | 263.04 | 1682 | 22 | 510 | 263 | 15058.8606 | 291.4571 | 1485.8264 | 1777.2834
MTNLK 1 | 800 | 19 | 385.4 | 2119.92 | 20 | 753 | 207 | 22543.6244 | 427.036 | 1823.1207 | 2250.1568
MTNLK 2 | 800 | 19 | 387.3 | 2101.56 | 20 | 755 | 189 | 22467.495 | 429.1413 | 1795.1452 | 2224.2865
MTNLK 3 | 800 | 19 | 318.8 | 2068.07 | 20 | 752 | 190 | 22390.5486 | 353.241 | 1754.4588 | 2107.6998
MOSES 1 | 600 | 17.1 | 370.527 | 1491.875 | 18 | 562 | 205 | 19187.9645 | 410.5562 | 1338.4471 | 1749.0034
MOSES 2 | 600 | 17.1 | 370 | 1500 | 18 | 554 | 197 | 18859.5906 | 409.9723 | 1300.0701 | 1710.0424
MOSES 3 | 800 | 22.8 | 417.482 | 1836.397 | 24 | 737 | 234 | 18601.6508 | 462.5839 | 1548.3906 | 2010.9745
MRGN CT A | 51 | 13.2 | 56.696 | 181.693 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT B | 51 | 13.2 | 57.364 | 181.234 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT C | 51 | 13.2 | 57.263 | 180.048 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT D | 51 | 13.2 | 56.804 | 179.856 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT E | 51 | 13.2 | 57.335 | 183.891 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT F | 51 | 13.2 | 57.222 | 178.088 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN 2 | 22 | 12.47 | 65.76 | 87.8 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0
MRGN 4 | 68 | 13.2 | 134.4 | 178.8 | 13.8 | 59 | -1 | 2468.7361 | 146.8959 | 123.1879 | 270.0838
MRGN 5 | 200 | 19 | 177.038 | 645.9 | 20 | 158 | 38 | 4691.1264 | 196.164 | 384.8469 | 581.0109
MRGN 6 | 535 | 21 | 291.2 | 1785 | 22 | 455 | -43 | 11993.8575 | 319.5937 | 1186.884 | 1506.4776
MTCK 3 | 66 | 13.2 | 173.79 | 207.65 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MTCK 6 | 150 | 13.2 | 110.58 | 717.32 | 13.8 | 111 | 69 | 5468.0143 | 120.8612 | 498.2632 | 619.1244
MTCK 7 | 140 | 14.4 | 122.7 | 540.6 | 15 | 124 | 73 | 5538.418 | 133.138 | 526.3052 | 659.4432
MTCK 8 | 625 | 20.9 | 356.787 | 1536.193 | 22 | 542 | 297 | 16219.3343 | 395.3319 | 1355.7063 | 1751.0382
NLK 1 | 200 | 13.2 | 153.84 | 648.821 | 13.8 | 164 | 91 | 7846.7476 | 168.1433 | 522.0516 | 690.1949
NLK 2 | 200 | 17.1 | 129.1 | 703.8 | 18 | 163 | 96 | 6067.6061 | 143.0471 | 568.2475 | 711.2946
NLK 3 | 370 | 19 | 245 | 1271 | 20 | 346 | 150 | 10886.3829 | 271.4681 | 1191.62 | 1463.0881
PARK 1 | 60 | 13.2 | 79 | 183 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PARK 2 | 150 | 13.2 | 193.4 | 754.7 | 13.8 | 110 | 0 | 4602.0674 | 211.3814 | 371.3359 | 582.7173
PARK 3 | 150 | 14.4 | 120.635 | 686.2 | 15 | 79 | 74 | 4166.3555 | 130.8974 | 329.3268 | 460.2242
PB 5 | 140 | 13.2 | 166.8 | 523.512 | 13.8 | 112 | 14 | 4722.2068 | 182.3083 | 311.3362 | 493.6445
PB 6 | 560 | 18 | 202.514 | 1712.217 | 18 | 527 | 22 | 16918.2554 | 202.514 | 1519.0084 | 1721.5224
PB CT A | 51 | 13.2 | 56.042 | 181.393 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT B | 51 | 13.2 | 57.471 | 181.163 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT C | 51 | 13.2 | 56.01 | 180.164 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT D | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT E | 51 | 13.5 | 59.525 | 65.142 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
RCST 1 | 130 | 13.2 | 195.24 | 647.7 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
SANDOW 4 | 642 | 20.9 | 250 | 1496.493 | 22 | 546 | 194 | 15206.3855 | 277.0083 | 1100.197 | 1377.2053
STRYK 1 | 200 | 13.2 | 142.72 | 729.5 | 13.8 | 175 | -4 | 7323.3831 | 155.9894 | 511.279 | 667.2684
STRYK 2 | 550 | 18.2 | 299.742 | 1639.672 | 19 | 455 | 142 | 14483.6967 | 326.6721 | 1129.9376 | 1456.6097
THSE 1 | 650 | 17.1 | 383.7 | 2046.565 | 18 | 535 | 240 | 18807.6959 | 425.1524 | 1503.0848 | 1928.2372
THSE 2 | 736.6 | 22.8 | 375.4 | 2109.9 | 24 | 745 | 333 | 19630.7641 | 415.9557 | 2337.0274 | 2752.9831
TDAD 6 | 265 | 21 | 276.587 | 1162.772 | 22 | 31 | 60 | 1772.3387 | 303.5558 | 68.8107 | 372.3665
VAL 1 | 200 | 19 | 137.7 | 709.344 | 20 | 166 | 0 | 4792.0072 | 152.5762 | 441.022 | 593.5982
VAL 2 | 600 | 20.9 | 265 | 1495 | 22 | 486 | 146 | 13317.2768 | 293.6288 | 965.1246 | 1258.7534
VAL 3 | 400 | 20.8 | 255 | 1316.2 | 22 | 345 | 25 | 9077.6418 | 285.2718 | 879.8242 | 1165.096
[9 empty] | TOTAL ALL UNITS |  | 59049.5317

## TU2
UNIT MAIN LOSSES 1700 HOURS 07/22/96
| STEPUP XFMR TEST DATA |  |  |  | GENERATOR OUTPUT |  |  |  | XFMR LOSSES
| BASE | LOW | NO LOAD | FULL LOAD | TERMINAL | REAL | REACTIVE
UNIT | RATING | SIDE | LOSS | LOSS | VOLTAGE | POWER | POWER | CURRENT | NO LOAD | AT LOAD | TOTAL
| MVA | kV | kW | kW | kV | MW | MVAR | A | kW | kW | kW
BBRN 1 | 600 | 17.1 | 410.646 | 1485.975 | 18 | 580 | 24 | 18619.4288 | 455.0094 | 1255.3221 | 1710.3315
BBRN 2 | 600 | 17.1 | 374.761 | 1423.391 | 18 | 537 | -90 | 17464.5143 | 415.2476 | 1057.9088 | 1473.1564
COLL 1 | 180 | 17.1 | 196 | 765.6 | 18 | 132 | 79 | 4934.2383 | 217.1745 | 504.6737 | 721.8482
CMPK 1 | 1300 | 20.9 | 783.84 | 2435.73 | 22 | 1086 | 358 | 30008.7223 | 868.5208 | 1700.7923 | 2569.3131
CMPK 2 | 1300 | 20.9 | 844.19 | 2375.73 | 22 | 1102 | 361 | 30432.2057 | 935.3906 | 1706.0473 | 2641.4379
DEC 1 | 825 | 22.8 | 341 | 2744.3 | 24 | 747 | 388 | 20249.4999 | 377.8393 | 2578.3581 | 2956.1975
DEC CT A | 51 | 13.5 | 58.283 | 63.93 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT B | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT C | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT D | 51 | 13.5 | 62 | 64 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
EGMT 1 | 112 | 15 | 215.8 | 520 | 15.5 | 114 | 47 | 4593.047 | 230.4264 | 590.3001 | 820.7265
EGMT 2 | 210 | 19 | 254.75 | 839.85 | 20 | 168 | 102 | 5673.6232 | 282.2715 | 663.9151 | 946.1866
EGMT 3 | 390 | 19 | 216.627 | 1268.339 | 20 | 323 | 153 | 10317.3802 | 240.0299 | 961.3321 | 1201.362
GRAM 1 | 280 | 19 | 159.362 | 1027.459 | 20 | 223 | -1 | 6437.5202 | 176.5784 | 588.1852 | 764.7636
GRAM 2 | 400 | 21 | 262.2 | 1131.5 | 22 | 364 | 50 | 9642.2223 | 287.766 | 869.8587 | 1157.6247
HAND 1 | 50 | 12.47 | 154.44 | 143.29 | 13 | 0 | 0 | 0 | 0 | 0 | 0
HAND 2 | 75 | 12.47 | 113 | 270.15 | 13 | 71 | 1 | 3153.5334 | 122.8096 | 222.8084 | 345.6179
HAND 3 | 460 | 18.1 | 288.67 | 1577.048 | 19 | 354 | 131 | 11469.8609 | 318.0912 | 963.6603 | 1281.7515
HAND 4 | 500 | 24.7 | 199.596 | 1392.607 | 26 | 437 | -3 | 9704.1543 | 221.159 | 960.1059 | 1181.2649
HAND 5 | 500 | 24.7 | 189.401 | 1409.23 | 26 | 427 | 48 | 9541.5886 | 209.8626 | 939.2872 | 1149.1498
LCRK 1 | 100 | 13.2 | 165 | 195 | 13.8 | 80 | 43 | 3799.8017 | 180.3409 | 147.1721 | 327.513
LCRK 2 | 250 | 19 | 170.445 | 718.294 | 20 | 193 | 80 | 6031.1 | 188.8587 | 452.7346 | 641.5934
LKHB 1 | 615 | 22 | 355.88 | 1550.208 | 24 | 341 | 149 | 8952.0973 | 423.5266 | 476.9314 | 900.458
LKHB 2 | 580 | 20.9 | 263.04 | 1682 | 22 | 497 | 246 | 14553.1466 | 291.4571 | 1387.7066 | 1679.1636
MTNLK 1 | 800 | 19 | 385.4 | 2119.92 | 20 | 746 | 185 | 22187.4777 | 427.036 | 1765.972 | 2193.008
MTNLK 2 | 800 | 19 | 387.3 | 2101.56 | 20 | 748 | 190 | 22278.6146 | 429.1413 | 1765.0891 | 2194.2304
MTNLK 3 | 800 | 19 | 318.8 | 2068.07 | 20 | 749 | 194 | 22335.2673 | 353.241 | 1745.8062 | 2099.0472
MOSES 1 | 600 | 17.1 | 370.527 | 1491.875 | 18 | 561 | 177 | 18868.453 | 410.5562 | 1294.2435 | 1704.7998
MOSES 2 | 600 | 17.1 | 370 | 1500 | 18 | 557 | 150 | 18502.2799 | 409.9723 | 1251.2749 | 1661.2472
MOSES 3 | 800 | 22.8 | 417.482 | 1836.397 | 24 | 740 | 213 | 18524.399 | 462.5839 | 1535.5565 | 1998.1404
MRGN CT A | 51 | 13.2 | 56.696 | 181.693 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT B | 51 | 13.2 | 57.364 | 181.234 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT C | 51 | 13.2 | 57.263 | 180.048 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT D | 51 | 13.2 | 56.804 | 179.856 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT E | 51 | 13.2 | 57.335 | 183.891 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT F | 51 | 13.2 | 57.222 | 178.088 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN 2 | 22 | 12.47 | 65.76 | 87.8 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0
MRGN 4 | 68 | 13.2 | 134.4 | 178.8 | 13.8 | 65 | 1 | 2719.7252 | 146.8959 | 149.5095 | 296.4054
MRGN 5 | 200 | 19 | 177.038 | 645.9 | 20 | 162 | -12 | 4689.3496 | 196.164 | 384.5555 | 580.7194
MRGN 6 | 535 | 21 | 291.2 | 1785 | 22 | 481 | -26 | 12641.4041 | 319.5937 | 1318.503 | 1638.0967
MTCK 3 | 66 | 13.2 | 173.79 | 207.65 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MTCK 6 | 150 | 13.2 | 110.58 | 717.32 | 13.8 | 114 | 63 | 5449.2561 | 120.8612 | 494.8505 | 615.7117
MTCK 7 | 140 | 14.4 | 122.7 | 540.6 | 15 | 123 | 57 | 5217.9178 | 133.138 | 467.1547 | 600.2927
MTCK 8 | 625 | 20.9 | 356.787 | 1536.193 | 22 | 536 | 326 | 16463.751 | 395.3319 | 1396.8737 | 1792.2056
NLK 1 | 200 | 13.2 | 153.84 | 648.821 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
NLK 2 | 200 | 17.1 | 129.1 | 703.8 | 18 | 165 | 98 | 6155.4787 | 143.0471 | 584.8256 | 727.8727
NLK 3 | 370 | 19 | 245 | 1271 | 20 | 347 | 181 | 11297.8612 | 271.4681 | 1283.4029 | 1554.8711
PARK 1 | 60 | 13.2 | 79 | 183 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PARK 2 | 150 | 13.2 | 193.4 | 754.7 | 13.8 | 93 | 37 | 4187.4612 | 211.3814 | 307.4415 | 518.8229
PARK 3 | 150 | 14.4 | 120.635 | 686.2 | 15 | 112 | 78 | 5253.2882 | 130.8974 | 523.5726 | 654.4699
PB 5 | 140 | 13.2 | 166.8 | 523.512 | 13.8 | 109 | 7 | 4569.6244 | 182.3083 | 291.5417 | 473.85
PB 6 | 560 | 18 | 202.514 | 1712.217 | 18 | 514 | 4 | 16487.0569 | 202.514 | 1442.5647 | 1645.0787
PB CT A | 51 | 13.2 | 56.042 | 181.393 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT B | 51 | 13.2 | 57.471 | 181.163 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT C | 51 | 13.2 | 56.01 | 180.164 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT D | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT E | 51 | 13.5 | 59.525 | 65.142 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
RCST 1 | 130 | 13.2 | 195.24 | 647.7 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
SANDOW 4 | 642 | 20.9 | 250 | 1496.493 | 22 | 556 | 167 | 15235.1856 | 277.0083 | 1104.3684 | 1381.3767
STRYK 1 | 200 | 13.2 | 142.72 | 729.5 | 13.8 | 175 | -5 | 7324.4586 | 155.9894 | 511.4291 | 667.4186
STRYK 2 | 550 | 18.2 | 299.742 | 1639.672 | 19 | 458 | 152 | 14663.6025 | 326.6721 | 1158.1825 | 1484.8546
THSE 1 | 650 | 17.1 | 383.7 | 2046.565 | 18 | 535 | 260 | 19079.2424 | 425.1524 | 1546.8014 | 1971.9538
THSE 2 | 736.6 | 22.8 | 375.4 | 2109.9 | 24 | 715 | 291 | 18570.2183 | 415.9557 | 2091.3341 | 2507.2897
TDAD 6 | 265 | 21 | 276.587 | 1162.772 | 22 | 220 | 60 | 5984.369 | 303.5558 | 784.5116 | 1088.0674
VAL 1 | 200 | 19 | 137.7 | 709.344 | 20 | 152 | 0 | 4387.862 | 152.5762 | 369.7697 | 522.3459
VAL 2 | 600 | 20.9 | 265 | 1495 | 22 | 481 | 134 | 13103.6607 | 293.6288 | 934.4107 | 1228.0395
VAL 3 | 400 | 20.8 | 255 | 1316.2 | 22 | 360 | 35 | 9492.0947 | 285.2718 | 961.9975 | 1247.2693
[9 empty] | TOTAL ALL UNITS |  | 59516.9454

## TU3
UNIT MAIN LOSSES 1700 HOURS 08/05/96
| STEPUP XFMR TEST DATA |  |  |  | GENERATOR OUTPUT |  |  |  | XFMR LOSSES
| BASE | LOW | NO LOAD | FULL LOAD | TERMINAL | REAL | REACTIVE
UNIT | RATING | SIDE | LOSS | LOSS | VOLTAGE | POWER | POWER | CURRENT | NO LOAD | AT LOAD | TOTAL
| MVA | kV | kW | kW | kV | MW | MVAR | A | kW | kW | kW
BBRN 1 | 600 | 17.1 | 410.646 | 1485.975 | 18 | 571 | 26 | 18333.8103 | 455.0094 | 1217.1047 | 1672.1141
BBRN 2 | 600 | 17.1 | 374.761 | 1423.391 | 18 | 529 | -96 | 17244.8179 | 415.2476 | 1031.4601 | 1446.7077
COLL 1 | 180 | 17.1 | 196 | 765.6 | 18 | 134 | 74 | 4909.8876 | 217.1745 | 499.7048 | 716.8793
CMPK 1 | 1300 | 20.9 | 783.84 | 2435.73 | 22 | 1085 | 273 | 29361.3612 | 868.5208 | 1628.2033 | 2496.7241
CMPK 2 | 1300 | 20.9 | 844.19 | 2375.73 | 22 | 1104 | 289 | 29948.728 | 935.3906 | 1652.2698 | 2587.6604
DEC 1 | 825 | 22.8 | 341 | 2744.3 | 24 | 729 | 382 | 19798.8291 | 377.8393 | 2464.8679 | 2842.7072
DEC CT A | 51 | 13.5 | 58.283 | 63.93 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT B | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT C | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT D | 51 | 13.5 | 62 | 64 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
EGMT 1 | 112 | 15 | 215.8 | 520 | 15.5 | 114 | 33 | 4420.6497 | 230.4264 | 546.8186 | 777.245
EGMT 2 | 210 | 19 | 254.75 | 839.85 | 20 | 168 | 37 | 4965.9675 | 282.2715 | 508.6269 | 790.8984
EGMT 3 | 390 | 19 | 216.627 | 1268.339 | 20 | 345 | 132 | 10663.3719 | 240.0299 | 1026.8895 | 1266.9194
GRAM 1 | 280 | 19 | 159.362 | 1027.459 | 20 | 230 | -11 | 6647.1172 | 176.5784 | 627.1098 | 803.6882
GRAM 2 | 400 | 21 | 262.2 | 1131.5 | 22 | 371 | 54 | 9838.8181 | 287.766 | 905.6915 | 1193.4575
HAND 1 | 50 | 12.47 | 154.44 | 143.29 | 13 | 0 | 0 | 0 | 0 | 0 | 0
HAND 2 | 75 | 12.47 | 113 | 270.15 | 13 | 70 | -2 | 3110.0778 | 122.8096 | 216.7101 | 339.5197
HAND 3 | 460 | 18.1 | 288.67 | 1577.048 | 19 | 359 | 117 | 11473.6037 | 318.0912 | 964.2893 | 1282.3805
HAND 4 | 500 | 24.7 | 199.596 | 1392.607 | 26 | 436 | 178 | 10457.4841 | 221.159 | 1114.9571 | 1336.1161
HAND 5 | 500 | 24.7 | 189.401 | 1409.23 | 26 | 427 | 133 | 9931.1734 | 209.8626 | 1017.5556 | 1227.4182
LCRK 1 | 100 | 13.2 | 165 | 195 | 13.8 | 83 | 51 | 4075.6173 | 180.3409 | 169.3131 | 349.654
LCRK 2 | 250 | 19 | 170.445 | 718.294 | 20 | 218 | 121 | 7197.5111 | 188.8587 | 644.7857 | 833.6444
LKHB 1 | 615 | 22 | 355.88 | 1550.208 | 24 | 341 | 93 | 8502.7909 | 423.5266 | 430.2584 | 853.785
LKHB 2 | 580 | 20.9 | 263.04 | 1682 | 22 | 509 | 249 | 14870.4692 | 291.4571 | 1448.8825 | 1740.3396
MTNLK 1 | 800 | 19 | 385.4 | 2119.92 | 20 | 759 | 178 | 22504.9069 | 427.036 | 1816.8639 | 2243.8999
MTNLK 2 | 800 | 19 | 387.3 | 2101.56 | 20 | 756 | 177 | 22414.0023 | 429.1413 | 1786.6073 | 2215.7486
MTNLK 3 | 800 | 19 | 318.8 | 2068.07 | 20 | 0 | 0 | 0 | 0 | 0 | 0
MOSES 1 | 600 | 17.1 | 370.527 | 1491.875 | 18 | 557 | 165 | 18633.182 | 410.5562 | 1262.1689 | 1672.7251
MOSES 2 | 600 | 17.1 | 370 | 1500 | 18 | 553 | 167 | 18528.6454 | 409.9723 | 1254.8435 | 1664.8158
MOSES 3 | 800 | 22.8 | 417.482 | 1836.397 | 24 | 741 | 167 | 18272.7851 | 462.5839 | 1494.1254 | 1956.7093
MRGN CT A | 51 | 13.2 | 56.696 | 181.693 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT B | 51 | 13.2 | 57.364 | 181.234 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT C | 51 | 13.2 | 57.263 | 180.048 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT D | 51 | 13.2 | 56.804 | 179.856 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT E | 51 | 13.2 | 57.335 | 183.891 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT F | 51 | 13.2 | 57.222 | 178.088 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN 2 | 22 | 12.47 | 65.76 | 87.8 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0
MRGN 4 | 68 | 13.2 | 134.4 | 178.8 | 13.8 | 62 | -2 | 2595.2417 | 146.8959 | 136.1365 | 283.0323
MRGN 5 | 200 | 19 | 177.038 | 645.9 | 20 | 170 | -5 | 4909.5994 | 196.164 | 421.5275 | 617.6914
MRGN 6 | 535 | 21 | 291.2 | 1785 | 22 | 482 | -5 | 12649.9001 | 319.5937 | 1320.2759 | 1639.8695
MTCK 3 | 66 | 13.2 | 173.79 | 207.65 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MTCK 6 | 150 | 13.2 | 110.58 | 717.32 | 13.8 | 114 | 50 | 5207.9894 | 120.8612 | 452.0013 | 572.8625
MTCK 7 | 140 | 14.4 | 122.7 | 540.6 | 15 | 125 | 49 | 5167.706 | 133.138 | 458.2071 | 591.3451
MTCK 8 | 625 | 20.9 | 356.787 | 1536.193 | 22 | 502 | 300 | 15347.3107 | 395.3319 | 1213.8475 | 1609.1794
NLK 1 | 200 | 13.2 | 153.84 | 648.821 | 13.8 | 163 | 75 | 7506.6775 | 168.1433 | 477.7817 | 645.925
NLK 2 | 200 | 17.1 | 129.1 | 703.8 | 18 | 165 | 86 | 5968.108 | 143.0471 | 549.7637 | 692.8108
NLK 3 | 370 | 19 | 245 | 1271 | 20 | 348 | 180 | 11310.1724 | 271.4681 | 1286.2015 | 1557.6696
PARK 1 | 60 | 13.2 | 79 | 183 | 13.8 | 73 | 39 | 3462.6259 | 86.345 | 318.5876 | 404.9326
PARK 2 | 150 | 13.2 | 193.4 | 754.7 | 13.8 | 82 | 73 | 4593.1208 | 211.3814 | 369.8935 | 581.2749
PARK 3 | 150 | 14.4 | 120.635 | 686.2 | 15 | 109 | 50 | 4615.754 | 130.8974 | 404.2032 | 535.1006
PB 5 | 140 | 13.2 | 166.8 | 523.512 | 13.8 | 108 | -5 | 4523.2331 | 182.3083 | 285.6522 | 467.9605
PB 6 | 560 | 18 | 202.514 | 1712.217 | 18 | 513 | -7 | 16456.0144 | 202.514 | 1437.1375 | 1639.6515
PB CT A | 51 | 13.2 | 56.042 | 181.393 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT B | 51 | 13.2 | 57.471 | 181.163 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT C | 51 | 13.2 | 56.01 | 180.164 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT D | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT E | 51 | 13.5 | 59.525 | 65.142 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
RCST 1 | 130 | 13.2 | 195.24 | 647.7 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
SANDOW 4 | 642 | 20.9 | 250 | 1496.493 | 22 | 558 | 173 | 15331.3494 | 277.0083 | 1118.3538 | 1395.3621
STRYK 1 | 200 | 13.2 | 142.72 | 729.5 | 13.8 | 175 | -8 | 7329.117 | 155.9894 | 512.0799 | 668.0693
STRYK 2 | 550 | 18.2 | 299.742 | 1639.672 | 19 | 466 | 98 | 14470.0155 | 326.6721 | 1127.804 | 1454.4761
THSE 1 | 650 | 17.1 | 383.7 | 2046.565 | 18 | 535 | 201 | 18331.2569 | 425.1524 | 1427.8967 | 1853.0491
THSE 2 | 736.6 | 22.8 | 375.4 | 2109.9 | 24 | 686 | 285 | 17870.1107 | 415.9557 | 1936.6176 | 2352.5733
TDAD 6 | 265 | 21 | 276.587 | 1162.772 | 22 | 231 | 8 | 6065.8122 | 303.5558 | 806.0103 | 1109.5661
VAL 1 | 200 | 19 | 137.7 | 709.344 | 20 | 162 | 0 | 4676.5372 | 152.5762 | 420.024 | 572.6002
VAL 2 | 600 | 20.9 | 265 | 1495 | 22 | 519 | 147 | 14156.008 | 293.6288 | 1090.5212 | 1384.15
VAL 3 | 400 | 20.8 | 255 | 1316.2 | 22 | 329 | 13 | 8640.7485 | 285.2718 | 797.173 | 1082.4448
[9 empty] | TOTAL ALL UNITS |  | 58023.3544

## TU4
UNIT MAIN LOSSES 1700 HOURS 09/10/96
| STEPUP XFMR TEST DATA |  |  |  | GENERATOR OUTPUT |  |  |  | XFMR LOSSES
| BASE | LOW | NO LOAD | FULL LOAD | TERMINAL | REAL | REACTIVE
UNIT | RATING | SIDE | LOSS | LOSS | VOLTAGE | POWER | POWER | CURRENT | NO LOAD | AT LOAD | TOTAL
| MVA | kV | kW | kW | kV | MW | MVAR | A | kW | kW | kW
BBRN 1 | 600 | 17.1 | 410.646 | 1485.975 | 18 | 494 | 87 | 16088.9055 | 455.0094 | 937.2932 | 1392.3026
BBRN 2 | 600 | 17.1 | 374.761 | 1423.391 | 18 | 536 | 87 | 17417.2057 | 415.2476 | 1052.1851 | 1467.4328
COLL 1 | 180 | 17.1 | 196 | 765.6 | 18 | 137 | 33 | 4519.9603 | 217.1745 | 423.4866 | 640.6611
CMPK 1 | 1300 | 20.9 | 783.84 | 2435.73 | 22 | 1088 | 248 | 29284.9589 | 868.5208 | 1619.7407 | 2488.2615
CMPK 2 | 1300 | 20.9 | 844.19 | 2375.73 | 22 | 1103 | 236 | 29601.4039 | 935.3906 | 1614.1683 | 2549.5589
DEC 1 | 825 | 22.8 | 341 | 2744.3 | 24 | 739 | 303 | 19213.861 | 377.8393 | 2321.3676 | 2699.207
DEC CT A | 51 | 13.5 | 58.283 | 63.93 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT B | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT C | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
DEC CT D | 51 | 13.5 | 62 | 64 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
EGMT 1 | 112 | 15 | 215.8 | 520 | 15.5 | 114 | 6 | 4252.1954 | 230.4264 | 505.9382 | 736.3647
EGMT 2 | 210 | 19 | 254.75 | 839.85 | 20 | 168 | 10 | 4858.3262 | 282.2715 | 486.8161 | 769.0876
EGMT 3 | 390 | 19 | 216.627 | 1268.339 | 20 | 351 | 102 | 10551.6586 | 240.0299 | 1005.4861 | 1245.516
GRAM 1 | 280 | 19 | 159.362 | 1027.459 | 20 | 0 | 0 | 0 | 0 | 0 | 0
GRAM 2 | 400 | 21 | 262.2 | 1131.5 | 22 | 319 | 30 | 8408.5176 | 287.766 | 661.5052 | 949.2712
HAND 1 | 50 | 12.47 | 154.44 | 143.29 | 13 | 0 | 0 | 0 | 0 | 0 | 0
HAND 2 | 75 | 12.47 | 113 | 270.15 | 13 | 69 | -2 | 3065.6846 | 122.8096 | 210.5676 | 333.3772
HAND 3 | 460 | 18.1 | 288.67 | 1577.048 | 19 | 0 | 0 | 0 | 0 | 0 | 0
HAND 4 | 500 | 24.7 | 199.596 | 1392.607 | 26 | 406 | 114 | 9364.2065 | 221.159 | 894.0168 | 1115.1758
HAND 5 | 500 | 24.7 | 189.401 | 1409.23 | 26 | 405 | 90 | 9212.7227 | 209.8626 | 875.655 | 1085.5176
LCRK 1 | 100 | 13.2 | 165 | 195 | 13.8 | 81 | 14 | 3439.0401 | 180.3409 | 120.5531 | 300.894
LCRK 2 | 250 | 19 | 170.445 | 718.294 | 20 | 0 | 0 | 0 | 0 | 0 | 0
LKHB 1 | 615 | 22 | 355.88 | 1550.208 | 24 | 0 | 0 | 0 | 0 | 0 | 0
LKHB 2 | 580 | 20.9 | 263.04 | 1682 | 22 | 398 | 54 | 10540.4899 | 291.4571 | 727.9565 | 1019.4136
MTNLK 1 | 800 | 19 | 385.4 | 2119.92 | 20 | 721 | 85 | 20957.616 | 427.036 | 1575.6208 | 2002.6568
MTNLK 2 | 800 | 19 | 387.3 | 2101.56 | 20 | 666 | 152 | 19720.1251 | 429.1413 | 1382.96 | 1812.1012
MTNLK 3 | 800 | 19 | 318.8 | 2068.07 | 20 | 724 | 86 | 21047.0109 | 353.241 | 1550.2244 | 1903.4654
MOSES 1 | 600 | 17.1 | 370.527 | 1491.875 | 18 | 558 | 108 | 18230.0119 | 410.5562 | 1208.1401 | 1618.6964
MOSES 2 | 600 | 17.1 | 370 | 1500 | 18 | 540 | 85 | 17533.7711 | 409.9723 | 1123.7065 | 1533.6788
MOSES 3 | 800 | 22.8 | 417.482 | 1836.397 | 24 | 703 | 123 | 17168.4533 | 462.5839 | 1318.9851 | 1781.569
MRGN CT A | 51 | 13.2 | 56.696 | 181.693 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT B | 51 | 13.2 | 57.364 | 181.234 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT C | 51 | 13.2 | 57.263 | 180.048 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT D | 51 | 13.2 | 56.804 | 179.856 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT E | 51 | 13.2 | 57.335 | 183.891 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN CT F | 51 | 13.2 | 57.222 | 178.088 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MRGN 2 | 22 | 12.47 | 65.76 | 87.8 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0
MRGN 4 | 68 | 13.2 | 134.4 | 178.8 | 13.8 | 68 | 7 | 2859.9483 | 146.8959 | 165.3237 | 312.2196
MRGN 5 | 200 | 19 | 177.038 | 645.9 | 20 | 0 | 0 | 0 | 0 | 0 | 0
MRGN 6 | 535 | 21 | 291.2 | 1785 | 22 | 457 | -12 | 11997.2736 | 319.5937 | 1187.5602 | 1507.1538
MTCK 3 | 66 | 13.2 | 173.79 | 207.65 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
MTCK 6 | 150 | 13.2 | 110.58 | 717.32 | 13.8 | 113 | 30 | 4891.3491 | 120.8612 | 398.7097 | 519.5709
MTCK 7 | 140 | 14.4 | 122.7 | 540.6 | 15 | 124 | 30 | 4910.4575 | 133.138 | 413.7234 | 546.8615
MTCK 8 | 625 | 20.9 | 356.787 | 1536.193 | 22 | 523 | 147 | 14257.0363 | 395.3319 | 1047.5098 | 1442.8416
NLK 1 | 200 | 13.2 | 153.84 | 648.821 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
NLK 2 | 200 | 17.1 | 129.1 | 703.8 | 18 | 146 | 23 | 4740.7046 | 143.0471 | 346.8874 | 489.9345
NLK 3 | 370 | 19 | 245 | 1271 | 20 | 346 | 163 | 11041.022 | 271.4681 | 1225.7139 | 1497.182
PARK 1 | 60 | 13.2 | 79 | 183 | 13.8 | 75 | 35 | 3462.6259 | 86.345 | 318.5876 | 404.9326
PARK 2 | 150 | 13.2 | 193.4 | 754.7 | 13.8 | 103 | 68 | 5163.6049 | 211.3814 | 467.4842 | 678.8656
PARK 3 | 150 | 14.4 | 120.635 | 686.2 | 15 | 0 | 0 | 0 | 0 | 0 | 0
PB 5 | 140 | 13.2 | 166.8 | 523.512 | 13.8 | 104 | -3 | 4352.8554 | 182.3083 | 264.5381 | 446.8463
PB 6 | 560 | 18 | 202.514 | 1712.217 | 18 | 514 | -9 | 16489.0848 | 202.514 | 1442.9196 | 1645.4336
PB CT A | 51 | 13.2 | 56.042 | 181.393 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT B | 51 | 13.2 | 57.471 | 181.163 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT C | 51 | 13.2 | 56.01 | 180.164 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT D | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
PB CT E | 51 | 13.5 | 59.525 | 65.142 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
RCST 1 | 130 | 13.2 | 195.24 | 647.7 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
SANDOW 4 | 642 | 20.9 | 250 | 1496.493 | 22 | 554 | 99 | 14769.0438 | 277.0083 | 1037.8228 | 1314.8311
STRYK 1 | 200 | 13.2 | 142.72 | 729.5 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0
STRYK 2 | 550 | 18.2 | 299.742 | 1639.672 | 19 | 67 | 5 | 2041.5807 | 326.6721 | 22.4506 | 349.1227
THSE 1 | 650 | 17.1 | 383.7 | 2046.565 | 18 | 510 | 212 | 17715.2837 | 425.1524 | 1333.5476 | 1758.7
THSE 2 | 736.6 | 22.8 | 375.4 | 2109.9 | 24 | 640 | 210 | 16203.6376 | 415.9557 | 1592.2616 | 2008.2173
TDAD 6 | 265 | 21 | 276.587 | 1162.772 | 22 | 230 | 16 | 6050.5219 | 303.5558 | 801.9519 | 1105.5077
VAL 1 | 200 | 19 | 137.7 | 709.344 | 20 | 153 | 9 | 4424.3644 | 152.5762 | 375.9474 | 528.5236
VAL 2 | 600 | 20.9 | 265 | 1495 | 22 | 490 | 65 | 12971.812 | 293.6288 | 915.7013 | 1209.3301
VAL 3 | 400 | 20.8 | 255 | 1316.2 | 22 | 249 | 148 | 7601.698 | 285.2718 | 616.98 | 902.2518
[9 empty] | TOTAL ALL UNITS |  | 48112.5356