## June28, 1999 @ 1700
| Generator Output @ Generator Terminals Gross MW | Generator Output @ Generator Terminals Gross MVAR | Generator Voltage @ Generator Terminals KV | Aux Load @Bus A MW | Aux Load @ Bus A MVAR | Aux Load @ Bus B MW | Aux Load @ Bus B MVAR | Aux Load Total MW | Aux Load Total MVAR | Auxilary Transformer Losses MW | Auxilary Transformer Losses MVAR | Aux Load @ Generator Terminals MW | Aux Load @ Generator Terminals MVAR | Generator Input To GSU Xfmr MW | Generator Input To GSU Xfmr MVAR | GSU Transformer Losses MW | GSU Transformer Losses MVAR | Generator Net Output @ 345 kV Bus MW | Generator Net Output @ 345 kV Bus MVAR
UNIT#1 | 149.8 | 15.5 | 18.5 | 9 | 6 | 8 | 6 | 17 | 12 | 0.081116 | 1.0522 | 17.0811 | 13.0522 | 132.7189 | 2.4478 | 0.38882 | 11.0093 | 132.3301 | -8.5615
UNIT#2 | 149.8 | 19.8 | 18.5 | 9 | 6 | 8 | 6 | 17 | 12 | 0.094612 | 0.95917 | 17.0946 | 12.9592 | 132.7054 | 6.8408 | 0.39131 | 10.8956 | 132.3141 | -4.0548
| Notes: | 1. Unit#1 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.147 @ 18 KV
No Load Loss = 118,100 Watts @ 18 KV
%Z = 12.84 @ 200 MVA, 18 KV
Load Loss = 633,231 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.267 @ 18 KV
No Load Loss = 17,840 Watts @ 18 KV
%Z = 5.77 @ 24 MVA, 18 KV
Load Loss = 87502 Watts @ 24 MVA, 18 KV
2. Unit#2 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.151 @ 18 KV
No Load Loss = 119,699 Watts @ 18 KV
%Z = 12.67 @ 200 MVA, 18 KV
Load Loss = 633,799 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.106 @ 18 KV
No Load Loss = 17,880 Watts @ 18 KV
%Z = 5.51 @ 24 MVA, 18 KV
Load Loss = 88,528 Watts @ 24 MVA, 18 KV
3. To calculate Generator Output MW & MVAR at the 345 KV bus, enter Generator Gross MW & MVAR values and Aux Load Bus A and Aux Load Bus B MW & MVAR values
for the appropriate unit.

## July 29, 1999 @ 1700
| Generator Output @ Generator Terminals Gross MW | Generator Output @ Generator Terminals Gross MVAR | Generator Voltage @ Generator Terminals KV | Aux Load @Bus A MW | Aux Load @ Bus A MVAR | Aux Load @ Bus B MW | Aux Load @ Bus B MVAR | Aux Load Total MW | Aux Load Total MVAR | Auxilary Transformer Losses MW | Auxilary Transformer Losses MVAR | Aux Load @ Generator Terminals MW | Aux Load @ Generator Terminals MVAR | Generator Input To GSU Xfmr MW | Generator Input To GSU Xfmr MVAR | GSU Transformer Losses MW | GSU Transformer Losses MVAR | Generator Net Output @ 345 kV Bus MW | Generator Net Output @ 345 kV Bus MVAR
UNIT#1 | 149 | 19.8 | 18.5 | 8.9 | 5.6 | 8.3 | 5.6 | 17.2 | 11.2 | 0.07943 | 1.0256 | 17.2794 | 12.2256 | 131.7206 | 7.5744 | 0.38563 | 10.8801 | 131.3349 | -3.3057
UNIT#2 | 149 | 17 | 18.5 | 8.5 | 5.7 | 8.1 | 5.7 | 16.6 | 11.4 | 0.089807 | 0.89958 | 16.6898 | 12.2996 | 132.3102 | 4.7004 | 0.38936 | 10.818 | 131.9208 | -6.1176
| Notes: | 1. Unit#1 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.147 @ 18 KV
No Load Loss = 118,100 Watts @ 18 KV
%Z = 12.84 @ 200 MVA, 18 KV
Load Loss = 633,231 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.267 @ 18 KV
No Load Loss = 17,840 Watts @ 18 KV
%Z = 5.77 @ 24 MVA, 18 KV
Load Loss = 87502 Watts @ 24 MVA, 18 KV
2. Unit#2 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.151 @ 18 KV
No Load Loss = 119,699 Watts @ 18 KV
%Z = 12.67 @ 200 MVA, 18 KV
Load Loss = 633,799 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.106 @ 18 KV
No Load Loss = 17,880 Watts @ 18 KV
%Z = 5.51 @ 24 MVA, 18 KV
Load Loss = 88,528 Watts @ 24 MVA, 18 KV
3. To calculate Generator Output MW & MVAR at the 345 KV bus, enter Generator Gross MW & MVAR values and Aux Load Bus A and Aux Load Bus B MW & MVAR values
for the appropriate unit.

## August 26, 1999 @ 1700
| Generator Output @ Generator Terminals Gross MW | Generator Output @ Generator Terminals Gross MVAR | Generator Voltage @ Generator Terminals KV | Aux Load @Bus A MW | Aux Load @ Bus A MVAR | Aux Load @ Bus B MW | Aux Load @ Bus B MVAR | Aux Load Total MW | Aux Load Total MVAR | Auxilary Transformer Losses MW | Auxilary Transformer Losses MVAR | Aux Load @ Generator Terminals MW | Aux Load @ Generator Terminals MVAR | Generator Input To GSU Xfmr MW | Generator Input To GSU Xfmr MVAR | GSU Transformer Losses MW | GSU Transformer Losses MVAR | Generator Net Output @ 345 kV Bus MW | Generator Net Output @ 345 kV Bus MVAR
UNIT#1 | 149.8 | 16.7 | 18.5 | 8.4 | 5.5 | 8.2 | 5.5 | 16.6 | 11 | 0.075875 | 0.96943 | 16.6759 | 11.9694 | 133.1241 | 4.7306 | 0.39068 | 11.0848 | 132.7334 | -6.3542
UNIT#2 | 145 | 21.7 | 18.5 | 8.6 | 5.7 | 8 | 5.7 | 16.6 | 11.4 | 0.089807 | 0.89958 | 16.6898 | 12.2996 | 128.3102 | 9.4004 | 0.37472 | 10.2328 | 127.9355 | -0.83233
| Notes: | 1. Unit#1 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.147 @ 18 KV
No Load Loss = 118,100 Watts @ 18 KV
%Z = 12.84 @ 200 MVA, 18 KV
Load Loss = 633,231 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.267 @ 18 KV
No Load Loss = 17,840 Watts @ 18 KV
%Z = 5.77 @ 24 MVA, 18 KV
Load Loss = 87502 Watts @ 24 MVA, 18 KV
2. Unit#2 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.151 @ 18 KV
No Load Loss = 119,699 Watts @ 18 KV
%Z = 12.67 @ 200 MVA, 18 KV
Load Loss = 633,799 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.106 @ 18 KV
No Load Loss = 17,880 Watts @ 18 KV
%Z = 5.51 @ 24 MVA, 18 KV
Load Loss = 88,528 Watts @ 24 MVA, 18 KV
3. To calculate Generator Output MW & MVAR at the 345 KV bus, enter Generator Gross MW & MVAR values and Aux Load Bus A and Aux Load Bus B MW & MVAR values
for the appropriate unit.

## September 7, 1999 @ 1700
| Generator Output @ Generator Terminals Gross MW | Generator Output @ Generator Terminals Gross MVAR | Generator Voltage @ Generator Terminals KV | Aux Load @Bus A MW | Aux Load @ Bus A MVAR | Aux Load @ Bus B MW | Aux Load @ Bus B MVAR | Aux Load Total MW | Aux Load Total MVAR | Auxilary Transformer Losses MW | Auxilary Transformer Losses MVAR | Aux Load @ Generator Terminals MW | Aux Load @ Generator Terminals MVAR | Generator Input To GSU Xfmr MW | Generator Input To GSU Xfmr MVAR | GSU Transformer Losses MW | GSU Transformer Losses MVAR | Generator Net Output @ 345 kV Bus MW | Generator Net Output @ 345 kV Bus MVAR
UNIT#1 | 148.6 | 15.8 | 18.5 | 8.5 | 5.3 | 7.9 | 5.2 | 16.4 | 10.5 | 0.07338 | 0.93002 | 16.4734 | 11.43 | 132.1266 | 4.37 | 0.38667 | 10.922 | 131.74 | -6.552
UNIT#2 | 149.4 | 18.3 | 18.5 | 8.6 | 5.7 | 8.2 | 5.7 | 16.8 | 11.4 | 0.090975 | 0.91406 | 16.891 | 12.3141 | 132.509 | 5.9859 | 0.39036 | 10.8578 | 132.1187 | -4.8719
| Notes: | 1. Unit#1 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.147 @ 18 KV
No Load Loss = 118,100 Watts @ 18 KV
%Z = 12.84 @ 200 MVA, 18 KV
Load Loss = 633,231 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.267 @ 18 KV
No Load Loss = 17,840 Watts @ 18 KV
%Z = 5.77 @ 24 MVA, 18 KV
Load Loss = 87502 Watts @ 24 MVA, 18 KV
2. Unit#2 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.151 @ 18 KV
No Load Loss = 119,699 Watts @ 18 KV
%Z = 12.67 @ 200 MVA, 18 KV
Load Loss = 633,799 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.106 @ 18 KV
No Load Loss = 17,880 Watts @ 18 KV
%Z = 5.51 @ 24 MVA, 18 KV
Load Loss = 88,528 Watts @ 24 MVA, 18 KV
3. To calculate Generator Output MW & MVAR at the 345 KV bus, enter Generator Gross MW & MVAR values and Aux Load Bus A and Aux Load Bus B MW & MVAR values
for the appropriate unit.