## CONTACT INFORMATION
Load Serving Entity Information
Load Serving Entity: | WEATL-CSWS
Contact Person: | Bruce McCamant
Mailing Address Line 1: | PO Box 660164
Mailing Address Line 2:
City: | Dallas
State: | Texas
Zip Code: | 75266-0164
Street Address Line 1: | 1616 Woodall Rodgers Frwy
Street Address Line 2:
City: | Dallas
State: | Texas
Zip Code: | 75202
Company Internal Mail Code: | S3SYO
Telephone Number: | 214-777-1139
Facsimile (FAX) Number: | 214-777-1429
Internet email address: | bmccamant@csw.com

## 1700 June 28, 1999
REPORT FOR LOAD ENTITY ==> | WEATL
LOAD ENTITY IN CONTROL AREA ==> | CSWSA
June 28, 1999 Hour Ending 17:00
RECEIVING TRANSACTION INFORMATION
Description | Amount kW | From Control Area | Sending Generation Entity
WTU | 55944 | CSWSA | WTU
Subtotal Receiving Transactions (A) | 55944
SENDING TRANSACTION INFORMATION
Description | Amount kW | To Control Area | Receiving Load Entity
Subtotal Sending Transactions (B) | 0
GENERATION INFORMATION
Generation kW | 0
Less Gen Unit Main XFMR Losses kW | 0 | <== Provide Calculations to ISO with Submission
Inadvertent kW | 0
Subtotal Net Generation (C) | 0
TOTAL LOAD CALCULATION
Subtotal Receiving Transactions (A) | 55944
Subtotal Sending Transactions (B) | 0
Subtotal Net Generation (C) | 0
Total Load Responsibility (A-B+C) | 55944

## 1700 July 29, 1999
REPORT FOR LOAD ENTITY ==> | WEATL
LOAD ENTITY IN CONTROL AREA ==> | CSWSA
July 29, 1999 Hour Ending 17:00
RECEIVING TRANSACTION INFORMATION
Description | Amount kW | From Control Area | Sending Generation Entity
WTU | 58884 | CSWSA | WTU
Subtotal Receiving Transactions (A) | 58884
SENDING TRANSACTION INFORMATION
Description | Amount kW | To Control Area | Receiving Load Entity
Subtotal Sending Transactions (B) | 0
GENERATION INFORMATION
Generation kW | 4000
Less Gen Unit Main XFMR Losses kW | 23 | <== Provide Calculations to ISO with Submission
Inadvertent kW | 0
Subtotal Net Generation (C) | 3977
TOTAL LOAD CALCULATION
Subtotal Receiving Transactions (A) | 58884
Subtotal Sending Transactions (B) | 0
Subtotal Net Generation (C) | 3977
Total Load Responsibility (A-B+C) | 62861

## 1700 August 26, 1999
REPORT FOR LOAD ENTITY ==> | WEATL
LOAD ENTITY IN CONTROL AREA ==> | CSWSA
August 26, 1999 Hour Ending 17:00
RECEIVING TRANSACTION INFORMATION
Description | Amount kW | From Control Area | Sending Generation Entity
WTU | 64399.2 | CSWSA | WTU
Subtotal Receiving Transactions (A) | 64399.2
SENDING TRANSACTION INFORMATION
Description | Amount kW | To Control Area | Receiving Load Entity
Subtotal Sending Transactions (B) | 0
GENERATION INFORMATION
Generation kW | 0
Less Gen Unit Main XFMR Losses kW | 0 | <== Provide Calculations to ISO with Submission
Inadvertent kW | 0
Subtotal Net Generation (C) | 0
TOTAL LOAD CALCULATION
Subtotal Receiving Transactions (A) | 64399.2
Subtotal Sending Transactions (B) | 0
Subtotal Net Generation (C) | 0
Total Load Responsibility (A-B+C) | 64399.2

## 1700 September 7, 1999
REPORT FOR LOAD ENTITY ==> | WEATL
LOAD ENTITY IN CONTROL AREA ==> | CSWSA
September 7, 1999 Hour Ending 17:00
RECEIVING TRANSACTION INFORMATION
Description | Amount kW | From Control Area | Sending Generation Entity
WTU | 56680.8 | CSWSA | WTU
Subtotal Receiving Transactions (A) | 56680.8
SENDING TRANSACTION INFORMATION
Description | Amount kW | To Control Area | Receiving Load Entity
Subtotal Sending Transactions (B) | 0
GENERATION INFORMATION
Generation kW | 0
Less Gen Unit Main XFMR Losses kW | 0 | <== Provide Calculations to ISO with Submission
Inadvertent kW | 0
Subtotal Net Generation (C) | 0
TOTAL LOAD CALCULATION
Subtotal Receiving Transactions (A) | 56680.8
Subtotal Sending Transactions (B) | 0
Subtotal Net Generation (C) | 0
Total Load Responsibility (A-B+C) | 56680.8

## Loss Calc
Weatherford Generator Loss Calculation:
|  | Gen Step-Up | Dist Bank | Gen Step-Up | Dist Bank
|  | (Estimated) |  | (Estimated)
Flow: | MW | 4 | 4 | 3 | 3
Transformer Data:
Base Rating | MVA | 5 | 12 | 5 | 12
Low Side | kV | 4.16 | 13.2 | 4.16 | 13.2
High Side | kV | 13.2 | 69 | 13.2 | 69
Impedance | p.u. | 5% | 7.64% | 5% | 7.64%
Estimated X/R | - | 12 | 10 | 12 | 10
Calculations:
Base Rating | VA | 5000000 | 12000000 | 5000000 | 12000000
S_Base(per phase) | VA | 1666666.6667 | 4000000 | 1666666.6667 | 4000000
V_Base (low side line to neutral) | V | 2401.7771 | 7621.0236 | 2401.7771 | 7621.0236
I_Base(per phase)=S_Base/V_Base | Amp | 693.9306 | 524.8639 | 693.9306 | 524.8639
Z_Base=V_Base/I_Base | Ohms | 3.4611 | 14.52 | 3.4611 | 14.52
Z(actual)=Z(p.u.)* Z_Base | Ohms | 0.17306 | 1.1093 | 0.17306 | 1.1093
X=sqrt(Z^2/(1 + 1/([EstX/R]^2) )) | Ohms | 0.17246 | 1.1038 | 0.17246 | 1.1038
R=sqrt(Z^2 - R^2) | Ohms | 0.014372 | 0.11038 | 0.014372 | 0.11038
Check X/R |  | 12 | 10 | 12 | 10
Check Z |  | 0.17306 | 1.1093 | 0.17306 | 1.1093
Pgen(per phase) | W | 1333333.3333 | 1333333.3333 | 1000000 | 1000000
Vgen(low side line to neutral) | V | 2401.7771 | 7621.0236 | 2401.7771 | 7621.0236
Igen(per phase) = Pgen / Vgen | Amps | 555.1445 | 174.9546 | 416.3584 | 131.216
Losses = 3 * I^2 * R / 1,000,000 | MW | 0.013287 | 0.010136 | 0.0074741 | 0.0057016
Percent Losses |  | 0.3322% | 0.2534% | 0.2491% | 0.1901%
Total loss in both transformers: | MW |  | 0.023423 |  | 0.013176
In summary the loss results are:
Generation Level: |  | 4 MW | 3 MW
Estimated Losses:
Gen Step-Up |  | 0.013 | 0.007 MW
Distribution Bank |  | 0.01 | 0.006 MW
|  | ------- | ------
Both Transformers: |  | 0.023 | 0.013 MW