## June2899
1700 June 28, 1999
| STEPUP XFMR TEST DATA |  |  |  | GENERATOR OUTPUT |  |  |  | XFMR LOSSES
| BASE | LOW | NO LOAD | FULL LOAD | TERMINAL | REAL | REACTIVE
UNIT | RATING | SIDE | LOSS | LOSS | VOLTAGE | POWER | POWER | CURRENT | NO LOAD | AT LOAD | TOTAL
| MVA | kV | kW | kW | kV | MW | MVAR | A | kW | kW | kW
BBRN 1 | 600 | 17.1 | 410.646 | 1485.975 | 18 | 578 | 163 | 19262.4552 | 455.0094 | 1343.525 | 1798.5344
BBRN 2 | 600 | 17.1 | 374.761 | 1423.391 | 18 | 564 | 158 | 18786.7609 | 415.2476 | 1224.1623 | 1639.41
COLL 1 | 180 | 17.1 | 196 | 765.6 | 18 | 145 | 3 | 4651.8725 | 217.1745 | 448.5656 | 665.7401
CMPK 1 | 1300 | 20.9 | 774.81 | 2178.89 | 22 | 1093 | 243 | 29384.1518 | 858.5152 | 1458.7765 | 2317.2917
CMPK 2 | 1300 | 20.9 | 844.19 | 2375.73 | 22 | 855 | 309 | 23858.3111 | 935.3906 | 1048.5849 | 1983.9755
DEC 1 | 825 | 22.8 | 341 | 2744.3 | 24 | 716 | 375 | 19443.6657 | 377.8393 | 2377.2285 | 2755.0678
DECCT1 | 51 | 13.5 | 58.28 | 63.93 | 13.8 | 70 | 5 | 2936.0497 | 60.899 | 115.8457 | 176.7447
DECCT2 | 51 | 13.5 | 59.32 | 64.28 | 13.8 | 70 | 3 | 2931.2766 | 61.9857 | 116.1015 | 178.0873
DECCT3 | 51 | 13.5 | 59.32 | 64.28 | 13.8 | 70 | 4 | 2933.3658 | 61.9857 | 116.2671 | 178.2528
DECCT4 | 51 | 13.5 | 21 | 64 | 13.8 | 69 | 5 | 2894.3206 | 21.9437 | 112.6994 | 134.6431
EGMT 1 | 112 | 15 | 215.8 | 520 | 15.5 | 111 | 77 | 5031.9823 | 230.4264 | 708.5154 | 938.9418
EGMT 2 | 210 | 19 | 254.75 | 839.85 | 20 | 108 | 74 | 3779.3297 | 282.2715 | 294.5921 | 576.8636
EGMT 3 | 390 | 19 | 216.627 | 1268.339 | 20 | 355 | 157 | 11205.4302 | 240.0299 | 1133.9441 | 1373.9741
GRAM 1 | 280 | 19 | 159.362 | 1027.459 | 20 | 223 | 47 | 6578.8804 | 176.5784 | 614.3005 | 790.8789
GRAM 2 | 400 | 21 | 262.2 | 1131.5 | 22 | -5 | -3 | 153.0228 | 287.766 | 0.21908 | 287.9851
HAND 1 | [5 empty] | 38 | 0
HAND 2 | 75 | 12.47 | 113 | 270.15 | 13 | 67 | 5 | 2983.8487 | 122.8096 | 199.4758 | 322.2854
HAND 3 | 460 | 18.1 | 288.67 | 1577.048 | 19 | 353 | 75 | 10965.9929 | 318.0912 | 880.8533 | 1198.9445
HAND 4 | 500 | 24.7 | 199.596 | 1392.607 | 26 | 434 | 73 | 9772.6877 | 221.159 | 973.7148 | 1194.8738
HAND 5 | 500 | 24.7 | 189.401 | 1409.23 | 26 | 427 | 32 | 9508.4567 | 209.8626 | 932.7754 | 1142.638
LCRK 1 | 100 | 13.2 | 165 | 195 | 13.8 | 85 | 43 | 3985.2877 | 180.3409 | 161.8911 | 342.232
LCRK 2 | 250 | 19 | 170.445 | 718.294 | 20 | 217 | 26 | 6309.0543 | 188.8587 | 495.4265 | 684.2852
LKHB 1 | 615 | 22 | 355.88 | 1550.208 | 24 | 373 | 141 | 9592.6887 | 423.5266 | 547.6298 | 971.1564
LKHB 2 | 580 | 20.9 | 263.04 | 1682 | 22 | 502 | 181 | 14004.2546 | 291.4571 | 1285.0021 | 1576.4591
MTNLK 1 | 800 | 19 | 385.4 | 2119.92 | 20 | 737 | 155 | 21740.7835 | 427.036 | 1695.5802 | 2122.6162
MTNLK 2 | 800 | 19 | 387.3 | 2101.56 | 20 | 743 | 172 | 22015.7709 | 429.1413 | 1723.6857 | 2152.8269
MTNLK 3 | 800 | 19 | 318.8 | 2068.07 | 20 | 743 | 183 | 22089.5526 | 353.241 | 1707.6055 | 2060.8465
MOSES 1 | 600 | 17.1 | 370.527 | 1491.875 | 18 | 554 | 38 | 17811.311 | 410.5562 | 1153.2811 | 1563.8374
MOSES 2 | 600 | 17.1 | 370 | 1500 | 18 | 540 | 83 | 17523.9108 | 409.9723 | 1122.443 | 1532.4153
MOSES 3 | 800 | 22.8 | 417.482 | 1836.397 | 24 | 714 | 133 | 17471.6205 | 462.5839 | 1365.9787 | 1828.5626
MRGN2 | [5 empty] | 19 | -1
MRGN3 | [5 empty] | 41 | -1
MRGN 4 | 68 | 13.2 | 134.4 | 178.8 | 13.8 | 65 | 2 | 2720.6904 | 146.8959 | 149.6157 | 296.5115
MRGN 5 | 200 | 19 | 177.038 | 645.9 | 20 | 149 | 24 | 4356.6998 | 196.164 | 331.9319 | 528.0959
MRGN 6 | 535 | 21 | 291.2 | 1785 | 22 | 462 | -41 | 12172.0053 | 319.5937 | 1222.404 | 1541.9977
MORCT1 | 51 | 13.2 | 56.7 | 181.69 | 13.8 | 0 | -40 | 1673.479 | 61.9717 | 102.2587 | 164.2304
MORCT2 | 51 | 13.2 | 57.36 | 181.23 | 13.8 | 69 | -47 | 3492.8238 | 62.6931 | 444.3367 | 507.0298
MORCT3 | 51 | 13.2 | 57.26 | 180.05 | 13.8 | 0 | -40 | 1673.479 | 62.5838 | 101.3357 | 163.9195
MORCT4 | 51 | 13.2 | 56.8 | 179.86 | 13.8 | 0 | -40 | 1673.479 | 62.081 | 101.2288 | 163.3097
MORCT5 | 51 | 13.2 | 57.34 | 183.89 | 13.8 | 68 | -1 | 2845.222 | 62.6712 | 299.1708 | 361.842
MORCT6 | 51 | 13.2 | 57.22 | 178.09 | 13.8 | 0 | -40 | 1673.479 | 62.54 | 100.2326 | 162.7726
MTCK 2 | [5 empty] | 27 | 4
MTCK 3 | [5 empty] | 61 | 5
MTCK 6 | 150 | 13.2 | 110.58 | 717.32 | 13.8 | 108 | 43 | 4863.3573 | 120.8612 | 394.1594 | 515.0206
MTCK 7 | 140 | 14.4 | 122.7 | 540.6 | 15 | 119 | 34 | 4763.5965 | 133.138 | 389.3464 | 522.4844
MTCK 8 | 625 | 20.9 | 356.787 | 1536.193 | 22 | 494 | 301 | 15181.115 | 395.3319 | 1187.7004 | 1583.0323
NLK 1 | 200 | 13.2 | 153.84 | 648.821 | 13.8 | 153 | 97 | 7579.0774 | 168.1433 | 487.0423 | 655.1856
NLK 2 | 200 | 17.1 | 129.1 | 703.8 | 18 | 168 | 107 | 6388.7279 | 143.0471 | 629.9869 | 773.034
NLK 3 | 370 | 19 | 245 | 1271 | 20 | 342 | 165 | 10961.6377 | 271.4681 | 1208.1516 | 1479.6198
NMN4 | [5 empty] | 82 | 0
PARK 1 | 60 | 13.2 | 79 | 183 | 13.8 | 74 | 28 | 3310.1483 | 86.345 | 291.1472 | 377.4922
PARK 2 | 150 | 13.2 | 193.4 | 754.7 | 13.8 | 97 | 56 | 4685.9281 | 211.3814 | 384.9924 | 596.3738
PARK 3 | 150 | 14.4 | 120.635 | 686.2 | 15 | 112 | 19 | 4372.4728 | 130.8974 | 362.7176 | 493.615
PB 5 | 140 | 13.2 | 166.8 | 523.512 | 13.8 | 107 | 11 | 4500.1497 | 182.3083 | 282.7441 | 465.0524
PB 6 | 560 | 18 | 202.514 | 1712.217 | 18 | 480 | 79 | 15603.1349 | 202.514 | 1292.0304 | 1494.5444
PB CT A | 51 | 13.2 | 56.04 | 181.39 | 13.8 | 66 | 0 | 2761.2404 | 61.2503 | 277.9397 | 339.19
PB CT B | 51 | 13.2 | 57.47 | 181.16 | 13.8 | 0 | -40 | 1673.479 | 62.8133 | 101.9604 | 164.7737
PB CT C | 51 | 13.2 | 56.01 | 180.16 | 13.8 | 68 | 0 | 2844.9144 | 61.2175 | 293.0391 | 354.2566
PB CT D | 51 | 13.2 | 59.32 | 64.28 | 13.8 | 68 | 4 | 2849.8321 | 64.8353 | 104.9164 | 169.7516
PB CT E | 51 | 13.2 | 59.53 | 65.14 | 13.8 | 0 | -40 | 1673.479 | 65.0648 | 36.6621 | 101.7269
RIV | [5 empty] | 106 | 3
SANDOW 4 | 642 | 20.9 | 250 | 1496.493 | 22 | 556 | 135 | 15015.1668 | 277.0083 | 1072.7012 | 1349.7096
STRYK 1 | 200 | 13.2 | 142.72 | 729.5 | 13.8 | 172 | -3 | 7197.0544 | 155.9894 | 493.7919 | 649.7814
STRYK 2 | 550 | 18.2 | 299.742 | 1639.672 | 19 | 453 | 103 | 14116.5836 | 326.6721 | 1073.3833 | 1400.0554
TDAD 6 | 265 | 21 | 276.587 | 1162.772 | 22 | 163 | 16 | 4298.1994 | 303.5558 | 404.7024 | 708.2582
THSE 1 | 650 | 17.1 | 383.7 | 2046.565 | 18 | 544 | 229 | 18931.7868 | 425.1524 | 1522.9846 | 1948.137
THSE 2 | 736.6 | 22.8 | 375.4 | 2109.9 | 24 | 698 | 271 | 18012.4218 | 415.9557 | 1967.5855 | 2383.5411
VAL 1 | 200 | 19 | 137.7 | 709.344 | 20 | 163 | 24 | 4756.1364 | 152.5762 | 434.4442 | 587.0203
VAL 2 | 600 | 20.9 | 265 | 1495 | 22 | 488 | 131 | 13260.0863 | 293.6288 | 956.853 | 1250.4818
VAL 3 | 400 | 20.8 | 255 | 1316.2 | 22 | 363 | 159 | 10400.0556 | 285.2718 | 1154.8382 | 1440.1101
[9 empty] | TOTAL ALL UNITS |  | 60182.3278
Notes:
(a) Cogeneration units are not included in the loss calculations as their output is measured and reported on the high side of the unit main transformer.
(b) TXU Electric generation units that were not operating during this hour, do not contribute to unit main transformer losses.

## July2999
1700 July 29, 1999
| STEPUP XFMR TEST DATA |  |  |  | GENERATOR OUTPUT |  |  |  | XFMR LOSSES
| BASE | LOW | NO LOAD | FULL LOAD | TERMINAL | REAL | REACTIVE
UNIT | RATING | SIDE | LOSS | LOSS | VOLTAGE | POWER | POWER | CURRENT | NO LOAD | AT LOAD | TOTAL
| MVA | kV | kW | kW | kV | MW | MVAR | A | kW | kW | kW
BBRN 1 | [5 empty] | 567 | 219
BBRN 2 | 600 | 17.1 | 374.761 | 1423.391 | 18 | 559 | 202 | 19064.6777 | 415.2476 | 1260.6488 | 1675.8965
COLL 1 | 180 | 17.1 | 196 | 765.6 | 18 | 128 | 58 | 4507.4241 | 217.1745 | 421.1407 | 638.3152
CMPK 1 | 1300 | 20.9 | 774.81 | 2178.89 | 22 | 1084 | 363 | 30000.287 | 858.5152 | 1520.5939 | 2379.1091
CMPK 2 | 1300 | 20.9 | 844.19 | 2375.73 | 22 | 1110 | 348 | 30527.9983 | 935.3906 | 1716.8046 | 2652.1952
DEC 1 | 825 | 22.8 | 341 | 2744.3 | 24 | 790 | 368 | 20965.1938 | 377.8393 | 2763.8368 | 3141.6762
DECCTA | 51 | 13.5 | 58.28 | 63.93 | 13.8 | 79 | 6 | 3314.6399 | 60.899 | 147.6474 | 208.5464
DEC CT B | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 79 | 5 | 3311.7343 | 61.9826 | 148.1864 | 210.169
DEC CT C | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 80 | 6 | 3356.3582 | 61.9826 | 152.2067 | 214.1893
DEC CT D | 51 | 13.5 | 62 | 64 | 13.8 | 78 | 3 | 3265.6969 | 64.7862 | 143.4763 | 208.2625
EGMT 1 | 112 | 15 | 215.8 | 520 | 15.5 | 114 | 87 | 5341.6082 | 230.4264 | 798.3901 | 1028.8165
EGMT 2 | [5 empty] | 0 | 0
EGMT 3 | 390 | 19 | 216.627 | 1268.339 | 20 | 371 | 173 | 11817.0075 | 240.0299 | 1261.1003 | 1501.1302
GRAM 1 | 280 | 19 | 159.362 | 1027.459 | 20 | 210 | 96 | 6665.5832 | 176.5784 | 630.5989 | 807.1773
GRAM 2 | 400 | 21 | 262.2 | 1131.5 | 22 | 374 | 89 | 10089.032 | 287.766 | 952.3431 | 1240.109
HAND 1 | [5 empty] | 18 | 5
HAND 2 | 75 | 12.47 | 113 | 270.15 | 13 | 71 | 5 | 3161.03 | 122.8096 | 223.8689 | 346.6785
HAND 3 | 460 | 18.1 | 288.67 | 1577.048 | 19 | 370 | 63 | 11404.9527 | 318.0912 | 952.7844 | 1270.8756
HAND 4 | 500 | 24.7 | 199.596 | 1392.607 | 26 | 446 | 72 | 10032.0001 | 221.159 | 1026.0742 | 1247.2332
HAND 5 | 500 | 24.7 | 189.401 | 1409.23 | 26 | 440 | 70 | 9893.4162 | 209.8626 | 1009.8331 | 1219.6957
LCRK 1 | 100 | 13.2 | 165 | 195 | 13.8 | 85 | 47 | 4063.5745 | 180.3409 | 168.314 | 348.6549
LCRK 2 | 250 | 19 | 170.445 | 718.294 | 20 | 230 | 88 | 7108.9146 | 188.8587 | 629.0096 | 817.8683
LKHB 1 | 615 | 22 | 355.88 | 1550.208 | 24 | 387 | 150 | 9984.6236 | 423.5266 | 593.2937 | 1016.8203
LKHB 2 | 580 | 20.9 | 263.04 | 1682 | 22 | 510 | 209 | 14464.2858 | 291.4571 | 1370.8118 | 1662.2688
MTNLK 1 | 800 | 19 | 385.4 | 2119.92 | 20 | 748 | 189 | 22271.5252 | 427.036 | 1779.3766 | 2206.4126
MTNLK 2 | 800 | 19 | 387.3 | 2101.56 | 20 | 746 | 171 | 22093.6831 | 429.1413 | 1735.9073 | 2165.0485
MTNLK 3 | 800 | 19 | 318.8 | 2068.07 | 20 | 751 | 192 | 22376.7923 | 353.241 | 1752.3037 | 2105.5447
MOSES 1 | 600 | 17.1 | 370.527 | 1491.875 | 18 | 548 | 118 | 17979.9843 | 410.5562 | 1175.2277 | 1585.784
MOSES 2 | 600 | 17.1 | 370 | 1500 | 18 | 521 | 106 | 17053.4442 | 409.9723 | 1062.9833 | 1472.9556
MOSES 3 | 800 | 22.8 | 417.482 | 1836.397 | 24 | 726 | 130 | 17742.6302 | 462.5839 | 1408.6839 | 1871.2678
MRGN 2 | [5 empty] | 18 | -2
MRGN 3 | [5 empty] | 43 | -1
MRGN 4 | 68 | 13.2 | 134.4 | 178.8 | 13.8 | 70 | 1 | 2928.8871 | 146.8959 | 173.39 | 320.2859
MRGN 5 | 200 | 19 | 177.038 | 645.9 | 20 | 132 | 80 | 4455.7079 | 196.164 | 347.19 | 543.354
MRGN 6 | 535 | 21 | 291.2 | 1785 | 22 | 465 | -10 | 12205.9068 | 319.5937 | 1229.2228 | 1548.8164
MRGN CT A | 51 | 13.2 | 56.696 | 181.693 | 13.8 | 69 | 2 | 2887.9638 | 61.9673 | 304.5443 | 366.5116
MRGN CT B | 51 | 13.2 | 57.364 | 181.234 | 13.8 | 70 | -46 | 3504.3306 | 62.6974 | 447.2791 | 509.9765
MRGN CT C | 51 | 13.2 | 57.263 | 180.048 | 13.8 | 69 | 1 | 2887.0545 | 62.587 | 301.597 | 364.184
MRGN CT D | 51 | 13.2 | 56.804 | 179.856 | 13.8 | 70 | 1 | 2928.8871 | 62.0854 | 310.0694 | 372.1548
MRGN CT E | 51 | 13.2 | 57.335 | 183.891 | 13.8 | 69 | 1 | 2887.0545 | 62.6657 | 308.0344 | 370.7001
MRGN CT F | 51 | 13.2 | 57.222 | 178.088 | 13.8 | 69 | 0 | 2886.7513 | 62.5422 | 298.2512 | 360.7934
MTCK 2 | [5 empty] | 28 | 0
MTCK 3 | [5 empty] | 65 | 2
MTCK 6 | 150 | 13.2 | 110.58 | 717.32 | 13.8 | -3 | 0 | 125.5109 | 120.8612 | 0.26252 | 121.1237
MTCK 7 | 140 | 14.4 | 122.7 | 540.6 | 15 | 113 | 16 | 4392.755 | 133.138 | 331.0855 | 464.2235
MTCK 8 | 625 | 20.9 | 356.787 | 1536.193 | 22 | 477 | 300 | 14787.9642 | 395.3319 | 1126.9804 | 1522.3122
NLK 1 | 200 | 13.2 | 153.84 | 648.821 | 13.8 | 153 | 95 | 7534.6059 | 168.1433 | 481.3435 | 649.4868
NLK 2 | 200 | 17.1 | 129.1 | 703.8 | 18 | 174 | 85 | 6211.3828 | 143.0471 | 595.4967 | 738.5438
NLK 3 | 370 | 19 | 245 | 1271 | 20 | 352 | 188 | 11519.838 | 271.4681 | 1334.3302 | 1605.7983
NMN 4 | [5 empty] | 82 | 0
PARK 1 | 60 | 13.2 | 79 | 183 | 13.8 | 77 | 30 | 3457.3141 | 86.345 | 317.6109 | 403.9559
PARK 2 | 150 | 13.2 | 193.4 | 754.7 | 13.8 | 97 | 76 | 5155.4631 | 211.3814 | 466.0112 | 677.3926
PARK 3 | 150 | 14.4 | 120.635 | 686.2 | 15 | 116 | 46 | 4803.0854 | 130.8974 | 437.6783 | 568.5757
PB 5 | 140 | 13.2 | 166.8 | 523.512 | 13.8 | 109 | 6 | 4567.134 | 182.3083 | 291.224 | 473.5323
PB 6 | 560 | 18 | 202.514 | 1712.217 | 18 | 448 | 14 | 14376.6214 | 202.514 | 1096.889 | 1299.403
PB CT A | 51 | 13.2 | 56.042 | 181.393 | 13.8 | 67 | 10 | 2834.127 | 61.2525 | 292.8114 | 354.0639
PB CT B | 51 | 13.2 | 57.471 | 181.163 | 13.8 | 68 | 9 | 2869.7238 | 62.8144 | 299.8323 | 362.6467
PB CT C | 51 | 13.2 | 56.01 | 180.164 | 13.8 | 68 | 3 | 2847.6816 | 61.2175 | 293.616 | 354.8335
PB CT D | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 69 | 10 | 2916.9105 | 61.9826 | 114.9591 | 176.9417
PB CT E | 51 | 13.5 | 59.525 | 65.142 | 13.8 | 69 | 16 | 2963.3458 | 62.2 | 120.247 | 182.4469
RIV | [5 empty] | 105 | 13
SANDOW 4 | 642 | 20.9 | 250 | 1496.493 | 22 | 552 | 226 | 15653.3558 | 277.0083 | 1165.825 | 1442.8333
STRYK 1 | 200 | 13.2 | 142.72 | 729.5 | 13.8 | 171 | 17 | 7189.3894 | 155.9894 | 492.7407 | 648.7301
STRYK 2 | 550 | 18.2 | 299.742 | 1639.672 | 19 | 495 | 142 | 15648.1689 | 326.6721 | 1318.9328 | 1645.6049
TDAD 6 | 265 | 21 | 276.587 | 1162.772 | 22 | 231 | 141 | 7102.2636 | 303.5558 | 1104.9846 | 1408.5404
THSE 1 | 650 | 17.1 | 383.7 | 2046.565 | 18 | 340 | 258 | 13689.8328 | 425.1524 | 796.3585 | 1221.5108
THSE 2 | 736.6 | 22.8 | 375.4 | 2109.9 | 24 | 813 | 315 | 20974.4388 | 415.9557 | 2667.9033 | 3083.859
VAL 1 | 200 | 19 | 137.7 | 709.344 | 20 | 167 | 79 | 5333.0729 | 152.5762 | 546.2361 | 698.8123
VAL 2 | 600 | 20.9 | 265 | 1495 | 22 | 536 | 143 | 14558.3513 | 293.6288 | 1153.3919 | 1447.0207
VAL 3 | 400 | 20.8 | 255 | 1316.2 | 22 | 353 | 180 | 10398.698 | 285.2718 | 1154.5367 | 1439.8086
[9 empty] | TOTAL ALL UNITS |  | 62991.4787
Notes:
(a) Cogeneration units are not included in the loss calculations as their output is measured and reported on the high side of the unit main transformer.
(b) TXU Electric generation units that were not operating during this hour, do not contribute to unit main transformer losses.

## Aug2699
1700 August 26, 1999
| STEPUP XFMR TEST DATA |  |  |  | GENERATOR OUTPUT |  |  |  | XFMR LOSSES
| BASE | LOW | NO LOAD | FULL LOAD | TERMINAL | REAL | REACTIVE
UNIT | RATING | SIDE | LOSS | LOSS | VOLTAGE | POWER | POWER | CURRENT | NO LOAD | AT LOAD | TOTAL
| MVA | kV | kW | kW | kV | MW | MVAR | A | kW | kW | kW
BBRN 1 | [5 empty] | 567 | 245
BBRN 2 | 600 | 17.1 | 374.761 | 1423.391 | 18 | 562 | 4 | 18026.615 | 415.2476 | 1127.1029 | 1542.3505
COLL 1 | 180 | 17.1 | 196 | 765.6 | 18 | 57 | 116 | 4145.6259 | 217.1745 | 356.2465 | 573.421
CMPK 1 | 1300 | 20.9 | 774.81 | 2178.89 | 22 | 1076 | 408 | 30199.5202 | 858.5152 | 1540.8576 | 2399.3729
CMPK 2 | 1300 | 20.9 | 844.19 | 2375.73 | 22 | 1102 | 399 | 30757.2585 | 935.3906 | 1742.6872 | 2678.0778
DEC 1 | 825 | 22.8 | 341 | 2744.3 | 24 | 780 | 376 | 20830.222 | 377.8393 | 2728.3648 | 3106.2041
DEC CT A | 51 | 13.5 | 58.283 | 63.93 | 13.8 | 78 | 27 | 3453.2616 | 60.9021 | 160.2552 | 221.1573
DEC CT B | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 79 | 29 | 3520.7748 | 61.9826 | 167.4842 | 229.4668
DEC CT C | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 79 | 27 | 3492.8238 | 61.9826 | 164.8355 | 226.8181
DEC CT D | 51 | 13.5 | 62 | 64 | 13.8 | 78 | 25 | 3426.8033 | 64.7862 | 157.9817 | 222.7679
EGMT 1 | 112 | 15 | 215.8 | 520 | 15.5 | 113 | 99 | 5595.9452 | 230.4264 | 876.2297 | 1106.6562
EGMT 2 | 210 | 19 | 254.75 | 839.85 | 20 | 169 | 102 | 5698.3185 | 282.2715 | 669.7073 | 951.9788
EGMT 3 | 390 | 19 | 216.627 | 1268.339 | 20 | 371 | 188 | 12006.4219 | 240.0299 | 1301.8525 | 1541.8824
GRAM 1 | 280 | 19 | 159.362 | 1027.459 | 20 | 240 | 149 | 8154.8043 | 176.5784 | 943.8522 | 1120.4306
GRAM 2 | 400 | 21 | 262.2 | 1131.5 | 22 | 395 | 116 | 10803.8165 | 287.766 | 1092.0658 | 1379.8318
HAND 1 | [5 empty] | 0 | 0
HAND 2 | 75 | 12.47 | 113 | 270.15 | 13 | 71 | 46 | 3757.1759 | 122.8096 | 316.2712 | 439.0808
HAND 3 | 460 | 18.1 | 288.67 | 1577.048 | 19 | 389 | 128 | 12443.9649 | 318.0912 | 1134.2929 | 1452.3841
HAND 4 | 500 | 24.7 | 199.596 | 1392.607 | 26 | 448 | 182 | 10737.7746 | 221.159 | 1175.5261 | 1396.6851
HAND 5 | 500 | 24.7 | 189.401 | 1409.23 | 26 | 442 | 198 | 10754.7522 | 209.8626 | 1193.3225 | 1403.1852
LCRK 1 | 100 | 13.2 | 165 | 195 | 13.8 | 83 | 50 | 4053.8713 | 180.3409 | 167.5111 | 347.852
LCRK 2 | 250 | 19 | 170.445 | 718.294 | 20 | 225 | 124 | 7416.2547 | 188.8587 | 684.5733 | 873.432
LKHB 1 | 615 | 22 | 355.88 | 1550.208 | 24 | 390 | 151 | 10060.6092 | 423.5266 | 602.3583 | 1025.8849
LKHB 2 | 580 | 20.9 | 263.04 | 1682 | 22 | 515 | 233 | 14834.1149 | 291.4571 | 1441.8069 | 1733.264
MTNLK 1 | 800 | 19 | 385.4 | 2119.92 | 20 | 736 | 242 | 22365.5241 | 427.036 | 1794.4283 | 2221.4643
MTNLK 2 | 800 | 19 | 387.3 | 2101.56 | 20 | 740 | 238 | 22439.6227 | 429.1413 | 1790.694 | 2219.8353
MTNLK 3 | 800 | 19 | 318.8 | 2068.07 | 20 | 737 | 260 | 22560.4558 | 353.241 | 1781.1868 | 2134.4278
MOSES 1 | 600 | 17.1 | 370.527 | 1491.875 | 18 | 542 | 225 | 18823.1153 | 410.5562 | 1288.0313 | 1698.5875
MOSES 2 | 600 | 17.1 | 370 | 1500 | 18 | 530 | 233 | 18569.9933 | 409.9723 | 1260.4503 | 1670.4226
MOSES 3 | 800 | 22.8 | 417.482 | 1836.397 | 24 | 722 | 256 | 18428.101 | 462.5839 | 1519.633 | 1982.2169
MRGN 2 | [5 empty] | 18 | -1
MRGN 3 | [5 empty] | 42 | 0
MRGN 4 | [5 empty] | 65 | 0
MRGN 5 | 200 | 19 | 177.038 | 645.9 | 20 | 145 | -25 | 4247.5483 | 196.164 | 315.508 | 511.672
MRGN 6 | 535 | 21 | 291.2 | 1785 | 22 | 414 | 29 | 10891.3049 | 319.5937 | 978.7017 | 1298.2953
MRGN CT A | 51 | 13.2 | 56.696 | 181.693 | 13.8 | 69 | 0 | 2886.7513 | 61.9673 | 304.2886 | 366.2559
MRGN CT B | 51 | 13.2 | 57.364 | 181.234 | 13.8 | 71 | -44 | 3494.5773 | 62.6974 | 444.7928 | 507.4902
MRGN CT C | 51 | 13.2 | 57.263 | 180.048 | 13.8 | 69 | 0 | 2886.7513 | 62.587 | 301.5337 | 364.1207
MRGN CT D | 51 | 13.2 | 56.804 | 179.856 | 13.8 | 70 | -1 | 2928.8871 | 62.0854 | 310.0694 | 372.1548
MRGN CT E | 51 | 13.2 | 57.335 | 183.891 | 13.8 | 69 | -1 | 2887.0545 | 62.6657 | 308.0344 | 370.7001
MRGN CT F | 51 | 13.2 | 57.222 | 178.088 | 13.8 | 70 | -1 | 2928.8871 | 62.5422 | 307.0214 | 369.5637
MTCK 2 | [5 empty] | 28 | 2
MTCK 3 | [5 empty] | 65 | 3
MTCK 6 | 150 | 13.2 | 110.58 | 717.32 | 13.8 | 113 | 64 | 5433.1721 | 120.8612 | 491.9336 | 612.7948
MTCK 7 | 140 | 14.4 | 122.7 | 540.6 | 15 | 117 | 63 | 5114.6847 | 133.138 | 448.8528 | 581.9908
MTCK 8 | 625 | 20.9 | 356.787 | 1536.193 | 22 | 520 | 357 | 16552.9662 | 395.3319 | 1412.0537 | 1807.3856
NLK 1 | 200 | 13.2 | 153.84 | 648.821 | 13.8 | 168 | 83 | 7839.6063 | 168.1433 | 521.1018 | 689.2451
NLK 2 | 200 | 17.1 | 129.1 | 703.8 | 18 | 175 | 116 | 6734.302 | 143.0471 | 699.9837 | 843.0308
NLK 3 | 370 | 19 | 245 | 1271 | 20 | 45 | -3 | 1301.9217 | 271.4681 | 17.0428 | 288.5109
NMN 4 | [5 empty] | 81 | 0
PARK 1 | 60 | 13.2 | 79 | 183 | 13.8 | 74 | 38 | 3480.2732 | 86.345 | 321.8432 | 408.1883
PARK 2 | 150 | 13.2 | 193.4 | 754.7 | 13.8 | 92 | 77 | 5019.2167 | 211.3814 | 441.7055 | 653.0869
PARK 3 | 150 | 14.4 | 120.635 | 686.2 | 15 | 113 | 67 | 5056.4224 | 130.8974 | 485.0663 | 615.9637
PB 5 | 140 | 13.2 | 166.8 | 523.512 | 13.8 | 110 | 0 | 4602.0674 | 182.3083 | 295.6961 | 478.0044
PB 6 | 560 | 18 | 202.514 | 1712.217 | 18 | 496 | 11 | 15913.1193 | 202.514 | 1343.8774 | 1546.3914
PB CT A | 51 | 13.2 | 56.042 | 181.393 | 13.8 | 67 | 3 | 2805.8859 | 61.2525 | 287.0049 | 348.2574
PB CT B | 51 | 13.2 | 57.471 | 181.163 | 13.8 | 67 | -1 | 2803.3896 | 62.8144 | 286.1312 | 348.9456
PB CT C | 51 | 13.2 | 56.01 | 180.164 | 13.8 | 69 | -1 | 2887.0545 | 61.2175 | 301.7913 | 363.0089
PB CT D | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 69 | 7 | 2901.5685 | 61.9826 | 113.753 | 175.7356
PB CT E | 51 | 13.5 | 59.525 | 65.142 | 13.8 | 69 | 0 | 2886.7513 | 62.2 | 114.1112 | 176.3112
RIV | [5 empty] | 113 | 30
SANDOW 4 | 642 | 20.9 | 250 | 1496.493 | 22 | 552 | 222 | 15613.8845 | 277.0083 | 1159.953 | 1436.9613
STRYK 1 | 200 | 13.2 | 142.72 | 729.5 | 13.8 | 173 | 22 | 7296.0855 | 155.9894 | 507.4745 | 663.464
STRYK 2 | 550 | 18.2 | 299.742 | 1639.672 | 19 | 495 | 161 | 15817.1103 | 326.6721 | 1347.5656 | 1674.2377
TDAD 6 | 265 | 21 | 276.587 | 1162.772 | 22 | 235 | 144 | 7232.8928 | 303.5558 | 1146.0055 | 1449.5613
THSE 1 | 650 | 17.1 | 383.7 | 2046.565 | 18 | 547 | 286 | 19798.4962 | 425.1524 | 1665.623 | 2090.7754
THSE 2 | 736.6 | 22.8 | 375.4 | 2109.9 | 24 | 788 | 316 | 20423.7516 | 415.9557 | 2529.65 | 2945.6056
VAL 1 | 200 | 19 | 137.7 | 709.344 | 20 | 164 | 91 | 5414.2559 | 152.5762 | 562.9929 | 715.5691
VAL 2 | 600 | 20.9 | 265 | 1495 | 22 | 539 | 227 | 15348.3428 | 293.6288 | 1281.963 | 1575.5918
VAL 3 | 400 | 20.8 | 255 | 1316.2 | 22 | 374 | 119 | 10299.8101 | 285.2718 | 1132.6827 | 1417.9545
[9 empty] | TOTAL ALL UNITS |  | 65965.9635
Notes:
(a) Cogeneration units are not included in the loss calculations as their output is measured and reported on the high side of the unit main transformer.
(b) TXU Electric generation units that were not operating during this hour, do not contribute to unit main transformer losses.

## Sep0799
1700 September 07, 1999
| STEPUP XFMR TEST DATA |  |  |  | GENERATOR OUTPUT |  |  |  | XFMR LOSSES
| BASE | LOW | NO LOAD | FULL LOAD | TERMINAL | REAL | REACTIVE
UNIT | RATING | SIDE | LOSS | LOSS | VOLTAGE | POWER | POWER | CURRENT | NO LOAD | AT LOAD | TOTAL
| MVA | kV | kW | kW | kV | MW | MVAR | A | kW | kW | kW
BBRN 1 | 600 | 17.1 | 410.646 | 1485.975 | 18 | 565 | 188 | 19099.2911 | 455.0094 | 1320.8606 | 1775.87
BBRN 2 | 600 | 17.1 | 374.761 | 1423.391 | 18 | 565 | -7 | 18123.7743 | 415.2476 | 1139.2853 | 1554.5329
COLL 1 | 180 | 17.1 | 196 | 765.6 | 18 | 0 | 0 | 0 | 217.1745 | 0 | 217.1745
CMPK 1 | 1300 | 20.9 | 774.81 | 2178.89 | 22 | 1088 | 288 | 29535.9892 | 858.5152 | 1473.8913 | 2332.4066
CMPK 2 | 1300 | 20.9 | 844.19 | 2375.73 | 22 | 1111 | 336 | 30460.3907 | 935.3906 | 1709.2089 | 2644.5995
DEC 1 | 825 | 22.8 | 341 | 2744.3 | 24 | 756 | 369 | 20237.2645 | 377.8393 | 2575.2432 | 2953.0826
DEC CT A | 51 | 13.5 | 58.283 | 63.93 | 13.8 | 70 | 5 | 2936.0497 | 60.9021 | 115.8457 | 176.7478
DEC CT B | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 71 | 4 | 2975.1356 | 61.9826 | 119.5944 | 181.577
DEC CT C | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 71 | 4 | 2975.1356 | 61.9826 | 119.5944 | 181.577
DEC CT D | 51 | 13.5 | 62 | 64 | 13.8 | 70 | 5 | 2936.0497 | 64.7862 | 115.9726 | 180.7587
EGMT 1 | 112 | 15 | 215.8 | 520 | 15.5 | 102 | 54 | 4298.9242 | 230.4264 | 517.1192 | 747.5456
EGMT 2 | [5 empty] | 111 | 57
EGMT 3 | 390 | 19 | 216.627 | 1268.339 | 20 | 329 | 53 | 9619.8579 | 240.0299 | 835.7414 | 1075.7713
GRAM 1 | 280 | 19 | 159.362 | 1027.459 | 20 | 229 | 76 | 6965.2112 | 176.5784 | 688.5658 | 865.1442
GRAM 2 | 400 | 21 | 262.2 | 1131.5 | 22 | 375 | 93 | 10139.3188 | 287.766 | 961.8602 | 1249.6262
HAND 1 | [5 empty] | 0 | 0
HAND 2 | 75 | 12.47 | 113 | 270.15 | 13 | 0 | 0 | 0 | 122.8096 | 0 | 122.8096
HAND 3 | 460 | 18.1 | 288.67 | 1577.048 | 19 | 358 | 142 | 11703.0037 | 318.0912 | 1003.2342 | 1321.3255
HAND 4 | 500 | 24.7 | 199.596 | 1392.607 | 26 | 427 | 195 | 10423.8102 | 221.159 | 1107.7881 | 1328.9472
HAND 5 | 500 | 24.7 | 189.401 | 1409.23 | 26 | 421 | 200 | 10349.9183 | 209.8626 | 1105.1745 | 1315.0372
LCRK 1 | 100 | 13.2 | 165 | 195 | 13.8 | 84 | 48 | 4047.6058 | 180.3409 | 166.9937 | 347.3346
LCRK 2 | 250 | 19 | 170.445 | 718.294 | 20 | 216 | 105 | 6933.0729 | 188.8587 | 598.2769 | 787.1356
LKHB 1 | 615 | 22 | 355.88 | 1550.208 | 24 | 369 | 63 | 9005.2068 | 423.5266 | 482.6071 | 906.1338
LKHB 2 | 580 | 20.9 | 263.04 | 1682 | 22 | 501 | 179 | 13961.8232 | 291.4571 | 1277.227 | 1568.6841
MTNLK 1 | 800 | 19 | 385.4 | 2119.92 | 20 | 722 | 151 | 21293.2892 | 427.036 | 1626.4977 | 2053.5337
MTNLK 2 | 800 | 19 | 387.3 | 2101.56 | 20 | 747 | 177 | 22161.1146 | 429.1413 | 1746.5196 | 2175.6609
MTNLK 3 | 800 | 19 | 318.8 | 2068.07 | 20 | 752 | 165 | 22224.7797 | 353.241 | 1728.5767 | 2081.8177
MOSES 1 | 600 | 17.1 | 370.527 | 1491.875 | 18 | 531 | 119 | 17454.2907 | 410.5562 | 1107.5104 | 1518.0667
MOSES 2 | 600 | 17.1 | 370 | 1500 | 18 | 524 | 89 | 17048.0138 | 409.9723 | 1062.3064 | 1472.2787
MOSES 3 | 800 | 22.8 | 417.482 | 1836.397 | 24 | 715 | 121 | 17444.7872 | 462.5839 | 1361.7861 | 1824.3701
MRGN 2 | [5 empty] | 0 | 0
MRGN 3 | [5 empty] | 0 | 0
MRGN 4 | 68 | 13.2 | 134.4 | 178.8 | 13.8 | 0 | 0 | 0 | 146.8959 | 0 | 146.8959
MRGN 5 | 200 | 19 | 177.038 | 645.9 | 20 | 171 | 4 | 4937.6951 | 196.164 | 426.3657 | 622.5297
MRGN 6 | 535 | 21 | 291.2 | 1785 | 22 | 467 | 7 | 12256.9483 | 319.5937 | 1239.5248 | 1559.1184
MRGN CT A | 51 | 13.2 | 56.696 | 181.693 | 13.8 | 67 | -1 | 2803.3896 | 61.9673 | 286.9683 | 348.9356
MRGN CT B | 51 | 13.2 | 57.364 | 181.234 | 13.8 | 69 | -47 | 3492.8238 | 62.6974 | 444.3465 | 507.044
MRGN CT C | 51 | 13.2 | 57.263 | 180.048 | 13.8 | 69 | -3 | 2889.4786 | 62.587 | 302.1037 | 364.6907
MRGN CT D | 51 | 13.2 | 56.804 | 179.856 | 13.8 | 69 | 1 | 2887.0545 | 62.0854 | 301.2754 | 363.3608
MRGN CT E | 51 | 13.2 | 57.335 | 183.891 | 13.8 | 69 | -1 | 2887.0545 | 62.6657 | 308.0344 | 370.7001
MRGN CT F | 51 | 13.2 | 57.222 | 178.088 | 13.8 | 69 | -2 | 2887.9638 | 62.5422 | 298.5018 | 361.044
MTCK 2 | [5 empty] | -1 | 0
MTCK 3 | [5 empty] | 0 | 0
MTCK 6 | 150 | 13.2 | 110.58 | 717.32 | 13.8 | 111 | 37 | 4895.105 | 120.8612 | 399.3223 | 520.1835
MTCK 7 | 140 | 14.4 | 122.7 | 540.6 | 15 | 112 | 31 | 4472.9641 | 133.138 | 343.2867 | 476.4248
MTCK 8 | 625 | 20.9 | 356.787 | 1536.193 | 22 | 533 | 273 | 15715.664 | 395.3319 | 1272.8143 | 1668.1461
NLK 1 | 200 | 13.2 | 153.84 | 648.821 | 13.8 | 159 | 92 | 7685.3739 | 168.1433 | 500.7997 | 668.943
NLK 2 | 200 | 17.1 | 129.1 | 703.8 | 18 | 168 | 93 | 6159.1546 | 143.0471 | 585.5243 | 728.5714
NLK 3 | 370 | 19 | 245 | 1271 | 20 | 342 | 176 | 11103.3028 | 271.4681 | 1239.581 | 1511.0492
NMN 4 | [5 empty] | 0 | 0
PARK 1 | 60 | 13.2 | 79 | 183 | 13.8 | 74 | 23 | 3242.0282 | 86.345 | 279.2874 | 365.6324
PARK 2 | 150 | 13.2 | 193.4 | 754.7 | 13.8 | 79 | 57 | 4075.6173 | 211.3814 | 291.2378 | 502.6192
PARK 3 | [5 empty] | 112 | 41
PB 5 | 140 | 13.2 | 166.8 | 523.512 | 13.8 | 110 | 11 | 4625.0205 | 182.3083 | 298.6531 | 480.9613
PB 6 | 560 | 18 | 202.514 | 1712.217 | 18 | 509 | 29 | 16352.6593 | 202.514 | 1419.1418 | 1621.6558
PB CT A | 51 | 13.2 | 56.042 | 181.393 | 13.8 | 67 | 2 | 2804.326 | 61.2525 | 286.6859 | 347.9384
PB CT B | 51 | 13.2 | 57.471 | 181.163 | 13.8 | 38 | 3 | 1594.7518 | 62.8144 | 92.5943 | 155.4087
PB CT C | 51 | 13.2 | 56.01 | 180.164 | 13.8 | 28 | 2 | 1174.4199 | 61.2175 | 49.9394 | 111.157
PB CT D | 51 | 13.5 | 59.317 | 64.276 | 13.8 | 28 | 1 | 1172.1822 | 61.9826 | 18.5647 | 80.5473
PB CT E | 51 | 13.5 | 59.525 | 65.142 | 13.8 | 36 | -2 | 1508.4536 | 62.2 | 31.1583 | 93.3582
RIV | [5 empty] | 0 | 0
SANDOW 4 | 642 | 20.9 | 250 | 1496.493 | 22 | 546 | 153 | 14880.7241 | 277.0083 | 1053.5778 | 1330.5861
STRYK 1 | 200 | 13.2 | 142.72 | 729.5 | 13.8 | 0 | 0 | 0 | 155.9894 | 0 | 155.9894
STRYK 2 | 550 | 18.2 | 299.742 | 1639.672 | 19 | 473 | 122 | 14843.3806 | 326.6721 | 1186.7556 | 1513.4277
THSE 1 | 650 | 17.1 | 383.7 | 2046.565 | 18 | 223 | 77 | 7567.1208 | 425.1524 | 243.3177 | 668.47
THSE 2 | 736.6 | 22.8 | 375.4 | 2109.9 | 24 | 519 | 206 | 13432.7242 | 415.9557 | 1094.2526 | 1510.2083
TDAD 6 | 265 | 21 | 276.587 | 1162.772 | 22 | 764 | 257 | 21153.7888 | 303.5558 | 9802.5483 | 10106.1041
VAL 1 | 200 | 19 | 137.7 | 709.344 | 20 | 141 | 49 | 4309.0989 | 152.5762 | 356.6139 | 509.1901
VAL 2 | 600 | 20.9 | 265 | 1495 | 22 | 507 | 109 | 13609.3166 | 293.6288 | 1007.9179 | 1301.5467
VAL 3 | 400 | 20.8 | 255 | 1316.2 | 22 | 356 | 120 | 9859.0619 | 285.2718 | 1037.8176 | 1323.0894
[9 empty] | TOTAL ALL UNITS |  | 67355.0763
Notes:
(a) Cogeneration units are not included in the loss calculations as their output is measured and reported on the high side of the unit main transformer.
(b) TXU Electric generation units that were not operating during this hour, do not contribute to unit main transformer losses.