## 062899Gen Data
| Amistad | Falcon | Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman
1999-06-28 | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1&2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6
01:00 | 0 | 4 | 67 | 568 | 66 | 45 | 96 | 6 | 10 | 11 | 35 | 10 | 10 | 60 | 0 | 25 | 36 | 28 | 154 | 239 | 28 | 10 | 103 | 211 | 274 | 294 | 296 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 676 | 0 | 0 | 46 | 61 | 44 | 49 | 24 | 21 | 70 | 2 | 29 | 41 | 0 | 0
02:00 | 0 | 4 | 67 | 567 | 35 | 38 | 74 | 6 | 10 | 10 | 35 | 9 | 10 | 54 | 0 | 26 | 37 | 29 | 154 | 222 | 9 | 8 | 67 | 207 | 240 | 246 | 296 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 675 | 0 | 0 | 36 | 34 | 39 | 51 | 24 | 22 | 67 | 2 | 29 | 40 | 0 | 0
03:00 | 0 | 4 | 65 | 571 | 8 | 40 | 79 | 6 | 9 | 10 | 36 | 9 | 10 | 53 | 0 | 25 | 36 | 30 | 153 | 224 | 9 | 9 | 69 | 87 | 226 | 255 | 298 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 676 | 0 | 0 | 18 | 26 | 39 | 51 | 22 | 22 | 67 | 2 | 29 | 39 | 0 | 0
04:00 | 0 | 4 | 67 | 571 | 10 | 35 | 65 | 6 | 10 | 10 | 35 | 9 | 11 | 53 | 0 | 26 | 37 | 28 | 153 | 213 | 9 | 8 | 66 | 66 | 226 | 228 | 292 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 676 | 0 | 0 | 15 | 26 | 38 | 51 | 23 | 21 | 66 | 2 | 29 | 40 | 0 | 0
05:00 | 0 | 4 | 66 | 573 | 10 | 31 | 47 | 6 | 9 | 10 | 37 | 8 | 10 | 54 | 0 | 26 | 37 | 29 | 153 | 191 | 11 | 9 | 64 | 62 | 226 | 184 | 292 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 674 | 0 | 0 | 15 | 27 | 38 | 50 | 23 | 22 | 62 | 2 | 28 | 40 | 0 | 0
06:00 | 0 | 4 | 67 | 576 | 11 | 32 | 51 | 6 | 11 | 10 | 35 | 9 | 11 | 54 | 0 | 26 | 37 | 28 | 152 | 198 | 9 | 8 | 66 | 62 | 225 | 197 | 298 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 672 | 0 | 0 | 15 | 25 | 38 | 52 | 23 | 21 | 64 | 3 | 29 | 41 | 0 | 0
07:00 | 6 | 4 | 67 | 574 | 9 | 34 | 53 | 6 | 10 | 10 | 37 | 9 | 9 | 55 | 0 | 25 | 37 | 29 | 153 | 203 | 9 | 10 | 65 | 63 | 226 | 208 | 295 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 672 | 0 | 0 | 15 | 26 | 39 | 52 | 23 | 21 | 63 | 2 | 29 | 40 | 0 | 0
08:00 | 16 | 4 | 66 | 575 | 10 | 34 | 52 | 6 | 13 | 11 | 70 | 9 | 10 | 61 | 0 | 26 | 51 | 28 | 153 | 255 | 11 | 8 | 73 | 84 | 255 | 261 | 291 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 674 | 0 | 4 | 15 | 27 | 40 | 51 | 25 | 22 | 71 | 2 | 28 | 41 | 0 | 0
09:00 | 1 | 4 | 66 | 566 | 10 | 45 | 87 | 6 | 18 | 10 | 85 | 10 | 11 | 92 | 0 | 26 | 60 | 29 | 156 | 293 | 9 | 9 | 80 | 105 | 259 | 306 | 299 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 674 | 2 | 8 | 15 | 27 | 51 | 53 | 34 | 21 | 77 | 0 | 28 | 45 | 0 | 0
10:00 | 0 | 4 | 73 | 569 | 9 | 64 | 154 | 5 | 25 | 16 | 90 | 9 | 10 | 122 | 0 | 33 | 54 | 29 | 160 | 345 | 10 | 8 | 92 | 138 | 285 | 313 | 290 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 674 | 8 | 9 | 15 | 27 | 70 | 81 | 47 | 21 | 91 | 0 | 28 | 65 | 0 | 0
11:00 | 10 | 4 | 85 | 569 | 9 | 67 | 164 | 6 | 22 | 18 | 93 | 9 | 10 | 129 | 0 | 37 | 74 | 29 | 159 | 346 | 17 | 8 | 98 | 145 | 298 | 313 | 297 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 674 | 10 | 10 | 16 | 27 | 75 | 86 | 54 | 21 | 92 | 0 | 28 | 70 | 0 | 0
12:00 | 23 | 4 | 102 | 572 | 9 | 84 | 217 | 5 | 28 | 25 | 98 | 10 | 10 | 153 | 2 | 60 | 97 | 29 | 161 | 346 | 21 | 11 | 105 | 181 | 315 | 312 | 296 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 672 | 10 | 10 | 15 | 34 | 89 | 107 | 69 | 19 | 96 | 1 | 27 | 72 | 0 | 0
13:00 | 23 | 0 | 102 | 571 | 12 | 87 | 217 | 6 | 29 | 28 | 100 | 22 | 17 | 153 | 48 | 66 | 99 | 29 | 160 | 347 | 28 | 25 | 107 | 188 | 316 | 313 | 289 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 673 | 10 | 10 | 15 | 37 | 92 | 111 | 71 | 21 | 97 | 0 | 28 | 75 | 0 | 0
14:00 | 24 | 0 | 103 | 558 | 13 | 102 | 223 | 5 | 28 | 30 | 99 | 23 | 23 | 153 | 49 | 65 | 101 | 28 | 161 | 346 | 41 | 38 | 115 | 222 | 316 | 311 | 293 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 675 | 10 | 10 | 15 | 50 | 109 | 137 | 79 | 20 | 97 | 1 | 28 | 85 | 0 | 0
15:00 | 23 | 0 | 102 | 572 | 47 | 86 | 206 | 6 | 29 | 30 | 99 | 23 | 22 | 152 | 49 | 66 | 104 | 29 | 163 | 346 | 52 | 55 | 112 | 234 | 316 | 312 | 297 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 675 | 10 | 10 | 15 | 50 | 109 | 134 | 81 | 20 | 96 | 1 | 28 | 85 | 0 | 0
16:00 | 23 | 0 | 107 | 570 | 63 | 85 | 201 | 5 | 28 | 30 | 100 | 23 | 23 | 154 | 48 | 65 | 104 | 28 | 163 | 344 | 54 | 62 | 126 | 236 | 316 | 312 | 289 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 675 | 13 | 13 | 24 | 66 | 127 | 166 | 80 | 20 | 98 | 0 | 28 | 88 | 0 | 0
17:00 | 3 | 0 | 106 | 570 | 63 | 85 | 200 | 6 | 28 | 30 | 99 | 22 | 24 | 153 | 49 | 65 | 104 | 29 | 163 | 346 | 64 | 70 | 122 | 238 | 315 | 312 | 297 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 676 | 27 | 26 | 40 | 58 | 118 | 152 | 79 | 20 | 97 | 0 | 28 | 89 | 0 | 0
18:00 | 0 | 0 | 107 | 566 | 63 | 85 | 200 | 6 | 30 | 30 | 99 | 23 | 23 | 152 | 48 | 65 | 103 | 28 | 163 | 344 | 66 | 69 | 124 | 238 | 316 | 311 | 296 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 677 | 27 | 30 | 40 | 62 | 122 | 156 | 80 | 19 | 97 | 0 | 28 | 88 | 0 | 0
19:00 | 0 | 0 | 102 | 568 | 64 | 83 | 201 | 6 | 28 | 29 | 98 | 23 | 23 | 153 | 49 | 65 | 104 | 28 | 164 | 345 | 64 | 70 | 110 | 233 | 314 | 313 | 291 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 675 | 28 | 30 | 40 | 57 | 104 | 127 | 78 | 21 | 96 | 0 | 28 | 79 | 0 | 0
20:00 | 0 | 0 | 92 | 573 | 63 | 68 | 205 | 5 | 28 | 29 | 94 | 22 | 23 | 153 | 49 | 55 | 102 | 28 | 163 | 329 | 66 | 69 | 105 | 229 | 316 | 311 | 295 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 674 | 27 | 30 | 40 | 57 | 82 | 97 | 62 | 20 | 94 | 0 | 28 | 69 | 0 | 0
21:00 | 0 | 0 | 95 | 572 | 63 | 56 | 168 | 6 | 27 | 25 | 94 | 23 | 24 | 153 | 49 | 31 | 100 | 28 | 163 | 331 | 65 | 70 | 85 | 231 | 315 | 312 | 296 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 677 | 17 | 20 | 23 | 57 | 76 | 87 | 56 | 20 | 92 | 0 | 23 | 66 | 0 | 0
22:00 | 0 | 0 | 99 | 571 | 63 | 66 | 187 | 5 | 26 | 28 | 96 | 20 | 22 | 152 | 19 | 37 | 101 | 27 | 163 | 335 | 65 | 69 | 89 | 229 | 316 | 311 | 297 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 677 | 13 | 9 | 16 | 56 | 83 | 100 | 63 | 21 | 94 | 0 | 15 | 70 | 0 | 0
23:00 | 0 | 0 | 96 | 572 | 64 | 53 | 158 | 6 | 25 | 14 | 94 | 9 | 13 | 154 | 0 | 32 | 99 | 28 | 164 | 323 | 66 | 69 | 84 | 231 | 315 | 312 | 294 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 675 | 13 | 10 | 15 | 56 | 72 | 81 | 53 | 21 | 90 | 0 | 14 | 64 | 0 | 0
24:00 | 0 | 0 | 99 | 571 | 57 | 37 | 85 | 4 | 18 | 11 | 87 | 9 | 11 | 140 | 0 | 24 | 85 | 29 | 138 | 257 | 63 | 65 | 74 | 228 | 300 | 312 | 293 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 650 | 13 | 10 | 16 | 54 | 50 | 53 | 35 | 21 | 76 | 0 | 13 | 48 | 0 | 0
0

## 062899GSU calc
| Amistad | Falcon | Ennis Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman |  | CPL | WTU
1999-06-28 | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1 | 2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6 |  |  | Total | Total | Total | check
01:00 | 0 | 0 | 0.04489 | 0.96787 | 0 | 0.02025 | 0.09216 | 0.021636 | 0.0113 | 0.011374 | 0.0343 | 0 | 0 | 0.0648 | 0 | 0.025625 | 0.044064 | 0.089376 | 0.47432 | 0.57121 | 0.03136 | 0.0054 | 0.19096 | 0.44521 | 0.52553 | 0.51862 | 0 | 0.071415 | 0.071415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2795 | 0 | 0 | 0.18198 | 0.1254 | 0.031557 | 0.026411 | 0.023962 | 0.065136 | 0.17689 | 0 | 0.056852 | 0.045219 | 0 |  | 6.346 | 4.1903 | 2.1558 | 6.346
02:00 | 0 | 0 | 0.04489 | 0.96447 | 0 | 0.01444 | 0.05476 | 0.021636 | 0.0113 | 0.0094 | 0.0343 | 0 | 0 | 0.052488 | 0 | 0.027716 | 0.046546 | 0.095874 | 0.47432 | 0.49284 | 0.00324 | 0.003456 | 0.080802 | 0.42849 | 0.4032 | 0.3631 | 0 | 0.06936 | 0.06936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2757 | 0 | 0 | 0.11146 | 0.038957 | 0.024792 | 0.028611 | 0.023962 | 0.071487 | 0.16205 | 0 | 0.056852 | 0.04304 | 0 |  | 5.6029 | 3.6273 | 1.9757 | 5.6029
03:00 | 0 | 0 | 0.04225 | 0.97812 | 0 | 0.016 | 0.06241 | 0.021636 | 0.009153 | 0.0094 | 0.036288 | 0 | 0 | 0.050562 | 0 | 0.025625 | 0.044064 | 0.1026 | 0.46818 | 0.50176 | 0.00324 | 0.004374 | 0.085698 | 0.07569 | 0.35753 | 0.39015 | 0 | 0.071415 | 0.071415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2795 | 0 | 0 | 0.027864 | 0.022781 | 0.024792 | 0.028611 | 0.020134 | 0.071487 | 0.16205 | 0 | 0.056852 | 0.040915 | 0 |  | 5.1626 | 3.2847 | 1.8779 | 5.1626
04:00 | 0 | 0 | 0.04489 | 0.97812 | 0 | 0.01225 | 0.04225 | 0.021636 | 0.0113 | 0.0094 | 0.0343 | 0 | 0 | 0.050562 | 0 | 0.027716 | 0.046546 | 0.089376 | 0.46818 | 0.45369 | 0.00324 | 0.003456 | 0.078408 | 0.04356 | 0.35753 | 0.3119 | 0 | 0.071415 | 0.071415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2795 | 0 | 0 | 0.01935 | 0.022781 | 0.023537 | 0.028611 | 0.022006 | 0.065136 | 0.15725 | 0 | 0.056852 | 0.04304 | 0 |  | 4.9492 | 3.0883 | 1.8609 | 4.9492
05:00 | 0 | 0 | 0.04356 | 0.98499 | 0 | 0.00961 | 0.02209 | 0.021636 | 0.009153 | 0.0094 | 0.038332 | 0 | 0 | 0.052488 | 0 | 0.027716 | 0.046546 | 0.095874 | 0.46818 | 0.36481 | 0.00484 | 0.004374 | 0.073728 | 0.03844 | 0.35753 | 0.20314 | 0 | 0.071415 | 0.071415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.272 | 0 | 0 | 0.01935 | 0.024567 | 0.023537 | 0.0275 | 0.022006 | 0.071487 | 0.13877 | 0 | 0.052998 | 0.04304 | 0 |  | 4.7145 | 2.8764 | 1.8381 | 4.7145
06:00 | 0 | 0 | 0.04489 | 0.99533 | 0 | 0.01024 | 0.02601 | 0.021636 | 0.013673 | 0.0094 | 0.0343 | 0 | 0 | 0.052488 | 0 | 0.027716 | 0.046546 | 0.089376 | 0.46208 | 0.39204 | 0.00324 | 0.003456 | 0.078408 | 0.03844 | 0.35437 | 0.23285 | 0 | 0.071415 | 0.071415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2644 | 0 | 0 | 0.01935 | 0.021063 | 0.023537 | 0.029744 | 0.022006 | 0.065136 | 0.14787 | 0 | 0.056852 | 0.045219 | 0 |  | 4.7745 | 2.9365 | 1.838 | 4.7745
07:00 | 0 | 0 | 0.04489 | 0.98843 | 0 | 0.01156 | 0.02809 | 0.021636 | 0.0113 | 0.0094 | 0.038332 | 0 | 0 | 0.05445 | 0 | 0.025625 | 0.046546 | 0.095874 | 0.46818 | 0.41209 | 0.00324 | 0.0054 | 0.07605 | 0.03969 | 0.35753 | 0.25958 | 0 | 0.098415 | 0.098415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2644 | 0 | 0 | 0.01935 | 0.022781 | 0.024792 | 0.029744 | 0.022006 | 0.065136 | 0.14328 | 0 | 0.056852 | 0.04304 | 0 |  | 4.8861 | 2.9979 | 1.8882 | 4.8861
08:00 | 0 | 0 | 0.04356 | 0.99187 | 0 | 0.01156 | 0.02704 | 0.021636 | 0.019097 | 0.011374 | 0.1372 | 0 | 0 | 0.066978 | 0 | 0.027716 | 0.088434 | 0.089376 | 0.46818 | 0.65025 | 0.00484 | 0.003456 | 0.095922 | 0.07056 | 0.45517 | 0.40873 | 0 | 0.093615 | 0.093615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.272 | 0 | 0.0006144 | 0.01935 | 0.024567 | 0.02608 | 0.028611 | 0.026 | 0.071487 | 0.18198 | 0 | 0.052998 | 0.045219 | 0 |  | 5.6291 | 3.693 | 1.9361 | 5.6291
09:00 | 0 | 0 | 0.04356 | 0.96107 | 0 | 0.02025 | 0.07569 | 0.021636 | 0.036612 | 0.0094 | 0.2023 | 0 | 0 | 0.15235 | 0 | 0.027716 | 0.1224 | 0.095874 | 0.48672 | 0.85849 | 0.00324 | 0.004374 | 0.1152 | 0.11025 | 0.46957 | 0.56182 | 0 | 0.093615 | 0.093615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.272 | 0.00015 | 0.0024576 | 0.01935 | 0.024567 | 0.042396 | 0.030899 | 0.04809 | 0.065136 | 0.21404 | 0 | 0.052998 | 0.054473 | 0 |  | 6.3923 | 4.3785 | 2.0138 | 6.3923
10:00 | 0 | 0 | 0.05329 | 0.97128 | 0 | 0.04096 | 0.23716 | 0.015025 | 0.070625 | 0.024064 | 0.2268 | 0 | 0 | 0.26791 | 0 | 0.044649 | 0.099144 | 0.095874 | 0.512 | 1.1903 | 0.004 | 0.003456 | 0.15235 | 0.19044 | 0.56858 | 0.58781 | 0 | 0.093615 | 0.093615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.272 | 0.0024 | 0.0031104 | 0.01935 | 0.024567 | 0.07987 | 0.072171 | 0.091894 | 0.065136 | 0.29894 | 0 | 0.052998 | 0.11365 | 0 |  | 7.639 | 5.3557 | 2.2833 | 7.639
11:00 | 0 | 0 | 0.07225 | 0.97128 | 0 | 0.04489 | 0.26896 | 0.021636 | 0.054692 | 0.030456 | 0.24217 | 0 | 0 | 0.29954 | 0 | 0.056129 | 0.18618 | 0.095874 | 0.50562 | 1.1972 | 0.01156 | 0.003456 | 0.17287 | 0.21025 | 0.62163 | 0.58781 | 0 | 0.093615 | 0.093615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.272 | 0.00375 | 0.00384 | 0.022016 | 0.024567 | 0.091688 | 0.081356 | 0.12131 | 0.065136 | 0.30555 | 0 | 0.052998 | 0.13181 | 0 |  | 8.0176 | 5.6544 | 2.3632 | 8.0176
12:00 | 0 | 0 | 0.10404 | 0.98155 | 0 | 0.07056 | 0.47089 | 0.015025 | 0.088592 | 0.05875 | 0.26891 | 0 | 0 | 0.42136 | 0.000172 | 0.1476 | 0.31991 | 0.095874 | 0.51842 | 1.1972 | 0.01764 | 0.006534 | 0.19845 | 0.32761 | 0.69458 | 0.58406 | 0 | 0.09126 | 0.09126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2644 | 0.00375 | 0.00384 | 0.01935 | 0.038957 | 0.12911 | 0.12594 | 0.19806 | 0.05332 | 0.3327 | 0 | 0.04928 | 0.13945 | 0 |  | 9.1284 | 6.5877 | 2.5407 | 9.1284
13:00 | 0 | 0 | 0.10404 | 0.97812 | 0 | 0.07569 | 0.47089 | 0.021636 | 0.095033 | 0.073696 | 0.28 | 0 | 0 | 0.42136 | 0.099072 | 0.1786 | 0.33323 | 0.095874 | 0.512 | 1.2041 | 0.03136 | 0.03375 | 0.20608 | 0.35344 | 0.69899 | 0.58781 | 0 | 0.09126 | 0.09126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2682 | 0.00375 | 0.00384 | 0.01935 | 0.046135 | 0.13796 | 0.13553 | 0.20971 | 0.065136 | 0.33966 | 0 | 0.052998 | 0.15131 | 0 |  | 9.4709 | 6.8548 | 2.6161 | 9.4709
14:00 | 0 | 0 | 0.10609 | 0.93409 | 0 | 0.10404 | 0.49729 | 0.015025 | 0.088592 | 0.0846 | 0.27443 | 0 | 0 | 0.42136 | 0.10324 | 0.17322 | 0.34683 | 0.089376 | 0.51842 | 1.1972 | 0.06724 | 0.077976 | 0.23805 | 0.49284 | 0.69899 | 0.58033 | 0 | 0.09126 | 0.09126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2757 | 0.00375 | 0.00384 | 0.01935 | 0.08425 | 0.19366 | 0.20646 | 0.25963 | 0.05908 | 0.33966 | 0 | 0.052998 | 0.19435 | 0 |  | 9.9845 | 7.1092 | 2.8753 | 9.9845
15:00 | 0 | 0 | 0.10404 | 0.98155 | 0 | 0.07396 | 0.42436 | 0.021636 | 0.095033 | 0.0846 | 0.27443 | 0 | 0 | 0.41587 | 0.10324 | 0.1786 | 0.36774 | 0.095874 | 0.53138 | 1.1972 | 0.10816 | 0.16335 | 0.22579 | 0.54756 | 0.69899 | 0.58406 | 0 | 0.088935 | 0.088935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2757 | 0.00375 | 0.00384 | 0.01935 | 0.08425 | 0.19366 | 0.19752 | 0.27294 | 0.05908 | 0.3327 | 0 | 0.052998 | 0.19435 | 0 |  | 10.1454 | 7.2774 | 2.8681 | 10.1454
16:00 | 0 | 0 | 0.11449 | 0.9747 | 0 | 0.07225 | 0.40401 | 0.015025 | 0.088592 | 0.0846 | 0.28 | 0 | 0 | 0.42689 | 0.099072 | 0.17322 | 0.36774 | 0.089376 | 0.53138 | 1.1834 | 0.11664 | 0.20758 | 0.28577 | 0.55696 | 0.69899 | 0.58406 | 0 | 0.093615 | 0.093615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2757 | 0.0063375 | 0.0064896 | 0.049536 | 0.1468 | 0.2629 | 0.30312 | 0.26624 | 0.05908 | 0.3467 | 0 | 0.052998 | 0.20831 | 0 |  | 10.5262 | 7.3547 | 3.1715 | 10.5262
17:00 | 0 | 0 | 0.11236 | 0.9747 | 0 | 0.07225 | 0.4 | 0.021636 | 0.088592 | 0.0846 | 0.27443 | 0 | 0 | 0.42136 | 0.10324 | 0.17322 | 0.36774 | 0.095874 | 0.53138 | 1.1972 | 0.16384 | 0.2646 | 0.26791 | 0.56644 | 0.69458 | 0.58406 | 0 | 0.09126 | 0.09126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2795 | 0.027338 | 0.025958 | 0.1376 | 0.11337 | 0.22696 | 0.25414 | 0.25963 | 0.05908 | 0.33966 | 0 | 0.052998 | 0.21307 | 0 |  | 10.6318 | 7.46 | 3.1719 | 10.6318
18:00 | 0 | 0 | 0.11449 | 0.96107 | 0 | 0.07225 | 0.4 | 0.021636 | 0.1017 | 0.0846 | 0.27443 | 0 | 0 | 0.41587 | 0.099072 | 0.17322 | 0.36071 | 0.089376 | 0.53138 | 1.1834 | 0.17424 | 0.25709 | 0.27677 | 0.56644 | 0.69899 | 0.58033 | 0 | 0.088935 | 0.088935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2833 | 0.027338 | 0.03456 | 0.1376 | 0.12954 | 0.24261 | 0.2677 | 0.26624 | 0.05332 | 0.33966 | 0 | 0.052998 | 0.20831 | 0 |  | 10.6581 | 7.437 | 3.2211 | 10.6581
19:00 | 0 | 0 | 0.10404 | 0.96787 | 0 | 0.06889 | 0.40401 | 0.021636 | 0.088592 | 0.079054 | 0.26891 | 0 | 0 | 0.42136 | 0.10324 | 0.17322 | 0.36774 | 0.089376 | 0.53792 | 1.1903 | 0.16384 | 0.2646 | 0.2178 | 0.54289 | 0.69017 | 0.58781 | 0 | 0.09126 | 0.09126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2757 | 0.0294 | 0.03456 | 0.1376 | 0.10949 | 0.1763 | 0.17742 | 0.25309 | 0.065136 | 0.3327 | 0 | 0.052998 | 0.16788 | 0 |  | 10.3481 | 7.3532 | 2.9949 | 10.3481
20:00 | 0 | 0 | 0.08464 | 0.98499 | 0 | 0.04624 | 0.42025 | 0.015025 | 0.088592 | 0.079054 | 0.24741 | 0 | 0 | 0.42136 | 0.10324 | 0.12402 | 0.35374 | 0.089376 | 0.53138 | 1.0824 | 0.17424 | 0.25709 | 0.19845 | 0.52441 | 0.69899 | 0.58033 | 0 | 0.09126 | 0.09126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.272 | 0.027338 | 0.03456 | 0.1376 | 0.10949 | 0.1096 | 0.1035 | 0.15991 | 0.05908 | 0.31898 | 0 | 0.052998 | 0.12807 | 0 |  | 9.8009 | 7.1052 | 2.6956 | 9.8009
21:00 | 0 | 0 | 0.09025 | 0.98155 | 0 | 0.03136 | 0.28224 | 0.021636 | 0.082377 | 0.05875 | 0.24741 | 0 | 0 | 0.42136 | 0.10324 | 0.039401 | 0.34 | 0.089376 | 0.53138 | 1.0956 | 0.169 | 0.2646 | 0.13005 | 0.53361 | 0.69458 | 0.58406 | 0 | 0.09126 | 0.09126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2833 | 0.010837 | 0.01536 | 0.045494 | 0.10949 | 0.094149 | 0.083259 | 0.13046 | 0.05908 | 0.30555 | 0 | 0.03576 | 0.11718 | 0 |  | 9.2643 | 6.7918 | 2.4725 | 9.2643
22:00 | 0 | 0 | 0.09801 | 0.97812 | 0 | 0.04356 | 0.34969 | 0.015025 | 0.076388 | 0.073696 | 0.25805 | 0 | 0 | 0.41587 | 0.015523 | 0.056129 | 0.34683 | 0.083106 | 0.53138 | 1.1222 | 0.169 | 0.25709 | 0.14258 | 0.52441 | 0.69899 | 0.58033 | 0 | 0.093615 | 0.093615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2833 | 0.0063375 | 0.0031104 | 0.022016 | 0.10568 | 0.11229 | 0.11 | 0.16511 | 0.065136 | 0.31898 | 0 | 0.01521 | 0.13181 | 0 |  | 9.3623 | 6.836 | 2.5262 | 9.3623
23:00 | 0 | 0 | 0.09216 | 0.98155 | 0 | 0.02809 | 0.24964 | 0.021636 | 0.070625 | 0.018424 | 0.24741 | 0 | 0 | 0.42689 | 0 | 0.041984 | 0.33323 | 0.089376 | 0.53792 | 1.0433 | 0.17424 | 0.25709 | 0.12701 | 0.53361 | 0.69458 | 0.58406 | 0 | 0.07776 | 0.07776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2757 | 0.0063375 | 0.00384 | 0.01935 | 0.10568 | 0.084499 | 0.072171 | 0.11685 | 0.065136 | 0.29241 | 0 | 0.01325 | 0.11018 | 0 |  | 8.8738 | 6.5528 | 2.321 | 8.8738
24:00 | 0 | 0 | 0.09801 | 0.97812 | 0 | 0.01369 | 0.07225 | 0.009616 | 0.036612 | 0.011374 | 0.21193 | 0 | 0 | 0.3528 | 0 | 0.023616 | 0.24565 | 0.095874 | 0.38088 | 0.66049 | 0.15876 | 0.22815 | 0.098568 | 0.51984 | 0.63 | 0.58406 | 0 | 0.093615 | 0.093615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.183 | 0.0063375 | 0.00384 | 0.022016 | 0.098269 | 0.04075 | 0.030899 | 0.05096 | 0.065136 | 0.20851 | 0 | 0.011424 | 0.061978 | 0 |  | 7.3807 | 5.4103 | 1.9704 | 7.3807
For Denison 1 & 2:
EMS has only one number for total Generation.
For calculation of GSU losses, total generation
is split evenly across the two units.
This method is conservative, will produce less
than actual losses.

## 062899GSU data
Station | Amistad | Falcon | Ennis Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman
Unit | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1 | 2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6
RPU | 0 | 0 | 0.001 | 0.0003 | 0 | 0.001 | 0.001 | 0.0601 | 0.0113 | 0.0094 | 0.0028 | 0 | 0 | 0.0018 | 0.0043 | 0.0041 | 0.0034 | 0.0114 | 0.002 | 0.001 | 0.004 | 0.0054 | 0.0018 | 0.001 | 0.0007 | 0.0006 | 0 | 0.006 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00766 | 0 | 0.00028 | 0.00375 | 0.00384 | 0.0086 | 0.00337 | 0.00163 | 0.0011 | 0.00416 | 0.01477 | 0.00361 | 0 | 0.00676 | 0.00269 | 0 | 0
MWH actual / 100 = per unit MVA this assumes 0 MVAR's
p.u. MVA / p.u. voltage = p.u. MA assume voltage = 1.0 p.u.
p.u. MA * p.u. MA * RPU * 100 = MW losses
To calculate GSU losses:
Actual MWH gen * Actual MWH gen * RPU / 100

## 072999Gen Data
| Amistad | Falcon | Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman
1999-07-29 | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1&2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6
01:00 | 0 | 0 | 150 | 620 | 23 | 64 | 163 | 4 | 22 | 16 | 89 | 9 | 9 | 127 | 0 | 25 | 71 | 11 | 155 | 331 | 31 | 39 | 103 | 150 | 293 | 78 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 14 | 19 | 653 | 29 | 10 | 15 | 29 | 60 | 61 | 43 | 23 | 86 | 3 | 13 | 54 | 0 | 0
02:00 | 0 | 0 | 133 | 615 | 17 | 55 | 130 | 4 | 19 | 13 | 81 | 9 | 9 | 99 | 0 | 23 | 54 | 9 | 154 | 322 | 30 | 40 | 97 | 131 | 291 | 79 | 614 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 13 | 20 | 652 | 28 | 9 | 15 | 27 | 36 | 47 | 21 | 22 | 59 | 3 | 14 | 41 | 0 | 0
03:00 | 0 | 0 | 107 | 622 | 15 | 41 | 83 | 4 | 15 | 10 | 68 | 8 | 8 | 67 | 0 | 23 | 36 | 10 | 118 | 289 | 36 | 39 | 77 | 106 | 257 | 78 | 627 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 14 | 20 | 648 | 29 | 10 | 16 | 27 | 44 | 48 | 29 | 22 | 70 | 3 | 13 | 45 | 0 | 0
04:00 | 0 | 0 | 100 | 622 | 15 | 37 | 66 | 4 | 13 | 11 | 62 | 10 | 9 | 58 | 0 | 25 | 33 | 10 | 98 | 277 | 35 | 35 | 76 | 97 | 258 | 78 | 613 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 14 | 19 | 645 | 28 | 10 | 15 | 28 | 40 | 48 | 25 | 22 | 71 | 3 | 13 | 43 | 0 | 0
05:00 | 0 | 0 | 80 | 620 | 14 | 35 | 41 | 4 | 10 | 10 | 57 | 9 | 10 | 58 | 0 | 23 | 32 | 11 | 63 | 249 | 35 | 34 | 71 | 78 | 233 | 85 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 13 | 20 | 643 | 28 | 10 | 15 | 28 | 37 | 49 | 22 | 23 | 64 | 3 | 13 | 41 | 0 | 0
06:00 | 0 | 0 | 72 | 571 | 15 | 36 | 37 | 4 | 11 | 10 | 61 | 9 | 9 | 58 | 0 | 23 | 33 | 10 | 46 | 228 | 37 | 34 | 67 | 79 | 216 | 189 | 626 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 13 | 20 | 645 | 29 | 10 | 15 | 28 | 38 | 48 | 21 | 23 | 62 | 3 | 13 | 40 | 0 | 0
07:00 | 0 | 0 | 87 | 618 | 14 | 36 | 46 | 4 | 10 | 17 | 65 | 9 | 9 | 58 | 0 | 25 | 32 | 10 | 59 | 252 | 36 | 35 | 72 | 83 | 228 | 231 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 11 | 18 | 645 | 28 | 10 | 16 | 28 | 42 | 50 | 27 | 22 | 68 | 3 | 13 | 44 | 0 | 0
08:00 | 0 | 0 | 96 | 623 | 14 | 38 | 60 | 4 | 12 | 26 | 69 | 9 | 9 | 58 | 0 | 28 | 43 | 11 | 74 | 263 | 35 | 35 | 74 | 91 | 232 | 276 | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 13 | 20 | 644 | 29 | 10 | 16 | 28 | 63 | 63 | 45 | 23 | 84 | 3 | 14 | 58 | 0 | 0
09:00 | 0 | 0 | 115 | 617 | 13 | 49 | 93 | 4 | 22 | 28 | 75 | 10 | 9 | 74 | 0 | 34 | 43 | 10 | 112 | 291 | 38 | 35 | 81 | 111 | 261 | 300 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 11 | 20 | 645 | 28 | 10 | 16 | 29 | 76 | 84 | 53 | 20 | 93 | 3 | 13 | 65 | 0 | 0
10:00 | 0 | 0 | 139 | 617 | 14 | 61 | 143 | 4 | 26 | 28 | 90 | 9 | 9 | 97 | 0 | 34 | 44 | 10 | 149 | 332 | 29 | 27 | 85 | 133 | 289 | 316 | 618 | 1 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 12 | 19 | 646 | 29 | 9 | 15 | 28 | 84 | 98 | 65 | 21 | 96 | 3 | 12 | 72 | 0 | 0
11:00 | 0 | 0 | 184 | 619 | 22 | 82 | 214 | 3 | 26 | 30 | 99 | 9 | 9 | 118 | 0 | 35 | 80 | 10 | 140 | 309 | 25 | 23 | 92 | 165 | 306 | 316 | 621 | 70 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 11 | 20 | 649 | 27 | 10 | 16 | 28 | 105 | 129 | 77 | 21 | 95 | 4 | 17 | 83 | 0 | 0
12:00 | 0 | 0 | 223 | 618 | 27 | 107 | 227 | 4 | 31 | 29 | 98 | 8 | 9 | 122 | 0 | 38 | 91 | 10 | 138 | 307 | 27 | 33 | 121 | 225 | 306 | 317 | 617 | 70 | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0 | 0 | 0 | 12 | 20 | 649 | 29 | 10 | 16 | 28 | 132 | 170 | 78 | 21 | 97 | 4 | 26 | 90 | 0 | 0
13:00 | 0 | 0 | 229 | 620 | 34 | 69 | 227 | 3 | 30 | 29 | 99 | 9 | 9 | 138 | 0 | 58 | 95 | 14 | 147 | 327 | 41 | 48 | 143 | 234 | 319 | 324 | 616 | 70 | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 0 | 0 | 0 | 13 | 19 | 647 | 28 | 10 | 15 | 36 | 147 | 190 | 79 | 21 | 96 | 3 | 29 | 90 | 0 | 0
14:00 | 0 | 0 | 251 | 618 | 67 | 40 | 228 | 4 | 30 | 29 | 100 | 18 | 10 | 132 | 33 | 64 | 94 | 29 | 148 | 314 | 56 | 57 | 144 | 228 | 331 | 338 | 626 | 70 | 2 | 0 | 0 | 0 | 0 | 18 | 3 | 0 | 0 | 0 | 12 | 19 | 650 | 28 | 10 | 16 | 83 | 147 | 190 | 80 | 21 | 97 | 4 | 30 | 89 | 0 | 7
15:00 | 0 | 0 | 251 | 612 | 70 | 79 | 227 | 3 | 30 | 31 | 97 | 21 | 21 | 139 | 50 | 65 | 95 | 30 | 146 | 335 | 52 | 53 | 146 | 235 | 330 | 340 | 623 | 69 | 8 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 0 | 11 | 20 | 650 | 29 | 10 | 16 | 93 | 146 | 187 | 79 | 20 | 96 | 3 | 32 | 90 | 0 | 8
16:00 | 0 | 0 | 253 | 617 | 69 | 153 | 225 | 4 | 30 | 30 | 98 | 23 | 24 | 146 | 50 | 65 | 99 | 30 | 153 | 340 | 51 | 51 | 143 | 233 | 330 | 338 | 621 | 70 | 8 | 0 | 0 | 0 | 0 | 18 | 1 | 0 | 0 | 0 | 12 | 20 | 659 | 28 | 10 | 14 | 85 | 142 | 185 | 79 | 20 | 98 | 3 | 32 | 90 | 0 | 14
17:00 | 0 | 0 | 252 | 614 | 67 | 154 | 227 | 3 | 29 | 32 | 98 | 23 | 23 | 145 | 50 | 64 | 99 | 29 | 154 | 339 | 58 | 58 | 146 | 238 | 328 | 336 | 625 | 70 | 8 | 0 | 0 | 0 | 0 | 19 | 4 | 0 | 0 | 0 | 12 | 19 | 650 | 29 | 12 | 17 | 95 | 148 | 190 | 79 | 21 | 96 | 3 | 32 | 91 | 0 | 12
18:00 | 0 | 0 | 253 | 616 | 63 | 144 | 227 | 4 | 31 | 31 | 98 | 22 | 23 | 145 | 51 | 65 | 98 | 30 | 150 | 335 | 50 | 50 | 142 | 233 | 330 | 338 | 620 | 69 | 8 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 0 | 0 | 11 | 5 | 652 | 28 | 28 | 35 | 74 | 128 | 166 | 79 | 20 | 98 | 3 | 32 | 88 | 0 | 7
19:00 | 0 | 0 | 252 | 618 | 62 | 110 | 226 | 4 | 30 | 31 | 98 | 23 | 23 | 145 | 51 | 64 | 97 | 29 | 148 | 333 | 33 | 33 | 136 | 217 | 327 | 338 | 613 | 70 | 7 | 0 | 0 | 0 | 0 | 18 | 3 | 0 | 0 | 0 | 12 | 13 | 656 | 29 | 32 | 46 | 63 | 94 | 112 | 72 | 21 | 95 | 4 | 32 | 66 | 0 | 0
20:00 | 0 | 0 | 253 | 620 | 62 | 65 | 226 | 4 | 30 | 30 | 97 | 23 | 23 | 137 | 53 | 65 | 78 | 29 | 148 | 334 | 34 | 33 | 112 | 165 | 330 | 337 | 621 | 69 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 11 | 19 | 659 | 28 | 30 | 45 | 63 | 108 | 136 | 79 | 20 | 97 | 4 | 32 | 79 | 0 | 0
21:00 | 0 | 0 | 226 | 619 | 63 | 73 | 221 | 4 | 30 | 28 | 99 | 23 | 23 | 132 | 31 | 46 | 72 | 27 | 149 | 335 | 32 | 32 | 114 | 168 | 331 | 340 | 622 | 70 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 11 | 17 | 660 | 28 | 27 | 35 | 64 | 106 | 131 | 80 | 21 | 96 | 3 | 32 | 80 | 0 | 0
22:00 | 0 | 0 | 207 | 620 | 62 | 96 | 216 | 4 | 29 | 30 | 99 | 23 | 22 | 145 | 0 | 31 | 96 | 29 | 148 | 335 | 30 | 32 | 132 | 212 | 330 | 339 | 612 | 69 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 15 | 658 | 29 | 10 | 16 | 66 | 115 | 148 | 79 | 21 | 97 | 4 | 32 | 87 | 0 | 0
23:00 | 0 | 0 | 195 | 619 | 48 | 88 | 216 | 4 | 31 | 30 | 98 | 17 | 23 | 143 | 0 | 25 | 91 | 16 | 148 | 334 | 31 | 30 | 126 | 188 | 317 | 321 | 625 | 2 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 15 | 651 | 28 | 10 | 15 | 50 | 111 | 139 | 76 | 22 | 95 | 4 | 32 | 84 | 0 | 0
24:00 | 0 | 0 | 157 | 619 | 19 | 64 | 180 | 4 | 24 | 19 | 95 | 8 | 11 | 134 | 0 | 23 | 75 | 10 | 148 | 332 | 20 | 31 | 107 | 151 | 301 | 309 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 9 | 15 | 650 | 29 | 10 | 14 | 36 | 89 | 111 | 69 | 20 | 96 | 4 | 21 | 75 | 0 | 0
0

## 072999GSU calc
| Amistad | Falcon | Ennis Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman |  | CPL | WTU
1999-07-29 | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1 | 2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6 |  |  | Total | Total | Total | check
01:00 | 0 | 0 | 0.225 | 1.1532 | 0 | 0.04096 | 0.26569 | 0.009616 | 0.054692 | 0.024064 | 0.22179 | 0 | 0 | 0.29032 | 0 | 0.025625 | 0.17139 | 0.013794 | 0.4805 | 1.0956 | 0.03844 | 0.082134 | 0.19096 | 0.225 | 0.60094 | 0.036504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015014 | 0 | 1.1939 | 0.031538 | 0.00384 | 0.01935 | 0.028342 | 0.05868 | 0.040931 | 0.076918 | 0.078133 | 0.267 | 0 | 0.011424 | 0.07844 | 0 |  | 7.1498 | 5.2462 | 1.9036 | 7.1498
02:00 | 0 | 0 | 0.17689 | 1.1347 | 0 | 0.03025 | 0.169 | 0.009616 | 0.040793 | 0.015886 | 0.18371 | 0 | 0 | 0.17642 | 0 | 0.021689 | 0.099144 | 0.009234 | 0.47432 | 1.0368 | 0.036 | 0.0864 | 0.16936 | 0.17161 | 0.59277 | 0.037446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012945 | 0 | 1.1903 | 0.0294 | 0.0031104 | 0.01935 | 0.024567 | 0.021125 | 0.024299 | 0.018346 | 0.071487 | 0.12566 | 0 | 0.01325 | 0.045219 | 0 |  | 6.2711 | 4.672 | 1.5991 | 6.2711
03:00 | 0 | 0 | 0.11449 | 1.1607 | 0 | 0.01681 | 0.06889 | 0.009616 | 0.025425 | 0.0094 | 0.12947 | 0 | 0 | 0.080802 | 0 | 0.021689 | 0.044064 | 0.0114 | 0.27848 | 0.83521 | 0.05184 | 0.082134 | 0.10672 | 0.11236 | 0.46234 | 0.036504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015014 | 0 | 1.1757 | 0.031538 | 0.00384 | 0.022016 | 0.024567 | 0.031557 | 0.025344 | 0.034986 | 0.071487 | 0.17689 | 0 | 0.011424 | 0.054473 | 0 |  | 5.3372 | 3.6583 | 1.6789 | 5.3372
04:00 | 0 | 0 | 0.1 | 1.1607 | 0 | 0.01369 | 0.04356 | 0.009616 | 0.019097 | 0.011374 | 0.10763 | 0 | 0 | 0.060552 | 0 | 0.025625 | 0.037026 | 0.0114 | 0.19208 | 0.76729 | 0.049 | 0.06615 | 0.10397 | 0.09409 | 0.46595 | 0.036504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015014 | 0 | 1.1649 | 0.0294 | 0.00384 | 0.01935 | 0.026421 | 0.02608 | 0.025344 | 0.026 | 0.071487 | 0.18198 | 0 | 0.011424 | 0.049738 | 0 |  | 5.0262 | 3.3753 | 1.6509 | 5.0262
05:00 | 0 | 0 | 0.064 | 1.1532 | 0 | 0.01225 | 0.01681 | 0.009616 | 0.0113 | 0.0094 | 0.090972 | 0 | 0 | 0.060552 | 0 | 0.021689 | 0.034816 | 0.013794 | 0.07938 | 0.62001 | 0.049 | 0.062424 | 0.090738 | 0.06084 | 0.38002 | 0.04335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012945 | 0 | 1.1577 | 0.0294 | 0.00384 | 0.01935 | 0.026421 | 0.022315 | 0.026411 | 0.020134 | 0.078133 | 0.14787 | 0 | 0.011424 | 0.045219 | 0 |  | 4.4853 | 2.8842 | 1.6011 | 4.4853
06:00 | 0 | 0 | 0.05184 | 0.97812 | 0 | 0.01296 | 0.01369 | 0.009616 | 0.013673 | 0.0094 | 0.10419 | 0 | 0 | 0.060552 | 0 | 0.021689 | 0.037026 | 0.0114 | 0.04232 | 0.51984 | 0.05476 | 0.062424 | 0.080802 | 0.06241 | 0.32659 | 0.21433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012945 | 0 | 1.1649 | 0.031538 | 0.00384 | 0.01935 | 0.026421 | 0.023537 | 0.025344 | 0.018346 | 0.078133 | 0.13877 | 0 | 0.011424 | 0.04304 | 0 |  | 4.2852 | 2.6876 | 1.5976 | 4.2852
07:00 | 0 | 0 | 0.07569 | 1.1458 | 0 | 0.01296 | 0.02116 | 0.009616 | 0.0113 | 0.027166 | 0.1183 | 0 | 0 | 0.060552 | 0 | 0.025625 | 0.034816 | 0.0114 | 0.06962 | 0.63504 | 0.05184 | 0.06615 | 0.093312 | 0.06889 | 0.36389 | 0.32017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092686 | 0 | 1.1649 | 0.0294 | 0.00384 | 0.022016 | 0.026421 | 0.028753 | 0.0275 | 0.030326 | 0.071487 | 0.16693 | 0 | 0.011424 | 0.052078 | 0 |  | 4.8676 | 3.2233 | 1.6443 | 4.8676
08:00 | 0 | 0 | 0.09216 | 1.1644 | 0 | 0.01444 | 0.036 | 0.009616 | 0.016272 | 0.063544 | 0.13331 | 0 | 0 | 0.060552 | 0 | 0.032144 | 0.062866 | 0.013794 | 0.10952 | 0.69169 | 0.049 | 0.06615 | 0.098568 | 0.08281 | 0.37677 | 0.45706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012945 | 0 | 1.1613 | 0.031538 | 0.00384 | 0.022016 | 0.026421 | 0.064695 | 0.043659 | 0.08424 | 0.078133 | 0.25472 | 0 | 0.01325 | 0.090492 | 0 |  | 5.5179 | 3.6306 | 1.8872 | 5.5179
09:00 | 0 | 0 | 0.13225 | 1.1421 | 0 | 0.02401 | 0.08649 | 0.009616 | 0.054692 | 0.073696 | 0.1575 | 0 | 0 | 0.098568 | 0 | 0.047396 | 0.062866 | 0.0114 | 0.25088 | 0.84681 | 0.05776 | 0.06615 | 0.1181 | 0.12321 | 0.47685 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092686 | 0 | 1.1649 | 0.0294 | 0.00384 | 0.022016 | 0.028342 | 0.094149 | 0.077616 | 0.11685 | 0.05908 | 0.31223 | 0 | 0.011424 | 0.11365 | 0 |  | 6.423 | 4.3803 | 2.0427 | 6.423
10:00 | 0 | 0 | 0.19321 | 1.1421 | 0 | 0.03721 | 0.20449 | 0.009616 | 0.076388 | 0.073696 | 0.2268 | 0 | 0 | 0.16936 | 0 | 0.047396 | 0.065824 | 0.0114 | 0.44402 | 1.1022 | 0.03364 | 0.039366 | 0.13005 | 0.17689 | 0.58465 | 0.59914 | 0 | 1.5e-05 | 1.5e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01103 | 0 | 1.1685 | 0.031538 | 0.0031104 | 0.01935 | 0.026421 | 0.11501 | 0.10564 | 0.17576 | 0.065136 | 0.3327 | 0 | 0.0097344 | 0.13945 | 0 |  | 7.5708 | 5.3674 | 2.2034 | 7.5708
11:00 | 0 | 0 | 0.33856 | 1.1495 | 0 | 0.06724 | 0.45796 | 0.005409 | 0.076388 | 0.0846 | 0.27443 | 0 | 0 | 0.25063 | 0 | 0.050225 | 0.2176 | 0.0114 | 0.392 | 0.95481 | 0.025 | 0.028566 | 0.15235 | 0.27225 | 0.65545 | 0.59914 | 0 | 0.0735 | 0.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092686 | 0 | 1.1794 | 0.027338 | 0.00384 | 0.022016 | 0.026421 | 0.17971 | 0.18305 | 0.24665 | 0.065136 | 0.3258 | 0 | 0.019536 | 0.18531 | 0 |  | 8.6839 | 6.0635 | 2.6204 | 8.6839
12:00 | 0 | 0 | 0.49729 | 1.1458 | 0 | 0.11449 | 0.51529 | 0.009616 | 0.10859 | 0.079054 | 0.26891 | 0 | 0 | 0.26791 | 0 | 0.059204 | 0.28155 | 0.0114 | 0.38088 | 0.94249 | 0.02916 | 0.058806 | 0.26354 | 0.50625 | 0.65545 | 0.60293 | 0 | 0.0735 | 0.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01103 | 0 | 1.1794 | 0.031538 | 0.00384 | 0.022016 | 0.026421 | 0.28401 | 0.3179 | 0.25309 | 0.065136 | 0.33966 | 0 | 0.045698 | 0.21789 | 0 |  | 9.7432 | 6.7986 | 2.9446 | 9.7432
13:00 | 0 | 0 | 0.52441 | 1.1532 | 0 | 0.04761 | 0.51529 | 0.005409 | 0.1017 | 0.079054 | 0.27443 | 0 | 0 | 0.34279 | 0 | 0.13792 | 0.30685 | 0.022344 | 0.43218 | 1.0693 | 0.06724 | 0.12442 | 0.36808 | 0.54756 | 0.71233 | 0.62986 | 0 | 0.0735 | 0.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012945 | 0 | 1.1721 | 0.0294 | 0.00384 | 0.01935 | 0.043675 | 0.35223 | 0.3971 | 0.25963 | 0.065136 | 0.3327 | 0 | 0.056852 | 0.21789 | 0 |  | 10.5718 | 7.462 | 3.1098 | 10.5718
14:00 | 0 | 0 | 0.63001 | 1.1458 | 0 | 0.016 | 0.51984 | 0.009616 | 0.1017 | 0.079054 | 0.28 | 0 | 0 | 0.31363 | 0.046827 | 0.16794 | 0.30042 | 0.095874 | 0.43808 | 0.98596 | 0.12544 | 0.17545 | 0.37325 | 0.51984 | 0.76693 | 0.68546 | 0 | 0.0735 | 0.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01103 | 0 | 1.183 | 0.0294 | 0.00384 | 0.022016 | 0.23216 | 0.35223 | 0.3971 | 0.26624 | 0.065136 | 0.33966 | 0 | 0.06084 | 0.21307 | 0 |  | 11.0998 | 7.7771 | 3.3227 | 11.0998
15:00 | 0 | 0 | 0.63001 | 1.1236 | 0 | 0.06241 | 0.51529 | 0.005409 | 0.1017 | 0.090334 | 0.26345 | 0 | 0 | 0.34778 | 0.1075 | 0.17322 | 0.30685 | 0.1026 | 0.42632 | 1.1222 | 0.10816 | 0.15169 | 0.38369 | 0.55225 | 0.7623 | 0.6936 | 0 | 0.071415 | 0.071415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092686 | 0 | 1.183 | 0.031538 | 0.00384 | 0.022016 | 0.29147 | 0.34745 | 0.38466 | 0.25963 | 0.05908 | 0.3327 | 0 | 0.069222 | 0.21789 | 0 |  | 11.385 | 8.0304 | 3.3546 | 11.385
16:00 | 0 | 0 | 0.64009 | 1.1421 | 0 | 0.23409 | 0.50625 | 0.009616 | 0.1017 | 0.0846 | 0.26891 | 0 | 0 | 0.38369 | 0.1075 | 0.17322 | 0.33323 | 0.1026 | 0.46818 | 1.156 | 0.10404 | 0.14045 | 0.36808 | 0.54289 | 0.7623 | 0.68546 | 0 | 0.0735 | 0.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01103 | 0 | 1.216 | 0.0294 | 0.00384 | 0.016856 | 0.24348 | 0.32867 | 0.37648 | 0.25963 | 0.05908 | 0.3467 | 0 | 0.069222 | 0.21789 | 0 |  | 11.6402 | 8.315 | 3.3253 | 11.6402
17:00 | 0 | 0 | 0.63504 | 1.131 | 0 | 0.23716 | 0.51529 | 0.005409 | 0.095033 | 0.096256 | 0.26891 | 0 | 0 | 0.37845 | 0.1075 | 0.16794 | 0.33323 | 0.095874 | 0.47432 | 1.1492 | 0.13456 | 0.18166 | 0.38369 | 0.56644 | 0.75309 | 0.67738 | 0 | 0.0735 | 0.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01103 | 0 | 1.183 | 0.031538 | 0.0055296 | 0.024854 | 0.30414 | 0.35704 | 0.3971 | 0.25963 | 0.065136 | 0.3327 | 0 | 0.069222 | 0.22276 | 0 |  | 11.7981 | 8.3874 | 3.4107 | 11.7981
18:00 | 0 | 0 | 0.64009 | 1.1384 | 0 | 0.20736 | 0.51529 | 0.009616 | 0.10859 | 0.090334 | 0.26891 | 0 | 0 | 0.37845 | 0.11184 | 0.17322 | 0.32654 | 0.1026 | 0.45 | 1.1222 | 0.1 | 0.135 | 0.36295 | 0.54289 | 0.7623 | 0.68546 | 0 | 0.071415 | 0.071415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092686 | 0 | 1.1903 | 0.0294 | 0.030106 | 0.10535 | 0.18454 | 0.26706 | 0.30312 | 0.25963 | 0.05908 | 0.3467 | 0 | 0.069222 | 0.20831 | 0 |  | 11.437 | 8.2321 | 3.2049 | 11.437
19:00 | 0 | 0 | 0.63504 | 1.1458 | 0 | 0.121 | 0.51076 | 0.009616 | 0.1017 | 0.090334 | 0.26891 | 0 | 0 | 0.37845 | 0.11184 | 0.16794 | 0.31991 | 0.095874 | 0.43808 | 1.1089 | 0.04356 | 0.058806 | 0.33293 | 0.47089 | 0.7485 | 0.68546 | 0 | 0.0735 | 0.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01103 | 0 | 1.2049 | 0.031538 | 0.039322 | 0.18198 | 0.13376 | 0.14403 | 0.13798 | 0.21565 | 0.065136 | 0.3258 | 0 | 0.069222 | 0.11718 | 0 |  | 10.6688 | 7.8443 | 2.8246 | 10.6688
20:00 | 0 | 0 | 0.64009 | 1.1532 | 0 | 0.04225 | 0.51076 | 0.009616 | 0.1017 | 0.0846 | 0.26345 | 0 | 0 | 0.33784 | 0.12079 | 0.17322 | 0.20686 | 0.095874 | 0.43808 | 1.1156 | 0.04624 | 0.058806 | 0.22579 | 0.27225 | 0.7623 | 0.68141 | 0 | 0.071415 | 0.071415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092686 | 0 | 1.216 | 0.0294 | 0.03456 | 0.17415 | 0.13376 | 0.19012 | 0.20346 | 0.25963 | 0.05908 | 0.33966 | 0 | 0.069222 | 0.16788 | 0 |  | 10.3697 | 7.3407 | 3.029 | 10.3697
21:00 | 0 | 0 | 0.51076 | 1.1495 | 0 | 0.05329 | 0.48841 | 0.009616 | 0.1017 | 0.073696 | 0.27443 | 0 | 0 | 0.31363 | 0.041323 | 0.086756 | 0.17626 | 0.083106 | 0.44402 | 1.1222 | 0.04096 | 0.055296 | 0.23393 | 0.28224 | 0.76693 | 0.6936 | 0 | 0.0735 | 0.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092686 | 0 | 1.2197 | 0.0294 | 0.027994 | 0.10535 | 0.13804 | 0.18315 | 0.18877 | 0.26624 | 0.065136 | 0.3327 | 0 | 0.069222 | 0.17216 | 0 |  | 9.9558 | 7.0017 | 2.9541 | 9.9558
22:00 | 0 | 0 | 0.42849 | 1.1532 | 0 | 0.09216 | 0.46656 | 0.009616 | 0.095033 | 0.0846 | 0.27443 | 0 | 0 | 0.37845 | 0 | 0.039401 | 0.31334 | 0.095874 | 0.43808 | 1.1222 | 0.036 | 0.055296 | 0.31363 | 0.44944 | 0.7623 | 0.68953 | 0 | 0.071415 | 0.071415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00766 | 0 | 1.2123 | 0.031538 | 0.00384 | 0.022016 | 0.1468 | 0.21557 | 0.24094 | 0.25963 | 0.065136 | 0.33966 | 0 | 0.069222 | 0.20361 | 0 |  | 10.2584 | 7.2977 | 2.9607 | 10.2584
23:00 | 0 | 0 | 0.38025 | 1.1495 | 0 | 0.07744 | 0.46656 | 0.009616 | 0.10859 | 0.0846 | 0.26891 | 0 | 0 | 0.36808 | 0 | 0.025625 | 0.28155 | 0.029184 | 0.43808 | 1.1156 | 0.03844 | 0.0486 | 0.28577 | 0.35344 | 0.70342 | 0.61825 | 0 | 6e-05 | 6e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00766 | 0 | 1.1866 | 0.0294 | 0.00384 | 0.01935 | 0.08425 | 0.20083 | 0.21253 | 0.24028 | 0.071487 | 0.3258 | 0 | 0.069222 | 0.18981 | 0 |  | 9.4927 | 6.8515 | 2.6412 | 9.4927
24:00 | 0 | 0 | 0.24649 | 1.1495 | 0 | 0.04096 | 0.324 | 0.009616 | 0.065088 | 0.033934 | 0.2527 | 0 | 0 | 0.32321 | 0 | 0.021689 | 0.19125 | 0.0114 | 0.43808 | 1.1022 | 0.016 | 0.051894 | 0.20608 | 0.22801 | 0.63421 | 0.57289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062046 | 0 | 1.183 | 0.031538 | 0.00384 | 0.016856 | 0.043675 | 0.12911 | 0.13553 | 0.19806 | 0.05908 | 0.3327 | 0 | 0.029812 | 0.15131 | 0 |  | 8.2399 | 5.9192 | 2.3207 | 8.2399
For Denison 1 & 2:
EMS has only one number for total Generation.
For calculation of GSU losses, total generation
is split evenly across the two units.
This method is conservative, will produce less
than actual losses.

## 072999GSU data
Station | Amistad | Falcon | Ennis Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman
Unit | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1 | 2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6
RPU | 0 | 0 | 0.001 | 0.0003 | 0 | 0.001 | 0.001 | 0.0601 | 0.0113 | 0.0094 | 0.0028 | 0 | 0 | 0.0018 | 0.0043 | 0.0041 | 0.0034 | 0.0114 | 0.002 | 0.001 | 0.004 | 0.0054 | 0.0018 | 0.001 | 0.0007 | 0.0006 | 0 | 0.006 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00766 | 0 | 0.00028 | 0.00375 | 0.00384 | 0.0086 | 0.00337 | 0.00163 | 0.0011 | 0.00416 | 0.01477 | 0.00361 | 0 | 0.00676 | 0.00269 | 0 | 0
MWH actual / 100 = per unit MVA this assumes 0 MVAR's
p.u. MVA / p.u. voltage = p.u. MA assume voltage = 1.0 p.u.
p.u. MA * p.u. MA * RPU * 100 = MW losses
To calculate GSU losses:
Actual MWH gen * Actual MWH gen * RPU / 100

## 082699Gen Data
| Amistad | Falcon | Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman | CPL | WTU
1999-08-26 | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1&2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6
01:00 | 0 | 0 | 77 | 622 | 11 | 29 | 44 | 5 | 15 | 10 | 66 | 9 | 10 | 61 | 0 | 24 | 42 | 10 | 73 | 236 | 25 | 26 | 76 | 83 | 214 | 230 | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 20 | 555 | 9 | 10 | 15 | 61 | 37 | 47 | 44 | 22 | 65 | 4 | 13 | 45 | 0 | 0 | 2622 | 956
02:00 | 0 | 0 | 66 | 622 | 12 | 25 | 37 | 6 | 10 | 10 | 45 | 9 | 9 | 56 | 0 | 24 | 34 | 10 | 70 | 160 | 25 | 24 | 57 | 53 | 162 | 134 | 619 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 18 | 557 | 11 | 11 | 15 | 33 | 39 | 49 | 20 | 22 | 53 | 4 | 13 | 46 | 0 | 0 | 2279 | 901
03:00 | 0 | 0 | 67 | 616 | 13 | 25 | 38 | 5 | 9 | 10 | 36 | 10 | 8 | 58 | 0 | 23 | 35 | 10 | 70 | 109 | 25 | 24 | 55 | 53 | 122 | 122 | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 557 | 10 | 9 | 15 | 25 | 39 | 50 | 21 | 22 | 54 | 4 | 13 | 45 | 0 | 0 | 2167 | 893
04:00 | 0 | 0 | 66 | 548 | 11 | 25 | 37 | 6 | 10 | 11 | 35 | 9 | 9 | 58 | 0 | 23 | 36 | 10 | 70 | 93 | 24 | 26 | 56 | 51 | 108 | 119 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 557 | 11 | 11 | 16 | 27 | 38 | 49 | 20 | 22 | 55 | 4 | 14 | 45 | 0 | 0 | 2061 | 898
05:00 | 0 | 0 | 66 | 547 | 10 | 25 | 38 | 5 | 11 | 9 | 35 | 9 | 9 | 57 | 0 | 25 | 35 | 10 | 71 | 89 | 26 | 24 | 55 | 53 | 96 | 121 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 18 | 555 | 10 | 10 | 16 | 25 | 39 | 51 | 20 | 22 | 54 | 5 | 13 | 47 | 0 | 0 | 2049 | 894
06:00 | 0 | 0 | 67 | 550 | 11 | 25 | 38 | 6 | 9 | 11 | 35 | 9 | 9 | 58 | 0 | 23 | 35 | 10 | 69 | 100 | 25 | 26 | 56 | 53 | 113 | 121 | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 19 | 550 | 11 | 10 | 15 | 26 | 39 | 49 | 20 | 22 | 53 | 4 | 13 | 45 | 0 | 0 | 2083 | 885
07:00 | 0 | 0 | 68 | 553 | 12 | 25 | 40 | 5 | 12 | 10 | 41 | 9 | 9 | 57 | 0 | 25 | 36 | 10 | 73 | 176 | 24 | 24 | 62 | 61 | 178 | 123 | 617 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 19 | 537 | 9 | 11 | 16 | 26 | 39 | 49 | 21 | 22 | 56 | 4 | 13 | 46 | 0 | 0 | 2250 | 879
08:00 | 0 | 0 | 73 | 616 | 12 | 26 | 40 | 6 | 13 | 10 | 64 | 8 | 9 | 58 | 0 | 24 | 35 | 9 | 71 | 232 | 25 | 24 | 73 | 79 | 219 | 173 | 619 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 19 | 537 | 11 | 10 | 14 | 26 | 36 | 49 | 20 | 23 | 63 | 4 | 13 | 45 | 0 | 0 | 2518 | 879
09:00 | 0 | 0 | 96 | 621 | 12 | 40 | 70 | 5 | 18 | 11 | 76 | 9 | 8 | 75 | 0 | 24 | 36 | 10 | 85 | 277 | 25 | 26 | 55 | 105 | 252 | 221 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 19 | 535 | 10 | 11 | 16 | 27 | 36 | 49 | 20 | 22 | 74 | 3 | 13 | 50 | 0 | 0 | 2780 | 894
10:00 | 0 | 0 | 106 | 622 | 11 | 44 | 102 | 6 | 20 | 14 | 84 | 8 | 8 | 97 | 0 | 24 | 44 | 10 | 93 | 300 | 25 | 25 | 91 | 118 | 267 | 259 | 628 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 19 | 541 | 10 | 10 | 15 | 26 | 60 | 69 | 43 | 21 | 83 | 3 | 13 | 55 | 0 | 0 | 3006 | 977
11:00 | 0 | 0 | 124 | 624 | 12 | 54 | 131 | 5 | 23 | 19 | 97 | 9 | 9 | 120 | 0 | 24 | 58 | 11 | 103 | 325 | 24 | 25 | 99 | 128 | 286 | 314 | 626 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 19 | 545 | 10 | 10 | 16 | 28 | 78 | 91 | 58 | 21 | 94 | 3 | 13 | 65 | 0 | 0 | 3250 | 1060
12:00 | 0 | 0 | 143 | 620 | 13 | 60 | 160 | 6 | 27 | 22 | 99 | 9 | 9 | 143 | 0 | 26 | 77 | 11 | 114 | 344 | 24 | 26 | 107 | 153 | 307 | 317 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 19 | 544 | 11 | 11 | 15 | 58 | 94 | 114 | 71 | 21 | 96 | 3 | 13 | 74 | 0 | 0 | 3439 | 1153
13:00 | 0 | 0 | 167 | 619 | 12 | 79 | 215 | 5 | 27 | 27 | 99 | 9 | 8 | 151 | 0 | 30 | 93 | 11 | 131 | 343 | 26 | 25 | 120 | 180 | 314 | 312 | 620 | 3 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 544 | 13 | 13 | 20 | 61 | 101 | 132 | 77 | 21 | 96 | 3 | 18 | 79 | 0 | 0 | 3623 | 1210
14:00 | 0 | 0 | 184 | 622 | 13 | 88 | 225 | 6 | 27 | 29 | 100 | 9 | 9 | 151 | 0 | 65 | 98 | 10 | 140 | 343 | 24 | 26 | 125 | 195 | 314 | 313 | 629 | 70 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 19 | 545 | 27 | 29 | 44 | 63 | 95 | 166 | 74 | 20 | 97 | 3 | 30 | 77 | 0 | 0 | 3745 | 1376
15:00 | 0 | 0 | 199 | 623 | 15 | 98 | 226 | 5 | 27 | 31 | 100 | 20 | 12 | 152 | 0 | 65 | 99 | 11 | 151 | 342 | 24 | 27 | 134 | 212 | 315 | 310 | 625 | 71 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 19 | 544 | 31 | 31 | 50 | 82 | 93 | 190 | 76 | 21 | 97 | 3 | 32 | 90 | 0 | 0 | 3823 | 1447
16:00 | 0 | 0 | 195 | 622 | 57 | 97 | 224 | 6 | 27 | 30 | 100 | 22 | 22 | 151 | 0 | 67 | 101 | 24 | 149 | 343 | 53 | 62 | 149 | 236 | 316 | 311 | 620 | 71 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 18 | 543 | 31 | 33 | 50 | 98 | 99 | 190 | 73 | 20 | 97 | 3 | 32 | 90 | 0 | 0 | 3984 | 1465
17:00 | 0 | 0 | 217 | 621 | 67 | 125 | 226 | 5 | 27 | 31 | 99 | 24 | 23 | 152 | 0 | 68 | 105 | 30 | 149 | 343 | 64 | 69 | 151 | 237 | 329 | 319 | 621 | 77 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 19 | 544 | 30 | 30 | 49 | 101 | 104 | 189 | 79 | 20 | 97 | 3 | 32 | 89 | 0 | 0 | 4102 | 1480
18:00 | 0 | 0 | 185 | 623 | 69 | 98 | 224 | 6 | 26 | 31 | 100 | 23 | 23 | 151 | 0 | 69 | 106 | 28 | 150 | 342 | 64 | 70 | 151 | 237 | 331 | 318 | 625 | 76 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 19 | 542 | 31 | 31 | 50 | 100 | 104 | 191 | 74 | 21 | 97 | 3 | 32 | 90 | 0 | 0 | 4050 | 1478
19:00 | 0 | 0 | 174 | 625 | 66 | 82 | 220 | 5 | 28 | 30 | 98 | 22 | 22 | 151 | 0 | 52 | 107 | 19 | 143 | 342 | 55 | 56 | 137 | 215 | 318 | 313 | 612 | 76 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 19 | 542 | 29 | 30 | 51 | 73 | 91 | 130 | 73 | 20 | 96 | 3 | 32 | 70 | 0 | 0 | 3892 | 1352
20:00 | 0 | 0 | 158 | 618 | 64 | 73 | 205 | 6 | 26 | 31 | 99 | 23 | 23 | 151 | 0 | 47 | 91 | 11 | 119 | 341 | 43 | 56 | 113 | 165 | 314 | 314 | 621 | 77 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 19 | 545 | 31 | 31 | 49 | 62 | 92 | 111 | 74 | 20 | 96 | 3 | 32 | 66 | 0 | 0 | 3712 | 1325
21:00 | 0 | 0 | 154 | 620 | 37 | 71 | 191 | 5 | 28 | 31 | 100 | 16 | 21 | 149 | 0 | 24 | 82 | 10 | 121 | 340 | 30 | 40 | 112 | 165 | 313 | 314 | 619 | 75 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 19 | 544 | 23 | 22 | 33 | 61 | 99 | 123 | 79 | 20 | 98 | 3 | 25 | 74 | 0 | 0 | 3593 | 1315
22:00 | 0 | 0 | 141 | 626 | 12 | 65 | 168 | 6 | 26 | 29 | 99 | 8 | 9 | 146 | 0 | 24 | 73 | 10 | 112 | 339 | 21 | 12 | 106 | 151 | 305 | 314 | 621 | 74 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 19 | 544 | 10 | 11 | 17 | 60 | 87 | 103 | 68 | 20 | 96 | 3 | 14 | 67 | 0 | 0 | 3423 | 1210
23:00 | 0 | 0 | 128 | 623 | 10 | 47 | 140 | 5 | 28 | 22 | 98 | 9 | 9 | 132 | 0 | 23 | 68 | 11 | 105 | 246 | 7 | 8 | 100 | 140 | 292 | 315 | 619 | 5 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 19 | 544 | 11 | 10 | 15 | 62 | 84 | 99 | 65 | 19 | 98 | 3 | 13 | 67 | 0 | 0 | 3185 | 1130
24:00 | 0 | 0 | 101 | 624 | 11 | 40 | 57 | 5 | 24 | 13 | 98 | 8 | 9 | 79 | 0 | 23 | 57 | 8 | 95 | 174 | 8 | 8 | 88 | 112 | 233 | 318 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 545 | 10 | 11 | 15 | 57 | 61 | 68 | 45 | 22 | 85 | 3 | 12 | 52 | 0 | 0 | 2815 | 1015
| 0 | 0 | 3022 | 14627 | 573 | 1366 | 3096 | 131 | 498 | 482 | 1903 | 300 | 296 | 2614 | 0 | 846 | 1583 | 304 | 2527 | 6279 | 716 | 759 | 2328 | 3235 | 6018 | 6025 | 14923 | 675 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 454 | 13096 | 400 | 406 | 627 | 1268 | 1684 | 2408 | 1235 | 506 | 1950 | 81 | 461 | 1519 | 0 | 0 | 74451 | 27072

## 082699GSU calc
| Amistad | Falcon | Ennis Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman |  | CPL | WTU
1999-08-26 | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1 | 2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6 |  |  | Total | Total | Total | check
01:00 | 0 | 0 | 0.05929 | 1.1607 | 0 | 0.00841 | 0.01936 | 0.015025 | 0.025425 | 0.0094 | 0.12197 | 0 | 0 | 0.066978 | 0 | 0.023616 | 0.059976 | 0.0114 | 0.10658 | 0.55696 | 0.025 | 0.036504 | 0.10397 | 0.06889 | 0.32057 | 0.3174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86247 | 0.0030375 | 0.00384 | 0.01935 | 0.1254 | 0.022315 | 0.024299 | 0.080538 | 0.071487 | 0.15252 | 0 | 0.011424 | 0.054473 | 0 |  | 4.5485 | 3.1174 | 1.4312 | 4.5485
02:00 | 0 | 0 | 0.04356 | 1.1607 | 0 | 0.00625 | 0.01369 | 0.021636 | 0.0113 | 0.0094 | 0.0567 | 0 | 0 | 0.056448 | 0 | 0.023616 | 0.039304 | 0.0114 | 0.098 | 0.256 | 0.025 | 0.031104 | 0.058482 | 0.02809 | 0.18371 | 0.10774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8687 | 0.0045375 | 0.0046464 | 0.01935 | 0.036699 | 0.024792 | 0.026411 | 0.01664 | 0.071487 | 0.1014 | 0 | 0.011424 | 0.05692 | 0 |  | 3.4851 | 2.2421 | 1.243 | 3.4851
03:00 | 0 | 0 | 0.04489 | 1.1384 | 0 | 0.00625 | 0.01444 | 0.015025 | 0.009153 | 0.0094 | 0.036288 | 0 | 0 | 0.060552 | 0 | 0.021689 | 0.04165 | 0.0114 | 0.098 | 0.11881 | 0.025 | 0.031104 | 0.05445 | 0.02809 | 0.10419 | 0.089304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8687 | 0.00375 | 0.0031104 | 0.01935 | 0.021063 | 0.024792 | 0.0275 | 0.018346 | 0.071487 | 0.10527 | 0 | 0.011424 | 0.054473 | 0 |  | 3.1873 | 1.9581 | 1.2293 | 3.1873
04:00 | 0 | 0 | 0.04356 | 0.90091 | 0 | 0.00625 | 0.01369 | 0.021636 | 0.0113 | 0.011374 | 0.0343 | 0 | 0 | 0.060552 | 0 | 0.021689 | 0.044064 | 0.0114 | 0.098 | 0.08649 | 0.02304 | 0.036504 | 0.056448 | 0.02601 | 0.081648 | 0.084966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8687 | 0.0045375 | 0.0046464 | 0.022016 | 0.024567 | 0.023537 | 0.026411 | 0.01664 | 0.071487 | 0.1092 | 0 | 0.01325 | 0.054473 | 0 |  | 2.9133 | 1.6738 | 1.2395 | 2.9133
05:00 | 0 | 0 | 0.04356 | 0.89763 | 0 | 0.00625 | 0.01444 | 0.015025 | 0.013673 | 0.007614 | 0.0343 | 0 | 0 | 0.058482 | 0 | 0.025625 | 0.04165 | 0.0114 | 0.10082 | 0.07921 | 0.02704 | 0.031104 | 0.05445 | 0.02809 | 0.064512 | 0.087846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86247 | 0.00375 | 0.00384 | 0.022016 | 0.021063 | 0.024792 | 0.028611 | 0.01664 | 0.071487 | 0.10527 | 0 | 0.011424 | 0.059422 | 0 |  | 2.8735 | 1.6427 | 1.2308 | 2.8735
06:00 | 0 | 0 | 0.04489 | 0.9075 | 0 | 0.00625 | 0.01444 | 0.021636 | 0.009153 | 0.011374 | 0.0343 | 0 | 0 | 0.060552 | 0 | 0.021689 | 0.04165 | 0.0114 | 0.09522 | 0.1 | 0.025 | 0.036504 | 0.056448 | 0.02809 | 0.089383 | 0.087846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.847 | 0.0045375 | 0.00384 | 0.01935 | 0.022781 | 0.024792 | 0.026411 | 0.01664 | 0.071487 | 0.1014 | 0 | 0.011424 | 0.054473 | 0 |  | 2.9075 | 1.7033 | 1.2041 | 2.9075
07:00 | 0 | 0 | 0.04624 | 0.91743 | 0 | 0.00625 | 0.016 | 0.015025 | 0.016272 | 0.0094 | 0.047068 | 0 | 0 | 0.058482 | 0 | 0.025625 | 0.044064 | 0.0114 | 0.10658 | 0.30976 | 0.02304 | 0.031104 | 0.069192 | 0.03721 | 0.22179 | 0.090774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80743 | 0.0030375 | 0.0046464 | 0.022016 | 0.022781 | 0.024792 | 0.026411 | 0.018346 | 0.071487 | 0.11321 | 0 | 0.011424 | 0.05692 | 0 |  | 3.2852 | 2.1027 | 1.1825 | 3.2852
08:00 | 0 | 0 | 0.05329 | 1.1384 | 0 | 0.00676 | 0.016 | 0.021636 | 0.019097 | 0.0094 | 0.11469 | 0 | 0 | 0.060552 | 0 | 0.023616 | 0.04165 | 0.009234 | 0.10082 | 0.53824 | 0.025 | 0.031104 | 0.095922 | 0.06241 | 0.33573 | 0.17957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80743 | 0.0045375 | 0.00384 | 0.016856 | 0.022781 | 0.021125 | 0.026411 | 0.01664 | 0.078133 | 0.14328 | 0 | 0.011424 | 0.054473 | 0 |  | 4.09 | 2.8831 | 1.2069 | 4.09
09:00 | 0 | 0 | 0.09216 | 1.1569 | 0 | 0.016 | 0.049 | 0.015025 | 0.036612 | 0.011374 | 0.16173 | 0 | 0 | 0.10125 | 0 | 0.023616 | 0.044064 | 0.0114 | 0.1445 | 0.76729 | 0.025 | 0.036504 | 0.05445 | 0.11025 | 0.44453 | 0.29305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80143 | 0.00375 | 0.0046464 | 0.022016 | 0.024567 | 0.021125 | 0.026411 | 0.01664 | 0.071487 | 0.19768 | 0 | 0.011424 | 0.06725 | 0 |  | 4.8632 | 3.5947 | 1.2684 | 4.8632
10:00 | 0 | 0 | 0.11236 | 1.1607 | 0 | 0.01936 | 0.10404 | 0.021636 | 0.0452 | 0.018424 | 0.19757 | 0 | 0 | 0.16936 | 0 | 0.023616 | 0.065824 | 0.0114 | 0.17298 | 0.9 | 0.025 | 0.03375 | 0.14906 | 0.13924 | 0.49902 | 0.40249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81951 | 0.00375 | 0.00384 | 0.01935 | 0.022781 | 0.05868 | 0.052371 | 0.076918 | 0.065136 | 0.24869 | 0 | 0.011424 | 0.081373 | 0 |  | 5.7348 | 4.271 | 1.4638 | 5.7348
11:00 | 0 | 0 | 0.15376 | 1.1681 | 0 | 0.02916 | 0.17161 | 0.015025 | 0.059777 | 0.033934 | 0.26345 | 0 | 0 | 0.2592 | 0 | 0.023616 | 0.11438 | 0.013794 | 0.21218 | 1.0562 | 0.02304 | 0.03375 | 0.17642 | 0.16384 | 0.57257 | 0.59158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83167 | 0.00375 | 0.00384 | 0.022016 | 0.026421 | 0.099169 | 0.091091 | 0.13994 | 0.065136 | 0.31898 | 0 | 0.011424 | 0.11365 | 0 |  | 6.8625 | 5.1355 | 1.7271 | 6.8625
12:00 | 0 | 0 | 0.20449 | 1.1532 | 0 | 0.036 | 0.256 | 0.021636 | 0.082377 | 0.045496 | 0.27443 | 0 | 0 | 0.36808 | 0 | 0.027716 | 0.20159 | 0.013794 | 0.25992 | 1.1834 | 0.02304 | 0.036504 | 0.20608 | 0.23409 | 0.65974 | 0.60293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82862 | 0.0045375 | 0.0046464 | 0.01935 | 0.11337 | 0.14403 | 0.14296 | 0.20971 | 0.065136 | 0.3327 | 0 | 0.011424 | 0.1473 | 0 |  | 7.9143 | 5.8905 | 2.0238 | 7.9143
13:00 | 0 | 0 | 0.27889 | 1.1495 | 0 | 0.06241 | 0.46225 | 0.015025 | 0.082377 | 0.068526 | 0.27443 | 0 | 0 | 0.41042 | 0 | 0.0369 | 0.29407 | 0.013794 | 0.34322 | 1.1765 | 0.02704 | 0.03375 | 0.2592 | 0.324 | 0.69017 | 0.58406 | 0 | 0.000135 | 0.000135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82862 | 0.0063375 | 0.0064896 | 0.0344 | 0.1254 | 0.16628 | 0.19166 | 0.24665 | 0.065136 | 0.3327 | 0 | 0.021902 | 0.16788 | 0 |  | 8.7802 | 6.5865 | 2.1937 | 8.7802
14:00 | 0 | 0 | 0.33856 | 1.1607 | 0 | 0.07744 | 0.50625 | 0.021636 | 0.082377 | 0.079054 | 0.28 | 0 | 0 | 0.41042 | 0 | 0.17322 | 0.32654 | 0.0114 | 0.392 | 1.1765 | 0.02304 | 0.036504 | 0.28125 | 0.38025 | 0.69017 | 0.58781 | 0 | 0.0735 | 0.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83167 | 0.027338 | 0.032294 | 0.1665 | 0.13376 | 0.14711 | 0.30312 | 0.2278 | 0.05908 | 0.33966 | 0 | 0.06084 | 0.15949 | 0 |  | 9.6707 | 7.0351 | 2.6357 | 9.6707
15:00 | 0 | 0 | 0.39601 | 1.1644 | 0 | 0.09604 | 0.51076 | 0.015025 | 0.082377 | 0.090334 | 0.28 | 0 | 0 | 0.41587 | 0 | 0.17322 | 0.33323 | 0.013794 | 0.45602 | 1.1696 | 0.02304 | 0.039366 | 0.32321 | 0.44944 | 0.69458 | 0.5766 | 0 | 0.075615 | 0.075615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82862 | 0.036038 | 0.036902 | 0.215 | 0.2266 | 0.14098 | 0.3971 | 0.24028 | 0.065136 | 0.33966 | 0 | 0.069222 | 0.21789 | 0 |  | 10.2676 | 7.3029 | 2.9647 | 10.2676
16:00 | 0 | 0 | 0.38025 | 1.1607 | 0 | 0.09409 | 0.50176 | 0.021636 | 0.082377 | 0.0846 | 0.28 | 0 | 0 | 0.41042 | 0 | 0.18405 | 0.34683 | 0.065664 | 0.44402 | 1.1765 | 0.11236 | 0.20758 | 0.39962 | 0.55696 | 0.69899 | 0.58033 | 0 | 0.075615 | 0.075615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82558 | 0.036038 | 0.041818 | 0.215 | 0.32365 | 0.15976 | 0.3971 | 0.22169 | 0.05908 | 0.33966 | 0 | 0.069222 | 0.21789 | 0 |  | 10.8464 | 7.7887 | 3.0577 | 10.8464
17:00 | 0 | 0 | 0.47089 | 1.1569 | 0 | 0.15625 | 0.51076 | 0.015025 | 0.082377 | 0.090334 | 0.27443 | 0 | 0 | 0.41587 | 0 | 0.18958 | 0.37485 | 0.1026 | 0.44402 | 1.1765 | 0.16384 | 0.25709 | 0.41042 | 0.56169 | 0.75769 | 0.61057 | 0 | 0.088935 | 0.088935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82862 | 0.03375 | 0.03456 | 0.20649 | 0.34377 | 0.1763 | 0.39293 | 0.25963 | 0.05908 | 0.33966 | 0 | 0.069222 | 0.21307 | 0 |  | 11.3567 | 8.2217 | 3.135 | 11.3567
18:00 | 0 | 0 | 0.34225 | 1.1644 | 0 | 0.09604 | 0.50176 | 0.021636 | 0.076388 | 0.090334 | 0.28 | 0 | 0 | 0.41042 | 0 | 0.1952 | 0.38202 | 0.089376 | 0.45 | 1.1696 | 0.16384 | 0.2646 | 0.41042 | 0.56169 | 0.76693 | 0.60674 | 0 | 0.08664 | 0.08664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82254 | 0.036038 | 0.036902 | 0.215 | 0.337 | 0.1763 | 0.40129 | 0.2278 | 0.065136 | 0.33966 | 0 | 0.069222 | 0.21789 | 0 |  | 11.1617 | 8.0437 | 3.1181 | 11.1617
19:00 | 0 | 0 | 0.30276 | 1.1719 | 0 | 0.06724 | 0.484 | 0.015025 | 0.088592 | 0.0846 | 0.26891 | 0 | 0 | 0.41042 | 0 | 0.11086 | 0.38927 | 0.041154 | 0.40898 | 1.1696 | 0.121 | 0.16934 | 0.33784 | 0.46225 | 0.70787 | 0.58781 | 0 | 0.08664 | 0.08664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82254 | 0.031538 | 0.03456 | 0.22369 | 0.17959 | 0.13498 | 0.1859 | 0.22169 | 0.05908 | 0.3327 | 0 | 0.069222 | 0.13181 | 0 |  | 10 | 7.3994 | 2.6006 | 10
20:00 | 0 | 0 | 0.24964 | 1.1458 | 0 | 0.05329 | 0.42025 | 0.021636 | 0.076388 | 0.090334 | 0.27443 | 0 | 0 | 0.41042 | 0 | 0.090569 | 0.28155 | 0.013794 | 0.28322 | 1.1628 | 0.07396 | 0.16934 | 0.22984 | 0.27225 | 0.69017 | 0.59158 | 0 | 0.088935 | 0.088935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83167 | 0.036038 | 0.036902 | 0.20649 | 0.12954 | 0.13796 | 0.13553 | 0.2278 | 0.05908 | 0.3327 | 0 | 0.069222 | 0.11718 | 0 |  | 9.0992 | 6.6012 | 2.498 | 9.0992
21:00 | 0 | 0 | 0.23716 | 1.1532 | 0 | 0.05041 | 0.36481 | 0.015025 | 0.088592 | 0.090334 | 0.28 | 0 | 0 | 0.39962 | 0 | 0.023616 | 0.22862 | 0.0114 | 0.29282 | 1.156 | 0.036 | 0.0864 | 0.22579 | 0.27225 | 0.68578 | 0.59158 | 0 | 0.084375 | 0.084375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82862 | 0.019838 | 0.018586 | 0.093654 | 0.1254 | 0.15976 | 0.16642 | 0.25963 | 0.05908 | 0.3467 | 0 | 0.04225 | 0.1473 | 0 |  | 8.7254 | 6.2894 | 2.436 | 8.7254
22:00 | 0 | 0 | 0.19881 | 1.1756 | 0 | 0.04225 | 0.28224 | 0.021636 | 0.076388 | 0.079054 | 0.27443 | 0 | 0 | 0.38369 | 0 | 0.023616 | 0.18119 | 0.0114 | 0.25088 | 1.1492 | 0.01764 | 0.007776 | 0.20225 | 0.22801 | 0.65117 | 0.59158 | 0 | 0.08214 | 0.08214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82862 | 0.00375 | 0.0046464 | 0.024854 | 0.12132 | 0.12337 | 0.1167 | 0.19236 | 0.05908 | 0.3327 | 0 | 0.01325 | 0.12075 | 0 |  | 7.9545 | 5.8488 | 2.1057 | 7.9545
23:00 | 0 | 0 | 0.16384 | 1.1644 | 0 | 0.02209 | 0.196 | 0.015025 | 0.088592 | 0.045496 | 0.26891 | 0 | 0 | 0.31363 | 0 | 0.021689 | 0.15722 | 0.013794 | 0.2205 | 0.60516 | 0.00196 | 0.003456 | 0.18 | 0.196 | 0.59685 | 0.59535 | 0 | 0.000375 | 0.000375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82862 | 0.0045375 | 0.00384 | 0.01935 | 0.12954 | 0.11501 | 0.10781 | 0.17576 | 0.05332 | 0.3467 | 0 | 0.011424 | 0.12075 | 0 |  | 6.7874 | 4.8699 | 1.9174 | 6.7874
24:00 | 0 | 0 | 0.10201 | 1.1681 | 0 | 0.016 | 0.03249 | 0.015025 | 0.065088 | 0.015886 | 0.26891 | 0 | 0 | 0.11234 | 0 | 0.021689 | 0.11047 | 0.007296 | 0.1805 | 0.30276 | 0.00256 | 0.003456 | 0.13939 | 0.12544 | 0.38002 | 0.60674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83167 | 0.00375 | 0.0046464 | 0.01935 | 0.10949 | 0.060652 | 0.050864 | 0.08424 | 0.071487 | 0.26082 | 0 | 0.0097344 | 0.072738 | 0 |  | 5.2556 | 3.6762 | 1.5794 | 5.2556
For Denison 1 & 2:
EMS has only one number for total Generation.
For calculation of GSU losses, total generation
is split evenly across the two units.
This method is conservative, will produce less
than actual losses.

## 082699GSU data
Station | Amistad | Falcon | Ennis Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman
Unit | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1 | 2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6
RPU | 0 | 0 | 0.001 | 0.0003 | 0 | 0.001 | 0.001 | 0.0601 | 0.0113 | 0.0094 | 0.0028 | 0 | 0 | 0.0018 | 0.0043 | 0.0041 | 0.0034 | 0.0114 | 0.002 | 0.001 | 0.004 | 0.0054 | 0.0018 | 0.001 | 0.0007 | 0.0006 | 0 | 0.006 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00766 | 0 | 0.00028 | 0.00375 | 0.00384 | 0.0086 | 0.00337 | 0.00163 | 0.0011 | 0.00416 | 0.01477 | 0.00361 | 0 | 0.00676 | 0.00269 | 0 | 0
MWH actual / 100 = per unit MVA this assumes 0 MVAR's
p.u. MVA / p.u. voltage = p.u. MA assume voltage = 1.0 p.u.
p.u. MA * p.u. MA * RPU * 100 = MW losses
To calculate GSU losses:
Actual MWH gen * Actual MWH gen * RPU / 100

## 090799Gen Data
| Amistad | Falcon | Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman
1999-09-07 | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1&2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6
01:00 | 0 | 0 | 68 | 618 | 12 | 23 | 38 | 4 | 10 | 11 | 47 | 0 | 0 | 57 | 0 | 23 | 30 | 0 | 72 | 222 | 25 | 22 | 66 | 66 | 204 | 200 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 15 | 72 | 38 | 46 | 24 | 22 | 71 | 4 | 13 | 41 | 0 | 0
02:00 | 0 | 0 | 66 | 621 | 9 | 22 | 39 | 5 | 10 | 10 | 38 | 0 | 0 | 56 | 0 | 25 | 31 | 0 | 71 | 195 | 25 | 24 | 58 | 52 | 187 | 117 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 0 | 0 | 15 | 71 | 35 | 47 | 20 | 22 | 63 | 3 | 13 | 40 | 0 | 0
03:00 | 0 | 0 | 66 | 624 | 11 | 22 | 37 | 4 | 10 | 10 | 36 | 0 | 0 | 56 | 0 | 22 | 30 | 0 | 69 | 160 | 24 | 22 | 55 | 52 | 170 | 94 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548 | 0 | 0 | 15 | 58 | 35 | 46 | 20 | 22 | 58 | 4 | 13 | 40 | 0 | 0
04:00 | 0 | 0 | 65 | 621 | 13 | 22 | 38 | 5 | 10 | 11 | 34 | 0 | 0 | 57 | 0 | 24 | 31 | 0 | 71 | 129 | 25 | 23 | 56 | 52 | 141 | 90 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 15 | 25 | 35 | 47 | 21 | 22 | 55 | 3 | 13 | 40 | 0 | 0
05:00 | 0 | 0 | 48 | 624 | 11 | 22 | 37 | 4 | 9 | 10 | 35 | 0 | 0 | 56 | 0 | 24 | 30 | 0 | 70 | 125 | 25 | 23 | 55 | 51 | 135 | 91 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 14 | 26 | 37 | 46 | 20 | 23 | 53 | 3 | 12 | 40 | 0 | 0
06:00 | 0 | 0 | 48 | 623 | 11 | 22 | 39 | 5 | 10 | 10 | 36 | 0 | 0 | 56 | 0 | 23 | 30 | 0 | 70 | 152 | 25 | 23 | 56 | 53 | 158 | 90 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 0 | 0 | 15 | 25 | 37 | 47 | 20 | 21 | 58 | 4 | 13 | 41 | 0 | 0
07:00 | 0 | 0 | 47 | 626 | 11 | 24 | 39 | 4 | 10 | 10 | 37 | 0 | 0 | 58 | 0 | 23 | 31 | 0 | 72 | 191 | 25 | 22 | 60 | 59 | 192 | 93 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 15 | 25 | 42 | 48 | 28 | 23 | 70 | 3 | 14 | 46 | 0 | 0
08:00 | 0 | 0 | 61 | 624 | 1 | 24 | 39 | 5 | 11 | 10 | 56 | 0 | 0 | 56 | 0 | 25 | 30 | 0 | 72 | 213 | 24 | 23 | 67 | 65 | 206 | 172 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 15 | 27 | 45 | 47 | 29 | 22 | 74 | 3 | 13 | 46 | 0 | 0
09:00 | 0 | 0 | 73 | 619 | 0 | 27 | 38 | 4 | 13 | 10 | 63 | 0 | 0 | 59 | 0 | 24 | 32 | 0 | 72 | 230 | 25 | 26 | 73 | 75 | 216 | 221 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 0 | 0 | 15 | 25 | 67 | 75 | 52 | 22 | 88 | 3 | 13 | 60 | 0 | 0
10:00 | 0 | 0 | 88 | 621 | 0 | 34 | 57 | 4 | 14 | 10 | 70 | 0 | 0 | 60 | 0 | 25 | 36 | 0 | 76 | 250 | 25 | 24 | 77 | 88 | 229 | 258 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 0 | 0 | 15 | 31 | 82 | 95 | 61 | 22 | 96 | 4 | 13 | 69 | 0 | 0
11:00 | 0 | 0 | 108 | 622 | 0 | 45 | 93 | 4 | 19 | 13 | 90 | 0 | 0 | 79 | 0 | 24 | 46 | 0 | 87 | 280 | 24 | 26 | 84 | 106 | 251 | 301 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 14 | 35 | 87 | 106 | 69 | 21 | 95 | 3 | 13 | 72 | 0 | 0
12:00 | 0 | 0 | 130 | 617 | 0 | 58 | 134 | 4 | 21 | 16 | 97 | 0 | 0 | 109 | 0 | 24 | 73 | 0 | 98 | 316 | 25 | 26 | 97 | 129 | 280 | 314 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548 | 0 | 0 | 15 | 45 | 101 | 125 | 77 | 20 | 96 | 4 | 25 | 80 | 0 | 0
13:00 | 0 | 0 | 174 | 615 | 0 | 86 | 211 | 4 | 27 | 23 | 98 | 0 | 0 | 154 | 0 | 33 | 94 | 0 | 133 | 346 | 43 | 27 | 119 | 180 | 315 | 314 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548 | 0 | 0 | 15 | 63 | 125 | 151 | 80 | 21 | 97 | 3 | 31 | 58 | 0 | 0
14:00 | 0 | 0 | 205 | 620 | 7 | 103 | 222 | 4 | 27 | 27 | 99 | 0 | 0 | 155 | 0 | 42 | 99 | 0 | 149 | 347 | 55 | 44 | 137 | 219 | 315 | 319 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547 | 0 | 0 | 27 | 83 | 143 | 184 | 81 | 21 | 96 | 3 | 32 | 40 | 0 | 0
15:00 | 0 | 0 | 202 | 621 | 23 | 115 | 223 | 4 | 28 | 28 | 99 | 0 | 0 | 153 | 0 | 51 | 98 | 0 | 150 | 346 | 63 | 67 | 140 | 222 | 319 | 326 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546 | 0 | 0 | 42 | 78 | 136 | 185 | 80 | 21 | 97 | 4 | 32 | 54 | 0 | 0
16:00 | 0 | 0 | 221 | 622 | 50 | 125 | 223 | 4 | 27 | 28 | 98 | 0 | 0 | 154 | 0 | 57 | 99 | 0 | 150 | 346 | 63 | 69 | 145 | 230 | 302 | 313 | 620 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549 | 0 | 0 | 25 | 71 | 122 | 173 | 79 | 20 | 96 | 3 | 32 | 87 | 0 | 0
17:00 | 0 | 0 | 226 | 620 | 64 | 128 | 223 | 4 | 28 | 28 | 99 | 0 | 0 | 155 | 0 | 56 | 97 | 0 | 149 | 345 | 62 | 69 | 146 | 231 | 298 | 314 | 621 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 25 | 66 | 127 | 166 | 80 | 21 | 96 | 3 | 32 | 88 | 0 | 0
18:00 | 0 | 0 | 226 | 622 | 65 | 114 | 223 | 5 | 28 | 27 | 99 | 0 | 0 | 154 | 0 | 54 | 98 | 0 | 150 | 345 | 62 | 70 | 146 | 230 | 298 | 308 | 620 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548 | 0 | 0 | 25 | 58 | 109 | 142 | 79 | 19 | 97 | 4 | 31 | 78 | 0 | 0
19:00 | 0 | 0 | 214 | 622 | 65 | 116 | 221 | 4 | 27 | 29 | 98 | 0 | 0 | 154 | 0 | 49 | 97 | 0 | 150 | 345 | 63 | 69 | 138 | 220 | 299 | 304 | 622 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549 | 0 | 0 | 25 | 70 | 123 | 161 | 79 | 21 | 96 | 4 | 32 | 83 | 0 | 0
20:00 | 0 | 0 | 147 | 622 | 64 | 60 | 167 | 5 | 27 | 23 | 96 | 0 | 0 | 154 | 0 | 22 | 86 | 0 | 122 | 344 | 62 | 62 | 103 | 146 | 298 | 304 | 621 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549 | 0 | 0 | 25 | 61 | 95 | 125 | 73 | 21 | 95 | 3 | 31 | 66 | 0 | 0
21:00 | 0 | 0 | 163 | 623 | 66 | 73 | 198 | 4 | 26 | 22 | 98 | 0 | 0 | 154 | 0 | 27 | 91 | 0 | 133 | 346 | 62 | 34 | 114 | 170 | 301 | 301 | 621 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 0 | 0 | 24 | 59 | 102 | 119 | 78 | 21 | 96 | 4 | 31 | 75 | 0 | 0
22:00 | 0 | 0 | 157 | 623 | 66 | 68 | 184 | 5 | 26 | 20 | 98 | 0 | 0 | 145 | 0 | 24 | 88 | 0 | 131 | 345 | 60 | 25 | 111 | 162 | 246 | 296 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552 | 0 | 0 | 17 | 41 | 97 | 120 | 76 | 21 | 96 | 3 | 15 | 74 | 0 | 0
23:00 | 0 | 0 | 154 | 622 | 67 | 65 | 167 | 4 | 23 | 12 | 93 | 0 | 0 | 135 | 0 | 26 | 94 | 0 | 133 | 345 | 27 | 25 | 110 | 162 | 125 | 290 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 0 | 0 | 15 | 37 | 92 | 112 | 70 | 21 | 96 | 3 | 13 | 72 | 0 | 0
24:00 | 0 | 0 | 129 | 623 | 65 | 42 | 103 | 4 | 20 | 10 | 74 | 0 | 0 | 99 | 0 | 24 | 91 | 0 | 109 | 326 | 9 | 25 | 95 | 128 | 122 | 289 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 0 | 0 | 14 | 27 | 76 | 89 | 52 | 21 | 91 | 3 | 13 | 63 | 0 | 0
0

## 090799GSU calc
| Amistad | Falcon | Ennis Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman |  | CPL | WTU
1999-09-07 | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1 | 2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6 |  |  | Total | Total | Total | check
01:00 | 0 | 0 | 0.04624 | 1.1458 | 0 | 0.00529 | 0.01444 | 0.009616 | 0.0113 | 0.011374 | 0.061852 | 0 | 0 | 0.058482 | 0 | 0.021689 | 0.0306 | 0 | 0.10368 | 0.49284 | 0.025 | 0.026136 | 0.078408 | 0.04356 | 0.29131 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0.01935 | 0.1747 | 0.023537 | 0.023276 | 0.023962 | 0.071487 | 0.18198 | 0 | 0.011424 | 0.045219 | 0 |  | 4.1395 | 2.7176 | 1.4219 | 4.1395
02:00 | 0 | 0 | 0.04356 | 1.1569 | 0 | 0.00484 | 0.01521 | 0.015025 | 0.0113 | 0.0094 | 0.040432 | 0 | 0 | 0.056448 | 0 | 0.025625 | 0.032674 | 0 | 0.10082 | 0.38025 | 0.025 | 0.031104 | 0.060552 | 0.02704 | 0.24478 | 0.082134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85008 | 0 | 0 | 0.01935 | 0.16988 | 0.019967 | 0.024299 | 0.01664 | 0.071487 | 0.14328 | 0 | 0.011424 | 0.04304 | 0 |  | 3.7326 | 2.3631 | 1.3695 | 3.7326
03:00 | 0 | 0 | 0.04356 | 1.1681 | 0 | 0.00484 | 0.01369 | 0.009616 | 0.0113 | 0.0094 | 0.036288 | 0 | 0 | 0.056448 | 0 | 0.019844 | 0.0306 | 0 | 0.09522 | 0.256 | 0.02304 | 0.026136 | 0.05445 | 0.02704 | 0.2023 | 0.053016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84085 | 0 | 0 | 0.01935 | 0.11337 | 0.019967 | 0.023276 | 0.01664 | 0.071487 | 0.12144 | 0 | 0.011424 | 0.04304 | 0 |  | 3.4218 | 2.1409 | 1.2808 | 3.4218
04:00 | 0 | 0 | 0.04225 | 1.1569 | 0 | 0.00484 | 0.01444 | 0.015025 | 0.0113 | 0.011374 | 0.032368 | 0 | 0 | 0.058482 | 0 | 0.023616 | 0.032674 | 0 | 0.10082 | 0.16641 | 0.025 | 0.028566 | 0.056448 | 0.02704 | 0.13917 | 0.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0.01935 | 0.021063 | 0.019967 | 0.024299 | 0.018346 | 0.071487 | 0.1092 | 0 | 0.011424 | 0.04304 | 0 |  | 3.1805 | 1.9953 | 1.1852 | 3.1805
05:00 | 0 | 0 | 0.02304 | 1.1681 | 0 | 0.00484 | 0.01369 | 0.009616 | 0.009153 | 0.0094 | 0.0343 | 0 | 0 | 0.056448 | 0 | 0.023616 | 0.0306 | 0 | 0.098 | 0.15625 | 0.025 | 0.028566 | 0.05445 | 0.02601 | 0.12757 | 0.049686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0.016856 | 0.022781 | 0.022315 | 0.023276 | 0.01664 | 0.078133 | 0.1014 | 0 | 0.0097344 | 0.04304 | 0 |  | 3.1295 | 1.9484 | 1.1812 | 3.1295
06:00 | 0 | 0 | 0.02304 | 1.1644 | 0 | 0.00484 | 0.01521 | 0.015025 | 0.0113 | 0.0094 | 0.036288 | 0 | 0 | 0.056448 | 0 | 0.021689 | 0.0306 | 0 | 0.098 | 0.23104 | 0.025 | 0.028566 | 0.056448 | 0.02809 | 0.17475 | 0.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85008 | 0 | 0 | 0.01935 | 0.021063 | 0.022315 | 0.024299 | 0.01664 | 0.065136 | 0.12144 | 0 | 0.011424 | 0.045219 | 0 |  | 3.2757 | 2.0787 | 1.197 | 3.2757
07:00 | 0 | 0 | 0.02209 | 1.1756 | 0 | 0.00576 | 0.01521 | 0.009616 | 0.0113 | 0.0094 | 0.038332 | 0 | 0 | 0.060552 | 0 | 0.021689 | 0.032674 | 0 | 0.10368 | 0.36481 | 0.025 | 0.026136 | 0.0648 | 0.03481 | 0.25805 | 0.051894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0.01935 | 0.021063 | 0.028753 | 0.025344 | 0.032614 | 0.078133 | 0.17689 | 0 | 0.01325 | 0.05692 | 0 |  | 3.6307 | 2.3314 | 1.2993 | 3.6307
08:00 | 0 | 0 | 0.03721 | 1.1681 | 0 | 0.00576 | 0.01521 | 0.015025 | 0.013673 | 0.0094 | 0.087808 | 0 | 0 | 0.056448 | 0 | 0.025625 | 0.0306 | 0 | 0.10368 | 0.45369 | 0.02304 | 0.028566 | 0.080802 | 0.04225 | 0.29705 | 0.1775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0.01935 | 0.024567 | 0.033008 | 0.024299 | 0.034986 | 0.071487 | 0.19768 | 0 | 0.011424 | 0.05692 | 0 |  | 3.9922 | 2.6715 | 1.3207 | 3.9922
09:00 | 0 | 0 | 0.05329 | 1.1495 | 0 | 0.00729 | 0.01444 | 0.009616 | 0.019097 | 0.0094 | 0.11113 | 0 | 0 | 0.062658 | 0 | 0.023616 | 0.034816 | 0 | 0.10368 | 0.529 | 0.025 | 0.036504 | 0.095922 | 0.05625 | 0.32659 | 0.29305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85008 | 0 | 0 | 0.01935 | 0.021063 | 0.073171 | 0.061875 | 0.11249 | 0.071487 | 0.27956 | 0 | 0.011424 | 0.09684 | 0 |  | 4.5582 | 2.9608 | 1.5973 | 4.5582
10:00 | 0 | 0 | 0.07744 | 1.1569 | 0 | 0.01156 | 0.03249 | 0.009616 | 0.022148 | 0.0094 | 0.1372 | 0 | 0 | 0.0648 | 0 | 0.025625 | 0.044064 | 0 | 0.11552 | 0.625 | 0.025 | 0.031104 | 0.10672 | 0.07744 | 0.36709 | 0.39938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85008 | 0 | 0 | 0.01935 | 0.032386 | 0.1096 | 0.099275 | 0.15479 | 0.071487 | 0.3327 | 0 | 0.011424 | 0.12807 | 0 |  | 5.1477 | 3.3385 | 1.8092 | 5.1477
11:00 | 0 | 0 | 0.11664 | 1.1607 | 0 | 0.02025 | 0.08649 | 0.009616 | 0.040793 | 0.015886 | 0.2268 | 0 | 0 | 0.11234 | 0 | 0.023616 | 0.071944 | 0 | 0.15138 | 0.784 | 0.02304 | 0.036504 | 0.12701 | 0.11236 | 0.44101 | 0.54361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0.016856 | 0.041282 | 0.12337 | 0.1236 | 0.19806 | 0.065136 | 0.3258 | 0 | 0.011424 | 0.13945 | 0 |  | 5.9959 | 4.1039 | 1.892 | 5.9959
12:00 | 0 | 0 | 0.169 | 1.1421 | 0 | 0.03364 | 0.17956 | 0.009616 | 0.049833 | 0.024064 | 0.26345 | 0 | 0 | 0.21386 | 0 | 0.023616 | 0.18119 | 0 | 0.19208 | 0.99856 | 0.025 | 0.036504 | 0.16936 | 0.16641 | 0.5488 | 0.59158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84085 | 0 | 0 | 0.01935 | 0.068242 | 0.16628 | 0.17188 | 0.24665 | 0.05908 | 0.3327 | 0 | 0.04225 | 0.17216 | 0 |  | 7.1376 | 5.0182 | 2.1194 | 7.1376
13:00 | 0 | 0 | 0.30276 | 1.1347 | 0 | 0.07396 | 0.44521 | 0.009616 | 0.082377 | 0.049726 | 0.26891 | 0 | 0 | 0.42689 | 0 | 0.044649 | 0.30042 | 0 | 0.35378 | 1.1972 | 0.07396 | 0.039366 | 0.2549 | 0.324 | 0.69458 | 0.59158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84085 | 0 | 0 | 0.01935 | 0.13376 | 0.25469 | 0.25081 | 0.26624 | 0.065136 | 0.33966 | 0 | 0.064964 | 0.090492 | 0 |  | 8.9945 | 6.6685 | 2.326 | 8.9945
14:00 | 0 | 0 | 0.42025 | 1.1532 | 0 | 0.10609 | 0.49284 | 0.009616 | 0.082377 | 0.068526 | 0.27443 | 0 | 0 | 0.43245 | 0 | 0.072324 | 0.33323 | 0 | 0.44402 | 1.2041 | 0.121 | 0.10454 | 0.33784 | 0.47961 | 0.69458 | 0.61057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83779 | 0 | 0 | 0.062694 | 0.23216 | 0.33332 | 0.37242 | 0.27294 | 0.065136 | 0.3327 | 0 | 0.069222 | 0.04304 | 0 |  | 10.063 | 7.4416 | 2.6214 | 10.063
15:00 | 0 | 0 | 0.40804 | 1.1569 | 0 | 0.13225 | 0.49729 | 0.009616 | 0.088592 | 0.073696 | 0.27443 | 0 | 0 | 0.42136 | 0 | 0.10664 | 0.32654 | 0 | 0.45 | 1.1972 | 0.15876 | 0.24241 | 0.3528 | 0.49284 | 0.71233 | 0.63766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83472 | 0 | 0 | 0.1517 | 0.20503 | 0.30148 | 0.37648 | 0.26624 | 0.065136 | 0.33966 | 0 | 0.069222 | 0.07844 | 0 |  | 10.4274 | 7.7393 | 2.6881 | 10.4274
16:00 | 0 | 0 | 0.48841 | 1.1607 | 0 | 0.15625 | 0.49729 | 0.009616 | 0.082377 | 0.073696 | 0.26891 | 0 | 0 | 0.42689 | 0 | 0.13321 | 0.33323 | 0 | 0.45 | 1.1972 | 0.15876 | 0.25709 | 0.37845 | 0.529 | 0.63843 | 0.58781 | 0 | 1.5e-05 | 1.5e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84392 | 0 | 0 | 0.05375 | 0.16988 | 0.24261 | 0.32922 | 0.25963 | 0.05908 | 0.3327 | 0 | 0.069222 | 0.20361 | 0 |  | 10.3909 | 7.8272 | 2.5636 | 10.3909
17:00 | 0 | 0 | 0.51076 | 1.1532 | 0 | 0.16384 | 0.49729 | 0.009616 | 0.088592 | 0.073696 | 0.27443 | 0 | 0 | 0.43245 | 0 | 0.12858 | 0.31991 | 0 | 0.44402 | 1.1903 | 0.15376 | 0.25709 | 0.38369 | 0.53361 | 0.62163 | 0.59158 | 0 | 0.071415 | 0.071415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0.05375 | 0.1468 | 0.2629 | 0.30312 | 0.26624 | 0.065136 | 0.3327 | 0 | 0.069222 | 0.20831 | 0 |  | 10.526 | 7.828 | 2.698 | 10.526
18:00 | 0 | 0 | 0.51076 | 1.1607 | 0 | 0.12996 | 0.49729 | 0.015025 | 0.088592 | 0.068526 | 0.27443 | 0 | 0 | 0.42689 | 0 | 0.11956 | 0.32654 | 0 | 0.45 | 1.1903 | 0.15376 | 0.2646 | 0.38369 | 0.529 | 0.62163 | 0.56918 | 0 | 0.075615 | 0.075615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84085 | 0 | 0 | 0.05375 | 0.11337 | 0.19366 | 0.2218 | 0.25963 | 0.05332 | 0.33966 | 0 | 0.064964 | 0.16366 | 0 |  | 10.2362 | 7.7803 | 2.4559 | 10.2362
19:00 | 0 | 0 | 0.45796 | 1.1607 | 0 | 0.13456 | 0.48841 | 0.009616 | 0.082377 | 0.079054 | 0.26891 | 0 | 0 | 0.42689 | 0 | 0.098441 | 0.31991 | 0 | 0.45 | 1.1903 | 0.15876 | 0.25709 | 0.34279 | 0.484 | 0.62581 | 0.5545 | 0 | 0.067335 | 0.067335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84392 | 0 | 0 | 0.05375 | 0.16513 | 0.2466 | 0.28513 | 0.25963 | 0.065136 | 0.3327 | 0 | 0.069222 | 0.18531 | 0 |  | 10.2312 | 7.59 | 2.6412 | 10.2312
20:00 | 0 | 0 | 0.21609 | 1.1607 | 0 | 0.036 | 0.27889 | 0.015025 | 0.082377 | 0.049726 | 0.25805 | 0 | 0 | 0.42689 | 0 | 0.019844 | 0.25146 | 0 | 0.29768 | 1.1834 | 0.15376 | 0.20758 | 0.19096 | 0.21316 | 0.62163 | 0.5545 | 0 | 0.071415 | 0.071415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84392 | 0 | 0 | 0.05375 | 0.1254 | 0.14711 | 0.17188 | 0.22169 | 0.065136 | 0.3258 | 0 | 0.064964 | 0.11718 | 0 |  | 8.4973 | 6.2176 | 2.2796 | 8.4973
21:00 | 0 | 0 | 0.26569 | 1.1644 | 0 | 0.05329 | 0.39204 | 0.009616 | 0.076388 | 0.045496 | 0.26891 | 0 | 0 | 0.42689 | 0 | 0.029889 | 0.28155 | 0 | 0.35378 | 1.1972 | 0.15376 | 0.062424 | 0.23393 | 0.289 | 0.63421 | 0.54361 | 0 | 0.000135 | 0.000135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85008 | 0 | 0 | 0.049536 | 0.11731 | 0.16959 | 0.15577 | 0.25309 | 0.065136 | 0.3327 | 0 | 0.064964 | 0.15131 | 0 |  | 8.6918 | 6.482 | 2.2098 | 8.6918
22:00 | 0 | 0 | 0.24649 | 1.1644 | 0 | 0.04624 | 0.33856 | 0.015025 | 0.076388 | 0.0376 | 0.26891 | 0 | 0 | 0.37845 | 0 | 0.023616 | 0.2633 | 0 | 0.34322 | 1.1903 | 0.144 | 0.03375 | 0.22178 | 0.26244 | 0.42361 | 0.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85317 | 0 | 0 | 0.024854 | 0.05665 | 0.15337 | 0.1584 | 0.24028 | 0.065136 | 0.3327 | 0 | 0.01521 | 0.1473 | 0 |  | 8.0508 | 6.0037 | 2.0471 | 8.0508
23:00 | 0 | 0 | 0.23716 | 1.1607 | 0 | 0.04225 | 0.27889 | 0.009616 | 0.059777 | 0.013536 | 0.24217 | 0 | 0 | 0.32805 | 0 | 0.027716 | 0.30042 | 0 | 0.35378 | 1.1903 | 0.02916 | 0.03375 | 0.2178 | 0.26244 | 0.10938 | 0.5046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85008 | 0 | 0 | 0.01935 | 0.046135 | 0.13796 | 0.13798 | 0.20384 | 0.065136 | 0.3327 | 0 | 0.011424 | 0.13945 | 0 |  | 7.3455 | 5.4014 | 1.9441 | 7.3455
24:00 | 0 | 0 | 0.16641 | 1.1644 | 0 | 0.01764 | 0.10609 | 0.009616 | 0.0452 | 0.0094 | 0.15333 | 0 | 0 | 0.17642 | 0 | 0.023616 | 0.28155 | 0 | 0.23762 | 1.0628 | 0.00324 | 0.03375 | 0.16245 | 0.16384 | 0.10419 | 0.50113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85627 | 0 | 0 | 0.016856 | 0.024567 | 0.094149 | 0.087131 | 0.11249 | 0.065136 | 0.29894 | 0 | 0.011424 | 0.10677 | 0 |  | 6.0964 | 4.4226 | 1.6737 | 6.0964
For Denison 1 & 2:
EMS has only one number for total Generation.
For calculation of GSU losses, total generation
is split evenly across the two units.
This method is conservative, will produce less
than actual losses.

## 090799GSU data
Station | Amistad | Falcon | Ennis Joslin | Coleto | Victoria | Victoria | Victoria | Eagle Pass | Laredo | Laredo | Laredo | La Palma | La Palma | La Palma | La Palma | Bates | Bates | Nueces Bay | Nueces Bay | Nueces Bay | Lon Hill | Lon Hill | Lon Hill | Lon Hill | Davis | Davis | STP | Denison | Denison | Vernon | Vernon | Vernon | Vernon | Vernon | Abilene | Fort Stockton | Presidio | Presidio | Presidio | Pauline | Pauline | Oklaunion | Paint Creek | Paint Creek | Paint Creek | Paint Creek | Fort Phantom | Fort Phantom | Oak Creek | San Angelo | San Angelo | Rio Pecos | Rio Pecos | Rio Pecos | NEDIN138 | EColeman
Unit | 1 | 1 | 1 | 1 | 4 | 5 | 6 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 1 | 2 | 1&2 | 1 | 2 | 1 | 2 | 3 | 4 | 7 | 4 | 2 | 1 | 5 | 6 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 6
RPU | 0 | 0 | 0.001 | 0.0003 | 0 | 0.001 | 0.001 | 0.0601 | 0.0113 | 0.0094 | 0.0028 | 0 | 0 | 0.0018 | 0.0043 | 0.0041 | 0.0034 | 0.0114 | 0.002 | 0.001 | 0.004 | 0.0054 | 0.0018 | 0.001 | 0.0007 | 0.0006 | 0 | 0.006 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00766 | 0 | 0.00028 | 0.00375 | 0.00384 | 0.0086 | 0.00337 | 0.00163 | 0.0011 | 0.00416 | 0.01477 | 0.00361 | 0 | 0.00676 | 0.00269 | 0 | 0
MWH actual / 100 = per unit MVA this assumes 0 MVAR's
p.u. MVA / p.u. voltage = p.u. MA assume voltage = 1.0 p.u.
p.u. MA * p.u. MA * RPU * 100 = MW losses
To calculate GSU losses:
Actual MWH gen * Actual MWH gen * RPU / 100