## June19, 1998 @ 1700
| Generator Output @ Generator Terminals Gross MW | Generator Output @ Generator Terminals Gross MVAR | Generator Voltage @ Generator Terminals KV | Aux Load @Bus A MW | Aux Load @ Bus A MVAR | Aux Load @ Bus B MW | Aux Load @ Bus B MVAR | Aux Load Total MW | Aux Load Total MVAR | Auxilary Transformer Losses MW | Auxilary Transformer Losses MVAR | Aux Load @ Generator Terminals MW | Aux Load @ Generator Terminals MVAR | Generator Input To GSU Xfmr MW | Generator Input To GSU Xfmr MVAR | GSU Transformer Losses MW | GSU Transformer Losses MVAR | Generator Net Output @ 345 kV Bus MW | Generator Net Output @ 345 kV Bus MVAR
UNIT#1 | 161.6 | 16.5 | 18.5 | 10 | 6 | 9.8 | 6 | 19.8 | 12 | 0.095934 | 1.2862 | 19.8959 | 13.2862 | 141.7041 | 3.2138 | 0.42584 | 12.5105 | 141.2782 | -9.2968
UNIT#2 | 158.4 | 17.6 | 18.5 | 9 | 6 | 8 | 6 | 17 | 12 | 0.094612 | 0.95917 | 17.0946 | 12.9592 | 141.3054 | 4.6408 | 0.42627 | 12.2933 | 140.8791 | -7.6524
| Notes: | 1. Unit#1 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.147 @ 18 KV
No Load Loss = 118,100 Watts @ 18 KV
%Z = 12.84 @ 200 MVA, 18 KV
Load Loss = 633,231 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.267 @ 18 KV
No Load Loss = 17,840 Watts @ 18 KV
%Z = 5.77 @ 24 MVA, 18 KV
Load Loss = 87502 Watts @ 24 MVA, 18 KV
2. Unit#2 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.151 @ 18 KV
No Load Loss = 119,699 Watts @ 18 KV
%Z = 12.67 @ 200 MVA, 18 KV
Load Loss = 633,799 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.106 @ 18 KV
No Load Loss = 17,880 Watts @ 18 KV
%Z = 5.51 @ 24 MVA, 18 KV
Load Loss = 88,528 Watts @ 24 MVA, 18 KV
3. To calculate Generator Output MW & MVAR at the 345 KV bus, enter Generator Gross MW & MVAR values and Aux Load Bus A and Aux Load Bus B MW & MVAR values
for the appropriate unit.

## July 31, 1998 @ 1700
| Generator Output @ Generator Terminals Gross MW | Generator Output @ Generator Terminals Gross MVAR | Generator Voltage @ Generator Terminals KV | Aux Load @Bus A MW | Aux Load @ Bus A MVAR | Aux Load @ Bus B MW | Aux Load @ Bus B MVAR | Aux Load Total MW | Aux Load Total MVAR | Auxilary Transformer Losses MW | Auxilary Transformer Losses MVAR | Aux Load @ Generator Terminals MW | Aux Load @ Generator Terminals MVAR | Generator Input To GSU Xfmr MW | Generator Input To GSU Xfmr MVAR | GSU Transformer Losses MW | GSU Transformer Losses MVAR | Generator Net Output @ 345 kV Bus MW | Generator Net Output @ 345 kV Bus MVAR
UNIT#1 | 117 | 26 | 18.5 | 8 | 5 | 7.4 | 5 | 15.4 | 10 | 0.067333 | 0.83451 | 15.4673 | 10.8345 | 101.5327 | 15.1655 | 0.28269 | 6.7055 | 101.25 | 8.46
UNIT#2 | 167 | 22 | 18.5 | 9 | 6 | 8.6 | 6 | 17.6 | 12 | 0.098243 | 1.0042 | 17.6982 | 13.0042 | 149.3018 | 8.9958 | 0.46202 | 13.7221 | 148.8397 | -4.7263
| Notes: | 1. Unit#1 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.147 @ 18 KV
No Load Loss = 118,100 Watts @ 18 KV
%Z = 12.84 @ 200 MVA, 18 KV
Load Loss = 633,231 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.267 @ 18 KV
No Load Loss = 17,840 Watts @ 18 KV
%Z = 5.77 @ 24 MVA, 18 KV
Load Loss = 87502 Watts @ 24 MVA, 18 KV
2. Unit#2 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.151 @ 18 KV
No Load Loss = 119,699 Watts @ 18 KV
%Z = 12.67 @ 200 MVA, 18 KV
Load Loss = 633,799 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.106 @ 18 KV
No Load Loss = 17,880 Watts @ 18 KV
%Z = 5.51 @ 24 MVA, 18 KV
Load Loss = 88,528 Watts @ 24 MVA, 18 KV
3. To calculate Generator Output MW & MVAR at the 345 KV bus, enter Generator Gross MW & MVAR values and Aux Load Bus A and Aux Load Bus B MW & MVAR values
for the appropriate unit.

## August 3, 1998 @ 1600
| Generator Output @ Generator Terminals Gross MW | Generator Output @ Generator Terminals Gross MVAR | Generator Voltage @ Generator Terminals KV | Aux Load @Bus A MW | Aux Load @ Bus A MVAR | Aux Load @ Bus B MW | Aux Load @ Bus B MVAR | Aux Load Total MW | Aux Load Total MVAR | Auxilary Transformer Losses MW | Auxilary Transformer Losses MVAR | Aux Load @ Generator Terminals MW | Aux Load @ Generator Terminals MVAR | Generator Input To GSU Xfmr MW | Generator Input To GSU Xfmr MVAR | GSU Transformer Losses MW | GSU Transformer Losses MVAR | Generator Net Output @ 345 kV Bus MW | Generator Net Output @ 345 kV Bus MVAR
UNIT#1 | 167.8 | 22.4 | 18.5 | 9.2 | 6 | 9 | 6 | 18.2 | 12 | 0.08719 | 1.1481 | 18.2872 | 13.1481 | 149.5128 | 9.2519 | 0.46105 | 13.9384 | 149.0518 | -4.6865
UNIT#2 | 167.8 | 19.9 | 18.5 | 9 | 6 | 8.4 | 6 | 17.4 | 12 | 0.097019 | 0.98901 | 17.497 | 12.989 | 150.303 | 6.911 | 0.46602 | 13.882 | 149.837 | -6.971
| Notes: | 1. Unit#1 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.147 @ 18 KV
No Load Loss = 118,100 Watts @ 18 KV
%Z = 12.84 @ 200 MVA, 18 KV
Load Loss = 633,231 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.267 @ 18 KV
No Load Loss = 17,840 Watts @ 18 KV
%Z = 5.77 @ 24 MVA, 18 KV
Load Loss = 87502 Watts @ 24 MVA, 18 KV
2. Unit#2 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.151 @ 18 KV
No Load Loss = 119,699 Watts @ 18 KV
%Z = 12.67 @ 200 MVA, 18 KV
Load Loss = 633,799 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.106 @ 18 KV
No Load Loss = 17,880 Watts @ 18 KV
%Z = 5.51 @ 24 MVA, 18 KV
Load Loss = 88,528 Watts @ 24 MVA, 18 KV
3. To calculate Generator Output MW & MVAR at the 345 KV bus, enter Generator Gross MW & MVAR values and Aux Load Bus A and Aux Load Bus B MW & MVAR values
for the appropriate unit.

## September 4, 1998 @ 1700
| Generator Output @ Generator Terminals Gross MW | Generator Output @ Generator Terminals Gross MVAR | Generator Voltage @ Generator Terminals KV | Aux Load @Bus A MW | Aux Load @ Bus A MVAR | Aux Load @ Bus B MW | Aux Load @ Bus B MVAR | Aux Load Total MW | Aux Load Total MVAR | Auxilary Transformer Losses MW | Auxilary Transformer Losses MVAR | Aux Load @ Generator Terminals MW | Aux Load @ Generator Terminals MVAR | Generator Input To GSU Xfmr MW | Generator Input To GSU Xfmr MVAR | GSU Transformer Losses MW | GSU Transformer Losses MVAR | Generator Net Output @ 345 kV Bus MW | Generator Net Output @ 345 kV Bus MVAR
UNIT#1 | 167.8 | 20.6 | 18.5 | 9.8 | 6 | 9 | 6 | 18.8 | 12 | 0.090383 | 1.1986 | 18.8904 | 13.1986 | 148.9096 | 7.4014 | 0.45789 | 13.8102 | 148.4517 | -6.4088
UNIT#2 | 168.6 | 19.3 | 18.5 | 9 | 6 | 8.6 | 6 | 17.6 | 12 | 0.098243 | 1.0042 | 17.6982 | 13.0042 | 150.9018 | 6.2958 | 0.46861 | 13.9853 | 150.4331 | -7.6895
| Notes: | 1. Unit#1 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.147 @ 18 KV
No Load Loss = 118,100 Watts @ 18 KV
%Z = 12.84 @ 200 MVA, 18 KV
Load Loss = 633,231 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.267 @ 18 KV
No Load Loss = 17,840 Watts @ 18 KV
%Z = 5.77 @ 24 MVA, 18 KV
Load Loss = 87502 Watts @ 24 MVA, 18 KV
2. Unit#2 Losses based on the following GSU and Aux Transformer Data
|  |  | GSU Xfmr: | %I = 0.151 @ 18 KV
No Load Loss = 119,699 Watts @ 18 KV
%Z = 12.67 @ 200 MVA, 18 KV
Load Loss = 633,799 Watts @ 200 MVA, 18 KV
|  |  | Aux Xfmr: | %I = 0.106 @ 18 KV
No Load Loss = 17,880 Watts @ 18 KV
%Z = 5.51 @ 24 MVA, 18 KV
Load Loss = 88,528 Watts @ 24 MVA, 18 KV
3. To calculate Generator Output MW & MVAR at the 345 KV bus, enter Generator Gross MW & MVAR values and Aux Load Bus A and Aux Load Bus B MW & MVAR values
for the appropriate unit.