## Slide 1
ERCOT Frequency Control Report
December 2021
ERCOT
Operations Planning
PDCWG | January 19th, 2022

## Slide 2: Summary of December 2021
CPS1: 170.03%
Current CPS1 12-Month Rolling Average: 169.28%
2 BAAL Exceedance(s)
6 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2021 RMS1 Statistics
  Mean: 16.37 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz
Energy Statistics
  Total Energy: 30,205,131 MWh
  Wind Energy: 9,617,446MWh
  Percent Energy from Wind: 31.84%
  Solar Energy: 1,016,276 MWh
  Percent Energy from Solar: 3.36%
Minimum System Inertia
  Mean: 162,176 MW*s
  Max: 246,027 MW*s on Dec 20th
  Min: 130,757 MW*s on Dec 24th
Notes: Mean: 162,176 MW*s
Max: 246,027 MW*s on Dec 20th
Min: 130,757 MW*s on Dec 24th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Dec-21 CPS1 (%): 170.03
Notes: 1. 81.64% @ 12/4/2021 HE 17:00
Expected Generation Deviation
Expected gen dev remained negative for the entire hour. The largest expected gen dev was -1666 MW @ 16:54 with contribution from solar for the most part.
IRR Ramps
Between 16:00 to 17:00 solar ramped down by ~2640 MW.
DC Ties
Between 16:40 to 17:00 DC Tie ramped down by ~460 MW.
Non-conforming Load
Between 16:40 to 17:00 non-conforming load increased by ~250 MW.
Regulation: Regulation up was exhausted in the end of the hour. A 250 MW SCED manual offset was applied.
2. 91.83% @ 12/18/2021 HE 22:00
Expected Generation Deviation
Expected gen dev remained negative for half of the hour. The largest expected gen dev was -1001 MW @ 21:30 with contribution from wind for the most part.
IRR Ramps
Between 21:21 to 21:46 wind ramped down by 844 MW.
Regulation: Regulation up was exhausted during the ramp intervals.
3. 21.78% @ 12/23/2021 HE 10:00
Expected Generation Deviation
Expected gen dev remained negative for majority of the hour. The largest expected gen dev was -2792MW @ 9:37 with contribution from mostly wind.
IRR Ramps
Between 9:00 to 10:00 wind ramped down by ~4200 MW.
Regulation: Regulation up was exhausted during the IRR ramp intervals. A 300 and 600 MW SCED manual offset were applied. 813 MW of RRS was deployed.
4. 96.92% @ 12/24/2021 HE 9:00
Expected Generation Deviation
Expected gen dev remained negative for two thirds of the hour. The largest expected gen dev was -887 MW @ 8:23 with contribution from mostly wind.
IRR Ramps
Between 8:00to 9:00 wind ramped down by ~1070 MW.
Regulation: Regulation up was exhausted for the wind ramp.
5. 94.24% @ 12/25/2021 HE 10:00
Expected Generation Deviation
Expected gen dev was negative for majority of the hour. The largest expected gen dev was -753 MW @ 9:34 with contribution from mostly wind.
IRR Ramps
Between 9:00to 10:00 solar ramped down by 3100 MW and wind ramped down by 1300 MW.
DC Ties
Between 9:26 to 9:36 DC Tie ramped down by ~250 MW.
Regulation: Regulation up was exhausted for most part of the hour.
6. 97.93% @ 12/25/2021 HE 11:00
Expected Generation Deviation
Expected gen dev was negative for majority of the hour. The largest expected gen dev was -851 MW @ 10:26 with contribution from solar and wind and thermal units.
IRR Ramps
A sudden solar down ramp Between 10:17 to 10:24 by ~270MW.
DC Ties
Between 10:16 to 10:24 DC Tie ramped down by ~110 MW.
Regulation: Regulation up was exhausted for most part of the hour..

## Slide 5: BAAL Exceedances & Violations
There are 2 BAAL exceedance(s) in December
Notes: Both occurred on 12/23/2021 due to significant wind down ramps

## Slide 6: 15-Minute Average CPS1%
Dec-21 CPS1 (%): 170.03

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 169.28%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 16.37 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: 16Mhz on avg

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 30,205,131 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 9,617,446 MWh

## Slide 23: % Energy from Wind Generation
Notes: 31.84%

## Slide 24: Total Energy From Solar Generation
Notes: 1,016,276 MWh

## Slide 25: % Energy from Solar Generation
Notes: 3.36%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 130,757 MW*s on 12/24/2021
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 162,176 MW*s
Max: 246,027 MW*s on Dec 20th
Min: 130,757 MW*s on Dec 24th

## Slide 28: Questions?
Thank you!