## Slide 1
2021 Voltage Reduction RFI
OWG
February 2022

## Slide 2: Disclaimer
Of the 172 RFI’s sent to TDSPs, 53 responses were received. All TOs responded, but many local TDSPs (municipalities and co-ops) did not respond.
  Some TOs responded that they do not provide service at distribution voltage and have no Distribution Voltage Reduction (DVR) while their member TSPs and DSPs responded that they do have DVR.
Some TOs explicitly stated that their responses include member TSPs and DSPs. Other TOs did not mention anything about TSP and/or DSP. Some of the 119 missing TSPs and DSPs responses may be included in TOs responses without our knowledge.

## Slide 3: ERCOT Distribution Voltage Reduction (DVR) Capability
Many entities have defined voltage percentages to reduce (up to 5% voltage reduction). Most TO’s DVR program starts at 2.5% and DVR response is minimal at 1% voltage reduction.
  Examples:
    TO1 only has 1% voltage reduction.
    TO2 only has 2.5% voltage reduction.
    TO3 only has 2.5% and 5.0% voltage reduction.
At 5% Voltage Reduction, estimated MW reduction is less than 1% of ERCOT System Load.
Benefit of DVR is slightly higher in winter than summer. Better response from resistive load.
 |  | Summer |  |  | Winter | 
ERCOT System Load (MW) | 60,000 | 70,000 | 80,000 | 55,000 | 65,000 | 75,000
1. Total MW with Distribution Voltage Reduction (DVR) Capability | 16,281 | 19,248 | 22,281 | 15,754 | 18,853 | 22,025
i) DVR Capability with SCADA Control (MW) | 5,926 | 6,992 | 8,075 | 7,129 | 8,521 | 9,943
ii) DVR Capability that can be implemented within 5 minutes (MW) | 394 | 460 | 526 | 362 | 427 | 493
iii) DVR Capability that can be implemented within 10 minutes (MW) | 513 | 599 | 684 | 470 | 556 | 642
iv) DVR Capability that can be implemented within 15 minutes (MW) | 5,003 | 5,915 | 6,850 | 6,286 | 7,526 | 8,795
v) DVR Capability that can be implemented within 30 minutes (MW) | 5,231 | 6,181 | 7,148 | 6,492 | 7,768 | 9,074
2. DVR Response by the Voltage Reduction Amount |  |  |  |  |  | 
i) Estimated MW reduction of DVR with 1% Voltage Reduction | 39 | 61 | 88 | 39 | 61 | 88
ii) Estimated Total MW reduction from DVR | 442 | 538 | 641 | 449 | 552 | 661

## Slide 4: Distribution Voltage Reduction (DVR)
Voltage Reduction Percentage | DVR Response (Load Reduction %)
At 1% | <1%
At 2.5% | 1-2%
At 5.0% | 2-3%
7 out of 21 TOs have DVR.
Some TOs does not have DVR to implement in response to ERCOT instruction, but continuously uses the Volt/Var optimization program.
One TO implements DVR only during summer.
Maximum DVR duration typically ranges from 15 minutes to 4 hours.
Typical response for TOs with the DVR program:

## Slide 5: Distribution Voltage Reduction Implementation Factors
Load Composition. DVR Capability decreases as:
  Induction Motor Load (including A/C) increases.
  Industrial Load increases
  Transmission Load increases
System Topology: Long radial lines reduce DVR Capability
Distributed Generation (DG) Penetration: DG is required to operate at a unity power factor so MW output decreases when voltage decreases.

## Slide 6: Barriers to Increase DVR with SCADA Control
Requires additional communication equipment and control updates.
  Multi-year, multi-million-dollar investment.
Some RFI responses questioned the estimated benefits vs. cost.
Physical Limitations:
  Existing Transformers’ Capability.
  Maintaining Voltage Limits especially for long radial circuits to prevent equipment damage.