## Slide 1
ERCOT Frequency Control Report
January 2022
ERCOT
Operations Planning
PDCWG | February 16th, 2022

## Slide 2: Summary of January 2022
CPS1: 175.89%
Current CPS1 12-Month Rolling Average: 169.60%
0 BAAL Exceedance(s)
1 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2022 RMS1 Statistics
  Mean: 16.37 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz
Energy Statistics
  Total Energy: 33,399,938 MWh
  Wind Energy: 8,448,159 MWh
  Percent Energy from Wind: 25.29 %
  Solar Energy: 1,335,908 MWh
  Percent Energy from Solar: 4.00%
Minimum System Inertia
  Mean: 196,374 MW*s
  Max: 303,097 MW*s on Jan 21st
  Min: 144,524 MW*s on Jan 16th
Notes: Mean: 162,176 MW*s
Max: 246,027 MW*s on Dec 20th
Min: 130,757 MW*s on Dec 24th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Jan-22 CPS1 (%): 175.89
Notes: 1. 75% @ 1/11/2022 HE 10:00
Expected Generation Deviation
Expected gen dev remained negative for the first half hour. The largest expected gen dev was -2553 MW @ 9:14 with signification contribution from thermal resources and wind generation.
IRR Ramps
Between 9:00 to 9:30 wind ramped down by ~900 MW.
Regulation: Regulation up was exhausted during the ramp intervals. A 550 MW SCED manual offset was applied and 635 MW of RRS was deployed.

## Slide 5: BAAL Exceedances & Violations
There are 0 BAAL exceedance(s) in January
Notes: Both occurred on 12/23/2021 due to significant wind down ramps

## Slide 6: 15-Minute Average CPS1%
Jan-22 CPS1 (%): 175.89

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 169.60%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 14.68 mHz
  Min: 12.51 mHz
  Max: 16.9 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: 16Mhz on avg

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 33,399,938 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 8,448,159 MWh

## Slide 23: % Energy from Wind Generation
Notes: 25.29 %

## Slide 24: Total Energy From Solar Generation
Notes: 1,335,908 MWh

## Slide 25: % Energy from Solar Generation
Notes: 4.00 %

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 144,524 MW*s on 1/16/2022
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 196,374 MW*s
Max: 303,097 MW*s on Jan 21st
Min: 144,524 MW*s on Jan 16th

## Slide 28: Questions?
Thank you!