## Slide 1
Update on NOGRR 226
February 17, 2022
OWG
ERCOT Operations Planning Staff

## Slide 2: Introduction
Issue:
NOGRR226 proposes to raise the first 5% Transmission Operator (TO) Load shedding relay set point requirement from 59.3 Hz to 59.4 Hz.
  NOGRR226 indicates that when the frequency falls below 59.4 Hz, there is risk of damage to turbine blades and that in order to avoid this damage, a relay is triggered that will trip the generator Off-Line after nine minutes.
Summary of Stakeholder Discussion thus far:
Under Frequency Load Shed (ULFS) settings are part of an interweaving of system operations and protection. Hence, there are several aspects that need to be considered holistically when assessing this proposal.
ERCOT had shared some preliminary thoughts on the areas that would be impacted by the proposed NOGR226 at the June 2021 PDCWG and OWG meetings.
At some follow up discussions at the OWG it was recommended that a holistic set of studies be performed on this topic.
Status Update:
ERCOT has kicked off studies to investigate the relevant impacts of changing the first-stage UFLS relay set point from 59.3 Hz to 59. 4 Hz and other relevant ideas (placeholder for ONCOR comments). ERCOT is currently targeting to complete this analysis by May 2022.

## Slide 3: Analysis to be Conducted in Feb & Mar
Impact on Responsive Reserve Service (RRS) Requirements & Critical Inertia
  Design Objective:
  RRS requirements are designed such that to meet NERC standard BAL-003-2, Interconnection Frequency Response Obligation. Per this standard, ERCOT must plan to operate such that the loss of 2805 MW does not trigger first stage of UFLS. (Note that ERCOT uses a 100 mHz margin when establishing RRS requirements)
  Critical Inertia is the minimum level of system inertia to be maintained to allow Load Resources with under frequency relays to deploy before frequency drops below the first-stage UFLS set point following the simultaneous loss of 2805 MW.
  Analysis Summary:
  Studies will be conducted to assess the impact of changing first stage of UFLS as proposed in NOGRR226 on RRS requirements and Critical Inertia.
Revisit Energy Emergency Alert (EEA) Level 3 Studies & Procedures
  Design Objective:
  Maintain frequency responsive PRC so that Most Severe Single Contingency (MSSC) will not cause 1st Stage UFLS to trip.
  Analysis Summary:
  Studies will be conducted under EEA Level 3 condition to assess the impact of changing first stage of UFLS as proposed in NOGRR226 on frequency response after tripping 1,430 MW under various inertia/net load conditions, with/without load ramp, etc.

## Slide 4: Analysis to be Conducted in Mar & Apr
Impact on UFLS
Design Objective:
  UFLS program is intended to arrest severe frequency declines and to facilitate the operation of the ERCOT interconnection as a single island during severe under-frequency events. UFLS program is designed such that it can effectively arrest the frequency decline when the system is subjected to severe imbalances so that the frequency and voltage/frequency performance requirements can be satisfied.
  Analysis Summary:
  Evaluate the impact of changing first stage set point of UFLS as proposed in NOGR226.
  Evaluate if the current/proposed UFLS block sizes/frequency setpoint may result in frequency swings that may cause generation units to trip. If so, consider if additional block/frequency setpoint combinations are warranted.
  Evaluate idea that ONCOR has proposed in its comments regarding adding a supplemental automatic load shed option prior to first stage UFLS primarily directed towards recovering frequency.

## Slide 5: Summary and Next Steps
ERCOT has kicked off a holistic review of the impact of changing the first-stage UFLS relay set point from 59.3 Hz to 59.4 Hz and other relevant ideas (placeholder for ONCOR comments).
  ERCOT is currently targeting to complete this analysis by May 2022.
  Upon completion of this effort ERCOT will share its observations and recommendations with OWG (and any other relevant stakeholder groups).
If stakeholders have any questions/comments/recommendations specific to this effort please send them via email to Nitika Mago (nmago@ercot.com) by CoB February 28, 2022.