## Slide 1: PANHANDLE GTC limit with VSAT
Panhandle GTC limit is determined as the lower of:
  Calculated static voltage stability limit from VSAT, or
  Table-based dynamic voltage stability limit under various outages
When VSAT calculates the voltage stability limit for the Panhandle export, it increases the wind resources in the Panhandle area until the system reaches voltage instability. However, depending on the transmission conditions and wind resource availability, it may not reach the instability even with all available wind dispatched. In that case, VSAT reports “dispatch limit”, not “stability limit”.

## Slide 2: PANHANDLE GTC limits in CRR/DAM/RTM
 | CRR | DAM | RTM
Before Dec. 2021 | Min(dispatch limit, table value) | Min(dispatch limit, table value) | Min(dispatch limit, table value)
Currently | Min(dispatch limit, table value) | Min(9999, table value) | Min(dispatch limit, table value)
After Mar. 2022 | Min(dispatch limit, table value) | Min(99999, table value) | Min(99999, table value)
VSAT is used in the process to calculate the Panhandle GTC limits for CRR, DAM and RTM. However, when VSAT reaches the “dispatch limit” instead of the “stability limit”, the dispatch limit value is applied differently in the markets. This table displays how the dispatch limits are applied (note changes coming in March 2022).