## Slide 1
Loss of Solar Event Analysis
IBRTF Meeting
February 18, 2022

## Slide 2: Agenda
Background
Event Detection Procedure
Events since June 2021
Next Steps
  Automation and Email Notification
  Improvements to Real-Time PMU Network

## Slide 3: Background
Detect and mitigate smaller events to prevent larger events
Cannot be dependent on models alone
Using actual events to improve model accuracy
Better data for analysis

## Slide 4: Event Detection Procedure (Currently)
Scan Solar.MW PI tags for reduction ~100 MW or greater
Match up with frequency deviations so not chasing telemetry dropouts
Developed tool to locate MW losses greater than 10 MW for every solar unit during user defined time frame
Replay in Real Time Dynamic Monitoring System (RTDMS) to look for possible faults
Track events and reach out to REs for any events of interest

## Slide 5: Solar Loss Events ~100 MW or Greater June – December 2021*
Chart: Solar Events
| June | July | August | September | October | November | December
# Events | 3 | 2 | 5 | 6 | 4 | 2 | 8
Pad Event
Pad MW
Total MW Loss | 722 | 353 | 1098 | 1015 | 495 | 314 | 1043
*Excluding June 26 Event

## Slide 6: Solar Loss Events ~100 MW or Greater June – December 2021
Total of 30 events ranging from 78 MW to 252 MW
9 events associated with a fault
2 events with MW losses at multiple plants, both associated with faults
  210 MW loss on 8/15 at 3 separate sites
  185 MW loss on 12/10 at 2 separate sites
Total of 18 plants and 27 units involved in at least one event
7 plants identified in NERC Odessa report involved in another event

## Slide 7: Next Steps – Automation and Process Improvements
Currently a manual process and events are often not found for days or weeks
ERCOT working on improving tools to scan continuously and send email or trigger alerts when events detected
Need to streamline communication process and develop event criteria for sending RFIs
Need better access to high resolution data

## Slide 8: Improvements to Real-Time PMU Network
PMUs streaming real-time data from POIs of solar farms are valuable to analysis
No need to wait for plants to provide data, which may be erased after 10 days
Can quickly replay events for analysis
3 TOs currently sending real-time PMU data – which operate 43 of the 57 POIs for solar sites
Currently receiving real-time PMU data from 13 POIs

## Slide 9
Questions?