ERCOT Nodal Operating Guides

Section 8

Attachment C

Turbine Governor Speed Tests

September 1, 2021

Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor	1

Example of a Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor	4

Turbine Governor Speed Regulation Test for Electro-Hydraulic Governor	6

Definitions	8

Generation Resource Frequency Response Test Procedure	9

Generation Resource FREQUENCY RESPONSE TEST FORM	11

HISTORICAL GENERATION RESOURCE OR CONTROLLABLE LOAD RESOURCE FREQUENCY RESPONSE TEST FORM	14

Intermittent renewable resource (IRR) FREQUENCY RESPONSE TEST FORM	18

Controllable load resource Frequency Response Test Procedure	19

Controllable load resource FREQUENCY RESPONSE TEST FORM	21

- Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor

General Information

Unit Code (16 characters):   			Location (County):

Unit Name:  					Date of test:

QSE:						Resource Entity:

- Steady State Speed Regulation at High-Speed Stop

Where:

A =	Speed with speed changer set at high-speed stop and with throttle (or stop) valves open and machine running idle on the Governor.

B =	Speed with speed changer set at high-speed stop and when governing valves just reach wide-open position.

- Steady State Speed Regulation at Synchronous Speed

Where:

C =	Speed with speed changer set for synchronous speed and with throttle (or stop) valves open and machine running idle on the Governor.

D =	Speed with speed changer set at the same position as in C above and when governing valves just reach wide open position.

- Steady State Speed Regulation at Low-Speed Stop

Where:

E =	Speed with speed changer set at low-speed stop and with throttle (or stop) valves open and machine running idle on the Governor.

F =	Speed with speed changer set at low-speed stop and when governing valves just reach wide-open position.

E, F @ Low Speed Stop

C, D @ Sync. Speed

A, B @ High Speed Stop

Test Data

| Point | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Speed, RPM |  |  |  |  |  |  |
| Frequency Hz |  |  |  |  |  |  |

Speed Changer Travel Time:

(a)	From Low-Speed Stop to High-Speed Stop in _________seconds.

(b)	From High-Speed Stop to Low-Speed Stop in _________seconds.

Over-speed Trip Test Speed at _________rpm.

Comments:

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Representative:

- Example of a Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor

- Steady State Speed Regulation at High-Speed Stop

Where:

A =	Speed with speed changer set at high-speed stop and with throttle (or stop) valves open and machine running idle on the Governor.

B =	Speed with speed changer set at high-speed stop and when governing valves just reach wide-open position.

- Steady State Speed Regulation at Synchronous Speed

Where:

C =	Speed with speed changer set for synchronous speed and with throttle (or stop) valves open and machine running idle on the Governor.

D =	Speed with speed changer set at the same position as in C above and when governing valves just reach wide open position.

- Steady State Speed Regulation at Low-Speed Stop

Where:

E =	Speed with speed changer set at low-speed stop and with throttle (or stop) valves open and machine running idle on the Governor.

F =	Speed with speed changer set at low-speed stop and when governing valves just reach wide-open position.

E, F @ Low Speed Stop

C, D @ Sync. Speed

A, B @ High Speed Stop

Test Data

| Point | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Speed, RPM | 3850 | 3570 | 3600 | 3310 | 3500 | 3210 |
| Frequency Hz | 64.2 | 59.5 | 60.0 | 55.0 | 58.3 | 53.5 |

Speed Changer Travel Time:

(a)	From low-speed stop to high-speed stop in 	73	seconds.

(b)	From high-speed stop to low-speed stop in 	74	seconds.

Over-speed trip test speed at 	3965	rpm.

Comments:

- Turbine Governor Speed Regulation Test for Electro-Hydraulic Governor

General Information

Unit Code (16 characters):   			Location (County):

Unit Name:  					Date of test:

QSE:						Resource Entity:

- Turbine Governor Speed Regulation Test Procedures

(a)	Simulate unit On-Line and turbine speed at 3600 RPM.

(b)	Set Load reference at minimum value.

(c)	Monitor valve demand signal and record as value “A” (in %).

(d)	Reduce speed until valve demand just reaches maximum value.
Record valve demand as value “B” (in %) and speed as value “C” (in RPM).

(e)	Set speed at 3600 and Load reference at maximum value.

(f)	Monitor valve demand signal and record as value “D” (in %).

(g)	Increase speed until valve demand just reaches minimum value.
Record valve demand as value “E” (in %) and speed as value “F” (in RPM).

- Turbine Governor Speed Regulation Test Results

|  | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Valve Demand (%) |  |  |  |  |  |  |
| Speed (rpm) |  |  |  |  |  |  |

- Speed Regulation With Decreasing Speed

- Speed Regulation With Increasing Speed

Comments:

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Representative:

- Definitions

| System Frequency Response | This response is a function of two key variables: the Primary Frequency Response from Governors and Load dampening of the connected Load. |
| --- | --- |
| Percent Droop Settings | Also known as Frequency Regulation, Speed Regulation, Speed Sensitivity, Speed Error and others. Percent droop is the percent change in nominal frequency that will cause generator output to change from no Load to full Load. It is the change in steady state rotor speed, expressed in percent of rated speed, when power output is gradually reduced from rated to zero power. A common percent droop setting is 5% for both high and low frequency excursions. |
| Dead-Band | The range of deviations of system frequency (+/-) that produces no turbine Governor response, and therefore, no frequency (speed) regulation. It is expressed in percent of rated speed, Hz, or RPM. |
| NOGRR204: Replace “Percent Droop Settings” and “Dead-Band” above with the following upon system implementation of NPRR989:] |  |
| Percent Droop Settings | Also known as Frequency Regulation, Speed Regulation, Speed Sensitivity, Speed Error and others. Percent droop is the percent change in nominal frequency that will cause generator output to change from no Load to full Load. For synchronous Resources, it is the change in steady state rotor speed, expressed in percent of rated speed, when power output is gradually reduced from rated to zero power. A common percent droop setting is 5% for both high and low frequency excursions. |
| Dead-Band | The range of deviations of system frequency (+/-) that produces no Governor response, and therefore, no frequency (speed) regulation. It is expressed in percent of rated speed, Hz, or RPM. |
| Valve Position Limiter | A device that acts on the speed and Load governing system to prevent the Governor-controlled valves from opening beyond a pre-set limit. |
| Blocked Governor Operation | Operating the generating unit with the control system adjusted to prevent the turbine governor from responding to system frequency (speed) variations. In an effort to reduce speed Governor operation in some generating units, turbine control systems can be adjusted to block the operation of the Governor after the unit is in parallel with the system and is running at its desired output. Selection of a high percent droop characteristic or a large Governor Dead-Band constitutes a form of blocked Governor action. |
| Variable Pressure Operation | Varying the boiler pressure to improve turbine efficiency at lower Loads. Two methods are normally used. The first method, the turbine control (G.E.) or Governor (Westinghouse) valves are positioned in the wide-open position and the generator is changed by changing the boiler pressure. With this method, there is very little, if any response to frequency excursions. The second method, the valves are positioned at approximately 50% open. The valves are still able to respond to system disturbances. Normal changes in generation requirements are made by varying the boiler pressure until the unit is at rated pressure. After full pressure is reached, the turbine valves are used to make the required generation changes. |

# Generation Resource Frequency Response Test Procedure

Description of the Test

1.	The frequency response function of the Generation Resource is tested On-Line at a Load level that allows the Generation Resource to increase or decrease Load without reaching low operating limits or high operating limits.  If the Generation Resource cannot be tested On-Line then it will notify ERCOT that it will be conducting an Off-Line test.  The recommended level is 92% Base Load or below.

2.	The test is performed by adding a frequency offset signal that exceeds the Governor Dead-Band value to the measured frequency signal.  This should create immediate step change in the measured frequency signal.

3.	The test starts at time t0 when the frequency Dead-Band is exceeded and signal “Generation Resource Frequency Response On” becomes active.

4.	The following signals should be recorded at least two seconds:  Unit MW Output, “Generation Resource Frequency Response On.”

5.	The duration of the test is 100 seconds.  After 100 seconds, the offset signal should be removed and the Generation Resource should return to pretest power output.

6.	The test should be conducted both with positive and negative frequency offsets.

7.	The test is considered successful after the signal becomes active if at least 70% of the calculated MW contribution is delivered within 16 seconds and the response is maintained for an additional 30 seconds.

8.	Governor droop and Governor Dead-Band settings shall be set in accordance with Section 2.2.7, Turbine Speed Governors.

Definitions

Generation Resource Base Load = maximum Load capability for the season when frequency response test is performed

Gain MW for 0.1Hz = P(Droop∗60−GovernorDead−Band)∗10

Where:

P = Generation Resource Base Load (MW)

Droop 	= droop (%)

Frequency Offset = +0.2 Hz and -0.2 Hz (+12 rpm and -12 rpm, for 3600 sync speed machines), outside Governor Dead-Band

Test frequency = Measured Frequency + Frequency Offset

MW Contribution = Gain MW to 0.1 Hz *10*Frequency Offset

Calculated droop = - P∗ΔHz60∗ΔMW

Where:

P = Generation Resource Base Load (MW)

ΔHz = Change in frequency (Hz), taking into account Governor Dead-Band

ΔMW = Change in power output (MW)

Example

Generation Resource Base Load = 150 MW

Droop = 0.05 or 5% (use 0.05 for calculation)

Governor Dead-Band = 0.034

Gain MW to 0.1 Hz = 150[(0.05∗60)−0.034]∗10 = +/- 5.06 MW/0.1 Hz

MW Contribution = 5.06*10*+/- (0.2) = +/-10.12 MW

Expected under-frequency response:	 +10.12 MW in 16 sec. for -0.2 Hz offset

Expected over-frequency response: 	-10.12 MW in 16 sec. for +0.2 Hz offset

Minimum accepted under-frequency response: +7.08 MW in 15 sec. for -0.2 Hz offset

Minimum accepted over-frequency response:    -7.08 MW in 15 sec. for +0.2 Hz offset

Calculated droop for 8 MW increase in power output in 16 sec. for -0.2 Hz offset:

Calculated droop = -150∗−0.260∗8 = 0.0625 or 6.25%

Generation Resource FREQUENCY RESPONSE TEST FORM

General Information

Unit Code (16 characters): 				Location (County):

Unit Name: 						Date of Test:

QSE: 							Resource Entity:

Test Results

|  |  | Test with +0.2 Hz | Test with -0.2 Hz |
| --- | --- | --- | --- |
| 1 | Generation Resource Base Load |  |  |
| 2 | GAIN MW to 0.1Hz |  |  |
| 3 | Calculated MW Contribution |  |  |
| 4 | MW at test start (t0) |  |  |
| 5 | MW at t0 + 16 sec |  |  |
| 6 | MW Contribution at t0 + 16 sec |  |  |
| 7 | MW at t0 + 46 sec |  |  |
| 8 | Calculated droop |  |  |
| 9 | CONCLUSION (PASSED/FAILED) |  |  |

Comments: ________________________________________________________________________________________________________________________________________________________________________________________________________________________

Submittal

Resource Entity Representative:  ____________________________________________

QSE Representative:  ______________________________________________________

Date submitted to ERCOT Representative: __________________________	______

[NOGRR204: Insert item “Energy Storage Resource Frequency Response Test Procedure” and “Energy Storage Resource Frequency Response Test Form” below upon system implementation of NPRR989:] - Energy Storage resource Frequency Response Test Procedure Description of the Test - An Energy Storage Resource (ESR) is tested On-Line in both maximum charging and discharging modes at a level that allows the ESR to increase or decrease Load without reaching its operating limits. If the ESR cannot be tested On-Line then it will notify ERCOT that it will be conducting an Off-Line test. 2. The test is performed by adding a frequency offset signal that exceeds the Governor Dead-Band value to the measured frequency signal. This should create an immediate step-change in the measured frequency signal. 3. The test starts at time t0 when the frequency dead-band is exceeded. 4. The following signals should be recorded for at least two seconds: unit MW level and frequency offset signal. 5. The duration of the test is 100 seconds. After 100 seconds, the offset signal should be removed and the Energy Storage Resource should return to the pretest MW level. 6. The test should be conducted with both positive and negative frequency offsets. 7. The test is considered successful after the signal becomes active if at least 70% of the calculated MW contribution is delivered within 16 seconds and the response is maintained for an additional 30 seconds. 8. Governor droop and Governor Dead-Band settings shall be set in accordance with Section 2.2.7, Turbine Speed Governors. Definitions Energy Storage Resource Base Load = for low frequency test maximum charging capability; for high frequency test maximum discharging capability 10 * ) 60 * ( Band GovernorDead Droop P   Gain MW for 0.1Hz = Where: P = Energy Storage Resource Base Load (MW) Droop = droop (%) Frequency Offset = +0.2 Hz and -0.2 Hz (+12 rpm and -12 rpm, for 3600 sync speed machines), outside Governor Dead-Band Test frequency = Measured Frequency + Frequency Offset MW Contribution = Gain MW to 0.1 Hz *10*Frequency Offset Calculated droop = - Where: P = Energy Storage Resource Base Load (MW) ΔHz = Change in frequency (Hz), taking into account Governor Dead-Band ΔMW = Change in power level (MW) Example Energy Storage Resource Base Load = 150 MW, when discharging Droop = 0.05 or 5% (use 0.05 for calculation) Governor Dead-Band = 0.017 Gain MW to 0.1 Hz = = +/- 5.03 MW/0.1 Hz MW Contribution (injection) = 5.03*10*+/- (0.2) = +/-10.06 MW Expected under-frequency response (injection): +10.06 MW in 16 sec. for -0.2 Hz offset Expected over-frequency response (withdrawal): -10.06 MW in 16 sec. for +0.2 Hz offset Minimum accepted under-frequency response (injection): +7.04 MW in 15 sec. for -0.2 Hz offset Minimum accepted over-frequency response (withdrawal): -7.04 MW in 15 sec. for +0.2 Hz offset Calculated droop for 8 MW increase in power output in 16 sec. for -0.2 Hz offset: Calculated droop = - = 0.0625 or 6.25% Energy Storage Resource FREQUENCY RESPONSE TEST FORM General Information Unit Code (16 characters): Location (County): Unit Name: Date of Test: QSE: Resource Entity: Test Results Test with +0.2 Hz; Test with -0.2 Hz. 1; Energy Storage Resource (ESR) Base Load. 2; GAIN MW to 0.1Hz. 3; Calculated MW Contribution. 4; MW at test start (t0). 5; MW at t0 + 16 sec. 6; MW Contribution at t0 + 16 sec. 7; MW at t0 + 46 sec. 8; Calculated droop. 9; CONCLUSION (PASSED/FAILED). Comments: ________________________________________________________________________________________________________________________________________________________________________________________________________________________ Submittal Resource Entity Representative: ____________________________________________ QSE Representative: ______________________________________________________ Date submitted to ERCOT Representative: __________________________ ______

Generation Resource and Controllable Load Resource Primary Frequency Response test Procedures Based on Historical Data

Description of Historical Verification

The purpose of this template is to allow the Entity that operates a Generation Resource or a Controllable Load Resource to demonstrate acceptable frequency response of its Generation Resource(s) or Controllable Load Resource(s) based on historical data in order to minimize testing costs, scheduling conflicts and the risk of damage to equipment or Forced Outage.

1.	All verifications will be based on at least one of the events from the published list of Frequency Measurable Events (FMEs).

2.	Governor droop and Governor Dead-Band settings shall be set in accordance with Section 2.2.7.  For Controllable Load Resources, Governor droop shall not exceed 5% and Governor Dead-Band shall not exceed +/-0.036Hz.

3.	For clarification purposes, the time of FME (t(0)), pre-perturbation average frequency and post-perturbation average frequency, as defined in Section 8, Attachment J, Initial and Sustained Measurements for Primary Frequency Response, will be used for the verification process.  The values of these metrics will be identified in the FME Report.

4.	The test is considered successful if the Generation Resource or the Controllable Load Resource is able to meet a minimum of 75% of its initial Primary Frequency Response and 75% of its sustained Primary Frequency Response as calculated in the FMEs report posted on the Market Information System (MIS) Certified Area.  Any Generation Resource or Controllable Load Resource may use the FME report in lieu of testing.

a.	The calculation of Generation Resources or Controllable Load Resources initial and sustained Primary Frequency Response is detailed in Section 8, Attachment J.

b.	ERCOT shall evaluate initial and sustained Primary Frequency Response using an expected performance Governor droop of 5.78% for combined-cycle Resources.

5.	Intermittent Renewable Resources (IRRs) located behind one Point of Interconnection (POI), metered by one ERCOT-Polled Settlement (EPS) Meter, and operated as an integrated Facility may combine IRRs for the purposes of this test.

Definitions

Generation Resource or Controllable Load Resource Base Load = maximum rated capability (this value is not reduced for temporary output limitations of the Generation Resource or Controllable Load Resource due to auxiliary equipment outages, weather conditions, or fuel limitations, it is the “nameplate” rating of the Generation Resource or Controllable Load Resource).  For the IRR, the Base Load for purposes of this test shall be the Real-Time telemetered High Sustained Limit (HSL) (MW) of the IRR at the time of the FME.  The IRR shall use only a FME in which the IRR’s HSL is greater than 50% of the IRR’s total design output capability.

# HISTORICAL GENERATION RESOURCE OR CONTROLLABLE LOAD RESOURCE FREQUENCY RESPONSE TEST FORM

General Information

Unit Code (16 characters): 			Location (County):

Unit Name: 					Date of FME:

QSE: 						Resource Entity:

Historical Results

| Evaluation Point | Frequency |
| --- | --- |
| Time (sec) of FME (t(0)) |  |
| Pre-Perturbation Average Frequency (t(-2) to t(-16)) |  |
| Post-Perturbation Average Frequency (t(20) to t(52)) |  |

| 1 | Pre-Perturbation Average MW [T(-2 ) to T(-16)] |  |
| --- | --- | --- |
| 2 | Post-Perturbation Average MW [T(+20 to T(+52)] |  |
| 3 | Expected Initial Primary Frequency Response (MW) |  |
| 4 | Expected Sustained Primary Frequency Response (MW) |  |
| 5 | Adjusted Actual Initial Primary Frequency Response (MW) |  |
| 6 | Adjusted Actual Sustained Primary Frequency Response (MW) |  |
| 7 | Initial Response P.U. Performance |  |
| 8 | Sustained Response P.U. Performance |  |

Comments: ________________________________________________________________________________________________________________________________________________________________________________________________________________________

Submittal

Resource Entity Representative:  _______________________________________

QSE Representative:  ________________________________________________

Date submitted to ERCOT Representative:

[NOGRR204: Replace “Generation Resource and Controllable Load Resource Primary Frequency Response Test Procedures Based on Historical Data” and “Generation Resource and Controllable Load Resource Frequency Response Test Form” with the following upon system implementation of NPRR989:] Generation Resource, ENERGY STORAGE RESOURCE, and Controllable Load Resource Primary Frequency Response test Procedures Based on Historical Data Description of Historical Verification The purpose of this template is to allow the Entity that operates a Generation Resource, Energy Storage Resource (ESR), or a Controllable Load Resource to demonstrate acceptable frequency response of its Generation Resource(s), ESR(s), or Controllable Load Resource(s) based on historical data in order to minimize testing costs, scheduling conflicts and the risk of damage to equipment or Forced Outage. 1. All verifications will be based on at least one of the events from the published list of Frequency Measurable Events (FMEs). 2. Governor droop and Governor Dead-Band settings shall be set in accordance with Section 2.2.7. 3. For clarification purposes, the time of FME (t(0)), pre-perturbation average frequency and post-perturbation average frequency, as defined in Section 8, Attachment J, Initial and Sustained Measurements for Primary Frequency Response, will be used for the verification process. The values of these metrics will be identified in the FME Report. 4. The test is considered successful if the Generation Resource, ESR, or the Controllable Load Resource is able to meet a minimum of 75% of its initial Primary Frequency Response and 75% of its sustained Primary Frequency Response as calculated in the FMEs report posted on the Market Information System (MIS) Certified Area. Any Generation Resource, ESR, or Controllable Load Resource may use the FME report in lieu of testing. a. The calculation of Generation Resources, ESRs, or Controllable Load Resources initial and sustained Primary Frequency Response is detailed in Section 8, Attachment J. b. ERCOT shall evaluate initial and sustained Primary Frequency Response using an expected performance Governor droop of 5.78% for combined-cycle Resources. 5. Intermittent Renewable Resources (IRRs) located behind one Point of Interconnection (POI), metered by one ERCOT-Polled Settlement (EPS) Meter, and operated as an integrated Facility may combine IRRs for the purposes of this test. Definitions Generation Resource, ESR, or Controllable Load Resource Base Load = maximum rated capability (this value is not reduced for temporary output limitations of the Generation Resource, ESR, or Controllable Load Resource due to auxiliary equipment outages, weather conditions, or fuel limitations, it is the “nameplate” rating of the Generation Resource, ESR, or Controllable Load Resource). For the IRR, the Base Load for purposes of this test shall be the Real-Time telemetered High Sustained Limit (HSL) (MW) of the IRR at the time of the FME. The IRR shall use only a FME in which the IRR’s HSL is greater than 50% of the IRR’s total design output capability. # HISTORICAL GENERATION RESOURCE, ENERGY STORAGE RESOURCE, OR CONTROLLABLE LOAD RESOURCE FREQUENCY RESPONSE TEST FORM General Information Unit Code (16 characters): Location (County): Unit Name: Date of FME: QSE: Resource Entity: Historical Results Evaluation Point; Frequency. Time (sec) of FME (t(0)). Pre-Perturbation Average Frequency (t(-2) to t(-16)). Post-Perturbation Average Frequency (t(20) to t(52)). 1; Pre-Perturbation Average MW [T(-2 ) to T(-16)]. 2; Post-Perturbation Average MW [T(+20 to T(+52)]. 3; Expected Initial Primary Frequency Response (MW). 4; Expected Sustained Primary Frequency Response (MW). 5; Adjusted Actual Initial Primary Frequency Response (MW). 6; Adjusted Actual Sustained Primary Frequency Response (MW). 7; Initial Response P.U. Performance. 8; Sustained Response P.U. Performance. Comments: ________________________________________________________________________________________________________________________________________________________________________________________________________________________ Submittal Resource Entity Representative: _______________________________________ QSE Representative: ________________________________________________ Date submitted to ERCOT Representative:

Intermittent renewable resource (IRR) Frequency Response Test Procedure

Description of the Test

1.	The frequency response function of the Intermittent Renewable Resource (IRR) is tested On-Line at a Load level that allows the IRRs to increase or decrease Load without reaching low operating limits or high operating limits.

2.	The test is performed by adding a frequency offset signal that exceeds the Governor Dead-Band value to the measured frequency signal.  This should create immediate step change in the measured frequency signal.

3.	The test starts at time t0 when the frequency Dead-Band is exceeded.

4.	The MW output signal should be recorded at least every two seconds.

5.	The duration of the test is 100 seconds.  After 100 seconds, the offset signal should be removed and the IRR should return to pretest power output.

6.	The test should be conducted both with positive and negative frequency offsets.

7.	The test is considered successful after the signal becomes active if at least 70% of the calculated MW contribution is delivered within 16 seconds and the response is maintained for an additional 30 seconds.

8.	Governor droop and Governor Dead-Band settings shall be set in accordance with Section 2.2.7.

9.	IRRs located behind one POI, metered by one ERCOT-Polled Settlement (EPS) Meter, and operated as an integrated Facility may combine IRRs for the purposes of this test.

Definitions

IRR Base Load = IRR telemetered High Sustained Limit (HSL) at the time of the test. The test shall be performed at an output level which is greater than 50% of IRR’s total design output capability.

Gain MW for 0.1Hz consistent with a selected droop percentage =

P∗10Droop∗60−GovernorDead−Band

Where:

P = IRR telemetered HSL (MW)

Droop 	= droop (%)

Frequency Offset = +0.2 Hz and -0.2 Hz, outside Governor Dead-Band

Test frequency = Measured Frequency + Frequency Offset

MW Contribution = Gain MW to 0.1 Hz * 10 * Frequency Offset

Calculated droop = - P∗ΔHz60∗ΔMW

Where:

P = IRR telemetered HSL (MW)

ΔHz = Change in frequency (Hz), taking into account Governor Dead-Band

ΔMW = Change in power output (MW)

Example

IRR telemetered HSL = 150 MW

Droop = 0.05 or 5% (use 0.05 for calculation)

Governor Dead-Band = 0.017 Hz

Gain MW for 0.1 Hz = 150[(0.05∗60)−0.017]∗10 = +/- 5.03 MW/0.1 Hz

∆MW Contribution = 5.03 * 10* +/-0.2 = +/-10.06 MW

Expected under-frequency response:	 +10.06 MW in 16 sec. for -0.2 Hz offset

Expected over-frequency response: 	-10.06 MW in 16 sec. for +0.2 Hz offset

Minimum accepted under-frequency response: +7.04 MW in 16 sec. for -0.2 Hz offset

Minimum accepted over-frequency response: -7.04 MW in 16 sec. for +0.2 Hz offset

Calculated droop for 8MW increase in power output in 16 sec. for -0.2 Hz offset:

Calculated percent droop = -150∗−0.260∗8 *100 = 6.25%

Intermittent renewable resource (IRR) FREQUENCY RESPONSE TEST FORM

General Information

Unit Code (16 characters): 				Location (County):

Unit Name: 						Date of Test:

QSE: 							Resource Entity:

Test Results

|  |  | Test with +0.2 Hz | Test with -0.2 Hz |
| --- | --- | --- | --- |
| 1 | IRR Base Load |  |  |
| 2 | GAIN MW to 0.1Hz |  |  |
| 3 | Calculated Minimum MW Contribution |  |  |
| 4 | MW at test start (t0) |  |  |
| 5 | MW at t0 + 16 sec |  |  |
| 6 | MW Contribution at t0 + 16 sec |  |  |
| 7 | MW at t0 + 46 sec |  |  |
| 8 | Calculated droop |  |  |
| 9 | CONCLUSION (PASSED/FAILED) |  |  |

Comments: ________________________________________________________________________________________________________________________________________________________________________________________________________________________

Submittal

Resource Entity Representative:  _____________________________________________

QSE Representative:  ______________________________________________________

Date submitted to ERCOT Control Area Authority Rep.: __________________________

# Controllable load resource Frequency Response Test Procedure

Description of the Test

1.	The frequency response function of the Controllable Load Resource is tested On-Line at a Load level that allows Controllable Load Resources to increase or decrease Load without reaching Low Power Consumption (LPC) or Maximum Power Consumption (MPC).

2.	The test is performed by adding a frequency offset signal that exceeds the Governor Dead-Band value to the measured frequency signal.  This should create an immediate step change in the measured frequency signal.

3.	The test starts at time t0 when the frequency Dead-Band is exceeded.

4.	The MW output signal should be recorded at least every two seconds.

5.	The duration of the test is 100 seconds.  After 100 seconds, the offset signal should be removed and the Controllable Load Resource should return to pretest power output.

6.	The test should be conducted both with positive and negative frequency offsets.

7.	The test is considered successful after the signal becomes active if at least 70% of the calculated MW contribution is delivered within 16 seconds and the response is maintained for an additional 30 seconds.

8.	Governor droop and Governor Dead-Band settings shall be set in accordance with Section 2.2.7.  For Controllable Load Resources, Governor droop shall not exceed 5% and Governor Dead-Band shall not exceed +/-0.036Hz.

[NOGRR204: Replace item (8) above with the following upon system implementation of NPRR989:] 8. Governor droop and Governor Dead-Band settings shall be set in accordance with Section 2.2.7.

Definitions

Controllable Load Resource Base Load = Controllable Load Resource telemetered MPC at the time of the test.  The test shall be performed at an output level that allows the Controllable Load Resource to increase or decrease Load without reaching LPC or MPC.

Gain MW for 0.1Hz consistent with a selected droop percentage =

P(Droop∗60−GovernorDead−Band)∗10

Where:

P = Controllable Load Resource telemetered MPC (MW)

Droop 	= droop (%)

Frequency Offset = +0.2 Hz and -0.2 Hz, outside Governor Dead-Band

Test frequency = Measured Frequency + Frequency Offset

MW Contribution = Gain MW to 0.1 Hz * 10 * Frequency Offset

Calculated droop = - P∗ΔHz60∗ΔMW

Where:

P = Controllable Load Resource telemetered MPC

ΔHz = Change in frequency (Hz), taking into account Governor Dead-Band

ΔMW = Change in power output (MW)

Example

Controllable Load Resource telemetered MPC = 150 MW

Droop = 5%

Governor Dead-Band = 0.036 Hz

Gain MW to 0.1 Hz = 150[(0.05∗60)−0.036]∗10 = +/- 5.06 MW/0.1 Hz

∆MW Contribution = 5 * 10* +/-0.2 = +/-10.12 MW

Expected under-frequency response:  -10.12 MW in 16 sec. for -0.2 Hz offset

Expected over-frequency response:  +10.12 MW in 16 sec. for +0.2 Hz offset

Minimum accepted under-frequency response:  -7.08 MW in 16 sec. for -0.2 Hz offset

Minimum accepted over-frequency response:  +7.08 MW in 16 sec. for +0.2 Hz offset

Note:  The negative sign in expected under-frequency response and minimum accepted under-frequency response denotes the required reduction in power consumption.  Similarly the positive sign in expected over-frequency response and minimum accepted over-frequency response denotes the required increase in power consumption.

Calculated droop for 8 MW increase in power output in 16 sec. for -0.2 Hz offset:

Calculated percent droop = -150∗−0.260∗8 = 6.25%

Controllable load resource FREQUENCY RESPONSE TEST FORM

General Information

Unit Code (16 characters): 				Location (County):

Unit Name: 						Date of Test:

QSE: 							Resource Entity:

Test Results

|  |  | Test with +0.2 Hz | Test with -0.2 Hz |
| --- | --- | --- | --- |
| 1 | Controllable Load Resource Base Load |  |  |
| 2 | GAIN MW to 0.1 Hz |  |  |
| 3 | Calculated Minimum MW Contribution |  |  |
| 4 | MW at test start (t0) |  |  |
| 5 | MW at t0 + 16 sec |  |  |
| 6 | MW Contribution at t0 + 16 sec |  |  |
| 7 | MW at t0 + 46 sec |  |  |
| 8 | Calculated droop |  |  |
| 9 | CONCLUSION (PASSED/FAILED) |  |  |

Comments: ________________________________________________________________________________________________________________________________________________________________________________________________________________________

Submittal

Resource Entity Representative:  _____________________________________________

QSE Representative:  ______________________________________________________

Date submitted to ERCOT Control Area Authority Rep.:__________________________

Westinghouse recommends using only this test.

Westinghouse recommends using only this test.