## Slide 1
PDCWG Report to ROS
Chair: Jimmy Jackson, CPS Energy
Vice Chair: Vacant
ROS
March 03, 2022

## Slide 2: Report Overview & Notes
Report Overview
    Meeting Minutes
    BAL-001-TRE-2 FMEs and IMFR
      1 FME in the month of January
    Frequency Control Report

## Slide 3: Meeting Minutes
  PDCWG Meeting 2/16/2022
  Open Meeting
    Update on RRS PFR Limit Study (GE)
    High level review of 2 Non-FMEs in January
    High level review of one FME in January
    Reviewed ERCOT Reports
      Frequency Control Metrics
      Regulation Reports
  Closed Meeting
    Detailed review of FME on 1/26/2022 2:27:47

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 1 FME in January
  1/26/2022 2:27:47
    Loss of 814 MW generation
    Interconnection Frequency Response: 1,131 MW/0.1 Hz
    39 Resources were evaluated. These includes,
      37 Generation Resources
      2 Controllable Load Resources
      0 Energy Storage Resources
    0 of 37 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    1 of 37 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 412 MW/0.1 Hz
IMFR Performance currently
1090.33 MW/0.1HZ

## Slide 7
Questions?

## Slide 8: Frequency Control Report
January 2022

## Slide 9: CPS1 Performance

## Slide 10: RMS1 Performance of ERCOT Frequency

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections

## Slide 13: ERCOT Total Energy
Notes: 33,399,938 MWh

## Slide 14: ERCOT Total Energy from Wind Generation
Notes: 8,448,159 MWh

## Slide 15: ERCOT % Energy from Wind Generation
Notes: 25.29 %

## Slide 16: ERCOT Total Energy from Solar Generation
Notes: 1,335,908 MWh

## Slide 17: ERCOT % Energy from Solar Generation
Notes: 4.00 %