## Improvement Cost Summary
| Project Cost | [5 empty] | XFMR MVA
| 345 | 138 | 115 | 69 | Total |  | 345 | 138 | 115 | 69 | Total
2024 Completed | 921499000 | 1620995446 | 0 | 486133577.09 | 3028628023.09 | 2024 Completed | 6950 | 498 | 0 | 0 | 7448 | For ROS and BOD Reports
2025 Completed | 524574000 | 728353000 | 0 | 101869000 | 1354796000 | 2025 Completed | 3600 | 0 | 0 | 120 | 3720 | ·All Projects (in engineering, routing, licensing and construction): | [5 empty] | 18966661200
2025 Planned | 1165249000 | 1494881000 | 0 | 310689000 | 2970819000 | 2025 Planned | 3700 | 378.8 | 0 | 300 | 4378.8 | ·Transmission Projects Energized in 2025: | [5 empty] | 1354796000
2026 | 3713653990 | 2584221500 | 15000000 | 684645000 | 6997520490 | 2026 | 9406 | 550 | 0 | 0 | 9956 | ·Transmission Projects Planned to Energize in 2025: | [5 empty] | 2970819000
2027 | 2366456000 | 1708659280 | 0 | 546185000 | 4621300280 | 2027 | 7122 | 355 | 0 | 0 | 7477
2028 | 803870000 | 894293430 | 0 | 327538000 | 2025701430 | 2028 | 2112 | 0 | 0 | 0 | 2112
2029 | 651170000 | 446625000 | 0 | 56320000 | 1154115000 | 2029 | 2022 | 0 | 0 | 0 | 2022
2030 | 704920000 | 303209000 | 0 | 2000000 | 1010129000 | 2030 | 5700 | 0 | 0 | 0 | 5700
2031 | 26000000 | 58400000 | 0 | 64986000 | 149386000 | 2031 | 0 | 0 | 0 | 0 | 0
2032 | 0 | 37690000 | 0 | 0 | 37690000 | 2032 | 0 | 0 | 0 | 0 | 0
2025 Completed | 524574000 | 728353000 | 0 | 101869000 | 1354796000 | 2025 Completed | 3600 | 0 | 0 | 120 | 3720
2025 Planned | 921598000 | 1291761000 | 0 | 198569000 | 2411928000 | 2025 Planned | 2800 | 40 | 0 | 300 | 3140
2024-2032 | 10877391990 | 9877327656 | 15000000 | 2580365577.09 | 23350085223.09 | 2024-2032 | 40612 | 1781.8 | 0 | 420 | 42813.8
2024-2025 | 2611322000 | 3844229446 | 0 | 898691577.09 | 7354243023.09 | 2024-2025 | 14250 | 876.8 | 0 | 420 | 15546.8
2026-2032 | 8266069990 | 6033098210 | 15000000 | 1681674000 | 15995842200 | 2026-2032 | 26362 | 905 | 0 | 0 | 27267
| Circuit Miles New |  |  |  |  | Circuit Miles Rebuilt, Reconductored or Upgraded | [5 empty] | Total Circuit Miles New, Rebuilt, Reconductored or Upgraded
| 345 | 138 | 115 | 69 | Total |  | 345 | 138 | 115 | 69 | Total |  | 345 | 138 | 115 | 69 | Total
2024 Completed | 187.18 | 56.574 | 0 | 9.8 | 253.554 | 2024 Completed | 27.32 | 566.41 | 0 | 210.68 | 804.41 | 2024 Completed | 214.5 | 622.984 | 0 | 220.48 | 1057.964
2025 Completed | 0.1 | 17.55 | 0 | 0 | 17.65 | 2025 Completed | 11.3 | 167.25 | 0 | 50.84 | 229.39 | 2025 Completed | 11.4 | 184.8 | 0 | 50.84 | 247.04
2025 Planned | 54.85 | 143.049 | 0 | 1.33 | 199.229 | 2025 Planned | 4.5 | 213.6 | 0 | 134.01 | 352.11 | 2025 Planned | 54.85 | 355.819 | 0 | 135.34 | 546.009
2026 | 683.33 | 119.48 | 3 | 1.1 | 806.91 | 2026 | 159.31 | 525.97 | 0 | 282.39 | 967.67 | 2026 | 842.64 | 645.45 | 3 | 283.49 | 1774.58
2027 | 82.8 | 47.62 | 0 | 2.7 | 133.12 | 2027 | 234.6 | 377.95 | 0 | 317.04 | 929.59 | 2027 | 317.4 | 425.57 | 0 | 319.74 | 1062.71
2028 | 47 | 96.8 | 0 | 0 | 143.8 | 2028 | 179.1 | 395.738 | 0 | 273.921 | 848.759 | 2028 | 226.1 | 487.038 | 0 | 273.921 | 987.059
2029 | 291.4 | 33.24 | 0 | 2 | 326.64 | 2029 | 46.2 | 106.41 | 0 | 78.39 | 231 | 2029 | 337.6 | 139.65 | 0 | 80.39 | 557.64
2030 | 357.12 | 49.9 | 0 | 0 | 407.02 | 2030 | 176.83 | 246.05 | 0 | 0 | 422.88 | 2030 | 533.95 | 295.95 | 0 | 0 | 829.9
2031 | 0 | 0 | 0 | 1.2 | 1.2 | 2031 | 92.1 | 32.48 | 0 | 38.18 | 162.76 | 2031 | 92.1 | 32.48 | 0 | 39.38 | 163.96
2032 | 0 | 1.7 | 0 | 0 | 1.7 | 2032 | 0 | 20.05 | 0 | 0 | 20.05 | 2032 | 0 | 21.75 | 0 | 0 | 21.75
2025 Completed | 0.1 | 17.55 | 0 | 0 | 17.65 | 2025 Completed | 11.3 | 167.25 | 0 | 50.84 | 229.39 | 2025 Completed | 11.4 | 184.8 | 0 | 50.84 | 247.04
2025 Planned | 54.55 | 141.139 | 0 | 1.33 | 197.019 | 2025 Planned | 4.5 | 158.45 | 0 | 70.42 | 233.37 | 2025 Planned | 54.55 | 299.589 | 0 | 71.75 | 425.889
2024-2032 | 1703.78 | 565.913 | 3 | 18.13 | 2290.823 | 2024-2032 | 931.26 | 2651.908 | 0 | 1385.451 | 4968.619 | 2024-2032 | 2630.54 | 3211.491 | 3 | 1403.581 | 7248.612
2024-2025 | 242.13 | 217.173 | 0 | 11.13 | 470.433 | 2024-2025 | 43.12 | 947.26 | 0 | 395.53 | 1385.91 | 2024-2025 | 280.75 | 1163.603 | 0 | 406.66 | 1851.013
2026-2032 | 1461.65 | 348.74 | 3 | 7 | 1820.39 | 2026-2032 | 888.14 | 1704.648 | 0 | 989.921 | 3582.709 | 2026-2032 | 2349.79 | 2047.888 | 3 | 996.921 | 5397.599

## Current Year Planned Projects
JUNE BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 6/1/2025
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar ) (-Reactor, +Capacitor ) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | RPG Number | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number | RTP Project Number
4010 | Rebuild Magnolia - Seminole 138 kV line. | *Project pushed back to 2023. |  | Magnolia Sub | Seminole Sub | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 | STE07216 | 2024-03-01 |  | 138 | 0 | 3.3 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 38950, 38990 | Y |  |  |  | 11530 | 4010
43212B | Caymus Capbanks in TNMP West Texas System | Expands Caymus Capacitor bank by 1 block of 20 Mvar. |  | Caymus (Bus #38410) | Caymus (Bus #38410) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 | NTE07819 | 2024-05-31 |  | 138 | 0 | 0 | 0 | 0,20 | Reeves | Reeves | Tier 4 |  |  |  |  | 38410 | Y |  |  |  | 48414 | 43212
48415B | TransPecos Capbank in TNMP West Texas System | Expands TransPecos Capacitor bank by 1 block of 20 Mvar. |  | TransPecos (Bus #38377) | TransPecos (Bus #38377) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 | NTE07919 | 2024-05-31 |  | 138 | 0 | 0 | 0 | 0,20 | Reeves | Reeves | Tier 4 |  |  |  |  | 38377 | Y |  |  |  | 48417 | 48415
66113 | Add WalnutSpr Auto & 138kV Switchyard |  |  | Oncor Walnut Springs (Bus # 1646, 1647) | TNMP Walnut Springs (Bus # 37680, 37681) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2024-06-01 |  | 138 | 0 | 0 | 208.8 |  | Bosque | Bosque | Tier 4 |  |  |  |  | 1646, 1647, 37680, 37681 | Y |  |  |  | 66115 | 66113
91774 | Janka: Construct New 345 kV Station | Interconnect the Evergrid load to the new Janka 345 kV station on the Edith Clarke to Tesla 345 kV line |  | Edith Clarke | Tesla | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | TP2025126 | 2025-01-23 |  | 345 | 0.2 | 0 | 0 |  | Hardeman | Hardeman | Tier 4 |  |  |  |  | 60139, 60501, 60505, 61616 | Y | N |  |  | 91775 | 91774
68252 | Lobo: Line settings | Interconnect Guajillo to the Lobo 345 kV station | Owner and Contact Update | Lobo |  | Under Construction |  | ETT | Michael Forcum mlforcum@aep.com 918-599-2674 |  | 2025-01-30 |  | 345 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  |  | 80219, 163223 | Y |  |  |  | 68253 | 68252
90004 | Juncus: Construct New 69 kV Temporary Tap | Interconnect the TEC Snodgrass load to the new Juncus 69 kV temporary tap on the Abilene South to Steamboat 69 kV line |  | Juncus |  | Planned |  | AEP TNC | Bill Edwards twang1@aep.com 918-599-2635 | TP2023074 | 2025-03-31 |  | 69 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  |  | 6326, 6328, 60002 | Y | Y |  |  | 91319 | 90004
81354 | GSEC_9452_Add_Snodgrass_Sub | Adding new Snodgrass sub to connect to AEP's Juncus Station. | Add New Load and Sub |  |  | Planned |  | GSEC | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2025-04-01 |  | 69 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  |  | 9452, 60002 | Y | Y |  |  | 81355 | 81354
45511 | Laredo to Del Mar: 138 kV Line Rebuild | Rebuild Laredo to Del Mar 138 kV Line |  | Laredo | Del Mar | Planned | 992 - 1170 | AEP TCC | William Lovelace mlforcum@aep.com 918-599-2674 | 3746 | 2025-04-30 |  | 138 | 0 | 2.73 | 0 |  | Webb | Webb | Tier 4 |  |  |  |  | 8293, 8645 | Y | N |  |  | 65531 | 45511 | 2018-S4
50847 | Sage: Expand 69 kV station | Build Heron 138 kV station with a 138/69 kV auto, expand the Kinnison 138 kV station, expand the Sage 69 kV station, rebuild Heron to Ollin and convert to a 138 kV line, and rebuild Kinnison to Sage 69 kV line | In-Service Date Update | Sage |  | Planned | 1048 - 1221 | AEP TNC | Gregory Crane twang1@aep.com 918-599-2635 | 2799 | 2025-04-30 |  | 69 | 0 | 0 | 0 |  | Crane |  | Tier 3 |  | 2019-06-21 | 2019-06-21 |  | 6604 | Y | N |  |  | 50848 | 50847
50900 | Mason to North Brady: Rebuild 69 kV line | Rehab Mason to North Brady 69 kV line |  | Mason | North Brady | Planned | 1046 - 1219 | AEP TNC | Chris Carroll twang1@aep.com 918-599-2635 | 2794 | 2025-04-30 |  | 69 | 0 | 30.24 | 0 |  | Mason | McCulloch | Tier 3 | 19RPG019 | 2019-10-01 | 2019-11-01 |  | 6006, 6381, 6393, 6406, 60386 | Y | N |  |  | 65550 | 50900
82829 | New Furhman Substation | Adds New Furhman switching station on Rayburn - Vanderbilt line for generator interconnect |  | Rayburn | Vanderbilt | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-04-30 |  | 138 | 0.84 | 0 | 0 |  | Victoria | Victoria | Tier 4 |  |  |  |  | 5502, 5506, 5584 | Y | N |  |  | 82830 | 82829
45174 | Ollin to LCRA Crane: Partial Build, Partial Rebuild, and Conversion | Build new Ollin 138 kV station; partial build, rebuild, and conversion to 138 kV of Ollin to LCRA Crane; and rebuild McElroy to Sage |  | Ollin | LCRA Crane | Planned | 939 - 1117 | AEP TNC | Greg Crane twang1@aep.com 918-599-2635 | 2767 | 2025-04-30 01:00 |  | 138 | 0.52 | 0 | 0 |  | Crane | Crane | Tier 4 | 19RPG013 |  |  |  | 6600, 6605, 6606, 6610, 6613, 6668, 6669, 60428, 60429, 60431, 60432, 60441, 76615 | Y | N |  |  | 65527 | 45174
81544 | GSEC_9466_Add_CampSprings_Sub | Add Big Country's Camp Springs Sub 9MW | ISD exceeds NMMS model load date |  |  | Planned |  | GSEC | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2025-05-01 |  | 138 | 0 | 0 | 0 |  | Fisher |  | Tier 4 |  |  |  |  | 9466, 68012 | Y |  |  |  | 81545 | 81544
76194 | Angstrom: Construct New 345 kV Terminal | Interconnect Pintail Pass BESS to the Angstrom 345 kV station |  | Angstrom |  | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 | TP2023132 | 2025-05-01 |  | 345 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  |  | 8249, 8956 | Y |  |  |  | 76195 | 76194
90446 | Avila BESS 138kV Gen Tie. |  |  |  |  | Under Construction | 88914 | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-05-01 |  | 138 | 0.22 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  |  | 38340, 136502 | Y |  |  |  | 90447 | 90446
65661 | Rebuild Wickett-Pyote 138 kV line |  |  | Wickett (but # 37981) | Pyote (bus # 38001) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-05-01 |  | 138 | 0 | 12.88 | 0 |  | Ward | Ward | Tier 4 |  |  |  |  | 37981, 38001 | Y |  |  |  | 65662 | 65661
90730 | TNMP Willow 345kV Switching Station |  |  |  |  | Under Construction |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-05-01 |  | 345 | 0 | 0 | 0 |  | Robertson | Robertson | Tier 4 |  |  |  |  | 3400, 39950, 39960, 121035 | Y |  |  |  | 90731 | 90730
71930 | Upgrade RIOHONDO to BURNS line | Upgrade RIOHONDO to BURNS line to be 478MVA capable |  | Rio Hondo | Burns | Under Construction | 7192671928 | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-05-01 |  | 138 | 0 | 12.2 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  |  | 5763, 8319 | Y |  |  |  | 71931 | 71930
70884 | Rebuild Rio Colorado - Bay City | Rebuild Rio Colorado - Bay City 795 ACSR |  | Rio Colorado | Bay City | Under Construction |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-05-01 |  | 69 | 0 | 9.5 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  |  | 5560, 5563 | Y |  |  |  | 70885 | 70884
90393 | Evelyn BESS 138kV Gen Tie. |  |  |  |  | Under Construction | 86784 | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-05-06 |  | 138 | 0.23 | 0 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 38900, 114262 | Y |  |  |  | 90443 | 90393
89984 | Kangaroo 345 kV Switch | Establish Kangaroo 345 kV Switch |  | Blackwater Draw Switch | Ogallala | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3030 | 2025-05-14 |  | 345 | 0 | 0 | 0 |  | Castro | Castro | Tier 4 |  |  |  |  | 23912, 23915, 23920, 144842 | Y |  |  |  | 89985 | 89984
66569 | Rebuild and reconfigure the existing Mulberry Creek 345 kV Switch | Rebuild and reconfigure the existing Mulberry Creek 345 kV Switch |  | Mulberry Creek | Mulberry Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R9022 | 2025-05-15 |  | 345 | 0 | 0 | 0 |  | Jones | Jones | Tier 3 | 21RPG021 | 2021-12-17 | 2022-01-12 |  | 1435, 1459, 6235, 11420 | Y |  |  |  | 81422 | 66569
76274 | Hamilton Road: Construct New 138 kV Terminal | Interconnect Tierra Seca BESS to the Hamilton Road 138 kV station | Status Update | Hamilton Road |  | Under Construction |  | AEP TCC/ETT | Robert Dougherty jlsolis@aep.com 361-881-5574 | TP2023133 | 2025-05-18 |  | 138 | 0.1 | 0 | 0 |  | Val Verde |  | Tier 4 |  |  |  |  | 8255, 8684, 8688, 8690 | Y |  |  |  | 76275 | 76274
48816 | Mulberry Creek: Rebuild 345 kV station | Rebuild Mulberry Creek 345 kV station and replace both autotransformers |  | Mulberry Creek |  | Under Construction | 1015 - 1193 | AEP TNC | Forrest Farson twang1@aep.com 918-599-2635 | 2776 | 2025-05-28 01:00 |  | 345 | 0 | 0 | 900 |  | Jones |  | Tier 4 | 21RPG021 | 2021-12-15 | 2022-01-13 |  | 1435, 1459, 6230, 6231, 6232, 6235, 11420, 60040, 60788, 60789 | Y | N |  |  | 65536 | 48816
93348 | Adds Cochise Customer Sub |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-05-30 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 38160, 38190 | Y |  |  |  | 93349 | 93348
70779 | Tortuga: Install Cap Bank | Install a 23.0 MVAR capacitor bank at the Tortuga 138 kV station |  | Tortuga |  | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 | TP2022188 | 2025-05-30 |  | 138 | 0 | 0 | 0 | 0,23 | Nueces |  | Tier 4 |  |  |  |  | 8697 | Y |  |  |  | 70780 | 70779
69467 | Dupont to Resnik: Rebuild 138 kV Line | Rebuild the Dupont to Resnik 138 kV line | Contact Update | Dupont | Resnik | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 |  | 2025-05-30 |  | 138 |  | 0.83 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  |  | 8422, 8580 | Y |  |  |  | 69468 | 69467
73408 | Odysseus: Build new 345 kV station | Interconnect Ulysses Solar to the Odysseus 345 kV Station on the Bluff Creek to SA Red Creek 345 kV line |  | Odysseus |  | Planned |  | AEP TNC | Zach Lachiusa twang1@aep.com 918-599-2635 |  | 2025-05-30 |  | 345 | 0 | 0 | 0 |  | Coke |  | Tier 4 |  |  |  |  | 6444, 60040, 60072 | Y | N |  |  | 73409 | 73408
76574 | TexasAg Wind Interconnection | Interconnect TexasAg to the Brisita 345 kV station |  | Brisita |  | Planned |  | ETT | John Solis jlsolis@aep.com 361-881-5574 | TP2023129 | 2025-05-30 |  | 345 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  |  | 8383, 8574, 8693, 88693 | Y |  |  |  | 76575 | 76574
87889 | Install 2x 40 MVAR Cap bank at League City. |  |  | League City (38920) |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-05-31 |  | 138 | 0 | 0 | 0 | 0,80 | Galveston | Galveston | Tier 4 |  |  |  |  | 38920 | Y |  |  |  | 87890 | 87889
78495 | Hillje 345kV Substation Expansion for Space City Solar - Generator Interconnection (21INR0341) | Expand Hillje 345kV substation and install one generator lead for new interconnection to MIDANE customer substation for Space City Solar |  | Hillje | MIDANE | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 |  | 345 | 0 | 0 | 0 |  | Wharton | Wharton | Tier 4 |  |  |  |  | 44200, 112261 | Y | N |  |  | 78496 | 78495
50845 | Kinnison: Expand 138 kV station | Build Heron 138 kV station with a 138/69 kV auto, expand the Kinnison 138 kV station, expand the Sage 69 kV station, rebuild Heron to Ollin and convert to a 138 kV line, and rebuild Kinnison to Sage 69 kV line | In-Service Date Update | Kinnison |  | Under Construction | 1048 - 1221 | AEP TNC | Gregory Crane twang1@aep.com 918-599-2635 | 2797 | 2025-05-31 |  | 138 | 0 | 0 | 130 |  | Crane |  | Tier 3 |  | 2019-06-21 | 2019-07-22 |  | 6604, 6607, 6611, 60431, 60432 | Y | N |  |  | 65545 | 50845
50868 | Rosata - Structure 31/8: Line Rebuild | Coleto Creek - Kenedy SS: Line Rebuild |  | Rosata | Kenedy SS | Planned | 1052 - 1225 | AEP TCC | Curtis Brown mlforcum@aep.com 918-599-2674 | 3780 | 2025-05-31 |  | 138 | 0 | 15.5 | 0 |  | Goliad | Karnes | Tier 3 | 20RPG014 | 2020-08-19 | 2020-09-11 |  | 8153, 8186 | Y | N |  |  | 50869 | 50868
49574 | Tesla: Build 345 kV terminal | Interconnect Misae II solar farm at Tesla | Status and In-Service Date Update | Tesla |  | Under Construction | 1023 - 1201 | ETT | Raza Ansari twang1@aep.com 918-599-2635 | 2785 | 2025-05-31 |  | 345 | 0 | 0 | 0 |  | Childress |  | Tier 4 |  |  |  |  | 60501, 143964 | Y | N |  |  | 49575 | 49574
86011 | Snug 138kV Substation expansion for Cottonwood Bayou Storage (21INR0443) | Install Cottonwood Bayou Storage (21INR0443) at Snug 138kV substation. Connect at the same generator lead as Cottonwood Bayou Solar. |  | Snug |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  |  | 44890, 113435 | Y | N |  |  | 86012 | 86011
63635 | Tribute: Build 138 kV Station | Build new 138 kV Station on the San Angelo Power to Red Creek 138 kV line | In-Service Date Update | Tribute |  | Planned | 1132 - 1310 | AEP TNC | Larry Brown twang1@aep.com 918-599-2635 | 1877 | 2025-05-31 |  | 138 | 0 | 0 | 0 |  | Tom Green |  | Tier 4 |  |  |  |  | 6442, 6473, 60008 | Y | N |  |  | 63636 | 63635
63924 | Quasar: Build New 345 kV Station | Interconnect Brass Fork Solar to the Clear Crossing to Coulomb 345 kV Line | In-Service Date Update | Quasar |  | Planned | 1138 - 1316 | ETT | Zach Lachiusa twang1@aep.com 918-599-2635 | 1883 | 2025-05-31 |  | 345 | 0 | 0 | 0 |  | Haskell |  | Tier 4 |  |  |  |  | 60514, 60703, 60712 | Y | N |  |  | 63925 | 63924
67921 | Sisseton: Build 69 kV tap | Build new 69 kV tap on the Aspermont to Hamlin 69 kV line | Contact Update | Sisseton |  | Planned |  | AEP TNC | Charles Burks twang1@aep.com 918-599-2635 |  | 2025-05-31 |  | 69 | 0 | 0 | 0 |  | Jones |  | Tier 4 |  |  |  |  | 6073, 6156, 6184, 6185, 6186, 6187, 60068 | Y |  |  |  | 67922 | 67921
70349 | Belknap to Fort Griffin: Rebuild 69 kV Line | Rehab Belknap to Fort Griffin 69 kV line | In-Service Date Update | Belknap | Fort Griffin | Planned |  | AEP TNC | Forrest Farson twang1@aep.com 918-599-2635 |  | 2025-05-31 |  | 69 | 0 | 23.6 | 0 |  | Jones | Shackelford | Tier 4 | 22RPG020 | 2022-06-27 | 2022-07-22 |  | 6178, 6210, 6214, 60398, 60409, 60445, 60466, 60471 | Y | N |  |  | 70350 | 70349
69463 | Gulch: Construct new 345 kV Station | Interconnect Arroyo Solar to the new Gulch 345 kV station on the La Palma to Rio Hondo 345 kV line | Contact and In-Service Date Update | Gulch |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2025-05-31 |  | 345 | 0.1 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  |  | 8317, 8318, 8704, 8705 | Y |  |  |  | 70802 | 69463
72880 | Sisseton: Build 69 kV station | Build 69 kV switch station on the Aspermont to Hamlin 69 kV line | Contact Update | Sisseton |  | Planned |  | AEP TNC | Charles Burks twang1@aep.com 918-599-2635 | TP2022059 | 2025-05-31 |  | 69 | 0 | 0 | 0 |  | Jones |  | Tier 4 |  |  |  |  | 6073, 6156, 6184, 6185, 6186, 6187, 60068 | Y |  |  |  | 72881 | 72880
72935 | Saragosa: Install 2nd Bay | Install 2nd Bay at Saragosa Substation |  | Saragosa |  | Planned |  | AEP TNC | Damian Raab twang1@aep.com 918-599-2635 |  | 2025-05-31 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  |  | 60716 | Y | N |  |  | 72936 | 72935
76151 | Gas Pad Tap: Replace CTVT | Replace CTVT combination unit at Gas Pad station along the Lote Bush to Yucca Drive 138 kV line | In-Service Date Update | Gas Pad Tap |  | Planned |  | AEP TNC | Bill Edwards twang1@aep.com 918-599-2635 |  | 2025-05-31 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  |  | 11245, 60397 | Y | N |  |  | 76152 | 76151
76918 | Primavera 138 kV: Construct new station | New station to serve Tesla load | In-Service Date Update | Primavera |  | Planned |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 | TP2023059 | 2025-05-31 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 8003, 8518, 8749, 8921, 88747 | Y |  |  |  | 76919 | 76918
82321 | PMCR for 2nd TX in Coachwhip | [6 empty] | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-05-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 38170 | Y |  |  |  | 82322 | 82321
75835A | Upgrade Ckt.66B Stone Lake to Tomball to increase thermal limits. Install 40 MVAR cap bank at Hockley substation and tapped on Ckt.66B Hockley to Stone Lake. | Partial reconductor Ckt.66B Stone Lake to Tomball. Upgrade equipment to increase thermal limits. Phase One of overall approved upgrades |  | Stone Lake | Tomball | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 |  | 138 | 0 | 5.71 | 0 |  | Harris | Harris | Tier 3 | 23RPG012 | 2023-05-04 | 2023-05-26 | 2023-05-26 | 44840, 46510, 48348 | Y | N |  |  | 90210 | 75835
78485B | Britmoore to Bellaire Ckt.24B Upgrades | Upgrade Ckt.09A Britmoore to Hayes to Alief to increase thermal limits. |  | Britmoore | Alief | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 |  | 138 | 0 | 2 | 0 |  | Harris | Harris | Tier 3 | 23RPG025 | 2023-09-06 | 2023-09-28 | 2023-09-28 | 44020, 44120, 44310 | Y | N |  |  | 90167 | 78485
51012 | Kinnison to Sage: Rebuild 69 kV line | Build Heron 138 kV station with a 138/69 kV auto, expand the Kinnison 138 kV station, expand the Sage 69 kV station, rebuild Heron to Ollin and convert to a 138 kV line, and rebuild Kinnison to Sage 69 kV line | In-Service Date Update | Kinnison | Sage | Planned | 1048 - 1221 | AEP TNC | Gregory Crane twang1@aep.com 918-599-2635 | 2823 | 2025-05-31 01:00 |  | 69 | 0 | 0.25 | 0 |  | Crane | Crane | Tier 3 |  | 2019-06-21 | 2019-07-17 |  | 6604, 60431 | Y | N |  |  | 65555 | 51012
81315 | add 19.2 MVAR Capacitor at Rossville | add 19.2 MVAR Capacitor at Rossville. 2023 RTP |  | Rossville |  | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-06-01 |  | 69 | 0 | 0 | 0 | 0,19.2 |  |  | Tier 4 |  |  |  |  | 5718 | Y |  |  |  | 87403 | 81315
80422 | Add_Triangle_Park_Load |  |  | Triangle Park |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2025-06-01 |  | 138 | 0 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  |  | 32854 | Y |  |  |  | 89954 | 80422
90450 | Headcamp BESS 138kV Gen Tie. |  |  |  |  | Under Construction | 85045 | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-06-16 |  | 138 | 0.1 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  |  | 38465, 136432 | Y |  |  |  | 90451 | 90450
78459 | Peters 138kV Substation Expansion for Walstrom BESS (22INR0540) | Expand Peters 138kV substation for generator lead to WALSTR (WAL) / Walstrom BESS (22INR0540). |  | Peters |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-06-19 00:01 |  | 138 | 0 | 0 | 0 |  | Austin | Austin | Tier 4 |  |  |  |  | 46220, 171382 | Y | N |  |  | 78460 | 78459
6253 | AEN_New_Kramer_Lane_Substation |  |  | 9238 | 9276 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2025-06-26 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9077, 9238, 9276 | Y |  |  |  | 13981 | 6253
86043 | Saxet Substation Addition Phase 2 | This PMCR models the phase 2 cut-in of T437 Nueces Bay – Lon Hill with the second Saxet Hard Tap. LCRA TSC will add a temporary Tap on T437 |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2025-06-30 | 2025-07-21 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 8441, 8452, 78568 | Y |  |  |  | 86044 | 86043
70704A | Florence Substation Addition |  |  | Andice | Glasscock | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-6320 | 2025-06-30 | 2025-05-15 | 138 | 0 | 0 | 0 |  | Williamson |  | Tier 4 |  |  |  |  | 7521, 7523, 70522 | Y | N |  |  | 70705 | 70704
76690 | Add Atchison POD | Add Atchison POD |  | Border Switch | Atchison | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8698 R8726 | 2025-06-30 |  | 138 | 7 | 0 | 0 |  | Loving | Loving | Tier 4 |  |  |  |  | 11089, 11189, 18670, 18672 | Y |  |  |  | 76691 | 76690
70019 | Add 138kV Locust-Hickory line 700MVA |  |  | Locust | Hickory | Planned |  | DME | Mark Zimmerer 940-349-7169 |  | 2025-06-30 | 2025-06-30 | 138 | 0 | 1.85 | 0 |  | Denton | Denton | Tier 4 | N/A |  |  |  | 922, 924 | Y | N |  |  | 70020 | 70019 | N/A
62068 | Lakeway - Marble Falls Transmission Line Storm Hardening | Increase the reliability of transmission facilities on the T497 Lakeway - Marble Falls 23-mile 138-kV transmission line. |  | Lakeway | Marble Falls | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2025-06-30 | 2025-05-16 | 138 | 0 | 0 | 0 |  | Travis | Burnet | Tier 4 | 22RPG031 | 2022-10-12 | 2022-11-03 |  | 7348, 7349, 7351, 7356, 7474, 7476, 7538, 7540 | Y | N | 22RPG031 reclassified as Tier 4 neutral by RPG review on 11/03/2022 |  | 62069 | 62068
66221M | Galena Park Area Conversion Project | Reconfigure Galena Park by removing the temporary Ckt.94M Galena Park loop. Tap Galena Park transformer on Ckt.21K between Fidelity and Witter. |  | Fidelity | Witter | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-06-30 00:06 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 3 | 21RPG020 | 2021-11-30 | 2021-12-22 | 2021-12-22 | 40611, 40630, 48610 | Y | N |  | Cost included in main entry | 90304 | 66221
45155 | Ollin: Build 138 kV station | Construct new Ollin 138 kV station | Status and In-Service Date Update | Ollin |  | Under Construction | 939 - 1117 | AEP TNC | Greg Crane twang1@aep.com 918-599-2635 | 2752 | 2025-06-30 01:00 |  | 138 | 0.1 | 0 | 0 |  | Crane |  | Tier 4 | 19RPG013 |  |  |  | 6600, 6604, 6605, 6606, 6607, 6610, 6611, 6613, 6668, 6669, 60428, 60429, 60431, 60432, 60441, 76615 | Y | N |  |  | 45156 | 45155
93003 | Adds TNMP Turkeyfoot 69kV Substation |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-07-01 |  | 69 | 0 | 0 | 0 |  | Bosque | Coryell | Tier 4 |  |  |  |  | 37470, 37515, 37520 | Y |  |  |  | 93183 | 93003
64776 | Upgrade 138kV DentonWest-RDWells line to 700MVA (SUM2024) |  |  | RD Wells | Denton West | Planned |  | DME | Mark Zimmerer 940-349-7169 |  | 2025-07-01 | 2025-07-01 | 138 | 0 | 4.47 | 0 |  | Denton | Denton | Tier 4 | N/A |  |  |  | 930, 986 | Y | N |  |  | 64777 | 64776 | N/A
5430O | Conversion to 138kV | Reconnect the 69kV Hickory - RD Wells to the 138kV Hickory and RD Wells substations. Line is already insulated for 138kV. |  | Hickory | RD Wells | Planned | N/A | DME | Mark Zimmerer Mark.Zimmerer@cityofdenton.com 940-349-7169 |  | 2025-07-01 | 2025-07-01 | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 |  | 2015-11-10 |  | 2016-01-20 | 922, 930 | Y | N | N/A |  | 55209 | 5430 | N/A
5430K | Conversion to 138kV | Construct new 138kV Hickory substation and terminate the existing Bonnie Brae - Hickory (which is already insulated for 138kV) at the new 138kV Hickory substation. |  | Bonnie Brae | Hickory | Planned | N/A | DME | Mark Zimmerer Mark.Zimmerer@cityofdenton.com 940-349-7169 |  | 2025-07-01 | 2025-07-01 | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 |  | 2015-11-10 |  | 2016-01-20 | 922, 931 | Y | N | N/A |  | 55205 | 5430 | N/A
86782 | Add Dansk load serving substation | Cuts in new Dansk load serving station on existing Red Bluff to Danevang transmission line |  |  |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-07-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  | 2024-02-01 |  | 5546, 5549, 5588 | Y | N |  |  | 86783 | 86782
77648B | Establish Tiger Creek 345 kV Switch for Jaguar Solar/BESS | Tiger Creek Switch - Jaguar Solar/BESS 345 kV Line |  | Tiger Creek Switch | Jaguar Solar/BESS | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6223 | 2025-07-14 |  | 345 | 0.5 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 3379, 153783 | Y |  |  |  | 87809 | 77648
90448 | Bocanova BESS 138kV Gen Tie. |  |  |  |  | Under Construction | 89822 | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-07-19 |  | 138 | 0.1 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 39030, 114342 | Y |  |  |  | 90449 | 90448
93681 | New Transformer will be added Loma Alta. |  |  | Loma Alta | Loma Alta | Planned |  | BPUB | Luis Martinez lugmartinez@brownsville-pub.com 956-983-6212 |  | 2025-07-24 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5943, 5962 | Y |  |  |  | 93682 | 93681
72882 | Lockhart - Luling 69-kV Transmission Line Overhaul | LCRA TSC will perform an overhaul on the 15.8-mile Lockhart – Luling (T157) 69-kV transmission line. This project will increase reliability of the structures and conductor by ensuring that the transmission line meets or exceeds current NESC and LCRA TSC design standards. |  | Lockhart | Luling | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2025-07-30 | 2025-06-27 | 69 | 0 | 15.83 | 0 |  | Caldwell | Caldwell | Tier 4 | 23RPG004 | 2023-02-24 | 2023-03-20 |  | 7215, 7218, 7220, 7223 | Y | N |  |  | 72883 | 72882
87479H | Upgrade to increase thermal limits as part of FRM upgrades | Upgrade Stadium to Fannin Ckt.08B to increase thermal limits as part of FRM upgrades |  | Stadium | Fannin | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 | [5 empty] | Y | N |  |  | 87824 | 87479
87479G | Upgrade to increase thermal limits as part of FRM upgrades | Upgrade Hyde Park to Downtown Ckt.32A to increase thermal limits as part of FRM upgrades |  | Hyde Park | Downtown | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47510, 47690 | Y | N |  |  | 87823 | 87479
90232F | Facility Ratings Methodology (FRM) Upgrades | Upgrade Bellaire to Jeanetta Ckt.64B to increase thermal limits as part of FRM upgrades |  | Bellaire | Jeanetta | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 345 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47000, 47300 | Y | N |  |  | 90915 | 90232
90232I | Facility Ratings Methodology (FRM) Upgrades | Upgrade Hyde Park to Downtown Ckt.32A to increase thermal limits as part of FRM upgrades |  | Hyde Park | Downtown | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47510, 47690 | Y | N |  |  | 90916 | 90232
90232B | Facility Ratings Methodology (FRM) Upgrades | Upgrade Ckt.99A PH Robinson to Meadow to increase thermal limits as part of FRM upgrades |  | PH Robinson | Meadow | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 345 | 0 | 0 | 0 |  | Galveston | Brazoria | Tier 4 |  |  |  |  | 42000, 43030 | Y | N |  |  | 90917 | 90232
90232D | Facility Ratings Methodology (FRM) Upgrades | Upgrade Bellaire to WAP Ckt.50A to increase thermal limits as part of FRM upgrades |  | Bellaire | WA Parish | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 345 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 44005, 47000 | Y | N |  |  | 90918 | 90232
90232G | Facility Ratings Methodology (FRM) Upgrades | Upgrade Stadium to Fannin Ckt.08B to increase thermal limits as part of FRM upgrades |  | Stadium | Fannin | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 345 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47090, 47420 | Y | N |  |  | 90919 | 90232
90232C | Facility Ratings Methodology (FRM) Upgrades | Upgrade Ckt.06D NASA to Webster to increase thermal limits as part of FRM upgrades |  | NASA | Webster | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 42970, 43500 | Y | N |  |  | 90920 | 90232
90232A | Facility Ratings Methodology (FRM) Upgrades | Upgrade Ckt.03A PSARCO to BIGVUE to increase thermal limits as part of FRM upgrades |  | PSARCO | BIGVUE | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40190, 41301 | Y | N |  |  | 90921 | 90232
90232E | Facility Ratings Methodology (FRM) Upgrades | Upgrade Jeanetta to WA Parish Ckt.64A to increase thermal limits as part of FRM upgrades |  | Jeanetta | WA Parish | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 345 | 0 | 0 | 0 |  | Harris | Fort Bend | Tier 4 |  |  |  |  | 44005, 47300 | Y | N |  |  | 90922 | 90232
64069 | Charger Solar Interconnection | Connect the Charger Interconnection to the Angstrom to STP 345 kV line | Status, Contact, and In-Service Date Update | Angstrom | STP | Under Construction |  | AEP TCC | Dave Goetz deevans@aep.com 918-599-2938 | TP2021165 | 2025-07-31 |  | 345 | 0 | 0 | 0 |  | Refugio |  | Tier 4 |  |  |  |  | 5915, 8249, 8676, 8678 | Y |  |  |  | 64070 | 64069
76234 | Wormser Road: Construct New 138 kV Terminal | Interconnect Seven Flags BESS to the Wormser Road 138 kV station | In-Service Date Update | Wormser Road |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 | TP2023311 | 2025-07-31 | 2958101 | 138 |  |  |  |  | Webb |  | Tier 4 |  |  |  |  | 8295 | Y |  |  |  | 76235 | 76234
87479F | Upgrade to increase thermal limits as part of FRM upgrades | Upgrade Bellaire to Jeanetta Ckt.64B to increase thermal limits as part of FRM upgrades |  | Bellaire | Jeanetta | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 345 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47000, 47300 | Y | N |  |  | 87822 | 87479
87479I | Upgrade to increase thermal limits as part of FRM upgrades | Upgrade Hyde Park to Downtown Ckt.32A to increase thermal limits as part of FRM upgrades |  | Kirby | Garrott | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47321, 47660 | Y | N |  |  | 87821 | 87479
87479D | Upgrade to increase thermal limits as part of FRM upgrades | Upgrade Bellaire to WAP Ckt.50A to increase thermal limits as part of FRM upgrades |  | Bellaire | WAP | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 345 | 0 | 0 | 0 |  | Harris | Fort Bend | Tier 4 |  |  |  |  | 44005, 47000 | Y | N |  |  | 87820 | 87479
87479C | Upgrade to increase thermal limits as part of FRM upgrades | Upgrade Ckt.06D NASA to Webster to increase thermal limits as part of FRM upgrades |  | NASA | Webster | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 42970, 43500 | Y | N |  |  | 87819 | 87479
87479B | Upgrade to increase thermal limits as part of FRM upgrades | Upgrade Ckt.99A PH Robinson to Meadow to increase thermal limits as part of FRM upgrades |  | PH Robinson | Meadow | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 345 | 0 | 0 | 0 |  | Galveston | Brazoria | Tier 4 | [5 empty] | Y | N |  |  | 87818 | 87479
87479A | Upgrade to increase thermal limits as part of FRM upgrades | Upgrade Ckt.03A PSARCO to BIGVUE to increase thermal limits as part of FRM upgrades |  | PSARCO | BIGVUE | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40190, 41305 | Y | N |  |  | 87817 | 87479
87479E | Upgrade to increase thermal limits as part of FRM upgrades | Upgrade Jeanetta to WA Parish Ckt.64A to increase thermal limits as part of FRM upgrades |  | Jeanetta | WAP | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-07-31 |  | 345 | 0 | 0 | 0 |  | Harris | Fort Bend | Tier 4 |  |  |  |  | 44005, 47300 | Y | N |  |  | 87825 | 87479
90452 | Red Egret BESS 138kV Gen Tie. |  |  |  |  | Under Construction | 76067 | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-08-01 |  | 138 | 1.15 | 0 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 38820, 113533 | Y |  |  |  | 90453 | 90452
90903 | ALUVIUM gen tie station |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-08-01 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 39500, 39515, 110505 | Y |  |  |  | 90905 | 90903
90353 | Establish Sandy Ranch 345 kV Switch | Establish Sandy Ranch 345 kV Switch |  |  |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3125 | 2025-08-01 |  | 345 | 0 | 0 | 0 |  | Hopkins | Hopkins | Tier 4 |  |  |  |  | 1697, 2464, 2621, 121022 | Y |  |  |  | 90354 | 90353
72647 | Add_Blue_Ridge_Load |  |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2025-08-01 |  | 69 | 0 | 0 | 0 |  | Collin | Collin | Tier 4 |  |  |  |  | 6803, 37240, 37245, 37280 | Y |  |  |  | 78600 | 72647
66200D | Upgrade Taylor - Holland 69 kV Line | Rebuild the Granger - Taylor 69 kV Line |  | Taylor | Holland | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6173 | 2025-08-15 |  | 69 | 0 | 5.9 | 0 |  | Williamson | Williamson | Tier 4 | 22RPG036 |  |  |  | 118, 3648, 3649, 13647 | Y |  |  |  | 71897 | 66200
92434 | Establish Gindale 345 kV Switch | Establish Gindale 345 kV Switch for Stillhouse Solar |  | Gindale | Gindale | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6286 | 2025-08-31 |  | 345 | 0 | 0 | 0 |  | Milam | Milam | Tier 4 |  |  |  |  | 3762, 154543 | Y |  |  |  | 92435 | 92434
91565 |  |  |  | Navarro Mills Tap | Navarro Mills | Under Construction |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2025-09-01 |  | 69 | 0 | 1.1 | 0 |  | Navarro | Navarro | Tier 4 |  |  |  |  | 186, 3511 | Y |  |  |  | 91566 | 91565
90851 | add 19.2 MVAR Capacitor at Rio Colorado |  |  |  |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-09-01 12:00 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5563 | Y |  |  |  | 90852 | 90851
66210 | Upgrade and convert Lake Creek - Marlin 69 kV Line to 138 kV | Upgrade and convert Lake Creek - Marlin 69 kV Line to 138 kV. Relocate the Lake Creek 138/69 kV Auto to Marlin. |  | Lake Creek | Marlin | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R1743 | 2025-09-15 |  | 138 | 0 | 13.7 | 0 |  | Falls | Falls | Tier 4 |  |  |  |  | 3410, 3411, 3416, 3418, 3694, 3695, 13401, 13639 | Y |  |  |  | 66211 | 66210
71950 | Twin Buttes Load 138-KV Circuit Breaker Addition | Provide a 138-kV point of interconnection at the Twin Buttes Substation to connect to a new Golden Spread Electric Cooperative Transmission line. Update contingencies |  | Twin Buttes |  | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2025-09-16 |  | 138 | 0 | 0 | 0 |  | Tom Green | Tom Green | Tier 4 | [5 empty] | Y | N |  |  | 78299 | 71950
90786 | Establish Yarrelton 345 kV Switch | Establish Yarrelton 345 kV Switch for Hermes Solar and Storage |  | Yarrelton | Yarrelton | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6261 | 2025-09-29 |  | 345 | 0 | 0 | 0 |  | Bell | Bell | Tier 4 |  |  |  |  | 3687, 3762, 3766, 154643 | Y |  |  |  | 90787 | 90786
76214 | North Edinburg: 345 kV Reconfigure | Reconfigure North Edinburg 345 kV station: 2nd reactor | Contact Update | North Edinburg |  | Planned |  | AEP TCC | Curtis Brown jlsolis@aep.com 361-881-5574 | TP2019168 | 2025-09-30 |  | 345 | 0 | 0 | 0 | -50,0 | Hidalgo |  | Tier 4 |  |  |  |  | 5660, 8341, 8383, 8452, 8455, 8901, 8905 | Y |  |  |  | 76215 | 76214
80466 | Oleander: Construct New 138 kV Terminal | Interconnect Citrus Flatts BESS to the Oleander 138 kV station |  | Oleander |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2025-09-30 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 | [5 empty] | Y |  |  |  | 80467 | 80466
76686 | Hog Mountain 138 kV POD | Add Hog Mountain 138 kV POD |  | Quartz Sand | Hog Mountain POD | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8673 R8791 | 2025-09-30 |  | 138 | 5.4 | 0 | 0 |  | Glasscock | Glasscock | Tier 4 |  |  |  |  | 1229, 18552 | Y |  |  |  | 76687 | 76686
71935 | Upgrade Hondo Creek to Castroville to 138kV | Upgrade Castroville sub to 138kV and line from Hondo creek to Castroville |  |  |  | Planned | 71917 | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-09-30 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 2 | 22RPG022 |  |  |  | 5804, 5807, 5808, 5810, 5819, 5821 | Y |  |  |  | 73097 | 71935
71937 | Caterpillar Substation | Add T6, 40 MVA. 138-26.08 kV PWT to Caterpillar Substation |  | Caterpillar |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2025-09-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 | [5 empty] | Y | N |  |  | 71938 | 71937
85965 | RGEC_Altuda 69-kV In-line_Breaker_Installation | Install 69-kV breaker between Alpine Switch and Persimmon Gap substation at Altuda substation. |  | Alpr2A (6665) | PrsmnGap2A (6669) | Planned |  | RGEC | Larry T. Powell lpowell@rgec.coop 830-563-6178 |  | 2025-09-30 |  | 69 | 0 | 0 | 0 |  | Brewster | Brewster | Tier 4 | [5 empty] | Y |  |  |  | 85966 | 85965
76139 | Juncus: Construct New 69 kV Station | Interconnect the TEC Snodgrass load to the new Juncus 69 kV station on the Abilene South to Steamboat 69 kV line |  | Juncus |  | Planned |  | AEP TNC | Bill Edwards twang1@aep.com 918-599-2635 | TP2023074 | 2025-09-30 |  | 69 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  |  | 6326, 6328, 60002 | Y | Y |  |  | 76140 | 76139
76076 | Laredo VFT North to North Laredo Switch: Rebuild 138 kV Line | Rebuild Las Cruces to Milo 138 kV line | In-Service Date Update | Las Cruces | Milo | Planned | 1116 - 1294 | AEP TCC/ETT | William Lovelace jlsolis@aep.com 361-881-5574 | 3835 | 2025-09-30 |  | 138 | 0 | 2.4 | 0 |  | Webb | Webb | Tier 4 |  |  |  |  | 8112, 8918 | Y |  |  |  | 76077 | 76076
73448 | Roma: Build new 138 kV terminal | Bordertown BESS interconnection to Roma Station on Roma Switch to Rio Grande City | In-Service Date Update | Roma |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2025-09-30 |  | 138 | 0 | 0 | 0 |  | Starr |  | Tier 4 |  |  |  |  | 8795, 8796, 87960 | Y |  |  |  | 73449 | 73448
59197 | Mason to Mason Switch: Rebuild 69 kV Line | Rehab the Mason to Mason Switch 69 kV Line |  | Mason | Mason Swicth | Planned | 1126 - 1304 | AEP TNC | Forrest Farson twang1@aep.com 918-599-2635 | 1871 | 2025-09-30 |  | 69 | 0 | 10.3 | 0 |  | Mason | Mason | Tier 4 |  |  |  |  | 6393, 6394, 6396, 6407, 60458 | Y | N |  |  | 59198 | 59197
91285 | TNMP Lago Mar Substation |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-09-30 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 38815, 38820, 38850 | Y |  |  |  | 91286 | 91285
50878 | North Edinburg: 345 kV Reconfigure | Reconfigure the North Edinburg 345 kV station | Contact Update | North Edinburg |  | Planned | 1056 - 1229 | AEP TCC | Curtis Brown jlsolis@aep.com 361-881-5574 | 3786 | 2025-09-30 |  | 345 | 0 | 0 | 0 | -100,0 | Hidalgo |  | Tier 4 |  |  |  |  | 8341, 8383 | Y | N |  |  | 50879 | 50878
76705 | Prairieland 345/138 kV Switch and 138 kV Line | Establish Prairieland 345/138 kV Switch and Prairieland – Quartz Sand 138 kV Line |  | Prairieland | Quartz Sand | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8632 | 2025-09-30 |  | 138 | 6 | 0 | 0 |  | Glasscock | Glasscock | Tier 2 |  |  |  |  | 1030, 1058, 1229, 11387, 18548, 18549, 18550, 18551, 18552 | Y |  |  |  | 91943 | 76705
76624 | WA Parish 345kV Substation Expansion for Crowned Heron Storage (24INR0405) | Expand 345kV WA Parish substation for Crowned Heron Storage (24INR0405) |  | WA Parish | HERON | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-09-30 00:01 |  | 345 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  |  | 44000, 114042 | Y | N |  |  | 93236 | 76624
92695 | Switchgrass station and Customer sub |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-10-01 |  | 138 | 0 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  |  | 38069, 38070, 38071, 38294 | Y |  |  |  | 94008 | 92695
91494 |  |  |  | Perry | Perry | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2025-10-01 |  | 69 | 0 | 0 | 100 |  | Falls | Falls | Tier 4 |  |  |  |  | 91, 92 | Y |  |  |  | 91495 | 91494
70012 | West Weatherford to Oran Voltage Conversion | West Weatherford to Oran Voltage Conversion |  | West Weatherford | Oran | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2025-10-03 |  | 138 | 0 | 0.1 | 0 |  | Palo Pinto | Parker | Tier 4 |  |  |  |  | 515, 518, 519, 785, 1569, 1585, 1589 | Y |  |  |  | 70013 | 70012
72344 | PALMETTO_CUTIN |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-10-23 | 2023-10-10 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 39500, 39510, 110505 | N |  |  |  | 72345 | 72344
91911 | Establish Gristmill 345 kV Switch | Establish Gristmill 345 kV Switch for Yaupon Solar and Storage |  | Gristmill | Gristmill | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6232 | 2025-10-30 |  | 345 | 0 | 0 | 0 |  | Milam | Milam | Tier 4 |  |  |  |  | 3706, 3765, 39950 | Y |  |  |  | 91912 | 91911
87285 | Establish Stouts Creek 345 kV Switch | Establish Stouts Creek 345 kV Switch |  |  |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R984 | 2025-10-30 |  | 345 | 0 | 0 | 0 |  | Hopkins | Hopkins | Tier 4 |  |  |  |  | 1696, 2514, 12464, 120976 | Y |  |  |  | 87286 | 87285
80852 | Lolita: Construct New 138 kV Terminal | Interconnect Third Coast BESS to the Lolita 138 kV station | Contact Update | Lolita |  | Planned | TP2023138 | AEP TCC | Chase Isaac deevans@aep.com 918-599-2938 |  | 2025-10-30 |  | 138 | 0 | 0 | 0 |  | Jackson |  | Tier 4 |  |  |  |  | 8125 | Y | N |  |  | 80853 | 80852
73364 | CPSE_New_Omicron_Substation |  |  |  |  | Planned | T-350, S-0975 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2025-10-31 |  | 138 | 0 | 0 | 0 |  | Bexar |  | Tier 4 |  |  |  |  | 5055, 5326, 5355 | Y |  |  |  | 73365 | 73364
88046 | Rebuild Omicron to Rafter |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2025-10-31 |  | 138 | 0 | 1.7 | 0 |  | Bexar | Medina | Tier 2 |  |  |  |  | 5326, 5355 | Y |  |  |  | 88047 | 88046
71004A | Julia CNP-Owned Sub for Melaza Solar (21INR0220) | Install new Julia (JUL) CNP substation for generator interconnection to Maleza Solar. Loop Ckt.72 into Julia substation to create new Ckt.72 Hillje to Julia to Blue |  | Julia | Hillje/Blue | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 |  | 345 | 0 | 0 | 0 |  | Wharton |  | Tier 4 |  |  |  |  | 44060, 44200, 44220 | Y | N |  |  | 87171 | 71004
78490B | Jeanetta Auto Upgrades | Replace existing 600 MVA Jeanetta Auto A3 with 800 MVA autotransformer |  | Jeanetta |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 |  | 345 | 0 | 0 | 200 |  | Harris |  | Tier 3 | 23RPG031 | 2023-10-04 | 2023-10-26 |  | 47300, 47310, 49082 | Y | N |  |  | 79426 | 78490
78490A | Jeanetta Auto Upgrades | Replace existing 600 MVA Jeanetta Auto A1 with 800 MVA autotransformer |  | Jeanetta |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 |  | 345 | 0 | 0 | 200 |  | Harris |  | Tier 3 | 23RPG031 | 2023-10-04 | 2023-10-26 |  | 47300, 47310, 49024 | Y | N |  |  | 79425 | 78490
72065 | Lake Jackson Distribution Substation Conversion to Low-Profile | Rebuild Lake Jackson 138/12kV distribution substation to low-profile |  | Lake Jackson |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  |  | 42880, 43172 | Y | N |  |  | 72066 | 72065
93117 | Gibson: Construct New Distribution Station | Construct new distribution station on the Abilene South to Putnam 138 kV line between Abilene South and Vinson | NEW |  |  | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | DR24N0009 | 2025-10-31 |  | 138 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  |  | 6260, 60080, 60355 | Y | N |  |  | 93118 | 93117
80486 | Loxley: Construct New 138 kV Station | Interconnect the Loxley load to the new Loxley 138 kV station on the Pleasanton to Trumbo 138 kV line | Contact Update | Loxley |  | Planned |  | AEP TCC | Bill Edwards jlsolis@aep.com 361-881-5574 |  | 2025-10-31 | 2958101 | 138 | 0.1 | 0 | 0 |  | Atascosa |  | Tier 4 |  |  |  |  | 5429, 8203, 80491 | Y |  |  |  | 80487 | 80486
80858 | Sterling City: Upgrade 69 kV Relays | Upgrade relays at the Sterling City 69 kV station on the Angora 69 kV terminal | In-Service Date Update | Sterling City |  | Planned | TP2023887 | AEP TNC | Wade Weller twang1@aep.com 918-599-2635 |  | 2025-10-31 |  | 69 | 0 | 0 | 0 |  | Sterling |  | Tier 4 |  |  |  |  | 6435, 6484 | Y | N |  |  | 80859 | 80858
69473 | Jaguar: Construct New Distribution Station | Construct new distribution station on the McGruder to Thomaston 138 kV line | In-Service Date Update | Jaguar |  | Under Construction |  | AEP TCC | Will Simmons deevans@aep.com 918-599-2938 |  | 2025-10-31 |  | 138 | 0 | 0 | 40 |  | Victoria |  | Tier 4 |  |  |  |  | 8183, 8194, 8724 | Y |  |  |  | 69474 | 69473
66122 | Tiempo: Build new 345 kV terminal | Interconnect Redonda Solar to the Tiempo 345 kV station | Status and Contact Update | Tiempo |  | Under Construction |  | ETT | Aaron Fahey jlsolis@aep.com 361-881-5574 | TP2022009 | 2025-10-31 |  | 345 | 0.1 | 0 | 0 |  | Zapata |  | Tier 4 |  |  |  |  | 80224, 80232 | Y |  |  |  | 66511 | 66122
78480A | Weinbrenner (WEI) 138kV CEHE Station for LONGPO (LNP) / Long Point Solar 19INR0042 | Loop new CEHE 138kV substation Weinbrenner (WEI) into Ckt.02J Burke to Eagle Nest to create new Ckt.02 Burke to Weinbrenner to Eagle Nest. |  | Weinbrenner | Burke/ Eagle Nest | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42410, 42430, 42990 | Y | N |  |  | 87161 | 78480
90157 | NRG THW GT at TH Wharton 345kV (24INR0482) | Install NRG THW GT at TH Wharton 345kV substation. Connect at the same generator lead as 05THWGEN |  | TH Wharton |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 |  | 345 | 0 | 0 | 0 |  | Harris |  | Tier 4 | [5 empty] | Y | N |  |  | 90159 | 90157
75810A | Install new 345kV Speedway substation for interconnection to Cradle Solar (23INR0150). Loop Ckt.18B into Speedway substation to create new Ckt.18 Oasis to Speedway to DOW. Install generator lead from Speedway to CRADLE solar | Install new 345kV Speedway (SPD) substation for generator interconnection to CRADLE/ Cradle Solar (23INR0150). Loop Ckt.18B into Speedway substation to create new Ckt.18 Oasis to Speedway to DOW. |  | Speedway | DOW/Oasis | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42500, 43035, 43060 | Y | N |  |  | 87165 | 75810
75776A | Samaritan 138kV Switching Station | In terms of completed Clute substation: Reconfigure Ckt.26 Angleton to Clute and loop into new CNP-owned 138kV Samaritan switching station to create new Ckt.26 Angleton to Samaritan to Clute. |  | Samaritan | Angleton/STRATT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42030, 42110, 43300 | Y | N |  |  | 87131 | 75776
75938 | Expand Zenith substation with addition of 35kV Distribution Facilities. Tap TR1 on Ckt.09J to create new Ckt.09J Zenith to Zenith TR1 tap to Fry Road tap. Tap TR2 on Ckt.76A to create new Ckt.76A Zenith to Zenith TR2 tap to Fry Road tap. | Expand Zenith substation with addition of 35kV Distribution Facilities. Tap TR1 on Ckt.09J to create new Ckt.09J Zenith to Zenith TR1 tap to Fry Road tap. Tap TR2 on Ckt.76A to create new Ckt.76A Zenith to Zenith TR2 tap to Fry Road tap. |  | Zenith | Fry Road | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 44910 | Y | N |  |  | 75939 | 75938
78427A | Bohemian (BOH) 138kV CEHE Substation for Destiny Storage (24INR0397) | Install new CEHE 138kV Bohemian (BOH) substation for generator interconnection to Destiny Storage. Loop Ckt.66K into substation to create new Ckt.66 Crosby to Bohemian to Eastgate. |  | Bohemian | Crosby/ Eastgate | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40390, 40690, 40970 | Y | N |  |  | 87352 | 78427
73371B | BP24 Sub Upgrades | Upgrade Bellaire Auto A5 CTs to increase thermal limits |  | Bellaire |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 00:01 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  |  | 47000, 47015, 49003 | Y | N |  |  | 89979 | 73371
75776B | Samaritan 138kV Switching Station | Connect Samaritan CNP substation with two leads to TNMP_White Oak distribution substation. |  | Samaritan | Angleton/Clute | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 00:01 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 39580, 42030 | Y | N |  |  | 87132 | 75776
75810B | Install new 345kV Speedway substation for interconnection to Cradle Solar (23INR0150). Loop Ckt.18B into Speedway substation to create new Ckt.18 Oasis to Speedway to DOW. Install generator lead from Speedway to CRADLE solar | Install generator lead from Speedway (SPD) substation to CRADLE (CDL) customer substation (23INR0150). |  | Speedway | CRADLE | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-10-31 00:01 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 | [5 empty] | Y | N |  |  | 87164 | 75810
72651 | Add_Josephine_Load | [6 empty] | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2025-11-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 991, 6991 | Y |  |  |  | 76031 | 72651
80508 | Kilby: Construct New 345 kV Station | Interconnect Quantum Solar to the new Kilby 345 kV station on the Clear Crossing to Pendulo 345 kV line |  | Kilby |  | Planned | TP2023844 | ETT | Dave Goetz twang1@aep.com 918-599-2635 |  | 2025-11-01 |  | 345 | 0 | 0 | 0 |  | Haskell |  | Tier 4 |  |  |  |  | 60089, 60507, 60514 | Y | N |  |  | 80509 | 80508
1205 | Planned reconductor from Hasse to Gustine | Planned reconductor from Hasse to Gustine |  | HASSE | GUSTINE | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2025-11-14 |  | 69 | 0 | 7.34 | 0 |  | Comanche | Comanche | Tier 4 |  |  |  |  | 273, 277 | Y |  |  |  | 54001 | 1205
87497 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2025-11-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 6903, 6908 | Y |  |  |  | 87498 | 87497
87905 | Hartring – Upland 138 kV Double Circuit Line | Construct new Hartring – Upland 138 kV Double Circuit Line |  | Ringo | LCRA Benedum | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8713 | 2025-11-15 12:00 |  | 138 | 18 | 0 | 0 |  | Upton | Reagan | Tier 2 | 24RPG024 | 2024-08-09 |  |  | 18671, 18674, 18675, 18676 | Y |  |  |  | 93273 | 87905
71879 | Update Ratings |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0939b | 2025-11-20 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5133, 5371 | Y |  |  |  | 71880 | 71879
72037A | Seabreeze 345kV Substation for Tanglewood Solar (23INR0054) | New 345kV Seabreeze (SEB) substation for generator interconnection to Tanglewood Solar (23INR0054). Loop Ckt.27B into Seabreeze substation to create new Ckt.27 DOW to Seabreeze to Oasis. |  | Seabreeze | DOW/Oasis | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-11-30 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42500, 43020, 43035 | Y | N |  |  | 87458 | 72037
80850 | Lon Hill to Sinton: Bypass Waterworks 69 kV station | Relocate portion of 69 kV line between Odem and Stevens Tap to bypass Waterworks 69 kV station | In-Service Date Update | Odem | Stevens Tap | Planned | TA2022133 | AEP TCC | Travis Coody deevans@aep.com 918-599-2938 |  | 2025-11-30 |  | 69 | 0 | 0.45 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 8810, 8865, 8867 | Y | N |  |  | 80851 | 80850
77122 | Mulberry Creek: Construct New 345 kV Terminal | Interconnect the Lancium load to the Mulberry Creek 345 kV station | In-Service Date and Dollars Update | Mulberry Creek |  | Planned | TP2023636 | AEP TNC | Forrest Farson twang1@aep.com 918-599-2635 |  | 2025-11-30 |  | 345 | 2.25 | 0 | 0 |  | Jones |  | Tier 4 |  |  |  |  | 6235 | Y | N |  |  | 77123 | 77122
80484 | Closner: Construct New 138 kV Terminal | Interconnect Gunnar BESS to the Closner 138 kV station. | In-Service Date Update | Closner |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2025-11-30 |  | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  |  | 8029 | Y |  |  |  | 80485 | 80484
80482 | North McAllen: Construct New 138 kV Terminal | Interconnect Carambola BESS to the North McAllen 138 kV station |  | North McAllen |  | Planned | TP2023631 | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2025-11-30 |  | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  |  | 8632 | Y |  |  |  | 80483 | 80482
48774 | Fincas: Build new 138 kV distribution station | Construct new distribution station on the University to Wormser 138 kV line | Status and In-Service Date Update | Fincas |  | Under Construction | 1026 - 1204 | AEP TCC | Travis Coody jlsolis@aep.com 361-881-5574 | 3765 | 2025-11-30 |  | 138 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  |  | 8039, 8649, 8653 | Y | N |  |  | 81145 | 48774
72566 | Cedar Valley to Friendship Storm Hardening | Rebuild single circuit section of Cedar Valley to Friendship and reconductor with bundled 795 ACSR Conductor, 440 MVA. Replaces Project ID 61268 |  | Cedar Valley | Friendship | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2025-11-30 |  | 138 | 0 | 4.3 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 70506, 70507 | Y | N |  |  | 72567 | 72566
72037B | Seabreeze 345kV Substation for Tanglewood Solar (23INR0054) | Install generator lead from Seabreeze (SEB) substation to TANGLE (TNG) customer substation (23INR0054). |  | Seabreeze | TANGLE | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-11-30 00:01 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 43020, 113341, 113345 | Y | N |  | Cost included in main phase | 87459 | 72037
93657 | [5 empty] | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-12-01 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 37513, 37520 | Y |  |  |  | 93658 | 93657
72588C | Trading Post to Cedar Valley Storm Hardening | Upgrading switch to bring line to full rating | [5 empty] | PEC | Charles Dewitt Charles.Dewitt@peci.com 830-868-5041 |  | 2025-12-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 70505, 70506 | Y |  |  |  | 91746 | 72588
92600 | John_Dumas_Circuit_Breaker_Addition | LCRA TSC will install transmission interconnection equipment and facilities at the John Dumas Substation, and cut-in T510 to John Dumas Substation. |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-7999 | 2025-12-01 |  | 345 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  |  | 7041, 7042 | Y |  |  |  | 92601 | 92600
82851 | Adds TNMP White Oak Substation |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-12-01 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 39580 | Y |  |  |  | 82852 | 82851
91419 | Max Zuehlke_Gay Hill_TL_Upgrade | Replace 336 (Linnet) conductor with 959 (Suwannee) and replace a limited number of structures to accommodate the new conductor. |  |  |  | Planned |  | BBEC | Curtis Fischer curtis.fischer@bluebonnet |  | 2025-12-01 |  | 138 | 0 | 0 | 0 |  | Washington | Washington | Tier 4 |  |  |  |  | 7565, 7572 | Y |  |  |  | 91420 | 91419
87475 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2025-12-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 2145, 6861 | Y |  |  |  | 87476 | 87475
82250 | TNMP Pilot Point Sub NB w/Tie to Oncor Gunter SW |  |  | Oncor 138kV Gunter Switching Station (bus # 2236) | TNMP Pilot Point Substation (bus # 37365) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-12-01 |  | 138 | 15.6 | 0 | 0 |  | Grayson | Denton | Tier 4 |  |  |  |  | 2236, 37365 | Y |  |  |  | 91908 | 82250
76788 | Upgrade Victoria-Rayburn | Upgrade Victoria- Loop 463- Rayburn to 403 MVA |  | Rayburn | Victoria | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-12-01 |  | 138 | 0 | 11.57 | 0 |  | Victoria | Victoria | Tier 4 |  |  |  |  | 5502, 5680, 8172 | Y |  |  |  | 76789 | 76788
66188 | Cedar Crest - Dealey - West Levee 138 kV Line | Upgrade the existing 138 kV Line |  | Ceadr Crest | West Levee | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4212 | 2025-12-01 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 2400, 2493, 2842 | Y |  |  |  | 66189 | 66188
71926 | Upgrade BURNS to Heidelberg line | Upgrade BURNS to Heidelberg line to be 478MVA capable |  | Burns | Heidelberg | Planned | 7192871930 | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-12-01 |  | 138 | 0 | 10 | 0 |  | Cameron | Hidalgo | Tier 4 |  |  |  |  | 5763, 5765 | Y |  |  |  | 71927 | 71926
71319 | Upgrade Pearsall Station | Upgrade Pearsall Station to breaker and a half |  | Pearsall | Pearsall | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-12-01 |  | 138 | 0 | 0 | 0 |  | Frio | Frio | Tier 4 |  |  |  |  | 5893, 5895 | Y |  |  |  | 71320 | 71319
70886 | Rebuild TinTop - Rio Colorado | Rebuild TinTop- Rio Colorado 795ACSR |  | Tin Top | Rio Colorado | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-12-01 |  | 69 | 0 | 15.5 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  |  | 5563, 5569 | Y |  |  |  | 70887 | 70886
55873 | Upgrade Moore to Hondo Creek 138 kV line | Replace the 336 ACSR with 1020 ACCC conductor while keeping the existing structures that still meet our standards. |  | Moore | Hondo Creek | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-12-01 |  | 138 | 0 | 13.5 | 0 |  | Medina | Frio | Tier 2 | 19RPG021 | 2019-11-20 | 2020-05-21 |  | 5819, 5827 | Y | N | Field engineering is still occurring due to short timeline for this upgrade. Details may change. | Current plan is to upgrade the line using mostly existing structures. Detailed field engineering is underway and could change the plan. | 55874 | 55873
89986 | Mule Deer 345 kV Switch | Establish Mule Deer 345 kV Switch |  | Windmill | Wallaby | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3031 | 2025-12-04 |  | 345 | 0 | 0 | 0 |  | Deaf Smith | Deaf Smith | Tier 4 |  |  |  |  | 23909, 23910, 23921 | Y |  |  |  | 89987 | 89986
86633 | Dusty Road 345 kV Switch | Establish Dusty Road 345 kV Switch |  | Tonkawa | Graham | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8809 | 2025-12-04 |  | 345 | 0 | 0 | 0 |  | Haskell | Haskell | Tier 4 |  |  |  |  | 1048, 1430, 11050 | Y |  |  |  | 86634 | 86633
70536 | New 138 kV Verde Circle Substation | New 138 kV Verde Circle Substation looping into existing 138 kV Westover Hills and VLSI line. |  |  |  | Planned | T-0316 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0971 | 2025-12-12 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5466, 5467, 5488 | Y |  |  |  | 70537 | 70536
66492A | Chico West - Grindstone Switch 69 kV Line rebuild | Upgrade Jacksboro Amoco - Jacksboro Sinclair 69 kV Line |  | Jacksboro Sinclair | Jacksboro Amoco | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3006 | 2025-12-15 |  | 69 | 0 | 14 | 0 |  | Jack | Jack | Tier 4 |  |  |  |  | 1542, 1555, 1556, 1557, 1558, 11556 | Y |  |  |  | 72962 | 66492
70900C | Roanoke Area Upgrades | Establish Exchange - Kingsridge 138 kV Double-Circuit Line |  | Exchange Switch | Kingsridge Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5281 M5144 M5146 M5148 | 2025-12-15 |  | 138 | 3.4 | 0 | 0 |  | Tarrant | Tarrant | Tier 1 | 21RPG008 | 2022-02-15 | 2022-03-15 | 2022-08-15 | 12036, 12080, 12081, 112033 | Y | N |  |  | 87468 | 70900
70900D | Roanoke Area Upgrades | Establish Dunham 345 kV Switch |  | Dunham Switch | Dunham Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5281 M5144 M5146 M5148 | 2025-12-15 |  | 345 | 0 | 0 | 0 |  | Tarrant | Tarrant | Tier 1 | 21RPG008 | 2022-02-15 | 2022-03-15 | 2022-08-15 | 646, 1730, 1849, 21851, 33646 | Y | N |  |  | 87469 | 70900
70900E | Roanoke Area Upgrades | Establish Ramhorn Hill 345 kV Switch and Ramhorn Hill – Dunham 345 kV Double-Circuit Line |  | Dunham Switch | Ramhorn Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5281 M5144 M5146 M5148 | 2025-12-15 |  | 345 | 36.8 | 0 | 0 |  | Tarrant | Tarrant | Tier 1 | 21RPG008 | 2022-02-15 | 2022-03-15 | 2022-08-15 | 1421, 2081, 21851, 31875 | Y | N |  |  | 87470 | 70900
72958 | Graham to Cottonwood 69 kV Line Rebuild | Graham to Cottonwood 69 kV Line Rebuild |  | Graham | Graham | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3001 | 2025-12-15 |  | 69 | 0 | 0 | 0 |  | Young | Young | Tier 4 |  |  |  |  | 1597, 1602, 1603 | Y |  |  |  | 72959 | 72958
62434 | Sargent Road - Industrial Blvd 138 kV DCKT Line | Upgrade existing 138 kV Line |  | Sargent Road Switch | Industrial Blvd Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4128 | 2025-12-15 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 2940, 2947, 2972, 2973, 2974, 2975 | Y |  |  |  | 62435 | 62434
71985 | Cypress Water 138 kV Switch | Rebuild the existing Northlake(Cypress Waters) 138 kV Switch |  | Northlake |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4353 | 2025-12-15 |  | 138 | 0 | 0 | 0 |  | Dallas |  | Tier 3 |  |  |  |  | 2362, 2363, 2367, 2385, 2386, 2390, 2395, 2587 | Y |  |  |  | 73110 | 71985
78363 | Gunter 345/138 kV Switch | Establish Gunter 345/138 kV Switch |  | Gunter |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3301 | 2025-12-15 |  | 345 | 0 | 0 | 600 | 75,0 | Collin |  | Tier 3 |  |  |  |  | 1730, 2235, 2236, 2373, 11735, 11757, 12235, 12468 | Y |  |  |  | 78364 | 78363
81175 | Salt Flat Road 138 kV Switch and Salt Flat Road - Barr Ranch - Reiter 138 kV Second Circuit | Add Salt Flat Road 138 kV Switch and Salt Flat Road - Barr Ranch - Reiter 138 kV Second Circuit & De-energize auto at Odessa EHV |  | Reiter | Salt Flat Road | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8704 | 2025-12-15 |  | 138 | 44 | 4.4 | 0 |  | Ector | Midland | Tier 3 |  |  |  |  | 1027, 1028, 1111, 1193, 1234, 1276, 11111, 11217, 11235, 11344, 18528, 18545, 18701, 23859 | Y |  |  |  | 93103 | 81175
91537 | Starlite_Substation_Addition | LCRA TSC will construct the 138-kV Starlite Substation to facilitate the Generation Interconnection Request (GINR) submitted for by the Interconnecting Entity, "Blanquilla BESS LLC" (Generator). |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2025-12-15 |  | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 8452, 78568, 78570 | Y |  |  |  | 91538 | 91537
81223 | Range Rider 138 kV Switch | Construct a new 138 kV switch replacing existing Range Rider 138 kV Switch. |  | Range Rider 138 kV Switch | Range Rider 138 kV Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8721 | 2025-12-15 |  | 345 | 0 | 0 | 0 |  | Mitchell | Mitchell | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1032 | Y |  |  |  | 81367 | 81223
72009 | Cattleman 345/138 kV Switch | Construct a new 345/138 kV Switch to replace existing Morgan Creek Switch |  | Cattleman | Cattleman | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8647 | 2025-12-15 |  | 345 | 0 | 0 | 1200 |  | Mitchell | Mitchell | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1030, 1032, 1058, 10053, 10054, 10055, 10056, 11395, 18548 | Y |  |  |  | 81376 | 72009
72596C | PEC_MarshallFord_Paleface_StormHardening | Upgrade to terminal equipment and update to final circuit rating. Terminal end equipment update to be completed Fall 2024 based on original project schedule. (Replaces ERCOT Project # 61274C) | 1/10/2023: Changes to description based on final design. | Paleface | Marshall Ford | Planned |  | PEC/LCRATSC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2025-12-15 |  | 138 | 0 | 11.5 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 70477, 77356 | Y | N |  |  | 73445 | 72596
76650 | Establish Walleye Creek 345/138 kV Switch | Establish Walleye Creek 345/138 kV Switch |  | Walleye Creek | Walleye Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6243 | 2025-12-15 |  | 345 |  | 4.5 | 600 | 0,110.4 | Milam | Milam | Tier 3 |  |  |  |  | 116, 3541, 3712, 3713, 3714, 3715, 3716, 3717, 3742, 7040, 13429, 13430 | Y |  |  |  | 76651 | 76650
80546B | Upgrade the Hutto & Round Rock - Salado 138 kV Line | Rebuild and double-circuit the Round Rock Westinghouse Tap - Georgetown East 138 kV Line Section |  | Round Rock Westinghouse Tap | Georgetown East | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6203, R6202 | 2025-12-15 |  | 138 | 9.1 | 9.1 | 0 |  | Williamson | Williamson | Tier 3 |  |  |  |  | 3664, 3669, 3677, 7528, 7532 | Y |  |  |  | 87619 | 80546 | 2023-SC17
80546A | Upgrade the Hutto & Round Rock - Salado 138 kV Line | Increase the maximum operating temperature the Hutto - Round Rock 138 kV Line |  | Hutto Switch | Round Rock Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6203, R6202 | 2025-12-15 |  | 138 | 0 | 8.8 | 0 |  | Williamson | Williamson | Tier 3 |  |  |  |  | 3664, 3666, 3667, 3668, 3670 | Y |  |  |  | 81498 | 80546 | 2023-SC17
90899 | Establish Woodbury 138 kV Switch | Establish Woodbury 138 kV Switch for Three W Solar |  | Woodbury | Woodbury | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6251 | 2025-12-15 |  | 138 | 0 | 0 | 0 |  | Hill | Hill | Tier 4 |  |  |  |  | 237, 3522, 3781 | Y |  |  |  | 90900 | 90899
87758 | Badger 345 kV Switch | Establish Badger 345 kV Switch for Sypert Branch Solar |  | Badger | Badger | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6317 | 2025-12-15 |  | 345 | 0 | 0 | 0 |  | Milam | Milam | Tier 4 |  |  |  |  | 3687, 3761, 13429 | Y |  |  |  | 87759 | 87758
5475 | Lufkin Switch - Redland Switch 345 kV Line | Construct a new 345 kV Line from Lufkin Switch to Redland Switch |  | Lufkin Switch | Redland Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6077 | 2025-12-15 |  | 345 | 8.1 | 0 | 0 |  | Angelina | Angelina | Tier 2 | 20RPG019 | 2020-10-01 | 2022-04-01 |  | 3117, 3321 | Y | N |  |  | 13180 | 5475
76135 | Hackberry Switch – DFW D-East 2 138 kV DCKT Line Section | Rebuild Hackberry Switch – DFW D-East 2 138 kV DCKT Line Section |  | Dallas | Dallas | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4347 M4357 | 2025-12-15 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 3 | 23RPG020 |  |  |  | 1996, 1997, 2001, 2010, 2388, 15020, 15021, 15025, 15026, 15045, 15046 | Y |  |  |  | 76136 | 76135 | 2022-NC6
66473 | Mesquite East Switch-Oates (GP&L)/Prairie Creek Switch 138 kV Double-Circuit Line | Upgrade the Mesquite East Switch-Oates (GP&L)/Prairie Creek Switch 138 kV Double-Circuit Line |  | Mesquite East | Oates | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4137 | 2025-12-15 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 831, 2742, 2747, 2756, 2764, 2765, 2766, 2767 | Y |  |  |  | 66475 | 66473
71178 | Seagoville-Watermill 138 kV Line | Rebuild Seagoville-Watermill 138 kV Line |  | Seagoville | Watermill | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4081 | 2025-12-15 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 3 |  |  |  |  | 2429, 2434, 3076, 3077, 3079, 3083 | Y |  |  |  | 71179 | 71178
66289B | Tyler to Athens 138 kV line Conversion | Establish Foggle Switch, Establish Poynor POI, Echols to Athens 69 kV Line Upgrade |  | Athens | Echols | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6094 | 2025-12-15 |  | 69 | 0 | 0 | 0 |  | Henderson | Henderson | Tier 3 | 22RPG015 | 2022-06-01 | 2022-07-01 |  | 3108, 3126, 3233, 3238, 3239, 3248, 3256, 3269, 3270, 3288, 3801, 6805 | Y |  |  |  | 92110 | 66289
62666B | Upgrade and convert McGregor - Waco West Line | McGregor Phillips - Waco West 138 kV Operation |  | McGregor Phillips | Waco West | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6172 | 2025-12-15 |  | 138 | 0 | 0 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  |  | 3370, 3372, 3436, 3437, 3440, 3441, 3446, 3562, 3584, 3585, 3594, 3596, 3793, 13436, 13438 | Y |  |  |  | 93100 | 62666
81389 | Sandhills Tap - Wolf 138 kV Line Rebuild | Sandhills Tap - Wolf 138 kV Line Rebuild |  | Odessa EHV | Wolf | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8528 | 2025-12-15 |  | 138 | 0 | 14.2 | 0 |  | Ector | Ward | Tier 3 |  |  |  |  | 1013, 1103, 11018 | Y |  |  |  | 87113 | 81389
81060 | Riverton-Border-Quarry Field 138 kV Second Circuit | Riverton-Border-Quarry Field 138 kV Second Circuit |  | Riverton | Quarry Field | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8733 | 2025-12-15 |  | 138 | 29.7 | 0 | 0 |  | Reeves | Loving | Tier 4 |  |  |  |  | 11083, 11089, 11189, 18672, 18677 | Y |  |  |  | 87856 | 81060
87830 | Oncor_FW__Blue Mountain 138 kV Capactior Bank | [6 empty] | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2025-12-15 |  | 138 | 0 | 0 | 0 | 0,110.4 |  |  | Tier 4 |  |  |  |  | 18680 | Y |  |  |  | 87831 | 87830
78471 | WA Parish 345kV Substation Expansion for Bypass Storage (23INR0336) | Expand 345kV WA Parish substation for Bypass Storage (23INR0336) |  | WA Parish | BYPASS | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-15 00:01 |  | 345 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  |  | 44000, 113801 | Y | N |  |  | 93237 | 78471
87861 | Range Rider - Ranger Camp 138 kV Double-Circuit Line | Construct a new 138 kV Double-Circuit Line from Range Rider to Ranger Camp Switch. |  | Ranger Camp 345/138 kV Switch | Range Rider 138 kV Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8722 | 2025-12-16 |  | 138 | 1.2 | 0 | 0 |  | Mitchell | Mitchell | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1032, 10050 | Y |  |  |  | 87862 | 87861
81274 | Ranger Camp – Cattleman 345 kV Double-Circuit Line | Construct a new 345 kV double-circuit line from Ranger Camp to Cattleman |  | Ranger Camp | Cattleman | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8648 | 2025-12-16 |  | 345 | 6.8 | 0 | 0 |  | Mitchell | Mitchell | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 10049, 10053 | Y |  |  |  | 81275 | 81274
72579A | PEC_MountainTop_Blanco_DevilsHill_VoltageUpgrade | Rebuild and upgrade Mountain Top to Blanco 69 kV circuit to 138 kV with bundled 795 kcmil conductor (440 MVA). (Replaces ERCOT Project # 70367A) |  | Mountain Top | Blanco | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2025-12-19 |  | 138 | 0 | 0 | 0 |  | Blanco | Blanco | Tier 4 | 22RPG033 |  | 2022-11-14 |  | 7148, 70480, 70482, 70484 | Y | Y |  |  | 72580 | 72579
69345 | Limmer Substation Addition | Construct a new LCRA TSC-owned Limmer Substation in the Hutto to Zorn 345 kV line approximately 3 miles east of Hutto. Limmer Substation will be installed initially as a five-breaker 345 kV breaker-and-a-half arrangement. |  | Zorn, Hutto | Limmer | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2025-12-22 |  | 345 | 0 | 0 | 0 |  | Williamson | Travis | Tier 3 | 22RPG027 | 2022-08-29 | 2022-09-27 |  | 3696, 7042, 7340, 7341 | Y | Y |  |  | 78338 | 69345
72574 | topo_update | Upgrade Junction from tap station to a three terminal ring bus. Replaces Project ID 63916. |  | NEW JUNCTION 70600 |  | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2025-12-25 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 70600 | Y |  |  |  | 80916 | 72574
72063 | Moody to Stewart Ckt.63 Upgrades P1041 | Reconductor portions of Ckt.63 Stewart to West Galveston as a Hardening project |  | Stewart | West Galveston | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-30 |  | 138 | 0 | 3.97 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 42950, 42951 | Y | N |  |  | 72064 | 72063
81270 | Construct the new Prong Moss 345 kV switch | Construct a new 345 kV switch |  | Prong Moss | Prong Moss | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3025 | 2025-12-30 |  | 345 | 0 | 0 | 0 |  | Howard | Howard | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1025, 10049, 10057, 10062 | Y |  |  |  | 81271 | 81270
70307 | BRYN_Standard_PMCR_Dansby_Rebuild_fix | Reference Project 4577 Dansby Rebuild. Project 4577 was added to convert Dansby 69kV bus to Breaker and a Half configuration. |  |  |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2025-12-31 |  | 69 | 0 | 0 | 200 |  | Brazos |  | Tier 4 |  |  |  |  | 32875, 32897 | Y |  |  |  | 75508 | 70307
68150 | Abilene South to Estes: Rebuild 138 kV Line | Rehab Abilene South to structure 33/7 |  | Abilene South | Estes | Under Construction |  | AEP TNC | Michael Glueck twang1@aep.com 918-599-2635 |  | 2025-12-31 | 2958101 | 138 | 0 | 18.3 | 0 |  | Taylor | Callahan | Tier 4 |  | 2022-02-01 | 2022-03-01 | 2022-03-01 | 6260, 6313, 60063, 60336, 60355, 60365, 60773, 61015 | Y | N |  |  | 68151 | 68150
72040B | Blueridge to WA Parish Ckt.02A Upgrades (22RPG041) | Upgrade portions of Ckt.02A Blueridge tap to DEWALT as a Hardening upgrade. |  | Blueridge | DEWALT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 |  | 138 | 0 | 2.94 | 0 |  | Harris | Fort Bend | Tier 4 | 22RPG041 | 2022-11-21 | 2022-12-15 | 2022-12-15 | 44180, 48163 | Y | N |  | Cost included in main entry | 91116 | 72040
86015 | King Substation - Add 3rd Distribution Transformer | Install the third King distribution transformer. Tap on Ckt.86E to create new Ckt.86E Newport to King tap to Jonte. |  | King | Newport/Jonte | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40912, 41150, 45660, 48182 | Y | N |  |  | 86016 | 86015
76350 | Install new TARGA 138kV customer substation as Ckt.86 Jordan to TARGA to CITIES. | Install new TARGA 138kV customer substation as Ckt.86 Jordan to TARGA to CITIES. |  | TARGA | Jordan/CITIES | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  |  | 40340, 40855, 40950 | Y | N |  |  | 87180 | 76350
65683 | To add Open Sky Station | To interconnect GINR 20INR0241 |  |  |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2025-12-31 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 68001, 68004, 68014 | Y | N |  |  | 65684 | 65683
75788 | This project will intercept the second circuit of a common tower at Reata station. | This project will intercept the second circuit of a common tower at Reata station. |  |  |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2025-12-31 |  | 345 | 0 | 0 | 0 |  | Eastland | Eastland | Tier 4 |  |  |  |  | 68008, 68011, 68051 | Y |  |  |  | 75789 | 75788
75792 | New substation for generation interconnection project for 21INR0359 | New substation for generation interconnection project for 21INR0359 |  |  |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2025-12-31 |  | 345 | 0 | 0 | 0 |  | Bosque | Bosque | Tier 4 |  |  |  |  | 68035, 68040, 68091 | Y |  |  |  | 75793 | 75792
73059 | Barrera: Construct New Distribution Station | Construct new distribution station on the North Laredo Switch to Reveille 138 kV line |  | Barrera |  | Planned |  | AEP TCC | Brooks Dow jlsolis@aep.com 361-881-5574 |  | 2025-12-31 |  | 138 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  |  | 8108, 8612, 8619, 8627, 8717, 88000 | Y |  |  |  | 73060 | 73059
70665C | Danek (DNK) CEHE Substation for Remy Jade - 23INR0339 | Upgrade Ckt.03A PSARCO to BIGVUE to increase thermal limits. Transmission portion of upgrade. |  | PSARCO | BIGVUE | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 | 2023-11-14 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  |  | 40190, 40890, 41301, 113219 | Y | N |  |  | 90171 | 70665
73332 | Install Hermann (HER) Distribution Substation | Install Hermann (HER) Distribution Substation. Loop on Ckt.08I to create new Ckt.08 Plaza to Hermann to Grant. |  | Hermann | Plaza/Grant | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 45120, 47110, 47350 | Y | N |  |  | 87181 | 73332
80630 | Angstrom to STP: Increase 345 kV Line MOT | Increase the MOT on the Angstrom to STP 345 kV line | Contact Update | Angstrom | STP | Planned | TA2024200 | AEP TCC | Dave Goetz deevans@aep.com 918-599-2938 |  | 2025-12-31 |  | 345 | 0 | 0 | 0 |  | San Patricio | Matagorda | Tier 4 |  |  |  |  | 5915, 8249, 8676 | Y |  |  |  | 80631 | 80630
76914 | Ocelot: Construct New 138 kV Station | Interconnect the Ocelot load to the new Ocelot 138 kV station on the Military Highway to Palo Alto 138 kV line | Terminal, Contact, and County Update | Ocelot |  | Planned | TP2023032 | AEP TCC | Robert Dougherty jlsolis@aep.com 361-881-5574 |  | 2025-12-31 |  | 138 | 0.189 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  |  | 8047, 8275, 8950 | Y |  |  |  | 76915 | 76914
72213 | Cedar Hill: Upgrade Relays | Upgrade relays for the Sterling City terminal and Miles terminal at the Cedar Hill 138 kV station | In-Service Date Update | Cedar Hill |  | Planned |  | AEP TNC | Douglas Jansen twang1@aep.com 918-599-2635 | TP2022739 | 2025-12-31 |  | 69 | 0 | 0 | 0 |  | Lee |  | Tier 4 |  |  |  |  | 6422, 6423, 6431 | Y | N |  |  | 72214 | 72213
57906 | Laredo to University: Rebuild 138 kV Line | Reconductor the Del Mar to University 138 kV line | Contact Update | Laredo | University | Planned | 1119 - 1297 | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 | 3838 | 2025-12-31 |  | 138 | 0 | 2.73 | 0 |  | Webb | Webb | Tier 4 |  |  |  |  | 8293, 8645, 8647 | Y | N |  |  | 65579 | 57906
87344 | Addicks 345kV to White oak Ckt.71B Upgrades | Upgrade Ckt.71B Addicks to White Oak to increase thermal limits |  | Addicks | White Oak | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 |  | 345 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 45600, 46600 | Y | N |  |  | 87345 | 87344
73123 | Sim Gideon - Swiftex Transmission Line Upgrade | LCRA TSC will upgrade T608 Sim Gideon - Swiftex 138-kV transmission line to achieve a higher operational rating. |  | Sim Gideon | Swiftex | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2025-12-31 |  | 138 | 0 | 10 | 0 |  | Bastrop | Bastrop | Tier 3 | 24RPG014 | 2024-05-02 | 2024-05-23 |  | 7310, 7319, 7326 | Y | N |  |  | 73124 | 73123 | 2023-SC15
90784 | Reconductor portions of Ckt.63C Moody to West Galveston as a Hardening project. |  |  | Moody | West Galveston | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 |  | 138 | 0 | 2.78 | 0 |  | Galveston | Galveston | Tier 4 | 24RPG037 | 2024-12-06 | 2025-01-02 |  | 42950, 43400 | Y | N |  | Related to MOD Project 72063 | 90785 | 90784
86013 | Fairmont Distribution Reconfigurations with 4th Transformer | Install fourth Fairmont distribution transformer on Ckt.95F to create new Ckt.95F SOUTH to Fairmont TR4 tap to Clear Lake tap to Polaris tap to Kemah tap to PH Robinson 138kV North. Remove Fairmont TR3 from Ckt.95F and onto the Ckt.35A Fairmont line position. |  | Fairmont |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 42610, 42613, 42614, 48108, 742613 | Y | N |  |  | 87387 | 86013
72040A | Blueridge to WA Parish Ckt.02A Upgrades (22RPG041) | Upgrade portions of Ckt.02A Quail Valley tap to WA Parish and Ckt.02A DEWALT to Sienna tap as a Hardening upgrade. |  | DEWALT | Sienna | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 | 2958101 | 138 | 0 | 6.14 | 0 |  | Harris | Fort Bend | Tier 4 | 22RPG041 | 2022-11-21 | 2022-12-15 | 2022-12-15 | 44180, 48302, 48335 | Y | N |  |  | 91115 | 72040
75830A | New 345kV Savannah (SAV) substation for generator interconnection to Cascade Solar (23INR0091). | New 345kV Savannah (SAV) substation for generator interconnection to Cascade Solar (23INR0091). Loop Ckt.27 into Savannah substation to create new Ckt.27 Seabreeze to Savannah to Oasis. |  | Savannah | Seabreeze/Oasis | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42500, 43020, 43035, 43180 | Y | N |  |  | 90909 | 75830
75856A | Rebuild and reconductor portions of Ckt.28A to prepare for ETHYL 138kV conversion. Loop into Ckt.96G to create new Ckt.96G PHILIP to ETHYL 138kV to BEARLE. Retire ETHYL 69kV substation and remaining portions of 69kV Ckt.16D and Ckt.28A. | Rebuild and reconductor portions of Ckt.28A to prepare for ETHYL 138kV conversion. |  | ETHYL | South Channel | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 |  | 69 | 1.33 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 41240, 41370 | Y | N |  |  | 90334 | 75856
75856B | Rebuild and reconductor portions of Ckt.28A to prepare for ETHYL 138kV conversion. Loop into Ckt.96G to create new Ckt.96G PHILIP to ETHYL 138kV to BEARLE. Retire ETHYL 69kV substation and remaining portions of 69kV Ckt.16D and Ckt.28A. | Convert ETHYL customer 69kV substation to 138kV. Loop into Ckt.96G to create new Ckt.96G PHILIP to ETHYL 138kV to BEARLE. Retire ETHYL 69kV substation and remaining portions of 69kV Ckt.16D and Ckt.28A. |  | ETHYL | PHILLIPS/BEARLE | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40550, 41230, 41250, 41270, 41381, 41382 | Y | N |  |  | 90335 | 75856
73352C | PH Robinson Area 138kV Upgrades | Upgrade Ckt.79C BIGBAY to BAYOU to increase thermal limits. Request customers to approve 110% Emergency rating of in-series equipment at BBP/BYU. |  | BIGBAY | BAYOU | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-12-31 00:02 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 42160, 42180 | Y | N |  |  | 73355 | 73352

## Future Projects
JUNE BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 6/1/2025
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar ) (-Reactor, +Capacitor ) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | RPG Number | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number | RTP Project Number
70196 | Kingsland 1 - Sandy Creek Transmission Line Overhaul | LCRA TSC will perform an overhaul on the 7.3-mile Kingsland 1 ¿ Sandy Creek (T400) 69-kV transmission line. |  | Kingsland 1 | Sandy Creek | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-01-14 |  | 69 | 0 | 7.3 | 0 |  | Llano | Llano | Tier 4 |  |  |  |  | 7121, 7400, 7404 | Y | Y |  |  | 70197 | 70196
75830B | New 345kV Savannah (SAV) substation for generator interconnection to Cascade Solar (23INR0091). | Install generator lead from Savannah (SAV) substation to CASCAD (CSC) customer substation (23INR0091). |  | Savannah | CASCAD | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-01-16 00:01 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 43180, 113751 | Y | N |  |  | 90910 | 75830
61404 | Boerne Split-Welfare Transmission Line Upgrade | This project will Increase the reliability of transmission facilities on the T228 Boerne to Welfare 138-kV and T656 Bergheim to Kendall 345-kV 7.3-mile double-circuit transmission line by replacing the aging conductor. |  | Boerne, Bergheim | Welfare, Kendall | Planned | 61406, 61358, 61392, 61350, 61234, 61362, 61356, 61400, 61402 | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2026-01-30 |  | 345 | 0 | 7.3 | 0 |  | Kendall | Kendall | Tier 3 | 22RPG005 | 2022-03-04 | 2022-09-09 |  | 7046, 7153, 7168, 7770 | Y | N |  |  | 78327 | 61404
88867 | Rosita Creek Substation 138-kV T2 Power Transformer Addition. Replacing Committed project 57343 | Add second 138/13.09-kV power transformer bay with new 138-kV transmission switch and circuit switcher interconnected at LCRA Switch# 12669. New power transformer capacity will be 15/20/25 MVA. Replaces committed project 57343. | Recent projected load increases beyond ALDR. Justification is to provide on-site backup power source for new and existing critical medical center, governmental and educational facility loads. Power transformer lead-time increases. |  |  | Planned |  | RGEC | Larry Powell lpowell@rgec.coop 830-563-6178 |  | 2026-01-30 | 2025-09-01 | 138 | 0 | 0 | 0 |  | Maverick | Maverick | Tier 4 |  |  |  |  | 78015 | Y |  |  |  | 88868 | 88867
80572 | Miel: Construct New 138 kV Station | Interconnect Nightfall Solar to the new Miel 138 kV station on the Razorback to Uvalde 138 kV line | In-Service Date Update | Miel |  | Planned | TP2023841 | ETT | Zachary Lachiusa jlsolis@aep.com 361-881-5574 |  | 2026-01-31 |  | 138 | 0 | 0 | 0 |  | Uvalde |  | Tier 4 |  |  |  |  | 8234, 8707, 8747 | Y | N |  |  | 80573 | 80572
64581A | New 138kV Waterfowl substation | Reconfigure existing Ckt.02F (move Seadoc/Seaway onto other circuit) resulting in Ckt.36 COPPER to Booster tap to Jones Creek. |  | COPPER | Jones Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-01-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 21RPG009 | 2021-05-24 | 2021-06-16 |  | 5568, 42195, 42199, 42215, 42540, 43211, 43212, 43221, 48006, 48007, 48039, 48333, 48334 | Y | N |  |  | 87023 | 64581
64581B | New 138kV Waterfowl substation | Install new CEHE-owned 138kV Waterfowl (WTR) substation. Reconfigure existing Ckt.02F and install new conductor to create new Ckt.54 Jones Creek to Waterfowl |  | Jones Creek | Waterfowl | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-01-31 00:01 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 21RPG009 | 2021-05-24 | 2021-06-16 |  | 42540, 43470 | Y | N |  | Cost included in main entry | 87024 | 64581
78427B | Bohemian (BOH) 138kV CEHE Substation for Destiny Storage (24INR0397) | Install generator lead from Bohemian (BOH) substation to Rhapsody / RHAPSO (RHA) / Destiny Storage |  | Rhapsody | Bohemian | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-01-31 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40970, 113861 | Y | N |  |  | 87353 | 78427
64581C | New 138kV Waterfowl substation | Install new CEHE-owned 138kV Waterfowl (WTR) substation. Convert customer-owned Seadoc substation to loop service. Reconfigure existing Ckt.02F and reconnect Seadoc/Seaway to create new Ckt.02x Jones creek to Seadoc loop to Seaway tap to Waterfowl. |  | Jones Creek | Waterfowl | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-01-31 00:02 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 21RPG009 | 2021-05-24 | 2021-06-16 |  | 42540, 43211, 43222, 43470, 48007 | Y | N |  | Cost included in main entry | 87025 | 64581
64581D | New 138kV Waterfowl substation | Install new CEHE-owned 138kV Waterfowl (WTR) substation. Remove existing Seaway Switchrack. Reconfigure existing Ckt.02F to create new Ckt.02y Waterfowl to Franklins Camp. |  | Waterfowl | Franklins Camp | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-01-31 00:03 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 21RPG009 | 2021-05-24 | 2021-06-16 |  | 5568, 43470 | Y | N |  | Cost included in main entry | 87026 | 64581
50866 | Structure 31/8 - Kenedy SS: Line Rebuild | Coleto Creek - Kenedy SS: Line Rebuild |  | Rosata | Kenedy SS | Planned | 1052 - 1225 | AEP TCC | Curtis Brown mlforcum@aep.com 918-599-2674 | 3779 | 2026-01-31 01:00 |  | 138 | 0 | 14.3 | 0 |  | Karnes | Karnes | Tier 3 | 20RPG014 | 2020-08-19 | 2020-09-11 |  | 8153, 8186 | Y | N |  |  | 50867 | 50866
44946 | CPSE_New_Scenic_Loop_138kV_Load_Serving_Station | The new Scenic Loop 138 kV load serving station will be looped into existing Ranchtown to LCRA (Menger Creek) 138 kV transmission line. The substation should be located south west of the existing Fair Oaks Ranch and north east of the existing Ranchtown substation. |  |  |  | Planned | S-0885 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | T-0275 | 2026-01-31 20:00 |  | 138 | 9 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5358, 5363, 7665 | Y |  |  |  | 44947 | 44946
61232 | RGEC Persimmon Gap Substation 69-kV Transmission Line Extension and Substation Expansion | Extend Alpine-Persimmon Gap 69-kV Transmission Line at Switch# 6669 and Install Circuit Switcher to accommodate new substation power transformer and distribution bays. New power transformer capacity will be 12/16/20 MVA. | Scheduled RUS Construction Work Plan Project | Persimmon Gap | Persimmon Gap | Planned |  | RGEC | Larry T. Powell lpowell@rgec.coop 830-563-6178 |  | 2026-02-01 |  | 69 | 0 | 0 | 0 |  | Brewster | Brewster | Tier 4 | [5 empty] | Y | N |  |  | 61233 | 61232
72268 | CPSE_New Ingram Rd Substation | [6 empty] | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2026-02-27 |  | 138 | 0 | 0 | 0 |  | Bexar |  | Tier 4 |  |  |  |  | 5102, 5241, 5346 | Y |  |  |  | 72269 | 72268
73661 | New transformer (T2) at BPUB Palo Alto Substation | Adding load (T2) on bus 5965 Palo Alto. |  | BPUB Palo Alto 5965 |  | Planned |  | BPUB/BROWNSVILLE PUB | Luis Martinez lugmartinez@brownsville-pub.com 956-983-6212 |  | 2026-02-27 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  |  | 5965 | Y | N |  |  | 80506 | 73661
73359 | Vertrees: Construct New Distribution Station | Construct new distribution station on the Stewart Road to Weslaco Unit 138 kV line | Contact Update | Vertrees |  | Planned |  | AEP TCC | Michael Pitts jlsolis@aep.com 361-881-5574 |  | 2026-02-28 | 2958101 | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  |  | 8348, 8662, 8737, 8951 | Y |  |  |  | 73360 | 73359
72942 | Bluff Creek: 138 kV Station Work | Replace fourteen (14) 138 kV Breakers and one (1) Circuit Switcher | Contact Update | Bluff Creek |  | Planned |  | AEP TNC | Remington Hajdik twang1@aep.com 918-599-2635 |  | 2026-02-28 |  | 138 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  |  | 6216, 6260, 6351, 60040, 60043, 66216, 66217, 180455, 180463 | Y | N |  |  | 72943 | 72942
87640 | New load customer interconnection RAOULT connecting on ckt 86 between DALTON and BRINE. | New load customer interconnection RAOULT connecting on ckt 86 between DALTON and BRINE. |  | RAOULT | DALTON/ BRINE | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-02-28 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  |  | 40220, 40740, 41740 | Y | N |  |  | 87641 | 87640
69489 | Shepley: Construct New Distribution Station | Construct new distribution station on the Victoria to Dupont Switch 138 kV line | Status and Contact Update | Shepley |  | Under Construction |  | AEP TCC | Will Simmons deevans@aep.com 918-599-2938 |  | 2026-02-28 |  | 138 | 0 | 0 | 50 |  | Victoria |  | Tier 4 |  |  |  |  | 8143, 8172, 8719 | Y |  |  |  | 69490 | 69489
71004B | Julia CNP-Owned Sub for Melaza Solar (21INR0220) | Install generator lead from Julia (JUL) CNP substation to MALEZA/Maleza Solar |  | Julia | MALEZA | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-03-01 00:01 |  | 345 | 0 | 0 | 0 |  | Wharton |  | Tier 4 |  |  |  |  | 44220, 113251 | Y | N |  |  | 87172 | 71004
78357 | Wilmer 345/138 kV Switch | Establish Wilmer 345/138 kV Switch |  | Wilmer |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4369 M4371 M4372 | 2026-03-02 |  | 345 | 0 | 0 | 1200 | 0,220.8 | Dallas |  | Tier 1 | 24RPG022 | 2024-07-02 | 2024-07-29 |  | 2261, 2342, 2344, 2427, 2429, 2432, 2967, 3083, 3084, 3085, 13082, 23082 | Y |  |  |  | 78373 | 78357
70714 | La Cima Substation Addition | Add new substation to 138 kV line between Ranch Road 12 and Hill Top and install 46.7 MVA distribution transformer. The new substation will be located approximately 0.30 miles from Ranch Road 12 substation. |  | Ranch Road 12 | La Cima | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-03-03 |  | 138 | 0 | 0 | 0 |  | Hays |  | Tier 4 |  |  |  |  | 7185, 7186, 7190 | Y | N |  |  | 70715 | 70714
80376 |  |  |  | WEST WEATHERFORD | SHADY GROVE | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2026-03-15 |  | 138 | 0 | 0 | 0 |  | Parker | Parker | Tier 4 |  |  |  |  | 477, 512, 513, 515, 1589 | Y |  |  |  | 80377 | 80376
78169 | Lewisville Switch to Highland | Lewisville Switch to Highland |  | Lewisville Switch | Highland | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2026-03-15 |  | 138 | 0 | 2.8 | 0 |  | Denton | Denton | Tier 4 |  |  |  |  | 645, 664 | Y |  |  |  | 78170 | 78169
87395 | Caldwell Substation Addition | LCRA TSC will build a new substation, Caldwell Substation, to manage 12 MW of load in the summer of 2024. This substation will be on the Cooks Point - Lyle Wolz 138-kV transmission line. The new substation will be approximately 5 miles south of Cooks Point substation. LCRA will install circuit breakers in a ring bus formation |  | Caldwell | Caldwell | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2026-03-16 01:00 |  | 138 | 0 | 0 | 0 |  | Burleson | Burleson | Tier 4 |  |  |  |  | 7566, 7567, 7569 | Y | N |  |  | 87396 | 87395
61394 | Portilla: Construct New Distribution Station | Construct new distribution station on the Lon Hill to Warburton 138 kV line | Status and In-Service Date Update | Portilla |  | Under Construction |  | AEP TCC | Damian Raab mlforcum@aep.com 918-599-2674 | DP21X0008 | 2026-03-31 |  | 138 | 1.5 | 0 | 0 | 0,14.4 | San Patricio | San Patricio | Tier 4 |  |  |  |  | 8020, 8027, 8046, 8920, 8924 | Y |  |  |  | 61395 | 61394
73025 | CPSE_New_Shaula_POI | [6 empty] | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2026-03-31 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5133, 5380, 5915 | Y |  |  |  | 73026 | 73025
90964 | Tier 3 project to add second autotransformer at Long Draw |  |  | Long Draw 345 kV | Long Draw 138 kV | Planned |  | WETT | Chris Ramirez cramirez@wettllc.com |  | 2026-03-31 |  | 345 | 0.5 | 0 | 706 |  | Borden | Borden | Tier 3 | 24RPG027 | 2024-08-28 | 2024-09-20 |  | 59900, 59906, 59991 | Y |  |  |  | 90965 | 90964
90336 | DURZNO (DUR) 138kV Customer Substation | Install new customer-owned 138kV DURZNO (DUR) substation. Loop into Ckt.54 to create new Ckt.54 Jones Creek to DURZNO to Waterfowl. |  | DURAZNO | Jones Creek/ Waterfowl | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-03-31 |  | 138 | 0.2 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42540, 43470, 43481 | Y | N |  |  | 90760 | 90336
92646 | Oncor_MNE_92646_Saddlewood 138 kV Switch |  |  |  |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2026-03-31 |  | 138 | 0 | 0 | 0 |  | Hunt | Hunt | Tier 4 |  |  |  |  | 1815, 1819, 2843 | Y |  |  |  | 92647 | 92646
80468 | Conoco: Construct New 138 kV Terminal | Interconnect Isaac Solar to the Conoco 138 kV station | Contact Update | Conoco |  | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 |  | 2026-03-31 12:00 |  | 138 | 0 | 0 | 0 |  | Matagorda |  | Tier 4 |  |  |  |  | 8114, 113651 | Y |  |  |  | 80469 | 80468
71917 | Upgrade STEC castroville to Pearson to 138kV | Upgrade STEC Bader station to 138kV. Upgrade STEC Castroville to bader and bader to pearson to 138kV |  | 5808 | 5813 | Planned | 71935 | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-04-01 |  | 138 | 0 | 10.51 | 0 |  | Medina | Medina | Tier 2 | 22RPG022 | 2022-08-08 | 2022-12-06 |  | 5802, 5804, 5810, 5811, 5813 | Y |  |  |  | 71918 | 71917
70880 | Rebuild Carancahua -TinTop | Rebuild Carancahua to TinTop with 795ACSR |  | Carancahua | Tin Top | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-04-01 |  | 69 | 0 | 12.93 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  |  | 5569, 5570, 5571, 5573 | Y |  |  |  | 70881 | 70880
89957 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2026-04-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 1819, 6856 | Y |  |  |  | 89958 | 89957
78480B | Weinbrenner (WEI) 138kV CEHE Station for LONGPO (LNP) / Long Point Solar 19INR0042 | Install one generator lead from CEHE 138kV substation Weinbrenner (WEI) to LONGPO (LNP) / Long Point Solar (19INR0042) |  | Weinbrenner | LONGPO | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-04-01 00:01 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42990, 114581 | Y | N |  |  | 87162 | 78480
72029A | Ashville (ASH) 138kV CEHE Station for SUNLIT/Dori BQ Solar (23INR0040) and Dori BQ BESS (24INR0196) | Loop new CEHE 138kV substation Ashville (ASH) into Ckt.06F Garden Villas to Holmes to create new Ckt.06 Garden Villas to Ashville to Holmes |  | Ashville | Garden Villas | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-04-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 42680, 42770, 47210 | Y | N |  |  | 90115 | 72029
92625 | Oncor_ME_TILLMAN 138 kV Switch |  |  |  |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2026-04-30 |  | 138 | 0 | 0 | 0 |  | Collin | Collin | Tier 4 |  |  |  |  | 2534, 2856, 12585 | Y |  |  |  | 92626 | 92625
64858 | La Palma Expansion | Construct 3 Breaker Ring Bus. Construct 345 kV Line from La Palma 345 kV station to Kingfisher 345 kV (Sharyland) station. | Contact Update | La Palma | Kingfisher | Planned |  | AEP TCC/SLU | Lorraine Timmerman jlsolis@aep.com 361-881-5574 | TP2021588 | 2026-04-30 |  | 345 | 6.5 | 0 | 0 |  | Cameron | Cameron | Tier 2 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 8317, 8383, 79500, 79501, 80137 | Y |  |  |  | 65264 | 64858
6572 | Ballinger to Eden 69 kV line: Rebuild taps | Rebuild Taps on the Ballinger to Eden 69 kV line | In-Service Date Update | Ballinger | Eden | Planned | 890 - 1068 | AEP TNC | Dewey Peters twang1@aep.com 918-599-2635 | 2814 | 2026-04-30 |  | 69 | 0 | 2.8 | 0 |  | Runnels | Concho | Tier 4 |  |  |  |  | 6338, 6369, 6370, 6372, 6376 | Y | N |  |  | 65513 | 6572
72029C | Ashville (ASH) 138kV CEHE Station for SUNLIT/Dori BQ Solar (23INR0040) and Dori BQ BESS (24INR0196) | Install one generator lead from CEHE 138kV substation Ashville (ASH) to SUNLIT/Dori BQ BESS. Utilize same generator lead as Dori BQ Solar. |  | Ashville | SUNLIT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-04-30 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 | [5 empty] | Y | N |  |  | 90117 | 72029
72029B | Ashville (ASH) 138kV CEHE Station for SUNLIT/Dori BQ Solar (23INR0040) and Dori BQ BESS (24INR0196) | Install one generator lead from CEHE 138kV substation Ashville (ASH) to SUNLIT/Dori BQ Solar. Utilize same generator lead as Dori BQ BESS. |  | Ashville | SUNLIT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-04-30 00:01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 | [5 empty] | Y | N |  |  | 90116 | 72029
48818 | Ballinger: Rebuild 138 kV Station | Rehab the 138/69 kV autotransformer at Ballinger | In-Service Date Update | Ballinger |  | Planned | 1016 - 1194 | AEP TNC | Dewey Peters twang1@aep.com 918-599-2635 | 2777 | 2026-04-30 01:00 |  | 138 | 0 | 0 | 130 |  | Runnels |  | Tier 4 |  |  |  |  | 6338, 6340 | Y | N |  |  | 65537 | 48818
49564 | Mantle: Construct New 345 kV Station | Mantle: Construct New 345 kV Station | Contact and In-Service Date Update | Mantle |  | Planned | 1035 - 1213 | AEP TCC | Tom Reynolds jlsolis@aep.com 361-881-5574 | 3774 TP2018166 | 2026-04-30 20:00 |  | 345 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  |  | 8059, 8383, 8573 | Y | N |  |  | 49565 | 49564
59959 | CPSE_New_Old_Hickory_Switchyard | Build a new Old Hickory 345 switchyard to connect Old Hickory Solar plant. |  | 5133 | 5915 | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | T-0303; S-0940 | 2026-04-30 20:00 |  | 345 | 0 | 0 | 0 |  | Jackson |  | Tier 4 |  |  |  |  | 5133, 5323, 5915 | Y |  |  |  | 59960 | 59959
78478 | Rebuild Oaks to Poteet to Pearsall 69 kV line | Rebuild Oaks to Poteet to Pearsall 69 kV line from 4/0 to 795. 2023 RTP |  | Oaks | Pearsall | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-05-01 |  | 69 | 0 | 38.95 | 0 |  |  |  | Tier 2 |  |  | 2020-05-21 |  | 5710, 5712, 5893 | Y | N |  |  | 78479 | 78478
78483 | Rebuild Nada to El Campo 69 kV line | Rebuild Nada to El Campo 69 kV line from 4/0 to 795. 2023 RTP |  | Nada | El Campo | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-05-01 |  | 69 | 0 | 15.44 | 0 |  | Colorado | Wharton | Tier 4 |  |  |  |  | 5536, 5538 | Y | N |  |  | 78484 | 78483
70371 | D'Hanis Capacitor addition | Add 9.6 MVAR capacitor step at D'Hanis |  | D'Hanis |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-05-01 |  | 69 | 0 | 0 | 0 | 0,9.6 |  |  | Tier 4 |  |  |  |  | 5814 | Y | N |  |  | 70372 | 70371
72582C | Nameless to Leander Transmission Line Upgrade | Upgrade final span into Nameless, upgrade terminal equipment, and achieve circuit rating of 440 MVA. (Replaces ERCOT Project # 61279C) | 1/10/2023: Added information to clarify circuit rating. | Hero Way | Nameless | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2026-05-01 | 2026-05-01 | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 70526, 70536 | Y | N |  |  | 72585 | 72582
70373 | Driscoll Capacitor addition | adds 3 9.6 MVAR capacitor steps at Driscoll |  | Driscoll |  |  |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-05-01 |  | 69 | 0 | 0 | 0 | 0,28.8 |  |  | Tier 4 |  |  |  |  | 5640 | Y |  |  |  | 70374 | 70373
71928 | Upgrade Heidelberg to AEP Weslaco line | Upgrade Heidelberg to STEC WESLACO and STEC WESLACO to AEP Weslaco lines to be 478MVA capable |  | Heidelberg | Weslaco | Planned | 7193071926 | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-05-01 |  | 138 | 0 | 8.6 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  |  | 5765, 5768, 8354 | Y |  |  |  | 71929 | 71928
89952 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2026-05-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 2585, 6857 | Y |  |  |  | 89953 | 89952
75255F | CPSE_Howard to San Miguel Double Circuit Line Addition |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2026-05-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  |  | 5260, 5385 | Y |  |  |  | 75960 | 75255
76109 | West Sinton Capacitor addition | Add a 3.6 MVAR step to existing West Sinton Capacitor |  | West Sinton |  | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-05-01 |  | 69 | 0 | 0 | 0 | 0,3.6 |  |  | Tier 4 |  |  |  |  | 5622 | Y | N |  |  | 76110 | 76109
76816 | Upgrade Loyola Auto | Upgrade Loyola Auto |  | Loyola | Loyola | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-05-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5648, 5650 | Y |  |  |  | 76817 | 76816
75989 | Rebuild Vanderbilt -Pt Lavaca | Rebuild Vanderbilt - Placedo - Kamey -Pt Lavaca 69kV to 795 ACSR |  | Vanderbilt | Port Lavaca | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-05-01 |  | 69 | 0 | 26.47 | 0 |  | Victoria | Calhoun | Tier 4 |  |  |  |  | 5582, 5586, 5590, 5591, 5592 | Y |  |  |  | 75990 | 75989
81229 | Upgrade Oaks Auto | Upgrade Oaks Auto to 150MVA |  | Oaks | Oaks | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-05-01 |  | 138 | 0 | 0 | 150 |  |  |  | Tier 4 |  |  |  |  | 5712, 5713 | Y |  |  |  | 81230 | 81229
82840 |  |  |  | HYDRA | Hydroponic | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2026-05-02 |  | 115 | 3 | 0 | 0 |  | Lubbock | Lubbock | Tier 4 |  |  |  |  | 700, 59122 | Y |  |  |  | 82841 | 82840
91847 | Hornsby Load Power Transformer Addition | CRA TSC will upgrade the 345-kV Hornsby Substation to accommodate the addition of T6 power transformers. New circuit breakers and switches should meet LCRA TSC minimum 345-kV design standards (4000 amps or higher) |  | Honrsby |  | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 | PLC-8186 | 2026-05-08 |  | 345 | 0 | 0 | 0 |  | Travis |  | Tier 4 |  |  |  |  | 7047 | Y |  |  |  | 91956 | 91847
91289 | LCRATSC_Settlers Substation Upgrade | Settlers Substation Addition project will construct a new substation connecting to LCRA TSC owned 138-kV transmission lines T171 Austrop to Sim Gideon and T231 Bastrop to Webberville via a hard tap installation. In this project, LCRA TSC will upgrade the hard tap installation to a breakered facility. |  |  |  | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 | PLC-6691 | 2026-05-11 |  | 138 | 0 | 0 | 0 |  | Bastrop |  | Tier 3 |  |  |  |  | 7322, 7327, 7328, 7329 | Y |  |  |  | 91959 | 91289
92565 | Sim_Gideon_Winchester_Transmission_Line_Upgrade | LCRA TSC will upgrade Sim Gideon - Winchester 138-kV transmission line to achieve a higher operational rating |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-7654 | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Bastrop | Bastrop | Tier 4 |  |  |  |  | 7306, 7310 | Y |  |  |  | 92566 | 92565 | 2023-SC15
92575 | LCRATSC_Canyon_San_Marcos_Transmission_Line_Upgrade |  |  | 7192 | 7200 | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org | PLC-7656 | 2026-05-15 |  | 138 | 0 | 2.8 | 0 |  | Hays | Hays | Tier 4 |  |  |  |  | 7192, 7200, 70502 | Y |  |  |  | 92576 | 92575 | 2024-SC1
92598 | Bluebonnet - Wyldwood Transmission Line Overhaul | Overhaul transmission line structures per LCRA TSC standards and current NESC requirements. Replace existing conductor with bundled-Suwannee. |  | 7210 | 7556 | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org | PLC-6949 | 2026-05-15 |  | 138 | 0 | 2.43 | 0 |  | Bastrop | Bastrop | Tier 4 |  |  |  |  | 7210, 7556 | Y |  |  |  | 92599 | 92598 | 2024-SC20
92622 | Elroy_Wolf_Lane_Transmission_Line_Overhaul | Overhaul transmission line structures per LCRA TSC standards and current NESC requirements. Replace existing conductor with bundled-Suwannee |  |  |  | In-Service |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-6950 | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Bastrop | Travis | Tier 4 |  |  |  |  | 7209, 7212 | Y |  |  |  | 92623 | 92622 | 2024-SC20
93191 | Bent Tree 138 kV Substation | Establish Bent Tree 138 kV Substation with 55.2 MVAR capacitor bank using 3-18.4 MVAR stages |  | Bent Tree Substation | Bent Tree Substation | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6388 | 2026-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Williamson | Williamson | Tier 4 |  |  |  |  | 3664, 3667, 3764 | Y |  |  |  | 93192 | 93191
92845 | Oncor_ME_92845_Watermill_Reindeer_Line_Upgrade | Upgrade Watermill to Reindeer 138 kV Line |  | Watermill Switch | Reindeer | Planned | M4430 | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2026-05-15 |  | 138 | 0 | 2.6 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 2429, 3065 | Y |  |  |  | 92846 | 92845
92849 | Oncor_ME_92849_Renner Switch 138kV Capacitor Bank | Install Capacitor Banks at Renner switch |  | Renner Switch | Renner Switch | Planned | M4021 | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 | 0,220 | Collin | Collin | Tier 4 |  |  |  |  | 2352, 2353 | Y |  |  |  | 92864 | 92849
92854 | Oncor_ME_Carrollton East Switch-Carrollton Tarpley Rd 138 kV Double-Circuit Line Section | Carrollton East Switch-Carrollton Tarpley Rd 138 kV Double-Circuit Line Section |  | Carrollton East | Carrollton Tarpley Road | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4246 | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 2558, 2559, 2577, 2578 | Y |  |  |  | 92855 | 92854
92867 | Oncor_ME_Renner Switch – Plano West Switch 138 kV Double-Circuit Line | Upgrade Renner Switch – Plano West Switch 138 kV Double-Circuit Line |  | Renner | Plano West | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4246 | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Collin | Collin | Tier 4 |  |  |  |  | 2352, 2353, 2669, 2670, 2671, 2673 | Y |  |  |  | 92869 | 92867
92870 | Oncor_ME_92870_Bradberry Switch 138kV Capacitor Bank |  |  | Bradberry Switch | Bradberry Switch | Planned | M4431 | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Dallas |  | Tier 4 |  |  |  |  | 3064 | Y |  |  |  | 92871 | 92870
92872 | Oncor_MW_92872_North Main 138kV Capacitor Bank |  |  | North Main | North Main | Planned | M5187 | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 | 0,110 | Tarrant | Tarrant | Tier 4 |  |  |  |  | 1961 | Y |  |  |  | 92873 | 92872
92629 | Gabriel - Rivery MLSE Upgrade | Remove an MLSE on T457 Gabriel - Rivery 138-kV transmission line to achieve the full conductor rating. |  | Gabriel Substation |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-762-3658 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | 7346, 7347 | Y |  |  |  | 92630 | 92629 | 2023-SC17
92680 | Oncor_ME_Stainback 345 kV Switch | Establish Stainback 345 kV Switch |  | Stainback 345 kV Switch |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2026-05-15 |  | 345 | 0 | 0 | 0 |  | Dallas |  | Tier 4 |  |  |  |  | 2217, 2427, 2466, 3159 | Y |  |  |  | 92681 | 92680
92865 | Oncor_ME_92865_Kirkland Park 138kV Capacitor Bank | Install capacitor banks at Kirkland Park |  | Kirkland Park | Kirkland Park | Planned | M4022 | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 | 0,110 | Dallas |  | Tier 4 |  |  |  |  | 2457 | Y |  |  |  | 92866 | 92865
91534 | Establish Glaze Lake 138 kV Switch |  |  | Glaze Lake 138 kV Switch | Glaze Lake 138 kV Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6345 | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Leon | Leon | Tier 4 |  |  |  |  | 3355, 3357, 3790 | Y |  |  |  | 91535 | 91534
81146 | Southmayd 138 kV Switch | Establish Southmayd 138 kV Switch |  | Southmayd |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4338 | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Grayson |  | Tier 4 |  |  |  |  | 1744, 2790, 11704 | Y |  |  |  | 81147 | 81146
81305 | Expanse - Vealmoor 138 kV Line Rebuild | Rebuild the existing Expanse – Vealmoor 138 kV Line with both circuits in place. |  | Expanse | Tredway | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8681 | 2026-05-15 |  | 345 | 0 | 27.7 | 0 |  | Martin | Martin | Tier 3 |  | 2023-09-29 |  |  | 1355, 10032, 10090, 10097, 10098, 10110, 10113, 11006, 11303, 11338, 11348, 11349, 11368, 11383, 23829, 23835, 23838, 23849, 23880 | Y |  |  |  | 93169 | 81305
78414 | SW3379 Replacement | Replacing existing 1200 Amp switch and 1800 Amp bypass jumper with new 3000 Amp switch. |  |  |  | Planned |  | NBU | Jeff Morriss jmorriss@nbutexas.com 830-608-8881 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Comal |  | Tier 4 | [5 empty] | Y |  |  |  | 78417 | 78414
80921 | Downtown Kyle Substation Addition | Models the addition of a planned substation in Kyle area. |  | DOWNTOWN KYLE 70503 |  | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Hays |  | Tier 4 |  |  |  |  | 70198, 70502, 70503 | Y |  |  |  | 80922 | 80921
78361A | Lake Creek - Rattlesnake Road 345 kV Line |  |  | Lake Creek | Rattlesnake Road | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6276 | 2026-05-15 |  | 345 | 0 | 5.1 | 0 |  | McLennan | McLennan | Tier 3 |  |  |  |  | 3384, 3399, 3409 | Y |  |  |  | 81575 | 78361
81067 | Balch Springs Tap – Balch Springs 138 kV Line Section | Rebuild Balch Springs Tap – Balch Springs 138 kV Line Section |  | Balch Springs Tap | Balch Springs | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4194 | 2026-05-15 |  | 138 | 0 | 3.6 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 2775, 2776, 2777, 2778 | Y |  |  |  | 81068 | 81067
78367 | Montfort Switch-Shankle Switch 138 kV Line | Rebuild Montfort Switch - Shankle Switch 138 kV Line |  | Montfort | Shankle | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4002 | 2026-05-15 |  | 138 | 0 | 18 | 0 |  | Navarro | Ellis | Tier 3 |  |  |  |  | 192, 2330, 2331, 3454, 12329 | Y |  |  |  | 78368 | 78367
78369 | Rebuild Sam Switch - Venus Switch 345 kV DCKT | Rebuild Sam Switch - Venus Switch 345 kV DCKT |  | Venus | Sam | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6293 | 2026-05-15 |  | 345 | 0 | 76 | 0 |  | Ellis | Hill | Tier 1 | 24RPG017 | 2024-06-07 | 2024-07-02 |  | 1906, 1907, 3374, 3389, 68090 | Y |  |  |  | 78370 | 78369
80546C | Upgrade the Hutto & Round Rock - Salado 138 kV Line | Rebuild and double-circuit the Georgetown East - Sonterra 138 kV Line Section |  | Georgetown East | Sonterra | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6203, R6202 | 2026-05-15 |  | 138 | 12.9 | 12.9 | 0 |  | Williamson | Williamson | Tier 3 |  |  |  |  | 121, 3688, 7346, 7528 | Y |  |  |  | 87631 | 80546 | 2023-SC17
85963 | FPP Yard 2 - Lytton Springs Transmission Line Overhaul | LCRA TSC will overhaul FPP Yard #2 - Lytton Springs 345-kV transmission line T255 to ensure structural integrity of the circuit. Engineering will review this transmission circuit for scope including hardware/insulator integrity, structural load issues, need for containment (dead-ends) structures, and clearances at highway and railroad crossings. |  | FPP Yard 2 | Lytton Springs | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-05-15 | 2958101 | 345 | 0 | 0 | 0 |  | Fayette | Caldwell | Tier 4 | 24RPG013 | 2024-04-11 | 2024-05-03 |  |  | Y |  |  |  | 85964 | 85963
87413 | Establish Fallstown Switch – Pleasant Valley/Fisher Road 138 kV Double-Circuit Line and Fallstown Switch – Ceramic/Wichita Falls PPG 138 kV Double-Circuit Line | Establish Fallstown Switch – Pleasant Valley/Fisher Road 138 kV Double-Circuit Line and Fallstown Switch – Ceramic/Wichita Falls PPG 138 kV Double-Circuit Line |  | Fallstown Switch | Pleasant Valley/Fisher Road | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R4024 | 2026-05-15 |  | 138 | 0 | 10.7 | 0 |  | Wichita | Wichita | Tier 4 |  |  |  |  | 1450, 1483, 1484, 1485, 1488, 17005 | Y |  |  |  | 87414 | 87413
87508 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 6894, 6902 | Y |  |  |  | 87509 | 87508
87510 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 6821, 6902 | Y |  |  |  | 87511 | 87510
87804 | Establish Notus 345 kV Switch | Establish Notus 345 kV Switch |  | Notus Switch | Notus Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6371 | 2026-05-15 |  | 345 | 0 | 0 | 0 |  | Navarro | Navarro | Tier 4 |  |  |  |  | 2255, 3376, 68091 | Y |  |  |  | 87805 | 87804
87799 | Old Country 345 kV Switch | Old Country 345 kV Switch |  | Old Country |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4172 | 2026-05-15 |  | 345 | 0 | 0 | 0 |  | Ellis | Ellis | Tier 4 |  |  |  |  | 1906, 2255, 68091 | Y |  |  |  | 87800 | 87799
88035 | Pastores 138 kV Switch | Construct a new 138 kV Switch |  | McDonald Road | Catclaw/Mudstone | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8817 | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Glasscock | Glasscock | Tier 4 |  |  |  |  | 1225, 1333, 10121, 11222 | Y |  |  |  | 88040 | 88035
85973 | Georgetown - Rivery Transmission Line Upgrade | LCRA TSC will upgrade T597 Georgetown - Rivery 138-kV transmission line to achieve a higher operational rating. |  | Georgetown Substation |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-762-3658 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | 7343, 7347 | Y |  |  |  | 85974 | 85973 | 2023-SC17
73106 | Lockhart - San Marcos Transmission Line Conversion | The five LCRA TSC-owned transmission line sections from Lockhart to San Marcos will be converted to 138-kV (T220 San Marcos to Camp Gary to Robert Brown Jr., T519 Robert Brown Jr. to Clear Fork, and T601 Clear Fork to Lockhart). |  | Lockhart | San Marcos | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Caldwell | Hays | Tier 4 |  |  |  |  | 7188, 7191, 7192, 7194, 7195, 7196, 7215, 7216 | Y | N |  |  | 78513 | 73106 | 2023-SC11
76669 | Rebuild the Eiland to Redberry (fka Elbow) 138 kV Line | L20 Rebuild the existing Eiland to Redberry (fka Elbow) 138 kV Line |  | Elbow | Eiland | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8665 | 2026-05-15 |  | 138 | 0 | 18.5 | 0 |  | Howard | Howard | Tier 3 |  |  |  |  | 10080, 23833, 23834 | Y |  |  |  | 77043 | 76669
77174 | Rebuild Old Lake Sw - Ringgold Magnolia 69 kV line | Rebuild Old Lake Sw - Ringgold Magnolia 69 kV line |  | Old Lake Switch | Ringgold Magnolia | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3508 | 2026-05-15 |  | 69 | 0 | 13 | 0 |  | Clay | Montague | Tier 4 |  |  |  |  | 1524, 11541, 11545 | Y |  |  |  | 77175 | 77174
76652 | Line Termination at Cypress Waters | Vineyard Switch – Hackberry Switch 138 kV Line Termination at Cypress Waters 138 kV Switch |  | Cypress Waters |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5344 | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Dallas |  | Tier 4 |  |  |  |  | 2017, 2386, 2392 | Y |  |  |  | 76653 | 76652
78408 | Henne Substation Bus Upgrade | LCRA TSC intends to build a new 138 kV line from Henne to Kohlenberg and accommodate this line at Henne. Henne substation will be converted to a breaker and half configuration to improve reliability and support the project. |  | Henne | Henne | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Comal | Comal | Tier 4 |  |  |  |  | 7172, 7173, 7174, 7176, 7182 | Y | N |  |  | 78411 | 78408
70534 | Hueco Springs Substation Addition | NBU is constructing a new 138-kV substation to serve a new residential development. LCRA TSC will provide transmission service to the new load serving substation on the T235 Henne to Comal. |  | Henne | Comal | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Comal | Comal | Tier 4 |  |  |  |  | 7174, 7176, 7179 | Y | N |  |  | 70535 | 70534
71130 | Centerville Switch - Lake Hubbard Switch 138 kV Double-Circuit Line | Upgrade the existing 138 kV Double-Circuit Line |  | Lake Hubbard | Centerville | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4126 | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 2401, 2402, 2439, 2450 | Y |  |  |  | 71131 | 71130
68681 | Lamar Blossom Switch - Clarksville 69 kV Line Rebuild | Rebuild the existing 69 kV Line |  | Lamar | River Crest | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5325 | 2026-05-15 |  | 69 | 0 | 0 | 0 |  | Lamar | Red River | Tier 4 |  |  |  |  | 1772, 1785, 11784 | Y |  |  |  | 68682 | 68681
70900F | Roanoke Area Upgrades | Establish Roanoke_Exchange 138 kV Line |  | Roanoke Switch | Exchange Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5281 M5144 M5146 M5148 | 2026-05-15 |  | 138 | 11.4 | 0 | 0 |  | Tarrant | Tarrant | Tier 1 | 21RPG008 | 2022-02-15 | 2022-03-15 | 2022-08-15 | 1854, 12077 | Y | N |  |  | 87471 | 70900
71912A | Killeen Fort Hood - Killeen Taft 138 kV Line | Rebuild the Killeen Fort Hood - Killeen Park Street Tap 138 kV Line |  | Killeen Fort Hood | Killeen Park Street Tap | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6245 | 2026-05-15 |  | 138 | 0 | 3.95 | 0 |  | Bell | Bell | Tier 4 |  |  |  |  | 3626, 3627, 3635, 13626 | Y |  |  |  | 71913 | 71912
72576B | Lago Vista to Nameless Transmission Line Upgrade | Upgrade final span into Nameless, upgrade terminal equipment, and achieve circuit rating of 440 MVA. (Replaces ERCOT Project #61277B) | 1/10/2023: Added information to clarify circuit rating. | Lago Vista | Nameless | Planned |  | PEC | Charles Dewitt Charles.Dewitt@peci.com 830-868-5041 |  | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 70352, 70526 | Y | N |  |  | 72578 | 72576
5526 | Three Creek 345/138 kV Switch (fka Forney) | Rebuild existing 345/138 kV switching |  | Forney |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4114 | 2026-05-15 |  | 345 | 0 | 0 | 600 |  | Kaufman |  | Tier 1 | 24RPG021 | 2024-07-02 | 2024-07-29 |  | 2437, 2438, 12438, 22438 | Y | N |  |  | 78356 | 5526
61601 | Add Coody Crossing 345 kV Switch | Add Coody Crossing 345 kV Switch |  | Clear Crossing | Tecumseh Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8560 | 2026-05-15 |  | 345 | 0 | 0 | 0 |  | Throckmorton | Throckmorton | Tier 4 |  |  |  |  | 11418, 11419, 60514 | Y |  |  |  | 64014 | 61601
62666C | Upgrade and convert McGregor - Waco West Line | Rebuild the Bewley - McGregor Phillips Line |  | Bewley Sub | McGregor Phillips Tap | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6172 | 2026-05-15 |  | 138 | 0 | 4 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  |  | 3372, 3594 | Y |  |  |  | 93107 | 62666
66218B | Hillsboro - Italy 69 kV Line | Rebuild the Milford-Italy 69 kV Line |  | Milford | Italy | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4326 | 2026-05-15 |  | 69 | 0 | 0 | 0 |  | Ellis | Ellis | Tier 4 |  | 2021-04-23 | 2021-05-18 |  | 2337, 2338 | Y |  |  |  | 73690 | 66218
66190 | East Levee - Industrial Blvd 138 kV DCKT Line | Rebuild East Levee - Industrial Blvd 138 kV DCKT Line |  | East Levee | Industrial | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4213 | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 2481, 2482, 2874, 2875, 2876, 2974, 2976 | Y |  |  |  | 66191 | 66190
63948 | Establish Fallstown 138 kV Switch | Establish Fallstown 138 kV Switch |  | Fallstown | Fallstown | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3018 | 2026-05-15 |  | 138 | 0 | 0 | 0 |  | Wichita | Wichita | Tier 4 | [5 empty] | Y |  |  |  | 87782 | 63948
78361B | Lake Creek - Rattlesnake Road 345 kV Line | Establish Possum Trot 345 kV Switch |  | Possum Trot | Possum Trot | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6276 | 2026-05-16 |  | 345 | 0 | 0 | 0 |  | McLennan | McLennan | Tier 3 |  |  |  |  | 3384, 3399, 3402, 3403, 3405, 3409, 3410, 3412, 3741, 3791, 13402, 13405, 13410 | Y |  |  |  | 91985 | 78361
71903 | Establish Launch Pad 138 kV Switch | Establish Launch Pad 138 kV Switch |  | Launch Pad | Launch Pad | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6156 | 2026-05-16 |  | 138 | 0 | 0 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  |  | 3372, 3593, 3594, 3601, 3709 | Y |  |  |  | 71904 | 71903
89889 | Three Creek 138 kV Capacitor Bank |  |  | Three Creek |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4114 | 2026-05-16 |  | 138 | 0 | 0 | 0 | 0,110.4 | Kaufman |  | Tier 4 |  |  |  |  | 2438 | Y | N |  |  | 89891 | 89889
87792 | Establish the Bynum 345 kV Switch | Establish the Bynum 345 kV Switch |  | Bynum Switch | Bynum Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6369 | 2026-05-16 |  | 345 | 0 | 0 | 0 |  | Hill | Hill | Tier 4 |  |  |  |  | 1907, 3383, 68090 | Y |  |  |  | 87793 | 87792
90180A | Clodine Reconfiguration for Houston IV BESS (24INR0584) | Install one new generator lead at the existing Clodine W670/W680 breaker position for Houston IV BESS. |  | Clodine | Generator | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 | [5 empty] | Y | N |  |  | 90181 | 90180
71106 | Dunlavy to HO Clarke Ckt.40A Partial Reconductor | Reconductor portions of Ckt.40A Dunlavy to HO Clarke ahead of future 138kV conversions |  | Dunlavy | HO Clarke | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-30 |  | 69 | 0 | 4.41 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47015, 47160, 47320, 47580 | Y | N |  |  | 71107 | 71106
85987A | Upgrade Ckt.26 STRATT to SINTEK to increase thermal limits. Upgrade Ckt.26F Velasco to CAMDEN to increase thermal limits. | Upgrade Ckt.26D STRATT to SINTEK to increase thermal limits. |  | Clute | SINTEK | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-30 |  | 138 | 0 | 5.26 | 0 |  | Brazoria | Brazoria | Tier 3 | 24RPG012 | 2024-04-10 | 2024-05-02 | 2024-05-02 | 43240, 43300 | Y | N |  |  | 85988 | 85987
90180B | Clodine Reconfiguration for Houston IV BESS (24INR0584) | Reposition Ckt.25B Clodine to Roark to the existing W670/W710 breaker position. |  | Clodine | Roark | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 | [5 empty] | Y | N |  |  | 90182 | 90180
73423 | Buddy Owens: Build new 138 kV Substation | Build new 138 kV substation on Key Switch to North McAllen 138 kV line | Contact Update | Buddy Owens |  | Conceptual |  | AEP TCC | Wade Weller jlsolis@aep.com 361-881-5574 |  | 2026-05-30 |  | 138 | 0 | 0 | 80 |  | Hidalgo |  | Tier 4 |  |  |  |  | 8632, 8773, 8973 | Y |  |  |  | 73424 | 73423
85987B | Upgrade Ckt.26 STRATT to SINTEK to increase thermal limits. Upgrade Ckt.26F Velasco to CAMDEN to increase thermal limits. | Upgrade Ckt.26F Velasco to CAMDEN to increase thermal limits. |  | CAMDEN | Velasco | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-30 00:01 |  | 138 | 0 | 0.28 | 0 |  | Brazoria | Brazoria | Tier 3 | 24RPG012 | 2024-04-10 | 2024-05-02 | 2024-05-02 | 43360, 43365 | Y | N |  |  | 85989 | 85987
85970A | Athena (ATH) 138kV CEHE Station for RAVEN (RVN) / Raven Solar & Storage (24INR0209 & 24INR0210) | Loop new Athena CEHE 138kV substation into Ckt.65C East Bernard to Wallis to create new Ckt.65 East Bernard to Athena to Wallis. |  | Athena | East Bernard/Wallis | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 0 | 0 | 0 |  | Wharton | Austin | Tier 4 |  |  |  |  | 44190, 44740, 46650 | Y | N |  |  | 87177 | 85970
87346 | Upgrade Ckt 25 Jeanetta to Westwood to increase thermal limits | Upgrade Ckt 25 Jeanetta to Westwood to increase thermal limits |  | Westwood | Jeanetta | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 0 | 2.16 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47310, 48417 | Y | N |  |  | 87347 | 87346
73578A | Heights 138kV Loop Conversion | Rebuild/Reconductor Dead Ckt.40Z Str #14606-26374 to prepare for 138kV Conversion. De-energize Ckt.31C Dunlavy to Heights and repurpose as Ckt.09D tap to Dunlavy TR1 load. |  | Dunlavy | Heights | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 45752, 46615, 47580, 47581, 47591, 47682 | Y | N |  |  | 90931 | 73578
78485D | Britmoore to Bellaire Ckt.24B Upgrades | Upgrade Ckt.24B Bellaire to Ulrich to Hillcroft to increase thermal limits. |  | Bellaire | Hillcroft | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 0 | 6.41 | 0 |  | Harris | Harris | Tier 3 | 23RPG025 | 2023-09-06 | 2023-09-28 | 2023-09-28 | 48146, 48378, 48512 | Y | N |  |  | 90168 | 78485
80464 | McKenzie Road: Rebuild 138 kV Station | Interconnect the Bootstrap loads to the rebuilt McKenzie Road 138 kV station | In-Service Date Update | Nueces | Nueces | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 | TP2023883 | 2026-05-31 |  | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 8520, 8545, 8858, 78569 | Y |  |  |  | 80465 | 80464
81215 | Oklaunion: Reconfigure 138 kV Station | Reconfigure the Oklaunion 138 kV station from a straight bus to a ring bus | Contact Update | Oklaunion |  | Planned | TP2023876 | AEP TNC/ETT | Lance Price twang1@aep.com 918-599-2635 |  | 2026-05-31 |  | 138 | 0 | 0 | 0 |  | Wilbarger |  | Tier 4 |  |  |  |  | 6066, 6097, 6098, 6100 | Y | N |  |  | 81216 | 81215
81006 | Add load at Diabox and thermally uprate Ckt 21 MOMENT-SOLMER-SRB |  |  | SOLMER | SR Bertron/ MOMENT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 0 | 2.12 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40480, 41090, 41400, 41480 | Y | N |  |  | 81007 | 81006
90242B | Clute to Velasco Ckt.82 Upgrades RPG | Upgrade Ckt.86 Clute to CAVERN to BIPORT to increase thermal limits. |  | CAVERN | Clute/BIPORT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 0 | 0.31 | 0 |  | Brazoria | Brazoria | Tier 4 | 24RPG012 | 2024-04-10 | 2024-05-02 | 2024-05-02 | 42190, 43150, 43330 | Y | N |  |  | 90764 | 90242
90242C | Clute to Velasco Ckt.82 Upgrades RPG | Upgrade Ckt.82G BIPORT to OYSTER CREEK to increase thermal limits. |  | BIPORT | OYSTER CREEK | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 0 | 0.21 | 0 |  | Brazoria | Brazoria | Tier 4 | 24RPG012 | 2024-04-10 | 2024-05-02 | 2024-05-02 | 42190, 43335 | Y | N |  |  | 90763 | 90242
90242D | Clute to Velasco Ckt.82 Upgrades RPG | Upgrade Ckt.82D GLOBAL to Velasco to increase thermal limits. |  | GLOBAL | Velasco | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 0 | 1.06 | 0 |  | Brazoria | Brazoria | Tier 4 | 24RPG012 | 2024-04-10 | 2024-05-02 | 2024-05-02 | 43345, 43360 | Y | N |  |  | 90762 | 90242
90242A | Clute to Velasco Ckt.82 Upgrades RPG | Upgrade Ckt.26E SINTEK to CAMDEN to increase thermal limits. |  | SINTEK | CAMDEN | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 0 | 0.62 | 0 |  | Brazoria | Brazoria | Tier 4 | 24RPG012 | 2024-04-10 | 2024-05-02 | 2024-05-02 | 43240, 43365 | Y | N |  |  | 90761 | 90242
92687 | Oncor_ME_92687_Burkett 138 kV Switch |  |  |  |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2026-05-31 |  | 138 | 0 | 0 | 0 |  | Ellis | Ellis | Tier 4 |  |  |  |  | 2471, 2710, 2893 | Y |  |  |  | 92688 | 92687
92998 | LeMay: Expand 138 kV Station | Interconnect the new White Water Midstream load to the existing LeMay 138 kV station |  | LeMay |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2026-05-31 |  | 138 | 0 | 0 | 0 |  | La Salle | La Salle | Tier 4 |  |  |  |  | 8079, 8627 | Y | N |  |  | 92999 | 92998
64042 | Barrilla Junction: 69 kV Loop Rebuild | Rebuild Barrilla Junction to Saragosa to Cherry Creek to Verhalen to Hoefs Road stations, convert to 138 kV |  | Barrilla Junction | Hoefs Road Station | Planned | 1141 - 1319 | AEP TNC | Brent Harris twang1@aep.com 918-599-2635 | 1886 | 2026-05-31 |  | 69 | 0 |  | 0 |  | Pecos | Reeves | Tier 3 | 21RPG023 | 2021-12-17 | 2022-01-14 |  | 6649, 6650, 6651, 6652, 6653, 6654, 60206, 60207, 60208, 60385, 60716, 60808, 69023, 69047 | Y | N |  |  | 64043 | 64042
63922 | Tiki Island Distribution Upgrades | Install double-tap distribution service to Tiki Island. Existing tap will remain on Ckt.63E La Marque to Stewart. Tap Ckt.93C La Marque to West Galveston for the new tap section to Tiki Island. |  | Tiki Island | LaMarque/West Galveston | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 0 | 0 | 0 |  | Galveston |  | Tier 4 |  |  |  |  | 42860, 43290, 43351, 43352, 43355, 43400, 48551, 48552, 48855 | Y | N |  |  | 91179 | 63922
66208 | Rebuild League City-Hidden Lakes with bundled 795 ACSS |  |  | Hidden Lakes (bus # 38900) | League City (bus # 38920) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-05-31 |  | 138 | 0 | 3.21 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 38900, 38920 | Y |  |  |  | 66209 | 66208
66077 | Reconductor both Pecos-Cedarvale 138 kV ckts |  |  | Pecos (bus # 38091) | Cedarvale (bus # 38145) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-05-31 |  | 138 | 0 | 15.34 | 0 |  | Reeves | Ward | Tier 4 |  |  |  |  | 38091, 38145 | Y |  |  |  | 66078 | 66077
61552 | Matador to Turkey: Rebuild 69 kV Line | Rebuild 69 kV line from Matador to Turkey |  | Matador | Turkey | Under Construction | 1128 - 1306 | AEP TNC | Chris Carroll twang1@aep.com 918-599-2635 | 1873 | 2026-05-31 |  | 69 | 0 | 26.9 | 0 |  | Motley | Hall | Tier 4 |  |  |  |  | 6020, 6024, 6039, 6041, 6044, 6140, 60351 | Y | N |  |  | 65596 | 61552
50890 | Port Lavaca: Station Rebuild (Cangrejo) | Rebuild the Port Lavaca (Cangrejo) station |  | Port Lavaca |  | Planned | 1057 - 1230 | AEP TCC | Lorraine Timmerman deevans@aep.com 918-599-2938 | 3787 TA2019045 | 2026-05-31 |  | 69 | 0 | 37.81 | 0 |  | Calhoun |  | Tier 1 | 21RPG002 | 2021-02-01 | 2021-09-16 | 2021-10-22 | 8135 | Y | N |  |  | 50891 | 50890
76232 | Reconductor Mivida-Coachwhip-Fishhook 2045 ACCC |  |  | Mivida PSSE Bus# 38152 | Fishhook PSSE Bus# 38180 | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-05-31 |  | 138 | 0 | 14.39 | 0 |  | Ward | Ward | Tier 4 |  |  |  |  | 38152, 38170, 38180 | Y |  |  |  | 76233 | 76232
76291 | Upgraded Cedarvale–BoneSpringsTap–Fishhook |  |  | Cedarvale to Bone Springs Tap | Bone Springs Tap to Fishhook | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-05-31 |  | 138 | 0 | 12.59 | 0 |  | Ward | Ward | Tier 4 |  |  |  |  | 38145, 38165, 38180 | Y |  |  |  | 76292 | 76291
76293 | Upgraded Cedvale-MiDiva138KV |  |  | Cerdarvale | Midiva | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-05-31 |  | 138 | 0 | 0.15 | 0 |  | Ward | Ward | Tier 4 |  |  |  |  | 38145, 38152 | Y |  |  |  | 76294 | 76293
76196 | Lobo: 138 kV Breaker Replacement | Replace 138 kV breakers at the Lobo 138 kV station | Contact and In-Service Date Update | Lobo |  | Planned |  | AEP TCC | Lance Price jlsolis@aep.com 361-881-5574 | TP2023015 | 2026-05-31 |  | 138 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  |  | 80221 | Y |  |  |  | 76197 | 76196
90130 | Install (2) new 100 MVA distribution transformers at Orchard substation. | Install two(2) new 100 MVA distribution transformers at Orchard substation. |  | Orchard | Beasly/ MARICK | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 0 | 0 | 0 |  | Fort Bend |  | Tier 4 | [5 empty] | Y | N |  |  | 90133 | 90130
80632 | Install Kilgore 35kV Distribution Substation. Loop on Ckt.86B to create new Ckt.86 CHEVRON to Kilgore to LANGSTON | Install Kilgore 35kV Distribution Substation. Loop on Ckt.86B to create new Ckt.86 CHEVRON to Kilgore to LANGSTON |  | Kilgore | CHEVRON/LANGSTON | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 5.12 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  |  | 40300, 40775, 44830 | Y | N |  |  | 87179 | 80632
78490C | Jeanetta Auto Upgrades | Upgrade Ckt.25B Roark equipment and reconductor near Roark substation to increase thermal limits |  | Clodine | Roark | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 345 | 0 | 0.04 | 0 |  | Harris | Harris | Tier 3 | 23RPG031 | 2023-10-04 | 2023-10-26 |  | 44590, 48315, 48316 | Y | N |  |  | 79427 | 78490
78490D | Jeanetta Auto Upgrades | Reconductor Ckt.25B Clodine to Roark TR8 tap to increase thermal limits. |  | Clodine | Roark | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 345 | 0 | 3.67 | 0 |  | Harris | Harris | Tier 3 | 23RPG031 | 2023-10-04 | 2023-10-26 |  | 44140, 48315 | Y | N |  |  | 79428 | 78490
69253 | Cangrejo to Dacosta: Rebuild 138 kV Line | Rehab 138 kV line from Cangrejo to Dacosta |  | Cangrejo | Dacosta | Planned |  | AEP TCC | Lorraine Timmerman mlforcum@aep.com 918-599-2674 |  | 2026-05-31 |  | 138 | 0 | 17.97 | 0 |  |  |  | Tier 1 | 21RPG002 | 2021-02-01 | 2021-09-16 | 2021-10-22 | 8133, 8135, 8136, 8140, 8141, 8143, 8169, 8536, 8721, 8722, 8723, 8756, 80064, 88133 | Y |  |  |  | 87986 | 69253
70898 | Flomot Tap: Rebuild 69 kV Line | Rehab Flomot Tap 69 kV Line |  | Flomot Tap | Flomot | Planned |  | AEP TNC | Chris Carroll twang1@aep.com 918-599-2635 |  | 2026-05-31 |  | 69 | 0 | 7.06 | 0 |  | Motley | Motley | Tier 4 |  |  |  |  | 6041, 6042 | Y | N |  |  | 70899 | 70898
4323 | CPSE_Braunig to Brooks_MLSE | Upgrade terminal at Brooks and ensure a rating of 2000 A (minimum) at both Braunig and Brooks terminals |  | Braunig | Brooks | In-Service |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0669 | 2026-05-31 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5045, 5394 | Y | Y |  |  | 11875 | 4323
78485C | Britmoore to Bellaire Ckt.24B Upgrades | Upgrade portions of Ckt.05E Bellaire to Sharpstown to Hillcroft to increase thermal limits. |  | Bellaire | Hillcroft | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 |  | 138 | 0 | 3.09 | 0 |  | Harris | Harris | Tier 3 | 23RPG025 | 2023-09-06 | 2023-09-28 | 2023-09-28 | 47015, 48145, 48343 | Y | N |  |  | 90169 | 78485
73578B | Heights 138kV Loop Conversion | Repurpose/retire existing 69kV Ckts 34A/34B. Unbundle parallel-bundled portions of Ckt.40A HOC to Dunlavy. Reconfigure Ckt.40A to reach a Minimum 1-2000AAC limiting conductor @ 90/120Deg. Upgrade HOC ine relaying on 69kV Ckt.40A HOC to Dunlavy. |  | Dunlavy | HO Clarke | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 00:01 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 | [5 empty] | Y | N |  |  | 90932 | 73578
85970B | Athena (ATH) 138kV CEHE Station for RAVEN (RVN) / Raven Solar & Storage (24INR0209 & 24INR0210) | Install one generator lead from Athena CEHE 138kV substation to RAVEN / Raven Solar & Storage (24INR0209 & 24INR0210). |  | Athena | RAVEN | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 00:01 |  | 138 | 0 | 0 | 0 |  | Wharton |  | Tier 4 | [5 empty] | Y | N |  |  | 87178 | 85970
73578D | Heights 138kV Loop Conversion | Convert Heights substation to 138kV service. Retire/repurpose portions of 69kV Ckts. 34A/34B for the new Heights 138kV loop. Reconfigure Ckt.09D to create new Ckt.09D Eureka TR2/TR3 tap to HE-DN_TR1 tap to Heights 138kV to White Oak. Reconductor any existing 1-795AAC limiting conductor to 2-959ACSS. Remove existing Heights 7.2 MVAR cap bank from Heights TR1. |  | Heights | San Felipe/White Oak | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 00:03 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 45752, 46615, 46620, 47160, 47581, 47591, 47680, 47682, 47685, 747680 | Y | N |  |  | 90933 | 73578
73371E | BP24 Sub Upgrades | Upgrade Whaley to WA Parish Ckt.72F to increase thermal limits |  | Whaley | WA Parish | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 00:04 | 2958101 | 345 | 0 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 4 |  |  |  |  | 44005, 44070 | Y | N |  |  | 89980 | 73371
73578E | Heights 138kV Loop Conversion | Remove White Oak auto A2/A4 and remaining 69kV facilities |  | White Oak |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-05-31 00:04 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 46615, 46620, 47680, 49021, 49042 | Y | N |  |  | 90934 | 73578
80384 |  | Reconductor Gibbons Creek to Greens Prairie Line |  | Gibbons Creek | Greens Pairie | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2026-06-01 |  | 138 | 0 | 12.9 | 0 |  | Grimes | Brazos | Tier 4 |  |  |  |  | 964, 32878 | Y |  |  |  | 80385 | 80384
65663 | Double Ckt Line M138-K | Project Delayed Indefinitely. |  | Pecos (bus # 38091) | Faulkner (bus # 38124) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-06-01 |  | 138 | 0 | 26.2 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  |  | 38091, 38124 | N |  |  |  | 65664 | 65663
61090 | Timbercreek 138kV substation | Change name to Establish 138kV Timbercreek substation with (2) 40MVA transformers and will cut into existing Ckt 948 (Onion Creek to Pilot Knob) |  | Onion Creek | Pilot Knob |  |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2026-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9240, 9251, 9259 | Y |  |  |  | 61091 | 61090
45029 | Grandview Highland Hills Rebuild | CPSE_Rebuild of 138 kV double circuit line Line between Grandview to Highland Hills. |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | T-0273 | 2026-06-01 |  | 138 | 0 | 11.6 | 0 |  | Bexar | Bexar | Tier 4 |  | 2019-01-11 |  |  | 5030, 5095, 5175, 5205 | Y |  |  |  | 45030 | 45029
80424 |  | Rebuild / Reconductor Dansby to Business Park 69kV for Rail Spur |  | Dansby | Bryn Business Park | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2026-06-01 |  | 69 | 0 | 3.3 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  |  | 32871, 32875 | Y |  |  |  | 80425 | 80424
80404 |  | Reroute East to Rodgers 69kV line to create East to Rayburn 69kV line to accommodate the TXDOT SH6 project. |  | BRYN EAST | RAYBURN | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2026-06-01 |  | 69 | 1 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  |  | 32849, 32861, 32874 | Y |  |  |  | 90442 | 80404
65906 | To add Jordan Station for GINR 21INR0031 |  |  |  |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2026-06-01 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 68001, 68014, 68016 | Y |  |  |  | 65907 | 65906
77320 | Add CapBANK in COYANOSA |  |  | COYANOSA |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-06-01 |  | 138 | 0 | 0 | 0 |  | Ward | Ward | Tier 4 |  |  |  |  | 38380 | Y |  |  |  | 77321 | 77320
76286 | Hecker to Resnik: Rebuild 138 kV Line | Rebuild the Hecker to Resnik 138 kV line | Contact Update | Hecker | Resnik | Planned |  | AEP TCC | Nathan Cowan deevans@aep.com 918-599-2938 | TP2023506 | 2026-06-01 |  | 138 | 0 | 0 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  |  | 8565, 8580 | Y |  |  |  | 76287 | 76286
87146 | GSEC_Tier4_9468_Add_Bull_Sub | New Substation Load out of 68001 Claytonville | Adding new 1400MW load with deposit and agreement. | Claytonville |  | Planned |  | GSEC | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2026-06-01 |  | 345 | 0 | 0 | 0 |  | Fisher |  | Tier 4 |  |  |  |  | 9468, 68001 | Y |  |  |  | 87147 | 87146
86323 | AEN_MagnesiumPlant_Northland_Ckt_979_RECONDUCTOR |  |  | 9128 | 9238 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2026-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9128, 9238 | Y | N |  |  | 86324 | 86323
89959 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2026-06-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 2710, 6972 | Y |  |  |  | 89960 | 89959
78455 | Oasis 345kV Substation / SOHO BESS II (25INR0162) | Install SOHO BESS II at Oasis 345kV substation… Connect at the same generator lead as SOHO BESS (SOHO BESS II - 25INR0162) |  | Oasis |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-06-01 00:01 |  | 345 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  |  | 43035, 113321 | Y | N |  |  | 78456 | 78455
91382 | Henne_Kohlenberg_Transmission_Line_Addition | New Braunfels Utilities will be building a new substation to serve new customer load near Kohlenberg Rd. LCRA TSC will build a new transmission line from Henne Substation to the new Kohlenberg substation and provide transmission service via a new transmission level bus. |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.prease@lcra.org 512-578-4514 | PLC-6682 | 2026-06-10 |  | 138 | 0 | 0 | 0 |  | Comal | Comal | Tier 4 |  |  |  |  | 7174, 7464 | Y |  |  |  | 91383 | 91382
76660 | Rebuild Temple Switch and install auto #2 | Rebuild Temple Switch and install auto #2 |  | Temple | Temple | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6197 | 2026-06-15 |  | 345 | 0 | 0 | 600 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 3414, 3415, 3718 | Y |  |  |  | 76661 | 76660 | 2023-NC60
76572 | Temple - Temple Pecan 138 kV 2nd Circuit | Temple - Temple Pecan 138 kV 2nd Circuit |  | Temple | Temple Pecan Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6235 | 2026-06-15 |  | 138 | 0 | 4.4 | 0 |  | Bell | Bell | Tier 1 |  |  |  |  | 3415, 3420 | Y |  |  |  | 76573 | 76572
67093 | New 138 kV station cut-in between Garfield and Hi-Cross | New 138 kV Easton Park Substation cut-in on CKT963 from Garfield to Hi-Cross substation to serve BBEC Load |  | 9143 |  | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2026-06-20 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9071, 9143, 9147 | Y |  |  |  | 67094 | 67093
61228 | AEN_McNeil__JustinLane__ckt_811_reconductor | Reconductor 3.98 miles of circuit to 3000 Amps. |  | McNeil [9080] | Justin Lane [9225] | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2026-06-21 |  | 138 | 0 | 3.98 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9080, 9225 | Y |  |  |  | 61229 | 61228
69709 | Bearkat - North McCamey Transmission Line Addition | LCRA TSC, Oncor , and WETT joint project to add the Bearkat-North McCamey 345-kV double-circuit transmission line and North McCamey-Sand Lake 345-kV double-circuit transmission line. 22RPG010 |  | Bearkat | Sand Lake | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2026-06-26 |  | 345 | 165 | 0 | 0 |  | Glasscock | Ward | Tier 1 | 22RPG010 | 2022-04-12 | 2022-07-13 |  | 11098, 59903, 76000 | Y | Y |  |  | 78333 | 69709 | 2021-FW15
45136 | CPSE_New Midtown Substation | New Mid Town substation looped into Comal St to Olmos transmission line. |  |  |  |  | S-0910 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | T-0283 | 2026-06-30 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5096, 5311, 5325 | Y |  |  |  | 45137 | 45136
76242 | Lytle: Construct New 138 kV Terminal | Convert the Big Foot to Lytle 69 kV line to 138 kV and interconnect Rowan Digital to the Lytle 138 kV station | Contact and In-Service Date Update | Lytle |  | Planned |  | ETT | John Solis jlsolis@aep.com 361-881-5574 | TP2022155 | 2026-06-30 |  | 138 | 0.1 | 0 | 0 | 0,23 | Medina |  | Tier 4 |  |  |  |  | 8962 | Y |  |  |  | 76243 | 76242
71952 | LCRA TSC Bluffton to Buchanan Transmission Line Overhaul | Overhaul circuit and replace conductor with single-Drake conductor (117 MVA) from Bluffton to Buchanan. Replacement structures should be 138-kV double-circuit capable of supporting a single-Suwannee conductor. Install OPGW. |  | Bluffton | Buchanan | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2026-06-30 |  | 69 | 0 | 7 | 0 |  | Llano | Llano | Tier 4 |  |  |  |  | 7101, 7406 | Y | N |  |  | 72467 | 71952
70192 | Doss - Headwaters Transmission Line Overhaul | LCRA TSC will perform an overhaul on the 14.2-mile Doss - Headwaters (T508) 69-kV transmission line. |  | Doss | Headwaters | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-06-30 | 2024-04-19 | 69 | 0 | 14.2 | 0 |  | Gillespie | Gillespie | Tier 4 |  |  |  |  | 7408, 7410 | Y | Y |  |  | 70193 | 70192
91402 | Buchanan_Burnet_TL_Overhaul | Perform an overhaul on the 11.4 mile T108 Buchanan - Burnet 69-kV (de-energized) transmission line |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-6943 | 2026-06-30 |  | 138 | 0 | 0 | 0 |  | Burnet | Burnet | Tier 4 |  |  |  |  | 7087, 7092, 7093, 7097, 7100 | Y |  |  |  | 91403 | 91402
67326 | Ajo to Reforzar: Construct New 345 kV Double Circuit Line | Construct a new 345 kV double circuit line from Ajo to Reforzar | Dollars Update | Ajo | Reforzar | Planned |  | AEP TCC/ETT | Curtis Brown jlsolis@aep.com 361-881-5574 | TP2022030 | 2026-06-30 |  | 345 | 11 | 0 | 0 |  | Kenedy | Brooks | Tier 1 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 80076, 80078 | Y |  |  |  | 67327 | 67326
73063 | Big Foot to Lytle: Convert to 138 kV | Convert the Big Foot to Lytle 69 kV line to 138 kV and interconnect Rowan Digital to the Lytle 138 kV station | In-Service Date Update | Big Foot | Lytle | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 | TP2022155 | 2026-06-30 |  | 138 | 0 | 12 | 0 | 0,23 | Medina | Frio | Tier 4 |  |  |  |  | 8208, 8216, 8218, 8221, 8223, 8622, 8732, 8962, 58280 | Y |  |  |  | 73064 | 73063
71002 | Tidehaven: Construct New Distribution Station | Construct new distribution station on the Blessing to Palacios 69 kV line | In-Service Date Update | Tidehaven |  | Planned | 1028 - 1206 | AEP TCC | Marc Wilson deevans@aep.com 918-599-2938 | 3767 DP21X0007 | 2026-06-30 |  | 138 | 0 | 0 | 0 |  | Matagorda |  | Tier 4 |  |  |  |  | 8044, 8119, 8121, 8131, 8132, 8133, 8555, 8666 | Y | N |  |  | 71003 | 71002
70186 | Buchanan CTEC - Kingsland 1 Transmission Line Overhaul | LCRA TSC will perform an overhaul on the 6.2-mile Buchanan to Kingsland 2 to Kingsland 1 (T291) 69-kV transmission line. |  | Buchanan CTEC | Kingsland 1 | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2026-06-30 |  | 69 | 0 | 6.2 | 0 |  | Llano | Llano | Tier 4 |  |  |  |  | 7101, 7402, 7404 | Y | Y |  |  | 78419 | 70186
63956 | Clear Crossing: Build 345 kV terminal | Interconnect HODL Ranch II at Clear Crossing 345 kV station | In-Service Date Update | Clear Crossing | HODL Ranch II | Planned | 1139 - 1317 | ETT | Adam Wells twang1@aep.com 918-599-2635 | 1884 | 2026-06-30 |  | 345 | 0 | 0 | 0 |  | Haskell | Haskell | Tier 4 |  |  |  |  | 60017, 60515 | Y | N |  |  | 63957 | 63956
73401 | Fredonia - Mason Transmission Line Overhaul | Perform an overhaul on the 11 mile T289 Fredonia (CTEC) - Mason (CTEC) 69-kV transmission line. Per LCRA TSC Transmission System Planning procedure, replacement structures will be capable of operating at 138-kV. |  | Fredonia | Mason | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-06-30 |  | 69 | 0 | 11 | 0 |  | Mason | Mason | Tier 4 |  |  |  |  | 7395, 76391 | Y | N |  |  | 73402 | 73401
91630 | Jim Treece: Interconnect New 345 kV Generator | Interconnect Blue Summit II Energy Storage to the existing Jim Treece 345 kV station | NEW | Jim Treece |  | Planned |  | ETT | Tong Wang twang1@aep.com 918-599-2635 | TP2025111 | 2026-06-30 |  | 345 | 0 | 0 | 0 |  | Wilbarger |  | Tier 4 | [5 empty] | Y | N |  |  | 91631 | 91630
77144 | Pompano: New 138 kV Station | New station for Next Decade/ Rio Grande LNG | In-Service Date and Circuit Miles Upgrade Update | Pompano |  | Planned |  | AEP TCC | Robert Younger jlsolis@aep.com 361-881-5574 | TP2015151 | 2026-06-30 |  | 138 | 0 | 20.4 | 0 | 0,276.4 | Cameron |  | Tier 4 |  |  |  |  | 8337, 8535, 79601 | Y |  |  |  | 77145 | 77144
90010 | Magill: Construct New 138 kV Terminal | Interconnect City Breeze BESS to the Magill 138 kV station | Contact Update | Magill |  | Planned |  | AEP TCC | Brooks Dow deevans@aep.com 918-599-2938 | TP2024104 | 2026-07-15 00:02 |  | 138 | 0 | 0 | 0 |  | Matagorda |  | Tier 4 |  |  |  |  | 8111, 114071 | Y |  |  |  | 90011 | 90010
86796 | Buccaneer: Construct New 69 kV Station | Interconnect the Oncor Regency station to the new Buccaneer 69 kV station on the Eden to North Brady 69 kV line between Melvin and North Brady | Contact Update | Buccaneer |  | Planned | TP2024028 | AEP TNC | Lance Price twang1@aep.com 918-599-2635 |  | 2026-07-31 |  | 69 | 0 | 0 | 0 |  | McCulloch |  | Tier 4 |  |  |  |  | 6006, 6380, 60005 | Y | N |  |  | 86797 | 86796
79462 | Expand HO Clarke substation for Callisto II (22INR0558) | Expand HO Clarke substation for Callisto II (22INR0558) |  | HO Clarke |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-07-31 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 | [5 empty] | Y | N |  |  | 79463 | 79462
90232H | Facility Ratings Methodology (FRM) Upgrades | Upgrade Kirby to Garrott Ckt.37A to increase thermal limits as part of FRM upgrades |  | Kirby | Garrott | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-07-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47320, 47660 | Y | N |  |  | 90923 | 90232
90008 | Tango to Pawnee: Rebuild 345 kV Line | Rebuild the Tango to Pawnee 345 kV line | Contact, In-Service Date, and RPG Update | Tango | Pawnee | Planned |  | AEP TCC/CPS,STEC | Craig Tabor jlsolis@aep.com 361-881-5574 | TP2024118 | 2026-07-31 |  | 345 | 1.2 | 1.2 | 0 |  | Bee | Karnes | Tier 1 | 22RPG048 | 2022-12-29 | 2024-04-10 | 2024-04-23 | 5725, 8689 | Y |  |  |  | 90009 | 90008
91555 | Switchyard to accommodate for Telios Large Load. |  |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2026-08-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 2 |  |  |  |  | 6879, 6882, 6915, 6950, 6980 | Y |  |  |  | 91556 | 91555
91558 | 138kV transmission upgrade to serve Kirkland large load. |  |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2026-08-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 2 |  |  |  |  | 6886, 12713 | Y |  |  |  | 91559 | 91558
61444 | GVEC Kicaster Substation Addition (formerly Wilson South) | Add a new load-serving substation 4.35 miles south of La Vernia along FM 775 with a 40 MVA PWT. |  | Wilson South |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2026-08-26 |  | 138 | 0 | 0 | 0 |  | Wilson |  | Tier 4 |  |  |  |  | 5418, 7615, 7629 | Y | N |  |  | 78418 | 61444
75790 | Placeholder Station for Erath Solar POI | Placeholder Station for Erath Solar POI |  |  |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2026-08-27 |  | 345 | 0 | 0 | 0 |  | Erath | Erath | Tier 4 |  |  |  |  | 68020, 68025, 68030 | Y |  |  |  | 75791 | 75790
82298 | PMCR for Adding TNMP Woodhouse New Station | [6 empty] | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-08-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  | 2024-02-27 | 38295, 38308, 38355, 60717 | Y |  |  |  | 82299 | 82298
90038 | McKenzie Road to Winthorp: Construct New 138 kV Line | Interconnect the new Winthorp load station to the existing McKenzie Road 138 kV station | NEW | McKenzie Road | Winthorp | Planned |  | AEP TCC/ETT | Douglas Evans deevans@aep.com 918-599-2938 | TP2024150 | 2026-08-31 |  | 138 | 0.15 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 8545, 8858 | Y | N |  |  | 90039 | 90038
90161B | Install new Mill Creek (MLC) distribution substation with (2) 100 MVA transformers. | Relocate existing Kluge 80 MVAR cap bank CB1 from Ckt.81F line position to Ckt.81G line position. |  | Kluge |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-08-31 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 | [5 empty] | Y | N |  |  | 91235 | 90161
90161A | Install new Mill Creek (MLC) distribution substation with (2) 100 MVA transformers. | Install new Mill Creek (MLC) distribution substation with (2) 100 MVA transformers. Loop substation on Ckt.81G to create new Ckt.81 Pinehurst to Mill Creek to Tomball. |  | Mill Creek | Pinehurst/ Tomball | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-08-31 |  | 138 | 9 | 0 | 0 |  | Montgomery | Harris | Tier 4 |  |  |  |  | 44850, 46240, 46510 | Y | N |  |  | 91233 | 90161
92655 | Oncor_MNE_92655_Farm Road 138 kV Switch |  |  |  |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2026-08-31 |  | 138 | 0 | 0 | 0 |  | Hopkins | Hopkins | Tier 4 |  |  |  |  | 1822, 1823, 2844 | Y |  |  |  | 92656 | 92655
90161C | Install new Mill Creek (MLC) distribution substation with (2) 100 MVA transformers. | Convert Pinehurst to unity power factor substation. |  | Pinehurst |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-08-31 |  | 138 | 0 | 0 | 0 |  | Montgomery |  | Tier 4 | [5 empty] | Y | N |  | No Transmission upgrades expected. | 91234 | 90161
89955 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2026-09-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 1823, 6792 | Y |  |  |  | 89956 | 89955
91584 |  |  |  | HOLDER | RISING STAR | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2026-09-01 |  | 138 | 0 | 0 | 0 |  | Comanche | Comanche | Tier 4 |  |  |  |  | 292, 33285, 33289 | Y |  |  |  | 91585 | 91584
43434 | This is the POI for High Noon Solar and Storage |  |  | Boot Hill | Boot Hill | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2026-09-01 |  | 138 | 0 | 0 | 0 |  | Hill | Hill | Tier 4 |  |  |  |  | 444, 445, 446 | Y |  |  |  | 43435 | 43434
72579B | PEC_MountainTop_Blanco_DevilsHill_VoltageUpgrade | Rebuild and upgrade Blanco to Devil's Hill 69 kV circuits to 138 kV with bundled 795 kcmil conductor (440 MVA). (Replaces ERCOT Project # 70367B) |  | Blanco | Devil's Hill | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2026-09-15 |  | 138 | 0 | 0 | 0 |  | Blanco | Blanco | Tier 4 | 22RPG033 |  | 2022-11-14 |  | 70482, 70484, 70493 | Y | Y |  |  | 72581 | 72579
66492B | Chico West - Grindstone Switch 69 kV Line rebuild | Upgrade Grindstone - Jacksboro Sinclair 69 kV Line |  | Jacksboro Sinclair | Grindstone | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3006 | 2026-09-15 |  | 69 | 0 | 15 | 0 |  | Jack | Palo Pinto | Tier 4 |  |  |  |  | 1557, 1572 | Y |  |  |  | 72964 | 66492
66289C | Tyler to Athens 138 kV line Conversion | Tyler to Athens 138 kV Operation |  | Tyler | Athens | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6094 | 2026-09-15 |  | 138 | 0 | 0 | 0 |  | Henderson | Henderson | Tier 3 | 22RPG015 | 2022-06-01 | 2022-07-01 |  | 3108, 3142, 3197, 3236, 3238, 13235 | Y |  |  |  | 87816 | 66289
66101 | Del Sol to Frontera: Build New 345 kV Double Circuit Line | Build new 345 kV double circuit line from Del Sol to Frontera. Expand Frontera Station and install two (2) autotransformers. | In-Service Date Update | Del Sol | Frontera | Planned |  | AEP TCC/ETT | Brent Harris jlsolis@aep.com 361-881-5574 | TP2020838 | 2026-09-30 |  | 345 | 36 | 0 | 1350 |  | Starr | Hidalgo | Tier 1 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 8355, 8980, 8992, 80119, 80355 | Y |  |  |  | 66102 | 66101
80830 | Zenaida: Construct New 138 kV Station | Interconnect Sun Cactus Solar to the new Zenaida 138 kV station on the Crestonio to Falfurrias 138 kV line | In-Service Date Update | Zenaida |  | Planned | TP2023851 | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2026-09-30 |  | 138 | 0 | 0 | 0 |  | Duval |  | Tier 4 |  |  |  |  | 80043 | Y | N |  |  | 80831 | 80830
67320 | Cruce to Reforzar: Construct New 345 kV Double Circuit Line | Construct a new 345 kV double circuit line from Cruce to Reforzar | Contact and In-Service Date Update | Cruce | Reforzar | Planned |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 | TP2022033 | 2026-09-30 |  | 345 | 48 | 0 | 0 |  | Jim Hogg | Brooks | Tier 1 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 80078, 80079 | Y |  |  |  | 67339 | 67320
80824 | Zenaida: Construct New 138 kV Station | Interconnect Dove Run Solar to the new Zenaida 138 kV station on the Crestonio to Falfurrias 138 kV line | In-Service Date Update | Zenaida |  | Planned | TP2023843 | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2026-09-30 |  | 138 | 0 | 0 | 0 |  | Duval |  | Tier 4 |  |  |  |  | 8510, 8695, 80043 | Y | N |  |  | 80825 | 80824
91496 |  |  |  | Perry | Ben Hur | Under Construction |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2026-10-01 |  | 138 | 0 | 0 | 100 |  | Limestone | Limestone | Tier 4 |  |  |  |  | 85, 91, 92, 97, 98, 99, 103, 154691 | Y |  |  |  | 91497 | 91496
76818 | Upgrade Rayburn Auto Station | Upgrade Rayburn Auto |  | Rayburn | Rayburn | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-10-01 |  | 138 | 0 | 0 | 0 |  | Victoria | Victoria | Tier 4 |  |  |  |  | 5500, 5502 | N |  |  |  | 76819 | 76818
78177 |  |  |  | Pleasant Grove | Pleasant Grove | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2026-10-15 |  | 69 | 0 | 0 | 0 | 0,7.2 | Falls | Falls | Tier 4 |  |  |  |  | 81 | Y |  |  |  | 78178 | 78177
78175 |  |  |  | Franklin | Franklin | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2026-10-15 |  | 138 | 0 | 0 | 0 | 0,9 | Robertson | Robertson | Tier 4 |  |  |  |  | 57 | Y |  |  |  | 78176 | 78175
78181 |  |  |  | Midway | Midway | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2026-10-15 |  | 69 | 0 | 0 | 0 | 0,7.2 | Falls | Falls | Tier 4 |  |  |  |  | 185 | Y |  |  |  | 78182 | 78181
91945 | Establish Alder 138 kV Switch | Establish Alder 138 kV Switch |  | Alder | Alder | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6329 | 2026-10-30 |  | 138 | 0 | 0 | 0 |  | Van Zandt | Van Zandt | Tier 2 | 24RPG007 |  |  |  | 3173, 3175, 3184 | Y |  |  |  | 91946 | 91945
73098 | Castroville Cut-in 138 kV | Cut the AEP line from Quihi to CPS Castroville into the newly converted to 138 kV STEC Castroville station. | In-Service Date Update | Quihi | Castroville (CPS) | Planned | TP2022982 | ETT | Jeremy Brazeal jlsolis@aep.com 361-881-5574 |  | 2026-10-31 | 2023-05-25 | 138 | 0.4 | 0 | 0 |  | Medina |  | Tier 2 | 22RPG022 | 2023-08-22 | 2023-11-22 |  | 5083, 5804, 8248 | Y |  |  |  | 73099 | 73098
79451A | Loop new Ancla CEHE 138kV substation into Ckt.04E Angleton to West Columbia to create new Ckt.04 Angleton to Ancla to West Columbia. Install one generator lead from Ancla CEHE 138kV substation to ROYAL / Royal River BESS. | Loop new Ancla CEHE 138kV substation into Ckt.04E Angleton to West Columbia to create new Ckt.04 Angleton to Ancla to West Columbia. |  | Ancla | Angleton/West Columbia | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-10-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42110, 43380, 46630 | Y | N |  |  | 87173 | 79451
73496 | Nelson Sharpe: Construct New 345 kV Terminal | Interconnect Noria Hondo Solar and BESS to the Nelson Sharpe 345 kV station | In-Service Date Update | Nelson Sharpe |  | Conceptual |  | AEP TCC | Robert Dougherty deevans@aep.com 918-599-2938 |  | 2026-10-31 |  | 345 | 1 | 0 | 0 |  | Nueces |  | Tier 4 | [5 empty] | Y |  |  |  | 73497 | 73496
49550 | Port Isabel: Rebuild As GIS Station | Rebuild Port Isabel as a GIS | In-Service Date Update | Port Isabel |  | Planned | 958 - 1136 | AEP TCC | Ali Abukar deevans@aep.com 918-599-2938 | 3716 | 2026-10-31 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  |  | 8338, 8744 | Y | N |  |  | 49551 | 49550
70305 | Camp Elizabeth: Build new 69 kV station | Construct new 69 kV box bay station with capacitor bank on the College Hills West to Sterling City 69 kV line | In-Service Date Update | Camp Elizabeth |  | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 |  | 2026-10-31 |  | 69 | 0 | 0 | 0 | 0,7.7 | Sterling |  | Tier 4 |  |  |  |  | 6417, 6435, 6436, 6641, 11352 | Y | N |  |  | 70306 | 70305
70662 | Cobra: Build new 345 kV station | Interconnect Garcitas Solar to the new Cobra 345 kV station on the Radiant to Static 345 kV line | In-Service Date Update | Cobra |  | Planned |  | AEP TCC | Zachary Lachiusa deevans@aep.com 918-599-2938 | TP2022750 | 2026-10-31 |  | 345 | 0 | 0 | 0 |  | Jackson |  | Tier 4 |  |  |  |  | 5915, 8676, 8715, 8728 | Y |  |  |  | 70663 | 70662
73352A | PH Robinson Area 138kV Upgrades | Reposition existing PH Robinson to BACLIF generator lead from the PHR_South bus to the PHR_North bus. |  | PH Robinson | BACLIF | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-10-31 |  | 138 | 0 | 0 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 42010, 42015, 111131 | Y | N |  |  | 73353 | 73352
73621A | Hawkinsville (HAW) CNP-Owned 345kV Substation for Lavaca Bay Solar (23INR0084) | New 345kV Hawkinsville (HAW) substation for generator interconnection to Lavaca Bay Solar. Loop Ckt.27D into substation to create new Ckt.27 Jones Creek to Hawkinsville to Refuge. |  | Refuge | Jones Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-10-31 |  | 345 | 1.4 | 0 | 0 |  | Matagorda | Brazoria | Tier 4 |  |  |  |  | 42400, 42440, 42530 | Y | N |  |  | 87138 | 73621
73362 | Uribe: Construct New Distribution Station | Construct new distribution station on the Molina to Zapata 138 kV line | Contact Update | Uribe |  | Planned |  | AEP TCC | Alex Perkins jlsolis@aep.com 361-881-5574 |  | 2026-10-31 | 2958101 | 138 | 0 | 0 | 0 |  | Zapata |  | Tier 4 |  |  |  |  | 8299, 8646, 8985, 8993, 80230 | Y | N |  |  | 73363 | 73362
73621B | Hawkinsville (HAW) CNP-Owned 345kV Substation for Lavaca Bay Solar (23INR0084) | Install generator lead from Hawkinsville (HAW) substation to LAVACA / Lavaca Bay Solar. |  | Hawkinsville |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-10-31 00:01 |  | 345 | 0 | 0 | 0 |  | Matagorda |  | Tier 4 | [5 empty] | Y | N |  |  | 87139 | 73621
79451B | Loop new Ancla CEHE 138kV substation into Ckt.04E Angleton to West Columbia to create new Ckt.04 Angleton to Ancla to West Columbia. Install one generator lead from Ancla CEHE 138kV substation to ROYAL / Royal River BESS. | Install one generator lead from Ancla CEHE 138kV substation to ROYAL / Royal River BESS. |  | Ancla | ROYAL | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-10-31 00:01 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 | [5 empty] | Y | N |  |  | 87174 | 79451
73352D | PH Robinson Area 138kV Upgrades | Upgrade PH Robinson 'North' Bus fault duty to 80KA |  | PH Robinson |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-10-31 00:03 |  | 138 | 0 | 0 | 0 |  | Galveston |  | Tier 4 | [5 empty] | Y | N |  |  | 73356 | 73352
70800 | Triada: Build New 345 kV Station | Interconnect Siete Wind to the new Triada 345 kV station on the Avanzada to Lobo 345 kV line | In-Service Date Update | Triada |  | Planned |  | ETT | Zachary Lachiusa jlsolis@aep.com 361-881-5574 | TP2022749 | 2026-10-31 12:00 |  | 345 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  |  | 8718, 80219, 80235 | Y |  |  |  | 70801 | 70800
91176 | Add Combine Switch station next to the existing Combine station. The new Combine switch will connect to Combine NTMWD | Add Combine Switch station next to the existing Combine station. The new Combine switch will connect to Combine NTMWD |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2026-11-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 6821, 6858, 6903, 6904, 6905 | Y |  |  |  | 91177 | 91176
87512 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2026-11-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 6821, 6904 | Y |  |  |  | 87513 | 87512
90059 | Cascabel: Construct New 345 kV Station | Interconnect Moccasin Solar to the new Cascabel 345 kV station on the Clear Crossing to Figaro 345 kV line between Clear Crossing and Kirchoff | NEW | Cascabel |  | Planned |  | ETT | Tong Wang twang1@aep.com 918-599-2635 | TP2024121 | 2026-11-30 |  | 345 | 0 | 0 | 0 |  | Jones |  | Tier 4 |  |  |  |  | 60124, 60515, 60705 | Y | N |  |  | 90060 | 90059
79988 | Lucero: Construct New 345 kV Station | Interconnect SanPat Solar I and SanPat Solar II to the new Lucero 345 kV station on the Angstrom to Naismith 345 kV line | Contact Update | Lucero |  | Planned | TP2023838 | AEP TCC | Zachary Lachiusa deevans@aep.com 918-599-2938 |  | 2026-11-30 |  | 345 | 0.2 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  |  | 8249, 8659, 80039 | Y | N |  |  | 79989 | 79988
85947 | Euclid Substation Addition | LCRA TSC provide a new transmission point of interconnection by constructing a new 345-kV substation and cut-in T510 Hutto - Zorn. T510 will also be looped into the new Limmer 345-kV substation |  | Euclid (7041) | Euclid (7041) | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-11-30 | 2958101 | 345 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  |  | 7042, 7045, 7341 | Y |  |  |  | 85949 | 85947
86882 | McKenzie to Westside: Reconductor 138 kV Line | Reconductor the McKenzie to Westside 138 kV line | Contact Update | McKenzie Road | Westside | Planned |  | AEP TCC/ETT | Douglas Evans deevans@aep.com 918-599-2938 | TP2024025 | 2026-11-30 |  | 138 | 0 | 0.32 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 8485, 8858 | Y | Y |  |  | 86883 | 86882
87031 | Primavera: Construct New 138 kV Terminal | Interconnect Project Lynx Storage to the Primavera 138 kV station | Contact and In-Service Date Update | Primavera |  | Planned |  | AEP TCC | Zachary Lachiusa deevans@aep.com 918-599-2938 | TP2024100 | 2026-11-30 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 8003 | Y |  |  |  | 87032 | 87031
68183 | Estes to Putnam: Rebuild 138 kV line | Rehab the Abilene South to Putnam 138 kV line |  | Estes | Putnam | Under Construction | 68150 | AEP TNC | Forrest Farson twang1@aep.com 918-599-2635 |  | 2026-11-30 | 2024-11-30 | 138 | 0 | 15 | 0 |  | Callahan | Callahan | Tier 4 |  | 2022-02-01 | 2022-03-01 | 2022-03-01 | 6309, 60365, 61015 | Y | N |  |  | 68184 | 68183
70630 | Ballinger to Santa Anna: Rebuild 69 kV line | Rebuild 69 kV line and rebuild taps on the Ballinger to Santa Anna 69 kV line. |  | Ballinger | Santa Anna | Planned |  | AEP TNC | Dewey Peters twang1@aep.com 918-599-2635 | TA2021193 | 2026-11-30 |  | 69 | 0 | 0 | 0 |  | Runnels | Coleman | Tier 3 | 22RPG028 | 2022-08-01 | 2022-09-01 |  | 6329, 6338, 6341, 6342, 6343, 6344, 6345, 6346, 6349, 6353, 60019, 60024, 60029 | Y |  |  |  | 70664 | 70630
68254 | Friend Ranch: Build new 138 kV Terminal | Interconnect Blue Sky Solar to the Friend Ranch 138 kV Station | In-Service Date Update | Friend Ranch |  | Planned |  | AEP TNC | Robert Younger twang1@aep.com 918-599-2635 |  | 2026-11-30 |  | 138 | 0 | 0 | 0 |  | Crockett |  | Tier 4 | [5 empty] | Y | N |  |  | 68255 | 68254
72479 | Cobia: Build new 138 kV Station | Build new 138 kV station along the Carbide to Joslin 138 kV line | Contact Update | Cobia |  | Planned |  | AEP TCC | Lorraine Timmerman deevans@aep.com 918-599-2938 |  | 2026-11-30 |  | 138 | 0.1 | 0 | 0 |  | Calhoun |  | Tier 4 |  |  |  |  | 8132, 8133, 8140, 8155, 8685, 8720, 8741, 8742, 88742, 708133 | Y |  |  |  | 72482 | 72479
44399 | South Padre Island: Rebuild as GIS station | Rebuild South Padre Island as a GIS | In-Service Date Update | South Padre Island | - | Planned | 948 - 1126 | AEP TCC | Ali Abukar deevans@aep.com 918-599-2938 | 3712 | 2026-11-30 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 | 24RPG036 | 2024-11-25 | 2024-12-27 |  | 8335, 8917 | Y | N |  |  | 44400 | 44399
45397 | Lion: 138 kV Station & Transmission Line | Lion: 138 kV Station with new line to Stewart Road |  | Lion | Stewart Road | Planned | 885 - 1063 | AEP TCC | Michael Glueck mlforcum@aep.com 918-599-2674 | 3672 TP2018218 | 2026-11-30 |  | 138 | 2.71 | 0 | 40 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  |  | 8758, 8951, 8969 | Y | N |  |  | 65528 | 45397
61396 | Hamilton Road to Maxwell: Rebuild 138 kV Line | Rebuild the Hamilton Road to Maxwell 138 kV line |  | Hamilton Road | Maxwell | Planned |  | AEP TCC | Jeremy Brazeal mlforcum@aep.com 918-599-2674 | TA2019800 | 2026-11-30 |  | 138 | 0 | 29 | 0 |  | Val Verde | Val Verde | Tier 3 | 20RPG022 | 2020-11-02 | 2021-01-19 |  | 8257, 8998 | Y |  |  |  | 65593 | 61396
66447 | Reforzar: Construct New 345 kV Station | Construct a new 345 kV station on the Lon Hill to North Edinburg 345 kV line | Status Update | Reforzar |  | Under Construction |  | AEP TCC | Chase Isaac jlsolis@aep.com 361-881-5574 | TP2022035 | 2026-11-30 |  | 345 | 0 | 0 | 0 |  | Brooks |  | Tier 1 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 8455, 8905, 80078 | Y |  |  |  | 67317 | 66447
67318 | Cruce: Construct New 345 kV Station | Construct a new 345 kV station on the Cenizo to Reforzar 345 kV line and the Del Sol to San Miguel 345 kV line | Dollars Update | Cruce |  | Planned |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 | TP2022034 | 2026-11-30 |  | 345 | 0 | 0 | 0 |  | Jim Hogg |  | Tier 1 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 80079 | Y |  |  |  | 67319 | 67318
67322 | Cenizo to Cruce: Construct New 345 kV Double Circuit Line | Construct a new 345 kV double circuit line from Cenizo to Cruce | Contact Update | Cenizo | Cruce | Planned |  | AEP TCC/ETT | Marc Wilson jlsolis@aep.com 361-881-5574 | TP2022031 | 2026-11-30 |  | 345 | 69 | 0 | 0 |  | Webb | Jim Hogg | Tier 1 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 80079, 80220 | Y |  |  |  | 67323 | 67322
67324 | Cruce to Del Sol: Construct New 345 kV Double Circuit Line | Construct a new 345 kV double circuit line from Cruce to Del Sol | Contact Update | Cruce | Del Sol | Planned |  | AEP TCC/ETT | Brent Harris jlsolis@aep.com 361-881-5574 | TP2022032 | 2026-11-30 |  | 345 | 54.2 | 0 | 0 |  | Jim Hogg | Starr | Tier 1 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 80079, 80355 | Y |  |  |  | 67325 | 67324
93163 | Diablo: Construct New Distribution Station | Construct new distribution station on the North McCamey to Palouse 138 kV line between Crossover and Palouse | NEW |  |  | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | DR24N0002 | 2026-11-30 |  | 138 | 0 | 0 | 0 |  | Upton |  | Tier 4 |  |  |  |  | 60115, 60723, 60728 | Y | N |  |  | 93164 | 93163
93127 | Lueders: Construct New Distribution Station | Construct new distribution station on the Fort Phantom to Paint Creek 138 kV line between California Creek and Fort Phantom | NEW |  |  | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | DR23N0002 | 2026-11-30 |  | 138 | 0 | 0 | 0 |  | Shackelford |  | Tier 4 |  |  |  |  | 6165, 6200, 60070 | Y | N |  |  | 93128 | 93127
70550 | Create_GP_Solar_POI_Bus | Created GP Solar POI bus. |  | Glen Pine | Explorer | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2026-12-01 |  | 138 | 0 | 0 | 0 |  | Van Zandt | Van Zandt | Tier 4 |  |  |  |  | 6802, 6829, 6833 | Y |  |  |  | 72028 | 70550
70299 | New Holleman Substation | [6 empty] | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2026-12-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 32005, 32892, 32893 | Y |  |  |  | 88269 | 70299
91988 | Oncor_FW_91988_Savanna - Canal Road 138 kV Line Rebuild | Savanna - Canal Road 138 kV Line Rebuild |  | Driver | Canal Road | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8637 | 2026-12-01 |  | 138 | 0 | 0 | 0 |  | Reagan | Upton | Tier 4 |  |  |  |  | 10025, 10037, 23870 | Y |  |  |  | 92188 | 91988
91851 | Establish Pinery 138 kV Switch | Establish Pinery 138 kV Switch |  |  |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2026-12-01 |  | 138 | 0 | 0 | 0 | 0,110.4 |  |  | Tier 4 |  |  |  |  | 1095, 11079, 18695 | Y |  |  |  | 91852 | 91851
91881 | Add Medallion138 kV Switch | Add Medallion138 kV Switch |  | Midland | Midland | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8821 | 2026-12-01 |  | 138 | 0 | 0 | 0 | 0,110.4 | Midland | Midland | Tier 4 |  |  |  |  | 1172, 1195, 1200, 10124, 11145 | Y |  |  |  | 91882 | 91881
78046 | TOYAH CREEK 345 kV Switch | Adding Oncor's portion of TNMP Silverleaf and Cowpen 345/138-kV Stations Project (23RPG013) |  | Sand Lake | Solstice | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8715 | 2026-12-01 |  | 345 | 0 | 0 | 0 |  | Ward | Pecos | Tier 1 | 23RPG013 | 2023-05-18 | 2023-06-09 |  | 11098, 18669, 60404 | Y |  |  |  | 78049 | 78046
15TPIT0044 | Fowlerton Capacitor | Add 19.2 MVAR capacitor |  | Fowlerton |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-12-01 |  | 138 | 0 | 0 | 0 | 0,19.2 | La Salle |  | Tier 4 |  |  |  |  | 5705 | Y | N |  |  | 9835 | 2554
70282 | New 138kV Brushy Creek Substation |  |  | Thompsons Creek | Snook | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2026-12-01 |  | 138 | 2.81 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  |  | 32857, 32863, 32867 | Y |  |  |  | 91640 | 70282
70882 | Rebuild Olivia - Carancahua | rebuild Olivia sw to Carancahua 795 ACSR |  | Olivia SW | Carancahua | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-12-01 |  | 69 | 0 | 8.71 | 0 |  | Jackson | Matagorda | Tier 4 |  |  |  |  | 5573, 5574 | Y |  |  |  | 70883 | 70882
71182 | Reiter 345/138 kV Switch | Construct a new 345/138 kV switch |  | Odessa EHV | Wolf/Moss | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8629 | 2026-12-01 |  | 345 | 0 | 0 | 1200 |  | Ector | Ector | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1018, 11010, 11028, 18544, 18545, 18546, 18547 | Y |  |  |  | 81601 | 71182
67329 | San Miguel to Cruce 345 kV lines | New San Miguel to Cruce 345 kV double circuit lines |  | San Miguel | Cruce | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2026-12-01 |  | 345 | 231.12 | 0 | 0 |  | Atascosa | Duval | Tier 1 | 21RPG017 | 2021-09-23 | 2021-12-23 |  | 5901, 80079 | Y |  |  |  | 67330 | 67329
87069 | LST_Phantomhill_Hub Conversion | Loop another circuit of the LST Crez line into Phantom Hill station as part of Gen Interconnection Project 23INR0244, 22INR0457 and 20INR0242 |  |  |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2026-12-01 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 68000, 68001, 68004 | Y |  |  |  | 87070 | 87069
78044 | ROCK DRAW 345 kV Switch | Adding Oncor's portion of TNMP Silverleaf and Cowpen 345/138-kV Stations Project (23RPG013) |  | Sand Lake | North McCamey | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8716 | 2026-12-01 |  | 345 | 0 | 0 | 0 |  | Ward | Upton | Tier 1 | 23RPG013 | 2023-05-18 | 2023-06-09 |  | 11098, 18668, 76000 | Y |  |  |  | 78048 | 78044
93061 | Adds Fullerton Switch 138 kV Capacitor Bank | Adds Fullerton Switch 138 kV Capacitor Bank |  | Fullerton Switch | Fullerton Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8874 | 2026-12-01 |  | 138 | 0 | 0 | 0 | 0,110.4 | Andrews | Andrews | Tier 4 |  |  |  |  | 1272 | Y |  |  |  | 93062 | 93061
93683 | New Transformer will be added at Titan Substation. |  |  | Titan | Titan | Planned |  | BPUB | Luis Martinez lugmartinez@brownsville-pub.com 956-983-6212 |  | 2026-12-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5963 | Y |  |  |  | 93684 | 93683
89988 | McGee 345 kV Switch |  |  | Wolf | Meteor | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8830 | 2026-12-03 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 10009, 10012, 11010 | Y |  |  |  | 91898 | 89988
91578B | buffalo_clover_substation_addition | Removing temporary 69 kV transformer to serve PEC load | [5 empty] | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2026-12-12 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 124, 70000 | Y |  |  |  | 91581 | 91578
75524 | This converts Bell County to Gabriel to 138 KV |  |  | Bell County | Gabriel | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2026-12-12 |  | 138 | 0 | 0 | 0 |  | Bell | Williamson | Tier 4 |  |  |  |  | 114, 118, 122, 132, 133, 7345, 7346 | Y |  |  |  | 75525 | 75524
91578C | buffalo_clover_substation_addition | Installing 138 kV substation and transformer to serve PEC load | [5 empty] | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2026-12-13 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 124, 70000 | Y |  |  |  | 91582 | 91578
91531 |  |  |  | Schwertner | Gabriel | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2026-12-13 |  | 138 | 0.3 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | 122, 124, 7345, 7346 | Y |  |  |  | 91532 | 91531
92852A | Oncor_92852_MNE_Monticello_Paris_Line_Upgrade | Upgrade Monticello - Woodard 345 kV Line |  | Monticello | Woodard | Planned | R986 | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R986 | 2026-12-14 |  | 345 | 0 | 33.3 | 0 |  | Titus | Lamar | Tier 1 |  |  |  |  | 1695, 11699 | Y |  |  |  | 93063 | 92852
91074 | POI for Fort Watt Storage (Emerald Hills Switch) | POI for Fort Watt Storage (Emerald Hills Switch) |  | Everman Switch | Burleson Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3512 | 2026-12-15 | 2024-05-15 | 138 | 0 | 0 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  |  | 1588, 1933, 2208 | Y |  |  |  | 91075 | 91074
92876 | Establish Bear Pen 345 kV Switch |  |  | Bear Pen 345 kV Switch |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3063 | 2026-12-15 |  | 345 | 0 | 0 | 0 |  | Franklin | Franklin | Tier 4 |  |  |  |  | 1695, 11699, 11702 | Y |  |  |  | 92877 | 92876
71156 | Ennis West Switch-Waxahachie Switch 138 kV Line Rebuild | Rebuild the Ennis West-Waxahachie 138 kV Line |  | Ennis West | Waxahachie | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4200 | 2026-12-15 |  | 138 | 0 | 0 | 0 |  | Ellis | Ellis | Tier 4 |  |  |  |  | 2241, 2321, 12320 | Y |  |  |  | 71160 | 71156
91457 | Establish Drane 345 kV Switch |  |  | Drane 345 kV Switch | Drane 345 kV Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6410 | 2026-12-15 |  | 345 | 0 | 0 | 0 |  | Navarro | Navarro | Tier 4 |  |  |  |  | 3295, 3376, 68091 | Y |  |  |  | 91458 | 91457
91461 | Establish Tarantula 345 kV Switch |  |  | Tarantula 345 kV Switch | Tarantula 345 kV Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6411 | 2026-12-15 |  | 345 | 0 | 0 | 0 |  | Navarro | Navarro | Tier 4 |  |  |  |  | 3344, 3380, 3381, 68091 | Y |  |  |  | 91462 | 91461
81232 | Cattleman – Bitter Creek/Champion Creek 345 kV Reroute | Terminate Morgan Creek – Bitter Creek/Champion Creek Double-Circuit 345 kV Line into Cattleman 345 kV Switch |  | Cattleman | Bitter Creek and Champion Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8647 | 2026-12-15 |  | 345 | 0 | 5 | 0 |  | Mitchell | Mitchell | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1030, 1414, 10053, 71050 | Y |  |  |  | 81665 | 81232
80546D | Upgrade the Hutto & Round Rock - Salado 138 kV Line | Rebuild and double-circuit the Sonterra - Salado 138 kV Line Section. Establish Salado 138 kV Switch and the Salado Switch - Round Rock Switch 138 kV Line |  | Sonterra | Salado Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6203, R6202 | 2026-12-15 |  | 138 | 0 | 0 | 0 |  | Williamson | Williamson | Tier 3 |  |  |  |  | 121, 3640, 3664, 3668, 3677, 3730, 3764, 3777, 13640, 13641 | Y |  |  |  | 87642 | 80546 | 2023-SC17
91459 | Establish Mosher 345 kV Switch |  |  | Mosher 345 kV Switch | Mosher 345 kV Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6321 | 2026-12-15 |  | 345 | 0 | 0 | 0 |  | Navarro | Navarro | Tier 4 |  |  |  |  | 2466, 3763, 68091 | Y |  |  |  | 91460 | 91459
92847 | Oncor_ME_Norwood 345 kV Terminal Equipment | Upgrade Norwood Switch 345 kV Terminal Equipment |  | Norwood |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4425 | 2026-12-15 |  | 345 | 0 | 0 | 0 |  | Dallas |  | Tier 4 |  |  |  |  | 1928, 2406 | Y |  |  |  | 92851 | 92847
87017 | Riverton - Sandlake 138 kV Line Conversion 345 kV and Riverton - Sandlake 138 kV Line | Convert Riverton – Sandlake 138 kV Line to 345 kV and Establish Riverton – Sandlake 138 kV Line |  | Riverton | Sandlake | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8793 | 2026-12-15 |  | 345 | 39.9 | 0 | 0 |  | Ward | Reeves | Tier 1 | 24RPG010 | 2024-03-18 |  |  | 1011, 11083, 11084, 11097, 11098 | Y |  |  |  | 87679 | 87017
64239 | Vineyard Switch-Cypress Waters Switch 138 kV Line | Construct a new 138 kV circuit from Vineyard to Cypress Waters |  | Cypress Waters Switch | Vineyard Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5320 | 2026-12-15 |  | 138 | 7.4 | 0 | 0 |  | Dallas | Tarrant | Tier 3 |  |  |  |  | 2017, 2022, 2386, 12012, 12013, 15030, 15031, 15035, 15040, 15041 | Y |  |  |  | 86787 | 64239
73567 | Berry Creek Substation Addition | Substation addition to provide Point of Interconnection for Oncor Andice substation addition. |  | Berry Creek |  | Conceptual |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-12-15 |  | 138 | 0 | 0 | 0 |  | Williamson |  | Tier 4 |  |  |  |  | 7361, 7521, 70522 | Y | N |  |  | 78401 | 73567
66214 | Upgrade and convert Brownwood - Lake Brownwood 69 kV Line to 138 kV | Upgrade and convert Brownwood - Firerock 69 kV Line to 138 kV, decommission the Brownwood 69 kV Switch and Autotransformer |  | Brownwood | Lake Brownwood | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6164 | 2026-12-15 |  | 138 | 0 | 10.8 | 0 |  | Brown | Brown | Tier 4 |  |  |  |  | 1637, 1661, 1662, 1670, 3800, 6408 | Y |  |  |  | 92939 | 66214
76312 | Establish Ramhorn 138kV Switch | Establish Ramhorn 138kV Switch and Ramhorn -Dunham 138 kV Line |  | Ramhorn | Dunham | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5007 | 2026-12-15 |  | 138 | 19 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  |  | 568, 1570, 1840, 1842 | Y |  |  |  | 82052 | 76312
76712 | Bluff Creek to China Grove Line Rebuild | Rebuild existing 138 kV Line |  | Bluff Creek 138 kV Switch | China Grove Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8655 | 2026-12-15 |  | 138 | 0 | 12.8 | 0 |  | Scurry | Mitchell | Tier 3 |  |  |  |  | 1309, 1318 | Y |  |  |  | 87645 | 76712
89912 | Olmos to Wilson, T297 | Rebuild 8.13 miles of 138 kV from 477 conductor wood pole line to 795 drake conductor concrete/steel transmission line |  | Olmos | LaVernia | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2026-12-15 |  | 138 | 0 | 0 | 0 |  | Guadalupe | Wilson | Tier 4 |  |  |  |  | 7613, 7615 | Y |  |  |  | 89913 | 89912
71910A | Rebuild the Hillsboro - Elm Mott 69 kV Line | Rebuild the Elm Mott Switch - West 69 kV Line |  | Elm Mott 69 kV Switch | West 69 kV Substation | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6221 | 2026-12-15 |  | 69 | 0 | 9 | 0 |  | McLennan | McLennan | Tier 3 |  |  |  |  | 3408, 3526, 3527, 3528, 3529, 13525 | Y |  |  |  | 91605 | 71910
22TPIT0000 | Parkway Substation | Replace T2, 20 MVA with a 40 MVA 138-13.09 kV transformer |  | Parkway |  | Planned |  | GVEC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2026-12-15 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  |  | 7611 | Y | N |  |  | 10680 | 3324
68706 | Edgewood Switch – Royse Switch 138 kV Line | Rebuild and convert the Edgewood-Iron Bridge 69 kV to 138 kV operation |  | Edgewood | Able Springs | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3227 | 2026-12-15 |  | 69 | 0 | 0 | 0 |  | Van Zandt | Kaufman | Tier 4 |  |  |  |  | 2471, 2721, 3163, 3165, 3167, 3168, 3169, 3181, 3182, 3185, 3188, 3189, 3191, 3192, 3193, 6920, 6922, 12467, 12469, 12470, 12472, 13188, 13191 | Y |  |  |  | 68707 | 68706
62445 | Base Camp (FKA Eagle Mountain) 138kV Switch Rebuild | Rebuild existing 138 kV Switch |  | Base Camp | Base Camp | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5261 | 2026-12-15 |  | 138 | 0 | 0 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  |  | 568, 1859, 1860, 1864, 1865, 11859, 11860, 11861, 11864, 11865, 11866, 12065 | Y |  |  |  | 70920 | 62445
81034 | Lamesa - Willow Valley 138 kV Line | Rebuild Lamesa to Willow Valley 138 kV line. |  | Lamesa Switch | Willow Valley Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8654 | 2026-12-15 |  | 138 | 0 | 32.1 | 0 |  | Borden | Dawson | Tier 3 |  |  |  |  | 1163, 1301, 1307, 1308 | Y |  |  |  | 81035 | 81034
61449 | Clark Church/Birdhouse (Ottine New) Substation | Build New 138 Substation adjacent to Birdhouse; replaces existing Ottine station, add 20MVA |  | Ottine | Ottine | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2026-12-17 |  | 138 | 0 | 0 | 0 |  | Gonzales |  | Tier 4 |  |  |  |  | 7594 | Y | N |  |  | 61450 | 61449
82714 | Rebuild of Airport of Substation | Atlas Substation will be replacing Airport Substation. |  | Filter Plant (BPUB), South Plant (BPUB), and Southmost (STEC) | Atlas (BPUB) | Planned |  | BPUB | Luis Martinez lugmartinez@brownsville-pub.com 956-983-6212 |  | 2026-12-22 | 2026-03-02 | 138 | 0 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  |  | 5789, 59420, 59440, 59500 | Y | N |  |  | 82715 | 82714
68205 | GENRAL to Garden Villas Rebuild | Rebuild and Reconductor portion of Ckt.12B Bringhurst (GENRAL) to Garden Villas to prepare for future 138kV Conversion |  | GENRAL | Garden Villas | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-30 |  | 69 | 0 | 9.91 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 42690, 47540 | Y | N |  |  | 68206 | 68205
72502 | Tarpley Substation Upgrades | Provide transmission point of interconnection to Battery energy storage system near the Tarpley Substation. Add a 138kV bay and associated circuit breaker to existing substation (25INR0196) |  | Tarpley |  | Planned |  | BEC | Jhonatan Guerrero Rivera j.rivera@banderaelectric. 830-612-0048 |  | 2026-12-30 |  | 69 | 0.1 | 0 | 0 |  | Bandera |  | Tier 4 | [5 empty] | Y | N |  |  | 72503 | 72502
81686 | Blu Lacy: Construct New 345 kV Station | Interconnect the Pi load to the new Blu Lacy 345 kV station on the Lon Hill to Reforzar and Lon Hill to Nelson Sharpe 345 kV lines and add capacitors |  | Blu Lacy |  | Conceptual |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 |  | 2026-12-30 |  | 345 | 0 | 0 | 0 | 0,523.6 | Nueces |  | Tier 3 |  |  |  |  | 8455, 80078, 84550, 85000 | Y | N |  |  | 81687 | 81686
77805 | TNMP Pecos County RPG |  |  | Leon Creek (bus # 38355) | Coyanosa (bus # 38380) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-12-31 |  | 138 | 31.2 | 0.6 | 0 |  | Pecos | Reeves | Tier 1 |  | 2023-08-02 | 2024-02-08 | 2024-03-06 | 6601, 38355, 38380, 38445 | Y |  |  |  | 77806 | 77805
77807 | Silverleaf 345kV station from TNMP submitted Cowpen/Silverleaf RPG |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-12-31 |  | 345 | 4.05 | 0 | 2250 |  | Ward | Ward | Tier 1 |  | 2023-05-11 | 2023-11-27 | 2024-01-09 | 18668, 38091, 38143, 38145, 38147, 38148, 38149, 38150, 38165 | Y |  |  |  | 77808 | 77807
75786 | This project will create a POI Bus (station) named Skydancer to interconnect 23INR0295 | This project will create a POI Bus (station) named Skydancer to interconnect 23INR0295 |  |  |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2026-12-31 |  | 345 | 0 | 0 | 0 |  | Bosque | Bosque | Tier 4 |  |  |  |  | 68055, 68080, 68090 | Y |  |  |  | 75787 | 75786
4320 | CPSE_Brooks to Chavaneaux MLSE | Upgrade terminals at Brooks and Chavaneaux to ensure a 1364 A rating (minimum) |  | Brooks | Chavaneaux |  |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0733 | 2026-12-31 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5045, 5085 | Y | Y |  |  | 11872 | 4320
64499 | Hyde Park to Downtown Ckt.32A Upgrades | Upgrade Hyde Park to Downtown Ckt.32A |  | Downtown | Hyde Park | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 |  | 69 | 0 | 1.2 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47500, 47510, 47570, 47690 | Y | N |  |  | 64500 | 64499
65719 | Rebuild/reconductor portions of Ckt.05A Missouri City to Sienna as a Hardening upgrade(24RPG030). | Rebuild and reconductor portion of Missouri City to Sienna Ckt.05A as a Hardening upgrade |  | Missouri City | Sienna | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 |  | 138 | 0 | 3.8 | 0 |  | Fort Bend | Fort Bend | Tier 4 | 24RPG030 | 2024-09-18 | 2024-10-10 | 2024-10-10 | 48237, 48336 | Y | N |  |  | 90165 | 65719
67422F | Greens Bayou to Clinton 138kV Conversion | Remove Wallisville substation from Ckt.10A service… Resulting in Ckt.10A Clinton to Greens Bayou |  | Clinton | Greens Bayou | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40250, 40352, 40720, 41680, 41682 | Y | N |  |  | 87579 | 67422
66366 | Rebuild Brazoria - Retrieve 138kV with bundled 795 ACSS | Planned ISD is Q4 2024, but project design currently under internal review. |  | TNMP Brazoria (bus # 39600) | CenterPoint Retrieve (bus # 43170) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-12-31 |  | 138 | 0 | 6.17 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 39600, 43170 | Y |  |  |  | 66367 | 66366
87637 | Install (2) new 100 MVA distribution transformers at Liberty substation to serve customer load. | Install (2) new 100 MVA distribution transformers at Liberty substation to serve customer load. |  | Liberty | Kenny/ Baytown | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40961, 40962 | Y | N |  |  | 90200 | 87637
87901 | Kallisto: Construct New 138 kV Station | Interconnect the Beta load to the new Kallisto 138 kV station on the Falfurrias to King Ranch Gas Plant 138 kV line | Project Title, Project Description, Terminal Location, Status, In-Service Date, Cost, and County Update | Kallisto |  | Conceptual |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2026-12-31 |  | 138 | 0 | 0 | 0 |  | Kleberg |  | Tier 4 |  |  |  |  | 80228 | Y |  |  |  | 87902 | 87901
91545 | Birdhouse Substation Upgrade | Upgrade Birdhouse substation to provide a new POI for GVEC PWT. |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | PLC-6656 | 2026-12-31 |  | 138 | 0 | 0 | 0 |  | Gonzales | Gonzales | Tier 4 |  |  |  |  | 7255 | Y |  |  |  | 91546 | 91545
90002 | Salvare: Install New 345 kV Capacitor Bank | Install a new capacitor bank at the Salvare 345 kV station | In-Service Date Update | Salvare |  | Planned |  | ETT | Tong Wang twang1@aep.com 918-599-2635 | TP2024109 | 2026-12-31 |  | 345 | 0 | 0 | 0 | 0,46.1 | Childress |  | Tier 4 |  |  |  |  | 60511 | Y | N |  |  | 91298 | 90002
90191 | Bromine 138/35kV Distribution Substation | Install Bromine 138/35kV Distribution Substation. Loop on Ckt.66A to create new Ckt.66A Katy tap to Bromine to Freeman. |  | Bromine | Katy/Freeman | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  |  | 45040, 45770, 48203 | Y | N |  |  | 90759 | 90191
81659 | Lytle: Construct New 138 kV Terminal | Interconnect the Cinco II load to the existing Lytle 138 kV station and add capacitors |  | Lytle |  | Conceptual |  | AEP TCC/ETT | John Solis jlsolis@aep.com 361-881-5574 |  | 2026-12-31 |  | 138 | 0 | 0 | 0 | 0,34.5 | Medina |  | Tier 4 |  |  |  |  | 8962 | Y |  |  |  | 81660 | 81659
81697 | Amber: Construct New 345 kV Station | Interconnect the Kappa load to the new Amber 345 kV station on the Blue Lacy to Reforzar and Blue Lacy to Nelson Sharpe 345 kV lines and add capacitors | Tier Update | Amber |  | Conceptual |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 |  | 2026-12-31 |  | 345 | 0 | 0 | 0 | 0,523.6 | Nueces |  | Tier 3 |  |  |  |  | 80078, 84550, 84555, 85000 | Y |  |  |  | 81698 | 81697
80319 | Devine: Install Cap Bank | Convert the Big Foot to Dilley 69 kV line to 138 kV, rebuild the Dilley to Dilley Switch 69 kV line, and reroute the Big Foot to Dilley line from Dilley to Dilley Switch |  | Devine |  | Planned |  | ETT | Will Simmons jlsolis@aep.com 361-881-5574 |  | 2026-12-31 |  | 138 | 0 | 0 | 0 | 0,23 | Medina |  | Tier 4 | 23RPG024 | 2024-08-23 | 2024-09-23 |  | 8732 | Y |  |  |  | 80322 | 80319
87429 | Reconductor Wickett to Staghorn 138kV line. |  |  | TNMP Wickett (37981) | TNMP Staghorn (37990) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-12-31 |  | 138 | 0 | 12.05 | 0 |  | Ward | Ward | Tier 4 |  |  |  |  | 37981, 37990 | Y |  |  |  | 87430 | 87429
87431 | Rebuild Wickett to Winkler 69kV line. |  |  | TNMP Winkler (37960) | TNMP Wickett (37980) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-12-31 |  | 138 | 0 | 6.8 | 0 |  | Winkler | Ward | Tier 4 |  |  |  |  | 37960, 37980 | Y |  |  |  | 87432 | 87431
86771 | Scissortail: Construct New 138 kV Station | Interconnect the TNMP Flycatcher station to the new Scissortail 138 kV station on the Saragosa to Solstice 138 kV line between Hoef's Road and Verhalen |  | Scissortail |  | Planned | TP2024044 | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 |  | 2026-12-31 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  |  | 6077, 60207, 60808 | Y | N |  |  | 86772 | 86771
87423 | Reconfigure TNMP Pyote 138kV Substation. |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-12-31 |  | 138 | 0.92 | 0 | 0 |  | Ward | Ward | Tier 4 |  |  |  |  | 37990, 38001, 38005 | Y |  |  |  | 87424 | 87423
85950 | Alford Substation Addition | This project will construct the new 138-kV Alford Substation. Alford will be near the existing Oncor Midkiff Substation and the planned Oncor Catclaw Switch. Alford will connect T594 Midkiff to Skywest and T611 Benedum to Midkiff and will provide two (2) 138-kV POIs for Oncor Catclaw Switch. | [5 empty] | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-12-31 |  | 138 | 0 | 0 | 0 |  | Upton | Upton | Tier 4 | 23RPG019 | 2023-08-03 | 2023-08-25 |  | 1210, 10058, 71210, 71211, 71213 | Y |  |  |  | 85951 | 85950 | 2023-FW8
76576 | Asherton to Uvalde: Convert to 138 kV | Convert Asherton to Uvalde 69 kV to 138 kV, rebuild Asherton 138 kV station, build new Poblano 138 kV station | Contact and In-Service Date Update | Asherton | Uvalde | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2026-12-31 |  | 138 | 0 | 59.74 | 0 |  | Dimmit | Uvalde | Tier 3 | 23RPG007 | 2023-04-12 | 2023-05-19 |  | 7867, 8005, 8006, 8007, 8008, 8231, 8242, 8243, 8244, 8280, 8283, 8284, 8672 | Y | N |  |  | 78243 | 76576
72868 | Benedum Circuit Breaker Addition | This project provides a point of interconnection for a new 307.46 MW Battery Energy Storage at the 138-kV Benedum Substation by adding a connection to the ring bus to accommodate the new interconnection. Update contingencies |  | Benedum |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2026-12-31 | 2958101 | 138 | 0.1 | 0 | 0 |  | Upton |  | Tier 4 | [5 empty] | Y | N |  |  | 78297 | 72868
77803 | Cowpen 345kV station from TNMP submitted Cowpen/Silverleaf RPG |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2026-12-31 |  | 345 | 14.26 | 0 | 1500 |  | Reeves | Reeves | Tier 1 |  | 2023-05-11 | 2023-11-27 | 2024-01-09 | 18669, 38023, 38027, 38042, 38043, 38044, 38045, 38048, 38055 | Y |  |  |  | 77804 | 77803
73067 | Marina: Construct New Station | Construct new network station on the Highway 9 to Morris St and Nueces Bay 138 kV lines | In-Service Date Update | Marina |  | Planned |  | AEP TCC | Marc Wilson deevans@aep.com 918-599-2938 |  | 2026-12-31 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 8064, 8441, 8470, 8474, 8620, 8623, 8733 | Y |  |  |  | 73068 | 73067
81783 | Ingleside to Seabird: Construct New 138 kV Line | Interconnect the Mu load to the new Seabird 138 kV station on the Homeport to Ingleside 138 kV line, construct a new 138 kV line from Ingleside to Seabird, and add capacitors |  | Ingleside | Seabird | Conceptual |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 |  | 2026-12-31 |  | 138 | 2.9 | 0 | 0 | 0,69.1 | San Patricio | Nueces | Tier 4 |  |  |  |  | 8425, 8808, 84250 | Y | N |  |  | 81784 | 81783
80315 | Big Foot to Pearsall: Convert to 138 kV | Convert the Big Foot to Dilley 69 kV line to 138 kV, rebuild the Dilley to Dilley Switch 69 kV line, and reroute the Big Foot to Dilley line from Dilley to Dilley Switch |  | Big Foot | Pearsall | Planned | 1104 - 1282 | AEP TCC | Will Simmons mlforcum@aep.com 918-599-2674 | 3821 | 2026-12-31 |  | 138 | 0 | 14.79 | 0 |  | Frio | Frio | Tier 4 | 23RPG024 | 2023-08-29 | 2023-09-28 |  | 8216, 8218, 8221, 8752 | Y |  |  |  | 80316 | 80315
80317 | Dilley Switch to Pearsall: Convert to 138 kV, Reroute from Dilley to Dilley Switch, Rebuild Dilley to Dilley Switch 69 kV, and Double Circuit Dilley Switch to Pearsall with Dilley to Dilley Switch | Convert the Big Foot to Dilley 69 kV line to 138 kV, rebuild the Dilley to Dilley Switch 69 kV line, and reroute the Big Foot to Dilley line from Dilley to Dilley Switch |  | Dilley Switch | Pearsall | Planned | 1104 - 1282 | AEP TCC | Will Simmons jlsolis@aep.com 361-881-5574 | 3822 | 2026-12-31 |  | 138 | 0 | 19.8 | 0 |  | Frio | Frio | Tier 4 | 23RPG024 | 2023-08-29 | 2023-09-28 |  | 8208, 8210, 8212, 8216, 8752 | Y |  |  |  | 80318 | 80317
69888A | Deepwater to Clinton Ckts.33B-33C Line Upgrades | Fully reconductor Ckt.33B Deepwater to Texpet Switchrack to Harrisburg ahead of future 138kV conversions. |  | Deepwater | Harrisburg | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 |  | 69 | 0 | 3.8 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40470, 40800, 41560, 41561 | Y | N |  |  | 91910 | 69888
70628 | Japhet 138kV Distribution Sub and Upgrades | Upgrade portions of 69kV Ckt.12 Garden Villas to Bringhurst to Clinton. Install new 138kV Japhet distribution substation. Move 69kV Bringhurst substation load to new Japhet substation and retire Bringhurst substation. Retire portions of Ckt.12 and convert the remaining portions of Ckt.12 to 138kV service. Loop new Japhet substation to create new 138kV Ckt.13 University to Japhet to Clinton. |  | Japhet | University/Clinton | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 |  | 138 | 0 | 4.4 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40350, 40352, 42690, 45070, 47540, 47700, 47760, 48764 | Y | N |  |  | 91551 | 70628
72044A | Clute 138kV Switching Station | Reconfigure existing Ckt.82F RIWOOD to CAVERN to BIPORT and loop into new CEHE-owned 138kV Clute switching station to create new Ckt.82 RIWOOD to Clute to CAVERN to BIPORT. |  | Clute | RIWOOD/CAVERN | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 22RPG038 | 2022-11-04 | 2022-12-01 | 2022-12-01 | 42050, 43150, 43330 | Y | N |  |  | 87454 | 72044
72044B | Clute 138kV Switching Station | [6 empty] | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 00:01 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 22RPG038 | 2022-11-04 | 2022-12-01 | 2022-12-01 |  | Y | N |  |  | 87455 | 72044
67422G | Greens Bayou to Clinton 138kV Conversion | Convert Wallisville substation from Ckt.10A service to 138kV loop service on 138kV TEXWAL to Clinton Ckt.13 to create new Ckt.13 Greens Bayou to TEXWAL to Wallisville to Clinton. |  | Greens Bayou | Clinton | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 00:01 |  | 138 | 2.17 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40250, 40350, 41575, 41660, 41680 | Y | N |  |  | 87580 | 67422
78461B | West Columbia to Damon and Needville to Big Creek Ckt.89A Upgrades | Rebuild/reconductor Needville to Big Creek Ckt.89 as a Hardening upgrade. |  | Needville | Big Creek | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 00:01 |  | 138 | 0 | 5.46 | 0 |  | Brazoria | Brazoria | Tier 4 | 23RPG021 | 2023-08-10 | 2023-08-31 | 2023-08-31 | 42380, 42390 | Y | N |  |  | 78463 | 78461
72044C | Clute 138kV Switching Station | Reconfigure existing Ckt.26D STRATT to SINTEK and loop into new CEHE-owned 138kV Clute switching station to create new Ckt.26 STRATT to Clute to SINTEK. |  | Clute | SINTEK | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 00:02 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 22RPG038 | 2022-11-04 | 2022-12-01 | 2022-12-01 | 42030, 42050, 42110, 42111, 43240, 43300 | Y | N |  |  | 87456 | 72044
72044D | Clute 138kV Switching Station | [6 empty] | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-12-31 00:03 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 22RPG038 | 2022-11-04 | 2022-12-01 | 2022-12-01 |  | Y | N |  |  | 87457 | 72044
76569 | Asherton: Rebuild 138 kV station | Convert Asherton to Uvalde 69 kV to 138 kV, rebuild Asherton 138 kV station, build new Poblano 138 kV station | In-Service Date Update | Asherton |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2026-12-31 02:00 |  | 138 | 0 | 0 | 0 |  | Dimmit |  | Tier 3 | 23RPG007 | 2023-04-12 | 2023-05-19 |  | 8005, 8242, 8244, 8280, 8283 | Y |  |  |  | 76570 | 76569
76580 | Poblano: Build new 138 kV station | Convert Asherton to Uvalde 69 kV to 138 kV, rebuild Asherton 138 kV station, build new Poblano 138 kV station | In-Service Date Update | Poblano |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2026-12-31 02:00 |  | 138 | 0 | 0 | 0 |  | Uvalde |  | Tier 3 | 23RPG007 | 2023-04-12 | 2023-05-19 |  | 8008, 8009, 8234, 8236 | Y |  |  |  | 76581 | 76580
81590 | Rio Medina substation | Adds Rio Medina Load serving station |  | Rio Medina |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2027-01-01 |  | 138 | 4.5 | 0 | 0 |  | Medina |  | Tier 2 |  |  | 2024-02-01 |  | 5804, 5805 | Y | N |  |  | 81591 | 81590
81895 | BPUB Branch Changes | Removing branch Price to Loma, adding Price to Stillman, adding another branch Loma Alta to Stillman. |  | 59410, 5962 | 79601, 79601 | Planned |  | BPUB | Luis Martinez lugmartinez@brownsville-pub.com 956-983-6212 |  | 2027-01-01 |  | 138 | 0 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  |  | 5962, 59410, 79601 | Y |  |  |  | 81896 | 81895
81410 | Reiter Switch Syncrhonous Condenser | Add Reiter Switch Syncrhonous Condenser |  | Reiter | Reiter | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | D20231 | 2027-01-01 |  | 345 | 0 | 0 | 0 | 0,350 | Ector | Ector | Tier 1 |  |  |  |  | 18544, 18553, 18554 | Y |  |  |  | 81411 | 81410
81594 | Dunlay substation | Adds STEC Dunlay Load serving station |  | Dunlay |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2027-01-01 |  | 138 |  | 0 | 0 |  | Medina |  | Tier 2 |  |  |  |  | 5802, 5807, 5813 | Y | N |  |  | 81595 | 81594
81415 | Tonkawa Switch Syncrhonous Condenser | Add Tonkawa Switch Syncrhonous Condenser |  | Tonkawa | Tonkawa | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | D20232 | 2027-01-15 |  | 345 | 0 | 0 | 0 | 0,350 | Scurry | Scurry | Tier 1 |  |  |  |  | 1048, 18556, 18557 | Y |  |  |  | 81416 | 81415
86800 | Pendulo: Construct New 345 kV Terminal | Interconnect Rubicon Alpha Wind to the Pendulo 345 kV station | Contact Update | Pendulo |  | Planned | TP2024057 | ETT | Lance Price twang1@aep.com 918-599-2635 |  | 2027-01-31 |  | 345 | 0 | 0 | 0 |  | Haskell |  | Tier 4 |  |  |  |  | 60507 | Y | N |  |  | 86801 | 86800
86829 | Fort Stockton Plant to Lynx: Rebuild 138 kV Line | Rehab the Fort Stockton Plant to Lynx 138 kV line | In-Service Date Update | Fort Stockton Plant | Lynx | Planned | TA2020218 | AEP TNC | Charity L Kreher twang1@aep.com 918-599-2635 |  | 2027-01-31 |  | 138 | 0 | 37 | 0 |  | Pecos | Pecos | Tier 4 | 23RPG008 | 2023-04-14 | 2023-05-05 |  | 6630, 6671, 60400 | Y | N |  |  | 86830 | 86829
80502 | Lon Hill: Construct New 345 kV Terminal | Interconnect the Tom Cruise load to the Lon Hill 345 kV station | In-Service Date Update | Lon Hill |  | Planned | TP2023885 | AEP TCC | LaRissa Lundry deevans@aep.com 918-599-2938 |  | 2027-01-31 |  | 345 | 0.1 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 8455, 80037 | Y |  |  |  | 80503 | 80502
78468A | Pradera (PRD) CEHE-Owned 345kV Substation for Austin Bayou Solar (25INR0102) | New 345kV Pradera (PRD) substation for generator interconnection to Austin Bayou Solar (25INR0102). Loop Ckt.27 into Pradera substation to create new Ckt.27 Seabreeze to Pradera to Savannah. |  | Pradera | Savannah/ Seabreeze | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-01-31 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42590, 43020, 43180 | Y | N |  |  | 90128 | 78468
80907 | Fort Stockton Plant: Rebuild 138/69 kV Station | Rebuild the Fort Stockton Plant 138/69 kV station | In-Service Date Update | Fort Stockton Plant |  | Planned | TP2023319 | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 |  | 2027-01-31 |  | 138 | 0 | 0 | 90 |  | Pecos |  | Tier 4 |  |  |  |  | 6630, 38355 | Y | N |  |  | 80908 | 80907
70675 | Aransas Pass to Rincon: Rebuild 69 kV Line | Rebuild the Aransas Pass to Gregory to Rincon 69 kV line | Contact and In-Service Date Update | Aransas Pass | Rincon | Planned |  | AEP TCC | LaRissa Lundry deevans@aep.com 918-599-2938 | TP2022132 | 2027-01-31 |  | 69 | 0 | 8.5 | 0 |  | San Patricio | San Patricio | Tier 2 | 24RPG035 | 2024-11-11 |  |  | 8416, 8421, 8427 | Y |  |  |  | 70676 | 70675
65154 | Mason Switch to Yellowjacket: Rebuild 69 kV Line | Rehab the Mason Switch to Yellowjacket 69 kV Line |  | Mason Switch | Yellowjacket | Planned | 1142 - 1320 | AEP TNC | Forrest Farson twang1@aep.com 918-599-2635 | 2836 | 2027-01-31 |  | 69 | 0 | 26.45 | 0 |  | Menard | Mason | Tier 4 | 21RPG014 | 2021-08-01 | 2021-09-01 |  | 6363, 6396, 23824 | Y | N |  |  | 65155 | 65154
65837 | New Cachena Substation |  |  | 5133 | 5323 | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-01-31 |  | 345 | 0 | 0 | 0 |  | Wilson |  | Tier 4 |  |  |  |  | 5068, 5133, 5323 | Y |  |  |  | 65838 | 65837
78468B | Pradera (PRD) CEHE-Owned 345kV Substation for Austin Bayou Solar (25INR0102) | Install generator lead from Pradera (PRD) substation to AUSTIN (ABY) customer substation (25INR0102). |  | Pradera | AUSTIN | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-01-31 00:01 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 | [5 empty] | Y | N |  |  | 90129 | 78468
86022 | Jordan 138kV Substation Expansion for Coneflower Storage (23INR0425) | Expand 138kV Jordan substation for Coneflower Storage generator interconnection (23INR0425) |  | Jordan |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-02-03 00:01 |  | 138 | 0 | 0 | 0 |  | Chambers |  | Tier 4 |  |  |  |  | 40855, 113981 | Y | N |  |  | 86023 | 86022
20TPIT0000 | Parkway Substation T1 Replacement | Replace T1, 20 MVA with a 40 MVA 138-13.09 kV transformer |  | Parkway |  | Planned |  | GVEC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2027-02-04 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  |  | 7611 | Y | N |  |  | 10679 | 3323
92651 | Oncor_MNE_92651_Barnett138 kV Switch |  |  |  |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2027-02-28 |  | 138 | 0 | 0 | 0 |  | Delta | Delta | Tier 4 |  |  |  |  | 1802, 1820, 2932 | Y |  |  |  | 92652 | 92651
6072 | Eldorado to Ft. McKavitt: Rebuild 69 kV Line | Rehab Eldorado to Ft. McKavitt 69 kV line | In-Service Date Update | Eldorado Tap | Ft. McKavitt | Planned | 786 - 0971 | AEP TNC | Dewey Peters twang1@aep.com 918-599-2635 | 2677 | 2027-02-28 |  | 69 | 0 | 19.41 | 0 |  | Schleicher | Schleicher | Tier 4 |  |  |  |  | 6505, 6506, 6507, 6508 | Y | N |  |  | 13794 | 6072
51005 | Rocksprings to Friess Ranch: Rebuild 69 kV line | Rehab Rocksprings to Sonora 69 kV line | In-Service Date Update | Rocksprings | Friess Ranch | Planned | 1044 - 1217 | AEP TCC/AEP TNC, ETT | Greg Crane deevans@aep.com 918-599-2938 | 2792 | 2027-02-28 |  | 69 | 0 | 22.6 | 0 |  | Edwards | Sutton | Tier 3 | 19RPG018 | 2019-10-24 | 2019-11-18 |  | 8238, 60210 | Y | N |  |  | 51006 | 51005
90045 | Vanhagar to Collier: Construct New 138 kV Line | Interconnect the new Collier load station to the new Vanhagar 138 kV station on the Saragosa to Solstice 138 kV line between Hoef's Road and Verhalen |  | Vanhagar | Collier | Planned |  | AEP TNC | William Simmons twang1@aep.com 918-599-2635 | TP2024119 | 2027-02-28 |  | 138 | 1.5 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  |  | 6077, 60127, 60128, 60808 | Y | N |  |  | 90914 | 90045
79456A | Install new 345kV Huizache (HUI) substation for generator interconnection to High Chap Solar (25INR0068) & BESS (25INR0072) | Install new 345kV Huizache (HUI) substation for generator interconnection to High Chap Solar (25INR0068) & BESS (25INR0072). Loop Ckt.18 into Huizache substation to create new Ckt.18 Speedway to Huizache to DOW. |  | Huizache | Speedway/DOW | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-02-28 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42500, 43060, 46640 | Y | N |  |  | 87175 | 79456
55550 | Brushline: Construct New Distribution Station | Construct new 138/13 kV station Brushline | Contact Update | Brushline |  | Planned | 1106 - 1284 | AEP TCC | Nathan Cowan twang1@aep.com 918-599-2635 | 3826 | 2027-02-28 |  | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  |  | 5754, 8963, 8972 | Y |  |  |  | 55551 | 55550
79456B | Install new 345kV Huizache (HUI) substation for generator interconnection to High Chap Solar (25INR0068) & BESS (25INR0072) | Install generator lead from Huizache (HUI) substation to customer substation HIGHCH (HIC) for generator interconnection to High Chap Solar (25INR0068) & BESS (25INR0072). |  | Huizache | HIGHCH (High Chap) | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-02-28 00:01 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 | [5 empty] | Y | N |  |  | 87176 | 79456
89961 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2027-03-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 1820, 6869 | Y |  |  |  | 89962 | 89961
90476 |  |  |  | Sivells Bend Tap | Sivells Bend | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-03-01 |  | 69 | 1.5 | 0 | 0 |  | Cooke | Cooke | Tier 4 |  |  |  |  | 716, 725, 727 | Y |  |  |  | 90477 | 90476
86912 |  |  |  | Gabriel | Schwertner | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-03-02 |  | 138 | 0 | 12.6 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | 122, 7346 | Y |  |  |  | 86913 | 86912
80336 |  |  |  | WESTLOOP | BROCK | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-03-15 |  | 138 | 0 | 2.23 | 0 |  | Parker | Parker | Tier 4 |  |  |  |  | 480, 487 | Y |  |  |  | 80337 | 80336 | 2023-NC26
80342 |  |  |  | HILLTOP LAKES | HILLTOP LAKES | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-03-15 |  | 138 | 0 | 0 | 60 |  | Leon | Leon | Tier 4 |  |  |  |  | 47, 48 | Y |  |  |  | 80343 | 80342
72568 | Friendship to Rutherford Storm Hardening | Rebuild single circuit section of Friendship to Rutherford and reconductor with bundled 795 ACSR Conductor, 440 MVA. Replaces Project ID 61270. |  | Friendship | Rutherford | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2027-03-15 |  | 138 | 0 | 4.5 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 70507, 70509 | Y | N |  |  | 72569 | 72568
78173 |  |  |  | Trimmier | Trimmier | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-03-15 |  | 138 | 0 | 0 | 0 | 0,12 | Bell | Bell | Tier 4 |  |  |  |  | 136 | Y |  |  |  | 78174 | 78173
80340 |  |  |  | Keith Switch | Iola | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-03-15 |  | 138 | 0 | 6.1 | 0 |  | Grimes | Grimes | Tier 4 |  |  |  |  | 2, 4 | Y |  |  |  | 80341 | 80340
78179 |  |  |  | Ding Dong | Ding Dong | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-03-15 |  | 138 | 0 | 0 | 0 | 0,12 | Bell | Bell | Tier 4 |  |  |  |  | 115 | Y |  |  |  | 78180 | 78179
77172 | Caravel: Construct New 138 kV Station | Interconnect the 1PointFive USA load to the new Caravel 138 kV station on the Barney Davis to Nelson Sharpe 138 kV line between Alazan and Barney Davis | Title, Description, Location, Owner, Contact, Project Number, and Dollars Update | Caravel |  | Planned |  | AEP TCC/ETT | LaRissa Lundry jlsolis@aep.com 361-881-5574 | TP2024088 | 2027-03-31 |  | 138 | 0 | 0 | 0 |  | Kleberg |  | Tier 4 |  |  |  |  | 8515 | Y |  |  |  | 77173 | 77172
90053 | Dokmai: Construct New 138 kV Station | Interconnect Hyfuels Western Farmland Wind to the new Dokmai 138 kV station on the Cangrejo to Dacosta 138 kV line between Beecher and Cangrejo | NEW | Dokmai |  | Planned |  | AEP TCC | Lance Price deevans@aep.com 918-599-2938 | TP2024120 | 2027-03-31 |  | 138 | 0 | 0 | 0 |  | Calhoun |  | Tier 4 |  |  |  |  | 8721, 8723, 80090 | Y | N |  |  | 90054 | 90053
81368 | Rio Pecos: Upgrade 138 kV Terminals | Upgrade the Soaptree and Whitebaker 138 kV terminals at the Rio Pecos 138 kV station | Contact and In-Service Date Update | Rio Pecos |  | Planned | TP2023625 | AEP TNC | Brooks Dow twang1@aep.com 918-599-2635 |  | 2027-03-31 |  | 138 | 0 | 0 | 0 |  | Crockett |  | Tier 4 |  |  |  |  | 6601, 38445 | Y | N |  |  | 81369 | 81368
92890 | Add Fresa load serving substation |  |  |  |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2027-04-01 |  | 69 | 0 | 0 | 0 |  | Atascosa | Atascosa | Tier 4 |  |  | 2024-02-01 |  | 5710, 5714, 5733, 595710 | Y | N |  |  | 92891 | 92890
91062 | Add Boles Station which taps the Quinlan North to Magness line |  |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2027-04-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 6817, 6823, 6883 | Y |  |  |  | 91063 | 91062
73663 | New transformer (T1) at BPUB Waterport Substation | BPUB new load T1 at bus 59450 |  | Waterport Substation (59450) |  | Planned |  | BPUB/BROWNSVILLE PUB | Luis Martinez lugmartinez@brownsville-pub.com 956-983-6212 |  | 2027-04-02 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 59450 | Y | N |  |  | 80507 | 73663
91259 | Phelps (PHE) CEHE Station for SKIPJA (SKP) / Skipjack Energy Storage (26INR0189) | Install new Phelps (PHE) 138kV Substation for generator interconnection to SKIPJA (SKP) - Skipjack Energy Storage. Loop into existing Ckt.02B WA Parish to Nash to create new Ckt.02 WA Parish to Phelps to Nash. Install one generator lead from Phelps (PHE) 138kV Substation to SKIPJA (SKP) / Skipjack Energy Storage (26INR0189) |  | WAP | Nash/PHELPS | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-04-04 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42460, 42980, 44010 | Y |  |  |  | 91260 | 91259
91549 | Gabriel - Split Transmission Line Upgrade | LCRA TSC will upgrade T223 Gabriel to Georgetown East & T224 Gabriel to Jarrell 138-kV double-circuit transmission line from Gabriel to Split to obtain a higher operational rating. This 1.1-mile transmission line is owned by LCRA TSC. The remaining portions of T223 and T224 from Split to Georgetown East and from Split to Jarrell, respectively, are owned by Oncor. Line ratings and impedances being updated on ONCOR's PMCR 80546, phase #87647. | [5 empty] | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-7996 | 2027-04-07 |  | 138 | 0 | 0 | 0 |  | Williamson | Williamson | Tier 4 | [5 empty] | Y |  |  |  | 91550 | 91549
80295 | Add 2nd transformer at Ponder | Add 2nd transformer at Ponder |  | Ponder | Ponder | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-04-15 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  |  | 642 | Y |  |  |  | 80296 | 80295
91108 | Fisk 345 kV Switch | Construct a new 345 kV Switch. |  | Brown Switch | Central Bluff | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6328 | 2027-04-17 |  | 345 | 0 | 0 | 0 |  | Coleman | Coleman | Tier 4 |  |  |  |  | 1444, 11263, 11406 | Y |  |  |  | 91109 | 91108
73032 | Mulberry Creek: Rebuild 138 kV Station | Rebuild Mulberry Creek 138 kV station |  | Mulberry Creek |  | Planned |  | AEP TNC | Forrest Farson twang1@aep.com 918-599-2635 |  | 2027-04-30 |  | 138 | 0 | 0 | 0 |  | Jones |  | Tier 4 |  |  |  |  | 6231, 6232, 6235, 6288 | Y | N |  |  | 73033 | 73032
81576 | Tesla: Construct New 345 kV Terminal | Interconnect the Lancium load to the existing Tesla 345 kV station | Contact Update | Tesla |  | Planned | TP2024048 | AEP TNC/ETT | Lance Price twang1@aep.com 918-599-2635 |  | 2027-04-30 |  | 345 | 0.5 | 0 | 0 |  | Childress |  | Tier 4 |  |  |  |  | 60501 | Y |  |  |  | 81577 | 81576
87019 | Rincon: Upgrade 138 kV Bus | Upgrade the Rincon 138 kV bus | Contact Update | Rincon |  | Planned |  | AEP TCC | Wade Weller deevans@aep.com 918-599-2938 | TP2024029 | 2027-04-30 |  | 138 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  |  | 8418, 8437, 8961 | Y |  |  |  | 87020 | 87019
58010 | North McAllen: Rebuild 138 kV Station | Rehab the North McAllen 138 kV station |  | McAllen |  | Planned | 1118 - 1296 | AEP TCC | Thomas Neils jlsolis@aep.com 361-881-5574 | 3837 | 2027-04-30 |  | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  |  | 8368, 8631, 8632 | Y |  |  |  | 65583 | 58010
93428 | Creosote to Toyah Creek: Construct New 345 kV Double Circuit Line | Construct a new 345 kV double circuit line from Creosote to Toyah Creek |  | Creosote | Toyah Creek | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | TP2024162 | 2027-04-30 |  | 345 | 23 | 0 | 0 |  | Reeves | Reeves | Tier 1 |  |  |  |  | 38376, 38380, 60140, 60141, 60142, 60143, 60144, 60145, 60377, 601402 | Y |  |  |  | 93429 | 93428
93453 | Creosote: Expand 345 kV Station | Install three 345/138 kV autotransformers at the Creosote 345/138 kV station | [5 empty] | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 |  | 2027-04-30 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 1 | [5 empty] | Y |  |  |  | 93454 | 93453
87027 | Black Bayou: Construct New 138 kV Terminal | Interconnect Two Brothers BESS to the Black Bayou 138 kV station |  | Black Bayou |  | Planned |  | AEP TCC | Doug Evans deevans@aep.com 918-599-2938 | TP2024060 | 2027-04-30 |  | 138 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  |  | 8911 | Y |  |  |  | 87028 | 87027
90049 | Yellowjacket: Construct New 138 kV Terminal | Interconnect Black and Gold Energy Storage to the Yellowjacket 138 kV station | Owner and Contact Update | Yellowjacket |  | Planned |  | ETT | Brooks Dow twang1@aep.com 918-599-2635 | TP2024115 | 2027-04-30 |  | 138 | 0.2 | 0 | 0 |  | Menard |  | Tier 4 | [5 empty] | Y |  |  |  | 90050 | 90049
90006 | Oklaunion: Construct New 345 kV Terminal | Interconnect the OPS load to the existing Oklaunion 345 kV station | Contact Update | Oklaunion |  | Planned |  | AEP TNC | Lance Price twang1@aep.com 918-599-2635 | TP2024106 | 2027-04-30 |  | 345 | 0 | 0 | 0 |  | Wilbarger |  | Tier 4 |  |  |  |  | 6100 | Y |  |  |  | 90007 | 90006
86933 | Paladio: Construct New 345 kV Station | Interconnect Argenta Solar and Storage to the new Paladio 345 kV station on the Goddard to Tango 345 kV line | In-Service Date Update | Paladio |  | Planned |  | AEP TCC | Brandon Clarke deevans@aep.com 918-599-2938 | TP2024012 | 2027-04-30 |  | 345 | 0 | 0 | 0 |  | Bee |  | Tier 4 |  |  |  |  | 8012, 8606, 8689 | Y |  |  |  | 86934 | 86933
93226 | Fort Stockton Switch: Expand 345 kV Station | Install three 345/138 kV autotransformers at the Fort Stockton Switch 345/138 kV station | NEW | Fort Stockton Switch |  | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | TP2025141 | 2027-04-30 |  | 345 | 0 | 0 | 2250 |  | Pecos |  | Tier 1 |  |  |  |  | 60146, 60147, 60148, 60149, 60152, 60153, 60404, 60717, 76002, 78926 | Y |  |  |  | 93227 | 93226
75255D | CPSE_Howard to San Miguel Double Circuit Line Addition |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-05-01 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  |  | 5056, 5231 | Y |  |  |  | 75850 | 75255
84892 | New transmission line between Tally and Ranchtown |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-05-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5358, 5422 | Y |  |  |  | 84893 | 84892
88041 | Rebuild Leon Creek to Pearsal |  |  |  |  | Planned | T-0396 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-05-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 2 |  |  |  |  | 5260, 5335 | Y |  |  |  | 88042 | 88041
84894 | Upgrade transmission line between Tally and Texas Research |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-05-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5422, 5430 | Y |  |  |  | 84895 | 84894
76123 | D'Hanis Capacitor 2nd step addition | D'Hanis Capacitor 2nd step addition 9.6 MVAR |  | D'Hanis |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2027-05-01 |  | 69 | 0 | 0 | 0 | 0,9.6 |  |  | Tier 4 |  |  |  |  | 5814 | Y | N |  |  | 76124 | 76123
75255E | CPSE_Howard to San Miguel Double Circuit Line Addition |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-05-01 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  |  | 5056, 5231 | Y |  |  |  | 75851 | 75255
76121 | Beeville Capacitor Addition | Add second 4.8 MVAR step at Beeville |  | Beeville |  | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2027-05-01 |  | 69 | 0 | 0 | 0 | 0,4.8 |  |  | Tier 4 |  |  |  |  | 5674 | Y | N |  |  | 76122 | 76121
73436 | Rockhound - Connell 345 kV Double-Circuit Line | Construct a new 345 kV Double-Circuit Line and establish a 345/138 kV Switch |  | Rockhound | Connell | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8718, R8807 | 2027-05-01 |  | 345 | 10 | 0 | 1200 |  | Martin | Midland | Tier 1 |  |  |  |  | 10036, 10062, 10085, 10086, 10087, 10088, 10089, 10175, 10176, 11371, 23840, 23841, 23855 | Y |  |  |  | 93058 | 73436
76777 | Rebuild Nursery-El Toro | Rebuild Nursery- Fordtran Sw- Inez - El Toro Sw Station to 795 ACSR |  | Nursery | El Toro | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2027-05-01 |  | 69 | 0 | 24.8 | 0 |  | Victoria | Jackson | Tier 4 |  |  |  |  | 5504, 5510, 5514, 5516 | Y |  |  |  | 76778 | 76777
91463 | New Station tapping Oak Grove to Rand 138kV line. | New Station tapping Oak Grove to Rand 138kV line. |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2027-05-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 6896, 6906, 6913 | Y |  |  |  | 91464 | 91463
92743 | Rebuild ~3 miles of double-ckt from VLSI to Grissom transmission line with normal and emergency ratings of at least 478MVA |  |  | 5467 | 5185 | Planned | T-0377 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-05-14 |  | 138 | 0 | 3.03 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5185, 5467 | Y |  |  |  | 92744 | 92743
93250A | Utley_Substation_and_Transmission_Line_Addition |  |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-8065 | 2027-05-14 |  | 138 | 0 | 0 | 0 |  | Bastrop | Bastrop | Tier 3 |  |  |  |  | 7316, 7317, 7322, 7327 | Y |  |  |  | 93251 | 93250
85977A | Cedar Hill - Swiftex Transmission Line Upgrade | Upgrade the existing T367 Cedar Hill - Swiftex 138-kV transmission line from Cedar Hill to Str 181 (Elgin Tap) |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2027-05-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 3 | 24RPG014 | 2024-05-02 | 2024-05-23 |  | 3674, 7326, 7331 | Y |  |  |  | 85978 | 85977 | 2023-SC15
85977B | Cedar Hill - Swiftex Transmission Line Upgrade | Corrects topology for Elgin Tap and its associated branches |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2027-05-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 3 | 24RPG014 | 2024-05-02 | 2024-05-23 |  | 7310, 7319, 7326, 7331, 7674, 13674 | Y |  |  |  | 90939 | 85977 | 2023-SC15
87514 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2027-05-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 6903, 6904 | Y |  |  |  | 87515 | 87514
87673 | Rebuild the Salado - Bell County 138 kV Line | Rebuild the Salado - Bell County 138 kV Line on new structures |  | Salado | Bell County | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6280 | 2027-05-15 |  | 138 | 7.8 | 0 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 132, 3640 | Y |  |  |  | 87674 | 87673
87675 | Rebuild the Bell County - Fryers Creek 138 kV Line | Rebuild the Bell County - Fryers Creek 138 kV Line on new structures |  | Bell County | Fryers Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6336 | 2027-05-15 |  | 138 | 3.2 | 0 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 132, 3493 | Y |  |  |  | 87676 | 87675
87677 | Rebuild the Fryers Creek - Temple 138 kV Line | Rebuild the Fryers Creek - Temple 138 kV Line on new structures |  | Fryers Creek | Temple | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6335 | 2027-05-15 |  | 138 | 4.5 | 0 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 3415, 3493 | Y |  |  |  | 87678 | 87677
87768 | Establish a 110.4 MVAR Capacitor Bank at Pintail 138 kV Switch | Establish a 110.4 MVAR Capacitor Bank at Pintail 138 kV Switch |  | Pintail | Pintail | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6167 | 2027-05-15 |  | 138 | 0 | 0 | 0 | 0,110.4 | Williamson | Williamson | Tier 4 |  |  |  |  | 3692 | Y |  |  |  | 87769 | 87768
91397 | Wolf_Lane_Wyldwood_Transmission_Line_Overhaul | Overhaul transmission line structures per LCRA TSC standards and current NESC requirements. Replace existing conductor with bundled-Suwannee |  | Wyldwood | Wolf Lane | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-6945 | 2027-05-15 |  | 138 | 0 | 0 | 0 |  | Bastrop | Bastrop | Tier 4 |  |  |  |  | 7210, 7212 | Y |  |  |  | 91398 | 91397 | 2024-SC20
92561 | LCRATSC_Colton_Elroy_Transmission_Line_Overhaul | Overhaul transmission line structures per LCRA TSC standards and current NESC requirements. |  | 7208 | 7209 | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org | PLC-6951 | 2027-05-15 |  | 138 | 0 | 3.27 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 7208, 7209 | Y |  |  |  | 92562 | 92561 | 2024-SC20
91626 | Upgrading Buda to Manchaca | Upgrading Buda to Manchaca branch to minimum of 379 MVA. | [5 empty] | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2027-05-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 70498, 70504 | Y |  |  |  | 91627 | 91626
92347 |  |  |  | New station Walston | Butler | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-05-15 |  | 138 | 0 | 0 | 0 |  | Freestone | Freestone | Tier 4 |  |  |  |  | 104, 105, 3283 | Y |  |  |  | 92348 | 92347
91404 | Howard Lane_Wells Branch_TL_Upgrade | LCRA TSC will upgrade T387 Howard Lane - Wells Branch 138-kV transmission line to achieve a higher operational rating. |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-7655 | 2027-05-15 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 7288, 7335 | Y |  |  |  | 91405 | 91404
92627 | Colton_Mendoza_Transmission_Line_Upgrade | Overhaul transmission line structures per LCRA TSC standards and current NESC requirements. Replace existing conductor with bundled-Suwannee |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-7994 | 2027-05-15 |  | 138 | 0 | 0 | 0 |  | Caldwell | Travis | Tier 4 |  |  |  |  | 7208, 7325 | Y |  |  |  | 92628 | 92627 | 2024-SC20
92778 | Oncor_MW_92778_Dunham 345-138 kV Switch | Establish Dunham 345/138 kV Switch |  | Dunham | Dunham | Planned | M5007 | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2027-05-15 |  | 345 | 0 | 0 | 600 |  | Denton | Denton | Tier 3 |  |  |  |  | 1840, 11840, 15114, 21851 | Y |  |  |  | 92779 | 92778
92911 | Add Capacitor Bank at Wildhorse POD | Adds Capacitor Bank at Wildhorse POD |  | Wildhorse POD | Wildhorse POD | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8664 | 2027-05-15 | 2027-05-15 | 138 | 0 | 0 | 0 | 0,55.2 |  |  | Tier 4 |  |  |  |  | 1397 | Y |  |  |  | 92912 | 92911
93274 | Bastrop_Mesquite_Substation_Addition | Construct a new 138-kV substation in a ring bus configuration to serve BBEC customer load |  | 7320 | 7320 | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-4500 | 2027-05-15 |  | 138 | 0 | 0 | 0 |  | Bastrop | Bastrop | Tier 4 |  |  |  |  | 7310, 7316, 7320, 7322 | Y |  |  |  | 93305 | 93274
4270 | Handley - Hemphill 138 kV Line | Upgrade existing line | Project Deferral | Handley | Hemphill | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5214 | 2027-05-15 |  | 138 | 0 | 7.4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  |  | 1950, 2164, 2167 | Y | N |  |  | 11818 | 4270
81373 |  |  |  | Longstreet | Buckholts | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-05-15 |  | 138 | 0 | 1.5 | 0 |  | Milam | Milam | Tier 4 |  |  |  |  | 65, 108, 110, 3749 | Y |  |  |  | 81374 | 81373
81440 | Wolf to Monahans to Pecos 138 kV Line Rebuild | 138 kV existing line rebuild. |  | Wolf | Pecos/Reiter | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8527 | 2027-05-15 |  | 138 | 0 | 11.6 | 0 |  | Ward | Ector | Tier 3 |  |  |  |  | 1013, 1107, 10006, 11111, 11117 | Y |  |  |  | 81441 | 81440
82826 | Sunflower 138 kV Switch | Establish Sunflower 138 kV Switch |  | Sunflower Switch | Sunflower Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6322 | 2027-05-15 |  | 138 | 0 | 0 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  |  | 170, 3592, 3722 | Y |  |  |  | 82827 | 82826
80870 | Bakersfield Dynamic Reactive Substation Upgrade | Add a 350 MVAR synchronous condenser at Bakersfield substation based on ERCOT recommendation. |  | Bakersfield (BAKESW) | Bakersfield (BAKESW) | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | 1030378 | 2027-05-15 |  | 345 | 0 | 0 | 0 | -350350 | Pecos | Pecos | Tier 1 | 23RPG027 | 2023-09-07 | 2023-09-28 |  | 76002, 76101, 76102 | Y |  |  |  | 80926 | 80870 | 2023-FW10
81299 | Ranger Camp – Prong Moss 345 kV Line Rebuild | Rebuild the existing 345 kV line and add a second circuit to the new line |  | Ranger Camp | Prong Moss | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3025 | 2027-05-15 |  | 345 | 0 | 61.4 | 0 |  | Mitchell | Howard | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1030, 10049, 10057 | Y |  |  |  | 81300 | 81299
81152 | China Grove to Tributary Line Rebuild | Rebuild China_Grove - Tributary 138 kV Line |  | China Grove | Tributary Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8656 | 2027-05-15 |  | 138 | 0 | 23.7 | 0 |  | Mitchell | Howard | Tier 3 |  |  |  |  | 1318, 10119 | Y |  |  |  | 87650 | 81152
85979 | Elgin - Elgin Tap Transmission Line Overhaul | Perform an overhaul on the 2.2 mile T728 Elgin (structure #17/7) - Elgin Tap 138-kV transmission line. |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2027-05-15 | 2958101 | 138 | 0 | 0 | 0 |  |  |  | Tier 3 | 24RPG014 | 2024-05-02 | 2024-05-23 |  | 3674, 7326, 7331, 13674 | Y |  |  |  | 85980 | 85979 | 2023-SC15
71187 | Reiter - Tesoro 345 kV Double-Circuit Line | Construct new 2.5-mile 345 kV double-circuit line from Tesoro to Reiter |  | Tesoro | Reiter | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8629 | 2027-05-16 |  | 345 | 5 | 0 | 0 |  | Midland | Ector | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 18540, 18544 | Y |  |  |  | 71189 | 71187
91293 | LCRATSC_Gabriel-Schwertner TL conversion | This project is needed to meet a request from BEPC to voltage convert (69-138-kV) and increase the capacity of the BEPC-owned Gabriel - Schwertner circuit on the TSC-owned 138-kV T359 transmission line. As part of this upgrade, LCRA TSC will upgrade conductor on T359 from Gabriel to Str. 21R. |  |  |  | Planned |  | LCRATSC | dylan.preas@lcra.org 512-578-4514 | PLC-8197 | 2027-05-17 |  | 138 | 0 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | 7345, 7346, 7523 | Y |  |  |  | 91970 | 91293
90255C | Jordan / Mont Belvieu Area Improvement Project | Upgrade Ckt.86A Cedar Bayou to CHEVRON to increase thermal limits. |  | Cedar Bayou | CHEVRON | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-30 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 24RPG026 | 2024-08-21 | 2024-09-12 | 2024-09-12 |  | Y | N |  |  | 92982 | 90255
90255D | Jordan / Mont Belvieu Area Improvement Project | Upgrade Ckt.86H BRINE to Mont Belvieu to increase thermal limits. |  | BRINE | Mont Belvieu | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-30 |  | 138 | 0 | 2.8 | 0 |  | Chambers | Chambers | Tier 3 | 24RPG026 | 2024-08-21 | 2024-09-12 | 2024-09-12 | 40220, 41111 | Y | N |  |  | 92981 | 90255
90255B | Jordan / Mont Belvieu Area Improvement Project | Upgrade Ckt.84D Cedar Bayou to CD/HOPSON to increase thermal limits. |  | Cedar Bayou | Cedar Bayou Distribution | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-30 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 24RPG026 | 2024-08-21 | 2024-09-12 | 2024-09-12 | 40015, 48065 | Y | N |  |  | 92980 | 90255
90255E | Jordan / Mont Belvieu Area Improvement Project | Apply 110% Emergency rating for the EAGLE customer substation 2000A equipment to increase thermal limits on Ckts 52B / 52C. Upgrade existing 515 / 515 MVA Mont Belvieu relay system limits on Ckt.52C line position. |  | EAGLE | WINFRE/Mont Belvieu | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-30 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 24RPG026 | 2024-08-21 | 2024-09-12 | 2024-09-12 | 40500, 40764, 41111 | Y | N |  |  | 92979 | 90255
90063 | Elm Creek to Mulberry Creek: Rebuild 138 kV Line | Rebuild the Elm Creek to Mulberry Creek 138 kV line | NEW | Elm Creek | Mulberry Creek | Planned |  | AEP TNC | Charles Burks twang1@aep.com 918-599-2635 | TP2023600 | 2027-05-31 |  | 138 | 0 | 5.7 | 0 |  | Taylor | Jones | Tier 4 |  |  |  |  | 6255, 60772 | Y | N |  |  | 90064 | 90063
90134A | Elvis (EVS) 138kV CEHE Substation for ROCK N ROLL Storage (24INR0234) | Install new Elvis (EVS) 138kV CEHE Substation for generator interconnection to Rock N Roll Storage. Connect to Ckt.26B WINMIL to Rosharon to create new Ckt.26 WINMIL to Elvis to Rosharon. |  | Elvis | WINMIL/ Rosharon | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42110, 44531, 44560, 44600 | Y | N |  |  | 90847 | 90134
90134B | Elvis (EVS) 138kV CEHE Substation for ROCK N ROLL Storage (24INR0234) | Install one generator lead from Elvis (EVS) 138kV CEHE Substation to customer-owned ROCK_N (RNR) for ROCK N ROLL Storage (24INR0234) customer substation. |  | ROCK_N |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 | [5 empty] | Y | N |  | Costs included in main entry | 90848 | 90134
55421 | Ballinger to Concho: Rebuild 69 kV line | Rebuild Ballinger to Concho 69 kV line, install POP switch for Rowena, install CB at Miles, install POP switch for Harriett REA | Contact and In-Service Date Update | Ballinger | San Angelo Concho | Planned | 1088 - 1271 | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | 1861 | 2027-05-31 |  | 69 | 0 | 20.45 | 0 |  | Runnels | Tom Green | Tier 3 | 20RPG004 | 2020-04-08 | 2020-04-30 | 2020-05-08 | 6338, 6409, 6410, 6411, 6412, 6413, 6450 | Y | N |  |  | 55422 | 55421
76082 | Union Carbide: Rebuild 138 kV Station | Rebuild Union Carbide as new AIS station Chalybe | In-Service Date Update | Union Carbide |  | Planned |  | AEP TCC | Charity Kreher jlsolis@aep.com 361-881-5574 |  | 2027-05-31 | 2958101 | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  |  | 5767, 5963, 5965, 8337, 8338, 8535, 8735, 79601 | Y |  |  |  | 76083 | 76082
67427B | MINING 138kV Conversion and BENTON customer substation removal(24RPG033). | Install new customer-owned MINING 138kV substation. Loop substation on existing Ckt.06G to create new Ckt.06 Pasadena to College tap to MINING to Jefferson. |  | MINING-138 | College/ Jefferson | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 | 24RPG033 | 2024-11-07 | 2024-12-02 | 2024-12-02 | 40470, 41030, 41061, 41071, 41240, 41380, 48171, 48177, 48274, 111102 | Y | N |  | Costs included in main entry | 91249 | 67427
67427A | MINING 138kV Conversion and BENTON customer substation removal(24RPG033). | Rebuild/Repurpose existing 69kV Ckt.16C MINING Switchrack to MINING tap section. Retire MINING Switchrack from Ckt.16C to create new Ckt.16C Deepwater to South Channel. Remove customer-owned BENTON substation from CEHE service. Retire MINING 69kV substation. |  | Deepwater | South Channel | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 | 24RPG033 | 2024-11-07 | 2024-12-02 | 2024-12-02 | 40470, 41380 | Y | N |  |  | 91250 | 67427
86791 | Crane to Rio Pecos: Rebuild 138 kV Line | Rebuild the Crane to Rio Pecos 138 kV line | In-Service Date Update | Crane | Rio Pecos | Planned | TP2024050 | AEP TNC | Brooks Dow twang1@aep.com 918-599-2635 |  | 2027-05-31 |  | 138 | 0 | 23.65 | 0 |  | Crane | Crockett | Tier 1 | 23RPG023 | 2023-08-11 | 2024-01-18 | 2024-01-24 | 6601, 76615 | Y | N |  |  | 86792 | 86791
69479 | Radiant: Build new 345 kV Station | Interconnect Lunis Creek Solar to the new Radiant 345 kV station on the Cobra to STP 345 kV line | In-Service Date Update | Radiant |  | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 |  | 2027-05-31 |  | 345 | 0.2 | 0 | 0 |  | Jackson |  | Tier 4 |  |  |  |  | 5915, 8676, 8715 | Y |  |  |  | 69480 | 69479
70891 | Eola Tap: Rebuild 69 kV Line | Rehab Eola Tap 69 kV Line | Contact Update | Eola Tap | Eola | Planned |  | AEP TNC | Dewey Peters twang1@aep.com 918-599-2635 |  | 2027-05-31 |  | 69 | 0 | 11.69 | 0 |  | Concho | Concho | Tier 4 |  |  |  |  | 6370, 6371 | Y | N |  |  | 70892 | 70891
77031 | Las Lomas: Construct New Distribution Station | Construct new distribution station on the La Grulla to Rio Grande City 138 kV line | Contact Update | Las Lomas |  | Planned |  | AEP TCC | Nathan Cowan jlsolis@aep.com 361-881-5574 | DP24X0003 | 2027-05-31 |  | 138 | 0 | 0 | 0 |  | Starr |  | Tier 4 |  |  |  |  | 8793, 8798, 8806 | Y |  |  |  | 77032 | 77031
75780A | Loop new Elmaton substation into Ckt.39A to create new Ckt.39 STP to Elmaton to WA Parish. Install generator lead from Elmaton (ELM) substation to DUFFY (DUF) / Duffy Solar (23INR0057) | Loop new Elmaton substation into Ckt.39A to create new Ckt.39 STP to Elmaton to WA Parish. |  | Elmaton | STP/WA Parish | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 5915, 43990, 44000 | Y | N |  |  | 87168 | 75780
75835C | Upgrade Ckt.66B Stone Lake to Tomball to increase thermal limits. Install 40 MVAR cap bank at Hockley substation and tapped on Ckt.66B Hockley to Stone Lake. | Upgrade Ckt.66B Stone Lake to Tomball to increase thermal limits. Phase Two of overall approved upgrades. |  | Stone Lake | Tomball | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 |  | 138 | 0 | 2.45 | 0 |  | Harris | Harris | Tier 3 | 23RPG012 | 2023-05-04 | 2023-05-26 | 2023-05-26 | 44840, 46510, 48348 | Y | N |  | Cost included in main entry | 90211 | 75835
73055 | Hamlin to Roby: Rebuild 69 kV line | Rehab Hamlin to Roby 69 kV line |  | Hamlin | Roby | Planned |  | AEP TNC | Damian Rabb mlforcum@aep.com 918-599-2674 |  | 2027-05-31 |  | 69 | 0 | 25.23 | 0 |  | Fisher | Jones | Tier 4 | 23RPG002 | 2023-02-01 | 2023-02-28 |  | 6185, 6192, 6193, 6194, 6195, 6638 | Y | N |  |  | 73056 | 73055
81548 | Haber: Construct New 345 kV Station | Interconnect the Theta load to the new Haber 345 kV station on the Cobra to Static 345 kV line | Project Description Update | Haber |  | Conceptual |  | AEP TCC | Doug Evans deevans@aep.com 918-599-2938 |  | 2027-05-31 |  | 345 | 7 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  |  | 8676, 8728, 81003, 81006 | Y |  |  |  | 81549 | 81548
80576 | Chalmers: Construct New Distribution Station | Construct new distribution station on the Lane City to Magill 138 kV line | Contact Update | Chalmers |  | Planned | DP23X0014 | AEP TCC | Lorraine Timmerman deevans@aep.com 918-599-2938 |  | 2027-05-31 |  | 138 | 0 | 0 | 0 |  | Matagorda |  | Tier 4 |  |  |  |  | 8111, 8127, 8668, 8750, 89500 | Y |  |  |  | 80577 | 80576
90020 | Firerock: Install New 138/69 kV Autotransformer | Install new 138/69 kV autotransformer at the Firerock 138/69 kV station |  | Firerock |  | Planned |  | AEP TNC | Tong Wang 918-599-2635 | TP2022133 | 2027-05-31 |  | 138 | 0 | 0 | 130 |  | Coleman |  | Tier 4 | [5 empty] | Y |  |  |  | 90021 | 90020
90047 | Big Hill to Rockefeller Storage: Construct New 345 kV Line | Interconnect Rockefeller Storage to the existing Big Hill 345 kV station | NEW | Big Hill | Rockefeller Storage | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | TP2024144 | 2027-05-31 |  | 345 | 0.2 | 0 | 0 |  | Schleicher | Schleicher | Tier 4 | [5 empty] | Y |  |  |  | 90048 | 90047
90255A | Jordan / Mont Belvieu Area Improvement Project | Install 120 MVAr cap bank at Mont Belvieu Ckt.84E to WARVUE. |  | Mont Belvieu | WARVUE | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 24RPG026 | 2024-08-21 | 2024-09-12 | 2024-09-12 | 41111, 41700 | Y | N |  |  | 92984 | 90255
90255F | Jordan / Mont Belvieu Area Improvement Project | Install new CEHE-owned Sjolander substation. Reconfigure existing Ckt.84D Cedar Bayou to CD/HOPSON and loop into Sjolander substation to create new Ckt.84 Cedar Bayou to Cedar Bayou tap to Sjolander to HOPSON. |  | Sjolander | Cedar Bayou/ HOPSON | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 |  | 138 | 2 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 24RPG026 | 2024-08-21 | 2024-09-12 | 2024-09-12 | 40012, 40015, 40050, 41690, 48065 | Y | N |  |  | 92983 | 90255
87029 | Parana: Construct New 138 kV Station | Interconnect Portside Energy Center Solar & Storage to the new Parana 138 kV station on the Big Three to Dupont SW 138 kV line | Title, Description, Location, In-Service Date, Circuit Miles, and County Update | Parana |  | Planned |  | AEP TCC | Doug Evans deevans@aep.com 918-599-2938 | TP2024062 | 2027-05-31 |  | 138 | 0 | 0 | 0 |  | Victoria | Victoria | Tier 4 |  |  |  |  | 80064 | Y |  |  |  | 87030 | 87029
90065 | Abilene Northwest to Mulberry Creek: Rebuild 138 kV Line | Rebuild the Abilene Northwest to Mulberry Creek 138 kV line |  | Abilene Northwest | Mulberry Creek | Planned |  | AEP TNC | Charles Burks twang1@aep.com 918-599-2635 | TP2023881 | 2027-05-31 |  | 138 | 0 | 2.58 | 0 |  | Taylor | Jones | Tier 4 |  |  |  |  | 6228, 6288 | Y | N |  |  | 90066 | 90065
89924 | Weinbrenner 138kV Substation Expansion for SWITCH (SWG)/Elio BESS (25INR0103) | Expand 138kV Weinbrenner substation for SWITCH (SWG)/Elio BESS (25INR0103). Install one new generator lead from Weinbrenner to SWITCH/Elio BESS |  | Weinbrenner |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  |  | 42990, 114681 | Y | N |  |  | 89925 | 89924
90255G | Jordan / Mont Belvieu Area Improvement Project | Install new CEHE-owned Sjolander substation. Reconfigure existing Ckt.86A Cedar Bayou to CHEVRON and loop into Sjolander substation to create new Ckt.86 Cedar Bayou to Sjolander to Kilgore to Langston. |  | Cedar Bayou | Sjolander | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 00:01 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 24RPG026 | 2024-08-21 | 2024-09-12 | 2024-09-12 | 40015, 40050, 40300 | Y | N |  |  | 92985 | 90255
90255H | Jordan / Mont Belvieu Area Improvement Project | Install new CEHE-owned Sjolander substation. Reconfigure existing Ckt.86 CHEVRON to Kilgore to LANGSTON and loop into Sjolander substation to create new Ckt.86 Sjolander to Kilgore to LANGSTON. |  | Kilgore | Sjolander/ LANGSTON | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 00:01 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 24RPG026 | 2024-08-21 | 2024-09-12 | 2024-09-12 | 40050, 44830 | Y | N |  |  | 92986 | 90255
90255I | Jordan / Mont Belvieu Area Improvement Project | Install new CEHE-owned Sjolander substation. Disconnect existing circuits 86A and 86B from CHEVRON customer substation. Reconnect CHEVRON substation to Sjolander substation as Ckt.xx Sjolander to CHEVRON and Ckt.yy Sjolander to CHEVRON. |  | Sjolander | CHEVRON | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-05-31 00:02 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 24RPG026 | 2024-08-21 | 2024-09-12 | 2024-09-12 | 40050, 40300, 44830 | Y | N |  |  | 92987 | 90255
86321 | AEN_Lakeshore_Northland_Ckt_916_Reconductor |  |  | 9128 | 9228 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2027-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9128, 9228 | Y |  |  |  | 86322 | 86321
81724 | Calabaza: Construct New 138 kV Station | Interconnect the Omicron load to the new Calabaza 138 kV station on the Gila to Tortuga and Nueces Bay to Saxet 138 kV lines |  | Calabaza |  | Conceptual |  | AEP TCC/LCRA | Doug Evans deevans@aep.com 918-599-2938 |  | 2027-06-01 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 8168, 8441, 78568, 80260, 80380 | Y |  |  |  | 81725 | 81724
67091 | Second 138 kV transmission Line from DL-DP CKT1034 | Second 138 kV transmission Line from Dunlap to Decker CKT1034 |  | 9045 | 9188 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2027-06-01 |  | 138 | 5.22 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9045, 9188 | Y |  |  |  | 67092 | 67091
15TPIT0031 | Chavaneaux_Chavaneaux Tap Rebuild (Brooks to Chavaneaux ckt) | Rebuild 138 kV transmission from Chavaneaux to Chavaneaux Tap. This rebuild is for Brooks to Chavaneaux ckt. |  | Brooks | Chavaneaux | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | T-0260 | 2027-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5045, 5085 | Y |  |  | There are no transformers associated with this project | 9555 | 2304
86313 | AEN_345kV_CRASCO_SWYD_Addition | Crasco Switchyard will serve Bottom Grass BESS..The new the switchyard will be cut-in to345Kv CKT 3123 Holman - Hillje. |  |  |  | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2027-06-01 |  | 345 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  |  | 9067, 9073, 44200 | Y |  |  |  | 86314 | 86313
93685 | New Transformer will be added at Titan Substation. |  |  | Titan | Titan | Planned |  | BPUB | Luis Martinez lugmartinez@brownsville-pub.com 956-983-6212 |  | 2027-06-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5963 | Y |  |  |  | 93686 | 93685
86331 | AEN_Wheless_Mueller_Ckt_1016_Reconductor |  |  | 9291 | 9342 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2027-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9291, 9342 | Y |  |  |  | 86332 | 86331
93242 | Saxet Substation Upgrade | This Saxet Substation Upgrade project (Phase 2) will be a continuation of the Saxet Substation Addition project (Phase 1) where LCRA TSC installed two new transmission hard taps with associated structures to LCRA TSC owned 138-kV transmission lines T522 Lon Hill – Weil Tract and T437 Lon Hill (AEP) – Nueces Bay (AEP). In this project, LCRA TSC will upgrade from the hard tap installations to a breakered facility and connect the LCRA TSC 138-kV transmission lines T522 Lon Hill – Weil Tract and T437 Lon Hill (AEP) – Nueces Bay (AEP) to the new Saxet substation. |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-7500 | 2027-06-10 |  | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 8452, 78568, 78569, 78570, 80380 | Y |  |  |  | 93247 | 93242
75255C | CPSE_Howard to San Miguel Double Circuit Line Addition |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-06-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  |  | 5230, 5260 | Y |  |  |  | 75849 | 75255
75255A | CPSE_Howard to San Miguel Double Circuit Line Addition |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-06-15 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  |  | 5231, 5901 | Y |  |  |  | 75256 | 75255
75255B | CPSE_Howard to San Miguel Double Circuit Line Addition |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-06-15 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  |  | 5230, 5231 | Y |  |  |  | 75848 | 75255
91596 | Addition of PEC Heidel Substation | Adding PEC_Heidel substation. Adding bus, branch, and load. | [5 empty] | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2027-06-29 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 70002, 70198, 70498 | Y |  |  |  | 91597 | 91596
90040 | Del Sol: Construct New 345 kV Terminal | Interconnect Diamondback Solar to the Del Sol 345 kV station | Contact and Owner Update | Del Sol |  | Planned |  | ETT | Lance Price 361-881-5574 | TP2024116 | 2027-06-30 |  | 345 | 0 | 0 | 0 |  | Starr |  | Tier 4 | [5 empty] | Y |  |  |  | 90041 | 90040
90018 | Sand Crab: Construct New 138 kV Terminal | Interconnect Canvasback BESS to the Sand Crab 138 kV station | NEW | Sand Crab |  | Planned |  | AEP TCC | Brooks Dow deevans@aep.com 918-599-2938 |  | 2027-06-30 |  | 138 | 0 | 0 | 0 |  | Calhoun |  | Tier 4 | [5 empty] | Y | N |  |  | 90019 | 90018
81227 | Cattleman – Gascondades 345 kV Reroute | Terminate Morgan Creek – Gascondades 345 kV Line into Cattleman 345 kV Switch |  | Cattleman | Gascondades | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8647 | 2027-06-30 |  | 345 | 0 | 2.5 | 0 |  | Mitchell | Mitchell | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1030, 10053, 11032, 11033, 11034, 76030 | Y |  |  |  | 81664 | 81227
90055 | Ursidae: Construct New 138 kV Station | Interconnect Northington Solar to the new Ursidae 138 kV station on the El Campo to Victoria 138 kV line between Corichi and El Campo | Contact Update | Ursidae |  | Planned |  | AEP TCC | Brooks Dow deevans@aep.com 918-599-2938 | TP2024151 | 2027-06-30 |  | 138 | 0 | 0 | 0 |  | Wharton |  | Tier 4 |  |  |  |  | 8099, 8102, 80101 | Y | N |  |  | 90056 | 90055
76916 | Snapdragon: Construct New 138 kV Station | Interconnect Desert Vine Solar to the new Snapdragon 138 kV station on the Revilla to Zapata 138 kV line | Contact and In-Service Date Update | Snapdragon |  | Planned |  | AEP TCC/ETT | Zachary Lachiusa jlsolis@aep.com 361-881-5574 | TP2023012 | 2027-06-30 |  | 138 | 0 | 0 | 0 |  | Zapata |  | Tier 4 |  |  |  |  | 8299, 8736, 8957 | Y | Y |  |  | 76917 | 76916
73061 | Falfurrias to King Ranch: 138 kV Line Rebuild | Rehab the Falfurrias to King Ranch 138 kV line | In-Service Date Update | Falfurrias | King Ranch | Conceptual |  | AEP TCC | Chase Isaac deevans@aep.com 918-599-2938 |  | 2027-06-30 |  | 138 | 0 | 20.5 | 0 |  | Brooks | Kleberg | Tier 4 |  | 2023-01-24 | 2023-02-24 |  | 8510, 80228 | Y | N |  |  | 73062 | 73061
90173A | Cedar Bayou 5 Generator Interconnection (23INR0029) | Connect new generation facility to Cedar Bayou 345kV substation with 721 MW combined cycle natural gas-fired units. |  | Cedar Bayou |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-06-30 |  | 345 | 0 | 0 | 0 |  | Chambers |  | Tier 4 | [5 empty] | Y | N |  |  | 90207 | 90173
90173B | Cedar Bayou 5 Generator Interconnection (23INR0029) | Upgrade Ckt.97E Cedar Bayou to Chambers to increase thermal limits. |  | Cedar Bayou | Chambers | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-06-30 |  | 345 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  |  | 40000, 40255 | Y | N |  |  | 90208 | 90173
90173C | Cedar Bayou 5 Generator Interconnection (23INR0029) | Upgrade Ckt.84K HOPSON to WARVUE to increase thermal limits. |  | HOPSON | WARVUE | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-06-30 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  |  | 41690, 41700 | Y | N |  |  | 90209 | 90173
87328 | Sunstone: Construct New 138 kV Station | Interconnect the Inner Harbor Desalination Plant load to the new Sunstone 138 kV station on the Morris Street to Nueces Bay 138 kV line | Contact Update | Sunstone |  | Planned |  | AEP TCC/ETT | LaRissa Lundry deevans@aep.com 918-599-2938 | TP2022754 | 2027-06-30 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 8022, 8441, 8733 | Y | Y |  |  | 87329 | 87328
90033 | Reveille to Navitas: Construct New 138 kV Line | Interconnect the new Navitas load station to the existing Reveille 138 kV station | Dollars and Reactive Capability Update | Reveille | Navitas | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 | TP2024157 | 2027-06-30 |  | 138 | 0.15 | 0 | 0 | 0,37.4 | La Salle | La Salle | Tier 4 |  |  |  |  | 8612, 80095 | Y | N |  |  | 90034 | 90033
49556 | Ozona: Rebuild 69 kV station | Replace existing Ozona 69 kV station with a new 69 kV ring bus |  | Ozona |  | Planned | 1018 - 1196 | AEP TNC | Robert Younger twang1@aep.com 918-599-2635 | 2780 | 2027-06-30 |  | 69 | 0 | 0 | 0 |  | Crockett |  | Tier 4 |  |  |  |  | 6550, 6560 | Y | N |  |  | 65538 | 49556
61406 | Kendall - Welfare Transmission Line Upgrade | This project will Increase the reliability of transmission facilities on the T584 Kendall to Welfare 138-kV and T656 Bergheim to Kendall 345-kV 10.2-mile double-circuit transmission line by replacing the aging conductor. |  | Kendall | Welfare | Planned | 61358, 61392, 61350, 61234, 61362, 61356, 61400, 61402, 61404 | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2027-06-30 |  | 138 | 0 | 10.2 | 0 |  | Kendall | Kendall | Tier 3 | 22RPG005 | 2022-03-04 | 2022-09-09 |  | 7046, 7152, 7153, 7770 | Y | N |  |  | 78330 | 61406
93048 | Add Liendo load serving substation |  |  |  |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2027-07-01 |  | 138 | 0 | 0 | 0 |  | Waller | Waller | Tier 4 |  |  | 2024-02-01 |  | 7272, 57668, 57674 | Y | N |  |  | 93049 | 93048
84896 | New Legend Falls Substation looped into the existing Tally to Texas Research transmission line. This station supports the RPG approved Rio Medina project |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-07-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5259, 5422, 5430 | Y |  |  |  | 84897 | 84896
91708 | New San Geronimo Substation | adds new San Geronimo station on STEC Rio Medina - CPS Legend Falls line |  | Rio Medina | Legend Falls | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2027-07-01 |  | 138 | 0 | 0 | 0 |  | Medina | Medina | Tier 4 |  |  |  |  | 5259, 5805, 5808 | Y | N |  |  | 91709 | 91708
71881 | Install 31.3 Mvar capacitor bank at Andice. | Install 31.3 Mvar capacitor bank at Andice. Formerly TPIT project number 70365. |  | Andice |  | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2027-07-01 |  | 138 | 0 | 0 | 0 | 0,31.2 | Williamson |  | Tier 4 |  |  |  |  | 70522 | Y | Y |  |  | 71882 | 71881
85008 | Add Rio Medina - Legend Falls Tline | Add Rio Medina - Legend Falls Tline as part of the Rio Medina RPG Project |  | Rio Medina |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2027-07-01 12:01 |  | 138 | 5.6 | 0 | 0 |  | Medina | Medina | Tier 2 |  |  | 2024-02-01 |  | 5259, 5805 | Y | N |  |  | 85009 | 85008
70712 | SAPS to Red Creek: Rebuild 138 kV Line | Rehab the SAPS to Red Creek 138 kV line | In-Service Date Update | SAPS | Red Creek | Planned |  | AEP TNC | Brent Harris twang1@aep.com 918-599-2635 | TA2020210 | 2027-07-31 |  | 138 | 0 | 0 | 0 |  | Tom Green | Tom Green | Tier 4 |  |  |  |  | 6442, 6473, 6480, 60008 | Y |  |  |  | 70713 | 70712
72884 | Gonzales: Build 69 kV STATCOM | Build new 69 kV STATCOM at the Gonzales 69 kV station | Contact and In-Service Date Update | Gonzales |  | Planned |  | ETT | Bradley Case twang1@aep.com 918-599-2635 | TP2022130 | 2027-07-31 |  | 69 | 0 | 0 | 0 | -25,25 | Presidio |  | Tier 4 |  |  |  |  | 6675, 60203 | Y | N |  |  | 72885 | 72884
90057 | Volar to XE Flying Kite Solar: Construct New 138 kV Line | Interconnect XE Flying Kite Solar to the new Volar 138 kV station on the Crystal City to Poblano 138 kV line between La Pryor and Poblano | Contact Update | Volar | XE Flying Kite Solar | Planned |  | AEP TCC | Nathan Cowan jlsolis@aep.com 361-881-5574 | TP2024145 | 2027-07-31 |  | 138 | 2 | 0 | 0 |  | Zavala | Zavala | Tier 4 | [5 empty] | Y |  |  |  | 90058 | 90057
87633 | WETT Buck Canyon Synchronous Condenser |  |  | Long Draw | Buck Canyon | Planned |  | WETT | Chris Ramirez cramirez@wettllc.com |  | 2027-07-31 |  | 345 | 0.25 | 0 | 0 |  | Borden | Borden | Tier 1 | 23RPG026 | 2023-09-01 | 2023-09-28 |  | 59900, 59916, 59917, 59918 | Y |  |  |  | 87634 | 87633
87899 | Vaso: Construct New 138 kV Station | Interconnect the Alpha load to the new Vaso 138 kV station on the Cantwell to Citgo North Oak 138 kV line | Project Title, Project Description, Terminal Location, Status, In-Service Date, and Cost Update | Vaso |  | Conceptual |  | AEP TCC | Doug Evans deevans@aep.com 918-599-2938 |  | 2027-08-31 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 8466 | Y |  |  |  | 87900 | 87899
90014 | Palafox: Construct New 138 kV Station | Construct new STEC distribution station on the North Laredo Switch to Reveille 138 kV line between Barrera and North Laredo Switch | Contact and In-Service Date Update | Palafox |  | Planned |  | AEP TCC | Brooks Dow jlsolis@aep.com 361-881-5574 | TP2024132 | 2027-08-31 |  | 138 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  |  | 8053, 8717, 8909, 88000 | Y |  |  |  | 90037 | 90014
52464 | Alamito Creek to Ft. Davis: Rebuild 69 kV Line | Alamito Creek to Ft. Davis: Rebuild 69 kV line |  | Alamito Creek | Ft Davis | Planned | 1070 - 1243 | AEP TNC | Dewey Peters twang1@aep.com 918-599-2635 | 2831 | 2027-08-31 |  | 69 | 0 | 20.5 | 0 |  | Presidio |  | Tier 4 |  |  |  |  | 6676, 6677, 6678, 6691, 6692 | Y | N |  |  | 65564 | 52464
69471 | Villa Cavazos: Construct New 138 kV Terminal | Interconnect Eval BESS to the Villa Cavazos 138 kV station | Contact and In-Service Date Update | Villa Cavazos |  | Planned |  | AEP TCC | Robert Dougherty jlsolis@aep.com 361-881-5574 |  | 2027-08-31 |  | 138 | 0.35 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  |  | 80229 | Y |  |  |  | 69472 | 69471
86327 | AEN_New_138kV_Southshore_Substation_Addition |  |  | 9179 | 9132 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2027-09-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9132, 9134, 9179 | Y |  |  |  | 86328 | 86327
90111 |  |  |  | Gainesville | Red River | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-09-01 |  | 69 | 1.2 | 0 | 0 |  | Cooke | Cooke | Tier 4 |  |  |  |  | 719, 726, 735 | Y |  |  |  | 90112 | 90111
86333 | AEN_OnionCreek_StoneyRidge_Ckt_1026_Reconductor |  |  | 9237 | 9251 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2027-09-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9237, 9251 | Y |  |  |  | 86334 | 86333
91611 |  |  |  | Spring | Rector | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-09-01 |  | 138 | 0 | 11.4 | 0 |  | Cooke | Denton | Tier 4 |  |  |  |  | 672, 680, 684 | Y |  |  |  | 91612 | 91611
91570 |  |  |  | Gustine | Pottsville | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-09-01 |  | 69 | 0 | 0 | 0 |  | Hamilton | Hamilton | Tier 4 |  |  |  |  | 178, 272, 273 | Y |  |  |  | 91571 | 91570
86317 | AEN_DP_OnionCreek_Ckt_924_Reconductor |  |  | 9187 | 9251 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2027-09-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9187, 9251 | Y |  |  |  | 86318 | 86317
66492C | Chico West - Grindstone Switch 69 kV Line rebuild | Upgrade Jacksboro Amoco - Chico City Services 69 kV Line |  | Jacksboro Amoco | Chico City Services | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3006 | 2027-09-15 |  | 69 | 0 | 7.3 | 0 |  | Jack | Wise | Tier 4 |  |  |  |  | 1554, 1555 | Y |  |  |  | 72963 | 66492
66202A | Upgrade Palestine-Crockett 69 kV Line | Rebuild the Palestine - Elkhart 69 kV Line |  | Palestine | Elkhart | Under Construction |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6182 | 2027-09-15 |  | 69 | 0 | 9.8 | 0 |  | Anderson | Anderson | Tier 3 | 22RPG035 | 2022-10-15 | 2022-11-15 |  | 3273, 3285 | Y |  |  |  | 66203 | 66202
66202B | Upgrade Palestine-Crockett 69 kV Line | Rebuild the Elkhart - Crockett 69 kV Line |  | Elkhart | Crockett | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6182 | 2027-09-15 |  | 69 | 0 | 19.5 | 0 |  | Anderson | Houston | Tier 3 | 22RPG035 | 2022-10-15 | 2022-11-15 |  | 3285, 3286, 3289, 3290 | Y |  |  |  | 71894 | 66202
54892 | Eden to North Brady: Rebuild 69 kV line | Rehab Eden to North Brady 69 kV line | Contact and In-Service Date Update | Eden | North Brady | Planned | 1039 - 1266 | AEP TNC | Charity Kreher twang1@aep.com 918-599-2635 | 1856 | 2027-09-30 |  | 69 | 0 | 32.7 | 0 |  | Concho | McCulloch | Tier 3 | 22RPG009 | 2022-03-23 | 2022-04-14 |  | 6006, 6372, 6380, 6384, 6385, 60005, 60797 | Y | N |  |  | 65568 | 54892
91843 | East Munday: Rebuild 138 kV Station | Rebuild the East Munday 138 kV station | NEW | East Munday |  | Planned |  | AEP TNC | Craig Tabor twang1@aep.com 918-599-2635 | TP2023800 | 2027-09-30 |  | 138 | 0 | 0 | 0 |  | Knox |  | Tier 3 | 25RPG002 | 2025-01-20 | 2025-02-12 |  | 6110, 6117, 6161, 6320 | Y | N |  |  | 91844 | 91843
87635 | WETT Pitchfork Synchronous Condenser |  |  | Cottonwood | Pitchfork | Planned |  | WETT | Chris Ramirez cramirez@wettllc.com |  | 2027-09-30 |  | 345 | 0 | 0 | 0 |  | Borden | Borden | Tier 1 | 23RPG026 | 2023-09-01 | 2023-09-28 |  | 59904, 59908, 59913, 59914, 59915 | Y |  |  |  | 87636 | 87635
87367 |  |  |  | Temple Switch | Poage | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2027-10-01 |  | 138 | 0 | 2 | 75 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 126, 130, 133, 3415, 33126 | Y |  |  |  | 87368 | 87367
91481 | New TVEC substation by tapping Oncor's line Kemp to Seven Points 138kV. |  |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2027-10-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 2726, 3264, 6901 | Y |  |  |  | 91482 | 91481
73366 | CPSE_New_Wiseman_Substation | Loop new 138 kV substation into existing 138kV Cagnon to Helotes Transmission Line. | [5 empty] | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2027-10-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5055, 5200, 5487 | Y |  |  |  | 73367 | 73366
73441 | Dupont Switch to Joslin: Rebuild 138 kV Line | Rehab the Dupont Switch to Joslin 138 kV Line | In-Service Date Update | Dupont | Joslin | Planned |  | AEP TCC | Travis Coody mlforcum@aep.com 918-599-2674 |  | 2027-10-31 |  | 138 | 0 | 32.6 | 0 |  | Victoria | Calhoun | Tier 4 | 22RPG040 | 2022-11-01 | 2022-12-01 |  | 8140, 8141, 8143, 80064 | Y |  |  |  | 73442 | 73441
90051 | Riley: Construct New 345 kV Terminal | Interconnect the Sabey Data Center load to the existing Riley 345 kV station | NEW | Riley |  | Planned |  | AEP TNC/ETT | Tong Wang twang1@aep.com 918-599-2635 | TP2024133 | 2027-10-31 |  | 345 | 0 | 0 | 0 |  | Wilbarger |  | Tier 4 |  |  |  |  | 6101, 60150, 60151 | Y |  |  |  | 90052 | 90051
59086 | Corichi to Victoria: Rebuild 138 kV Line | Rebuild the Corichi to Victoria 138 kV line | In-Service Date Update | Corichi | Victoria | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 | TP2020888 | 2027-10-31 |  | 138 | 0 | 42.76 | 0 |  | Jackson | Victoria | Tier 3 |  | 2022-02-22 | 2022-03-01 |  | 8118, 8172 | Y | N |  |  | 65585 | 59086
89939A | Install new Skains (SKA) 345kV Substation for generator interconnection to Hollow Branch Creek Solar (24INR0422) | Install new Skains (SKA) 345kV Substation for generator interconnection to Hollow Branch Creek Solar (24INR0422). Loop into existing Ckt.74 Singleton to Jewett (ONCOR) to create new Ckt.74 Singleton to Skains to Jewett. |  | Skains | Singleton/Jewett | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-10-31 |  | 345 | 0 | 0 | 0 |  | Grimes | Leon | Tier 4 |  |  |  |  | 3391, 44645, 44660 | Y | N |  |  | 90853 | 89939
90031 | LLaves: Construct New 345 kV Station | Interconnect Keys Hollow Solar & Storage to the new Llaves 345 kV station on the Coleto Creek to Raptor 345 kV line | Cost Update | Llaves |  | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 | TP2024167 | 2027-10-31 |  | 345 | 0 | 0 | 0 |  | Goliad |  | Tier 4 | [5 empty] | Y | N |  |  | 90032 | 90031
89922 | Whaley 345kV Substation Expansion for ROSE/Rock Rose Energy BESS (26INR0201) | Expand Whaley 345kV Substation for ROSE / Rock Rose Energy BESS (26INR0201). Connect generator through one new generator lead. |  | Whaley |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-10-31 |  | 345 | 0 | 0 | 0 |  | Fort Bend |  | Tier 4 | [5 empty] | Y | N |  |  | 89923 | 89922
89939B | Install new Skains (SKA) 345kV Substation for generator interconnection to Hollow Branch Creek Solar (24INR0422) | Install one generator lead from Skains (SKA) 345kV CEHE Substation to HOLLOW (HLW) / Hollow Branch Solar (24INR0422) |  | Skains | HOLLOW | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-10-31 00:01 |  | 345 | 0 | 0 | 0 |  | Grimes |  | Tier 4 | [5 empty] | Y | N |  | Costs included in main entry | 90854 | 89939
91135 | Add the Frankston station which taps the Coffee to Blackburn line | Adding the Frankston station, tapping Rayburn's Coffee and Oncor's Blackburn stations. |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2027-11-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 3325, 6855, 6871 | Y |  |  |  | 91136 | 91135
91986 | Establish the Wofford/Berryville POI | Establish the Wofford/Berryville POI |  | Frankston | Berryville | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6332 | 2027-11-06 |  | 138 | 2 | 0 | 0 |  | Anderson | Anderson | Tier 4 |  |  |  |  | 3782, 3783, 6871 | Y |  |  |  | 91987 | 91986
90340B | South Lane City substation expansion for BRP Diran BESS (23INR0137) | Relocate existing Ckt.60D South Lane City to Dyann with expansion of South Lane City to BAAH configuration. |  | South Lane City | Dyann | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-11-30 |  | 138 | 0 | 0 | 0 |  | Wharton | Wharton | Tier 4 | [5 empty] | Y | N |  | Costs included in main entry | 90342 | 90340
90189 | Meadow 345kV Substation Expansion for Aldrin 345 BESS(25INR0425). | Expand 345kV Meadow (MDO) substation for ALDRIN (ALD) / Aldrin 345 BESS (25INR0425). |  | Meadow |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-11-30 |  | 345 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 | [5 empty] | Y | N |  |  | 90190 | 90189
70710 | Eden to Yellowjacket: Rebuild 69 kV Line | Rehab the Eden to Yellowjacket 69 kV line |  | Eden | Yellowjacket | Planned |  | AEP TNC | Damian Raab twang1@aep.com 918-599-2635 | TA2021119 | 2027-11-30 |  | 69 | 0 | 0 | 0 |  | Concho | Menard | Tier 3 |  |  |  |  | 6363, 6372 | Y |  |  |  | 70711 | 70710
72999 | Haskell to Munday: Rebuild 69 kV Line | Rehab Haskell to Munday 69 kV Line |  | Haskell | Munday | Planned |  | AEP TNC | Bill Edwards twang1@aep.com 918-599-2635 |  | 2027-11-30 |  | 69 | 0 | 21.71 | 0 |  | Haskell | Knox | Tier 4 | 22RPG043 | 2022-12-15 | 2023-01-11 |  | 6107, 6122, 6123, 6124, 6125, 6126, 60021 | Y | N |  |  | 73000 | 72999
87629 | WETT Binturong Synchronous Condenser |  |  | Bearkat | Binturong | Planned |  | WETT | Chris Ramirez cramirez@wettllc.com |  | 2027-11-30 | 2958101 | 345 | 0.25 | 0 | 0 |  | Glasscock | Glasscock | Tier 1 | 23RPG026 | 2023-09-01 | 2023-09-28 |  | 59903, 59919, 59920, 59921 | Y |  |  |  | 87630 | 87629
90340A | South Lane City substation expansion for BRP Diran BESS (23INR0137) | Expand South Lane City substation for generator interconnection to BRP Diran BESS. Convert South Lane City to BAAH configuration. |  | South Lane City | BRP Diran BESS | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-11-30 |  | 138 | 0 | 0 | 0 |  | Wharton |  | Tier 4 | [5 empty] | Y | N |  |  | 90341 | 90340
91553 | 180MW load connecting to a new load serving station from RCEC's Union Valley Station to Blackland RC |  |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2027-12-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 2 |  |  |  |  | 6860, 6886, 6981 | Y |  |  |  | 91554 | 91553
6777 | Establish Division Sub Cedar Hill - Liggett 138 kV Line | Establish Division Sub and Loop Cedar Hill - Liggett 138 kV line in to Great Southwest / General Motors | Project Deferral | Grand Prairie West | Mayfield Tap | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5280 | 2027-12-14 02:01 |  | 138 | 6 | 0 | 0 |  | Dallas | Tarrant | Tier 2 |  |  |  |  | 1919, 2137, 2138, 2140, 2143, 2265, 2274, 12265 | Y | N |  |  | 72912 | 6777
87699 | Belton - Killeen 138 kV Line via Belton Southwest | Upgrade Belton - Killeen 138 kV Line via Belton Southwest |  | Belton | Killeen | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R902 | 2027-12-15 |  | 138 | 0 | 17.2 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 3423, 3610, 3633, 13610 | Y |  |  |  | 87700 | 87699 | 2023-NC36
92852B | Oncor_92852_MNE_Monticello_Paris_Line_Upgrade | Upgrade Woodard - Paris 345 kV Line |  | Woodard | Paris | Planned | R986 | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R986 | 2027-12-15 |  | 345 | 0 | 16.8 | 0 |  | Lamar | Lamar | Tier 1 |  |  |  |  | 1692, 11699 | Y |  |  |  | 93064 | 92852
87707 | Salado 345/138 kV Autotransformer #1 and #2 | Install Salado 345/138 kV Autotransformer #1 and #2 |  | Salado | Salado | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6354 | 2027-12-15 |  | 345 | 0 | 0 | 600 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 3640, 3699, 3745, 3746 | Y |  |  |  | 87708 | 87707
85955 | Olmos to LaVernia TL, T533 | Olmos to LaVernia TL, Rebuild 5.1 miles of 69 kV line to 138 kV transmission line |  | Olmos | LaVernia | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2027-12-15 | 2958101 | 69 | 0 | 5.1 | 0 |  | Wilson | Wilson | Tier 4 | [5 empty] | Y |  |  |  | 85956 | 85955
87010 | Establish Drill Hole 345/138 kV Switch | Establish Drill Hole 345/138 kV Switch |  | Drill Hole Switch | Drill Hole Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8725 | 2027-12-15 |  | 345 | 0 | 0 | 1200 |  | Culberson | Culberson | Tier 1 | 24RPG010 | 2024-03-18 |  |  | 10073, 10074, 10075, 10076, 11090, 11271, 11272, 18709 | Y |  |  |  | 87735 | 87010
81236 | Cattleman – Longshore 345 kV Double-Circuit Line Rebuild | Rebuild the existing 345 kV Double Circuit Line |  | Cattleman | Longshore | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3027 R8719 | 2027-12-15 |  | 345 | 0 | 66.8 | 0 |  | Howard | Midland | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1058, 10053, 18548 | Y |  |  |  | 81385 | 81236
81296 | Prong Moss – Rockhound 345 kV Line Rebuild | Rebuild the existing 345 kV line and add a second circuit to the new line |  | Prong Moss | Rockhound | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3025 | 2027-12-15 |  | 345 | 0 | 60.2 | 0 |  | Midland | Howard | Tier 1 | 23RPG029 |  |  |  | 10057, 10062 | Y |  |  |  | 81297 | 81296
81418 | Reiter to Yarbrough 138 kV Line Rebuild | 138 kV existing line rebuild. |  | Reiter | Yarbrough | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8527 | 2027-12-15 |  | 138 | 0 | 27.2 | 0 |  | Ector | Crane | Tier 3 |  |  |  |  | 11111, 18545 | Y |  |  |  | 81419 | 81418
76728 | Skyview 345/138 kV Switch | Establish Skyview 345/138 kV Switch |  | Skyview |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4350 | 2027-12-15 |  | 138 | 0 | 0 | 0 |  | Dallas |  | Tier 3 |  |  |  |  | 1922, 1924, 1927, 2119, 2120, 2123, 2124, 2125, 2127, 2128, 2129, 2130, 2131, 2132, 2134, 2231, 2243, 2244, 11938 | Y |  |  |  | 76831 | 76728
76654 | Establish Voss Lake 345/138 kV Switch | Establish Voss Lake 345/138 kV Switch |  | Voss Lake | Voss Lake | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6278 | 2027-12-15 |  | 345 | 0 | 5.6 | 600 | 0,110.4 | Milam | Milam | Tier 1 | 25RPG009 |  |  |  | 3675, 3687, 3717, 3740, 3750, 3751, 3752, 3761, 13429, 13430 | Y |  |  |  | 76655 | 76654 | 2023-SC9
72011 | Tonkawa - Ranger Camp 345 kV Line Rebuild | Rebuild the existing 345 kV line and add a second circuit to the new line |  | Tonkawa | Ranger Camp | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3025 | 2027-12-15 |  | 345 | 0 | 21.3 | 0 |  | Mitchell | Scurry | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1030, 10049, 11048 | Y |  |  |  | 81371 | 72011
71910B | Rebuild the Hillsboro - Elm Mott 69 kV Line | Rebuild the West - Abbott 69 kV Line |  | West 69 kV Substation | Abbott 69 kV Substation | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6221 | 2027-12-15 |  | 69 | 0 | 6.3 | 0 |  | McLennan | Hill | Tier 3 |  |  |  |  | 3524, 3525 | Y |  |  |  | 91606 | 71910
71912B | Killeen Fort Hood - Killeen Taft 138 kV Line | Rebuild the Killeen Park Street Tap - Killeen Taft 138 kV Line |  | Killeen Park Street Tap | Killeen Taft | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6245 | 2027-12-15 |  | 138 | 0 | 3.95 | 0 |  | Bell | Bell | Tier 4 |  |  |  |  | 3367, 3619, 3621, 3622, 3623, 3635 | Y |  |  |  | 71914 | 71912
68700 | Bonham - Toco Switch 69 kV Line Rebuild | Rebuild the existing 69 kV Line |  | Bonham | Toco | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3016 | 2027-12-15 |  | 69 | 0 | 35 | 0 |  | Fannin | Lamar | Tier 4 |  |  |  |  | 1703, 1761, 1788, 1789, 1790, 11789 | Y |  |  |  | 68701 | 68700
93466 | Rebuild Existing 138 kV Double Circuit Line | Rebuild Odessa EHV - Reiter 138 kV Double Circuit Line |  | Odessa EHV | Reiter | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | PB L17 | 2027-12-15 |  | 138 | 0 | 0 | 0 |  | Ector | Ector | Tier 3 |  |  |  |  | 1027, 18545 | Y |  |  |  | 93467 | 93466
87021 | Construct Drill Hole – Riverton 345 kV Double-Circuit | Construct Drill Hole – Riverton 345 kV Double-Circuit |  | Drill Hole Switch | Riverton Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8748 | 2027-12-16 |  | 345 | 36 | 0 | 0 |  | Culberson | Reeves | Tier 1 | 24RPG010 | 2024-03-18 |  |  | 10073, 11084 | Y |  |  |  | 87022 | 87021
78404 | BBEC Bastrop Colony Substation Addition (formerly Bastrop Village) |  |  | Bastrop Colony |  | Planned |  | BBEC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-8067 | 2027-12-31 |  | 138 | 0 | 0 | 0 |  | Bastrop | Bastrop | Tier 4 |  |  |  |  | 7555, 7556, 7561 | Y | N |  |  | 92458 | 78404
72032 | Stewart to West Bay Ckts 48A & 59A Upgrades | Reconductor Ckts. 48A & 59A Stewart to West Bay as a Hardening upgrade. |  | Stewart | West Bay | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-12-31 |  | 138 | 0 | 40 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 43290, 43520, 43521 | N |  |  |  | 72033 | 72032
73065 | Magana Hein: Build new 138 kV distribution station | Construct new distribution station on the Molina to Wormser Road 138 kV line | In-Service Date Update | Magana Hein |  | Planned |  | AEP TCC | Travis Coody jlsolis@aep.com 361-881-5574 |  | 2027-12-31 |  | 138 | 2.6 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  |  | 8295, 8641, 8646, 8801, 80230 | Y |  |  |  | 73066 | 73065
78461A | West Columbia to Damon and Needville to Big Creek Ckt.89A Upgrades | Rebuild/reconductor portions of West Columbia to Damon Ckt.89A as a Hardening upgrade. |  | West Columbia | Damon | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-12-31 |  | 138 | 0 | 6.6 | 0 |  | Brazoria | Brazoria | Tier 4 | 23RPG021 | 2023-08-10 | 2023-08-31 | 2023-08-31 | 42370, 43380, 49914 | Y | N |  |  | 78462 | 78461
91392 | Bergheim_Autotransformer_Upgrade | To improve efficiency and reliability of the transmission system, LCRA TSC will replace the existing Bergheim AT1 autotransformer with a higher capacity unit and install a second autotransformer at Bergheim Substation. |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-7662 | 2027-12-31 |  | 345 | 0 | 0 | 672 |  | Comal | Comal | Tier 3 |  |  |  |  | 7170, 7770, 7771, 7772, 70170, 70493 | Y |  |  |  | 91408 | 91392
70706 | Tungsten (Carbide): Rebuild 138/69 kV Station | Rehab the Tungsten (Carbide) 138/69 kV station | In-Service Date Update | Tungsten |  | Planned |  | AEP TCC | LaRissa Lundry deevans@aep.com 918-599-2938 |  | 2027-12-31 |  | 138 | 0 | 0 | 0 |  | Calhoun |  | Tier 4 | 21RPG024 | 2021-12-16 | 2022-01-18 |  | 5598, 8144, 8149, 8152, 8154, 8159, 8161, 8189, 8190, 8536, 8723, 80135, 110331, 110332, 110334, 110335, 110336 | Y |  |  |  | 78605 | 70706
76237 | Lobo: Construct New 345 kV Terminal | Interconnect Cuchillas Solar to the Lobo 345 kV station | Contact Update | Lobo |  | Planned |  | ETT | John Solis jlsolis@aep.com 361-881-5574 | TP2023320 | 2027-12-31 | 2025-06-01 | 345 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  |  | 80219 | Y |  |  |  | 76238 | 76237
91386 | Smithville_Substation_Upgrade | Increase the reliability of the Smithville substation by replacing assets identified as a high failure risk, removing the 138x69-kV auto transformer, and converting T344 New Rosanky - Smithville to 138-kV |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-7727 | 2027-12-31 |  | 138 | 0 | 0 | 0 |  | Bastrop | Bastrop | Tier 4 |  |  |  |  | 7314, 7315, 7558 | Y |  |  |  | 91387 | 91386
90035 | Edith Clarke to Seine BESS: Construct New 345 kV Line | Interconnect Seine BESS to the existing Edith Clarke 345 kV station | Cost Update | Edith Clarke | Seine BESS | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | TP2024193 | 2027-12-31 |  | 345 | 0.3 | 0 | 0 |  | Foard | Foard | Tier 4 | [5 empty] | Y | N |  |  | 91677 | 90035
73100 | Asherton to Piloncillo: Rebuild 138 kV Line | Rehab the Asherton to Piloncillo 138 kV line |  | Asherton | Piloncillo | Planned | TA2021030 | AEP TCC | William Simmons jlsolis@aep.com 361-881-5574 |  | 2027-12-31 | 2958101 | 138 | 0 | 13.43 | 0 |  | Dimmit | Dimmit | Tier 4 |  |  |  |  | 8283, 8970, 80481 | Y |  |  |  | 73101 | 73100
75780B | Loop new Elmaton substation into Ckt.39A to create new Ckt.39 STP to Elmaton to WA Parish. Install generator lead from Elmaton (ELM) substation to DUFFY (DUF) / Duffy Solar (23INR0057) | Install generator lead from Elmaton (ELM) substation to DUFFY (DUF) / Duffy Solar (23INR0057) |  | Elmaton | DUFFY | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-12-31 00:01 |  | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 43990, 114361 | Y | N |  |  | 87169 | 75780
72059 | Hillje 345kV Substation Expansion for Ramsey Storage - Generator Interconnection to FLATLA (FLA) (21INR0505) | Expand Hillje 345kV substation and install one generator lead for new interconnection to FLATLA (FLA) customer substation for Ramsey Storage |  | Hillje |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-12-31 00:01 |  | 345 | 0 | 0 | 0 |  | Wharton |  | Tier 4 |  |  |  |  | 44200, 113595 | Y | N |  |  | 90911 | 72059
87092 | Arcadia to Southside: Upgrade 138 kV Line | Upgrade the Arcadia to Southside 138 kV line | Contact Update | Arcadia | Southside | Planned | 994 - 1172 | AEP TCC | Craig Tabor deevans@aep.com 918-599-2938 | 3747 TP-2019-065 | 2028-01-30 |  | 138 | 0 | 2.59 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 8483, 8486, 8496, 8609, 8617, 8618 | Y | N |  |  | 87093 | 87092
45566 | Holly to Southside: Upgrade 138 kV Line | Upgrade the Holly to Southside 138 kV line | Contact Update | Holly | Southside | Planned | 994 - 1172 | AEP TCC | Craig Tabor deevans@aep.com 918-599-2938 | 3747 TP-2019-065 | 2028-01-30 |  | 138 | 0 | 1.8 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 8483, 8486 | Y | N |  |  | 65532 | 45566
64067 | Bessel to King Ranch: 138 kV Line Rebuild | Rehab the Bessel to King Ranch 138 kV line |  | Bessel | Stratton | Planned |  | AEP TCC | Robert Dougherty deevans@aep.com 918-599-2938 | TA2020081 | 2028-01-31 |  | 138 | 0 | 26.59 | 0 |  | Nueces | Kleberg | Tier 4 | 23RPG001 | 2023-01-25 | 2023-02-24 |  | 8060, 8498, 8512, 8514, 8665, 80228 | Y |  |  |  | 64068 | 64067
80970 | Joule: Construct New 345 kV Station | Interconnect Zeissel Solar and Storage to the new Joule 345 kV station on the Clear Crossing to Coulomb 345 kV line | Contact Update | Joule |  | Planned | TP2024020 | ETT | Brandon Clarke twang1@aep.com 918-599-2635 |  | 2028-02-28 |  | 345 | 0 | 0 | 0 |  | Knox |  | Tier 4 |  |  |  |  | 60094, 60702, 60722 | Y | Y |  |  | 80971 | 80970
55626 | Ganso to Hamilton Road: Rebuild 138 kV line | Rebuild 138 kV line from Ganso to Hamilton Road |  | Maverick | Hamilton Road | Planned | 1105 - 1283 | AEP TCC | Jeremy Brazeal jlsolis@aep.com 361-881-5574 | 3824 | 2028-02-28 |  | 138 | 0 | 41.1 | 0 |  | Maverick | Val Verde | Tier 3 | 22RPG044 | 2022-12-15 | 2023-01-17 |  | 8255, 8267, 8692 | Y |  |  |  | 65576 | 55626
55624 | Escondido to Ganso: Rebuild 138 kV line | Rebuild 138 kV line from Escondido to Ganso | Contact Update | Escondido | Ganso | Planned | 1105 - 1283 | AEP TCC | Jeremy Brazeal jlsolis@aep.com 361-881-5574 | 3825 | 2028-02-28 |  | 138 | 0 | 10.198 | 0 |  | Maverick | Maverick | Tier 4 |  |  |  |  | 8260, 8267 | Y |  |  |  | 65575 | 55624
91744A | New 138kV CEHE Station Grassland for OCI SunRoper (24INR0257) | Loop new Grassland CEHE 138kV substation into Ckt.60D Dyann to South Lane City to create new Ckt.60 Dyann to Grassland to South Lane City. |  | Grassland | Dyann/South Lane City | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2028-02-29 |  | 138 | 0 | 0 | 0 |  | Wharton | Wharton | Tier 4 |  |  |  |  | 42730, 42985, 43190 | Y | N |  |  | 92897 | 91744
91744B | New 138kV CEHE Station Grassland for OCI SunRoper (24INR0257) | Install one generator lead from Grassland CEHE 138kV substation to SUNROP/ OCI SunRoper |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2028-02-29 |  | 138 | 0 | 0 | 0 |  | Wharton |  | Tier 4 | [5 empty] | Y |  |  |  | 92898 | 91744
91394 | Mendoza_Substation_Upgrade | Increase the transformation capacity at Mendoza Substation by installing an additional power transformer and upgrade the existing bus configuration to an improved bus arrangement. |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-8202 | 2028-03-07 |  | 138 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  |  | 7325 | Y |  |  |  | 91395 | 91394
80330 |  |  |  | DWU Southside | McCree | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2028-03-15 |  | 69 | 0 | 7.45 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 230, 832 | Y |  |  |  | 80331 | 80330 | 2023-NC24
80334 |  |  |  | CONCORD | WILDCAT TAP | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2028-03-15 |  | 138 | 0 | 4.9 | 0 |  | Johnson | Johnson | Tier 4 |  |  |  |  | 388, 394 | Y |  |  |  | 80335 | 80334 | 2023-NC25
80327 | RTP projects included the addition of 18.4 MVAR capacitor at Whitesboro SW | RTP projects included the addition of 18.4 MVAR capacitor at Whitesboro SW |  | Whitesboro SW | Whitesboro SW | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2028-03-15 |  | 138 | 0 | 0 | 0 | 0,18.4 | Grayson | Grayson | Tier 4 |  |  |  |  | 718 | Y |  |  |  | 80328 | 80327 | 2023-N14
51001 | Friess Ranch to Sonora: Rebuild 69 kV line | Rehab Rocksprings to Sonora 69 kV line |  | Friess Ranch | Sonora | Planned | 1044 - 1217 | AEP TNC/AEP TCC | Greg Crane twang1@aep.com 918-599-2635 | 2791 | 2028-03-31 12:00 |  | 69 | 0 | 24.3 | 0 |  | Sutton | Sutton | Tier 3 | 19RPG018 | 2019-10-24 | 2019-11-18 |  | 6513, 6570, 8238, 8239, 60210, 60438 | Y | N |  |  | 65554 | 51001
91174 | Upgrade Eustace-Walton line to Cumberland conductor | Upgrade Eustace-Walton line to Cumberland conductor |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2028-05-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 6899, 6951 | Y |  |  |  | 91175 | 91174
88049 | Loop in Cagnon to Howard into Omicron |  |  |  |  | Planned | T-0394 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2028-05-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 2 |  |  |  |  | 5054, 5230, 5326 | Y |  |  |  | 88050 | 88049
76107 | City of Robstown Capacitor | Add a new cap bank at City of Robstown sub with 2 9.6 MVAR steps |  | City of Robstown |  | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2028-05-01 |  | 69 | 0 | 0 | 0 | 0,19.2 |  |  | Tier 4 |  |  |  |  | 5630 | N | N |  |  | 76108 | 76107
76786 | Upgrade Calallen- Loyola | Upgrade Calallen- Robstown - CC Sw- Driscol-Ricardo-Riviera-Loyola to 959.6 ACSS |  | Calallen | Loyola | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2028-05-01 |  | 69 | 0 | 46.57 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 5626, 5634, 5636, 5640, 5645, 5646, 5650 | Y |  |  |  | 76787 | 76786
76768 | Upgrade Pearson -Pearsall | Upgrade the Pearson-Natalia-Devine-Moore-Pearsall to 795 ACSR |  | Pearson | Pearsall | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2028-05-01 |  | 69 | 0 | 34.62 | 0 |  | Frio | Medina | Tier 4 |  |  |  |  | 5811, 5828, 5830, 5857, 5858, 5893, 58570 | Y |  |  |  | 76769 | 76768
45125 | Quintana Rd to South San Rebuild | Rebuild 1.3 miles of 138 kV transmission line form Quintana Rd substation to South San substation. |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | T-0271 | 2028-05-01 |  | 138 | 0 | 1.29 | 0 |  | Bexar | Bexar | Tier 4 |  | 2019-01-15 |  |  | 5350, 5385 | Y |  |  |  | 45126 | 45125
91312A | Austrop - Zorn Transmission Line Upgrade |  |  | 7040 | 7048 |  |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG | PLC-8063, PLC-8139, PLC-8140 | 2028-05-15 |  | 345 | 0 | 16.8 | 0 |  | Travis | Bastrop | Tier 1 |  |  |  |  | 7040, 7042, 7048 | Y |  |  |  | 91313 | 91312 | 2024-SC19
73762 | Peppergrass Substation Addition | American Electric Power (AEP) is building a new load serving substation and needs transmission service from the LCRA TSC owned 138-kV T470 Abilene South to McElmurray transmission line. LCRA TSC will install a new 138-kV bus and provide transmission service to the new AEP substation. |  | Peppergrass |  | Planned |  | LCRATSC | Dylan PReas dylan.preas@lcra.org | PLC-4477 | 2028-05-15 |  | 138 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  |  | 6260, 76316, 76317 | Y | N |  |  | 73763 | 73762
87701 | Establish the Watercrest 138 kV Switch | Establish the Watercrest 138 kV Switch |  | Watercrest | Watercrest | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6353 | 2028-05-15 |  | 138 | 0 | 0 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 3626, 3627, 3744, 13628 | Y |  |  |  | 87702 | 87701 | 2023-NC57
92602 | Bastrop West - Bluebonnet Transmission Line Upgrade | Overhaul transmission line structures per LCRA TSC standards and current NESC requirements. Replace existing conductor with bundled-Suwannee. |  | 7555 | 7556 | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org | PLC-8101 | 2028-05-15 |  | 138 | 0 | 6.1 | 0 |  | Bastrop | Bastrop | Tier 4 |  |  |  |  | 7555, 7556, 7561 | Y |  |  |  | 92603 | 92602 | 2024-SC20
92572 | Lockhart Mendoza Transmission Line Overhaul | Overhaul transmission line structures per LCRA TSC standards and current NESC requirements. Replace existing conductor with bundled-Suwannee |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-8191 | 2028-05-15 |  | 138 | 0 | 0 | 0 |  | Caldwell | Caldwell | Tier 4 |  |  |  |  | 7206, 7215, 7216, 7325 | Y |  |  |  | 92573 | 92572 | 2024-SC20
81225 | Cattleman - Range Rider 138 kV Double-Circuit Line | Construct a new 138 kV double-circuit line from Cattleman to Range Rider Switch |  | Cattleman | Range Rider | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8722 | 2028-05-15 |  | 345 | 0 | 6.6 | 0 |  | Mitchell | Mitchell | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1032, 10054 | Y |  |  |  | 81226 | 81225
91628 | Upgrading Buda to Rutherford | Upgrading Buda to Rutherford branch to minimum 379 MVA. | [5 empty] | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2028-05-15 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 70498, 70509 | Y |  |  |  | 91629 | 91628
91312B | Austrop - Zorn Transmission Line Upgrade |  |  | 7048 | 9074 |  |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG | PLC-8063, PLC-8139, PLC-8140 | 2028-05-15 |  | 345 | 0 | 24.7 | 0 |  | Bastrop | Caldwell | Tier 1 |  |  |  |  | 7040, 7042, 7048, 9074 | Y |  |  |  | 91314 | 91312 | 2024-SC19
73570 | Steger Substation Addition | Substation addition to provide Point of Interconnection for Oncor New Sweden substation addition. |  | Steger |  | Conceptual |  | LCRATSC | Dylan PReas dylan.preas@lcra.org 512-578-4514 |  | 2028-05-15 |  | 138 | 0 | 0 | 0 |  | Travis |  | Tier 4 |  |  |  |  | 7336, 7337, 7339 | Y | N |  |  | 73571 | 73570
66023 | T340 T-Line Upgrade | Upgrading the Marion to Sheriff's Posse Transmission Line T340 from 795 ACSR to 959 ACSS conductor. Upgrades to conductor and structures are included. Structures designed for ultimate build-out of double-circuit bundled 959 ACSS in preparation for additional future capacity. |  | Marion | Sheriff's Posse | Planned |  | NBU | Jeff Morriss jmorriss@nbutexas.com 830-608-8881 |  | 2028-05-15 |  | 138 | 0 | 3.4 | 0 |  | Guadalupe | Comal | Tier 4 |  |  |  |  | 7178, 7460 | Y | N |  |  | 78403 | 66023
17TPIT0001 | 36th St to Merida - 138 kV Transmission Line Rebuild | Rebuild approximately four circuit miles of 138 kV transmission from 36th Street to Merida |  | 36th Street | Merida | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | T-0196 | 2028-05-15 |  | 138 | 0 | 4 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5310, 5427 | Y | N |  | There are no transformers associated with this project | 9559 | 2308
93679 | New BPUB substation |  |  | Loma Alta/CRONUS | NIMZO | Planned |  | BPUB | Luis Martinez lugmartinez@brownsville-pub.com 956-983-6212 |  | 2028-05-25 |  | 138 | 24 | 0 | 0 |  |  |  | Tier 2 |  |  |  |  | 5962, 59551 | Y |  |  |  | 93680 | 93679
93250B | Utley_Substation_and_Transmission_Line_Addition |  |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-8065 | 2028-05-31 |  | 138 | 0 | 0 | 0 |  | Bastrop | Bastrop | Tier 3 |  |  |  |  | 7310, 7316, 7327 | Y |  |  |  | 93252 | 93250
93224 | Eastpoint: Construct New Distribution Station | Construct new distribution station on the North Laredo Switch to Wormser Road 138 kV line between Gateway West Tap and Unitec |  | Eastpoint |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2028-05-31 |  | 138 | 7.2 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  |  | 8080, 8134, 8650 | Y |  |  |  | 93225 | 93224
91896 | La Palma to Military Highway: Rebuild 138 kV Line | Rebuild the La Palma to Military Highway 138 kV line | NEW | La Palma | Military Highway | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 | TP2025011 | 2028-05-31 |  | 138 | 0 | 22.2 | 0 |  | Cameron | Cameron | Tier 1 | 24RPG008 | 2025-03-24 | 2025-09-24 | 2025-12-24 | 8314, 8339, 80229 | Y |  |  |  | 91897 | 91896
91883 | La Palma to Stillman: Rebuild 138 kV Line | Rebuild the La Palma to Stillman 138 kV line | NEW | La Palma | Stillman | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 | TP2025011 | 2028-05-31 |  | 138 | 0 | 22.3 | 0 |  | Cameron | Cameron | Tier 1 | 24RPG008 | 2024-03-07 | 2024-09-27 | 2024-12-03 | 8314, 8333, 79601 | Y |  |  |  | 91884 | 91883
90027 | Cross Plains to Rising Star: Rebuild 69 kV Line | Rehab the Cross Plains to Rising Star 69 kV line | NEW | Cross Plains | Rising Star | Planned | TA2024101 | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 |  | 2028-05-31 |  | 69 | 0 | 12.96 | 0 |  | Callahan | Eastland | Tier 4 |  |  |  |  | 6357, 6358 | Y | N |  |  | 92899 | 90027
91621 | Adding Highway 71 between Wirtz and Johnson city | Adding highway 71 into the model Summer 2028 | [5 empty] | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2028-06-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 7104, 70003, 70516 | Y |  |  |  | 91622 | 91621
80420 |  | Rebuild / Reconductor Greens Prairie to South Switch 138kV Line |  | Bryn South Switch | Greens Pairie | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2028-06-01 |  | 138 | 0 | 4.5 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  |  | 32007, 32878, 32880, 32893 | Y |  |  |  | 80421 | 80420
81588 | Chalybe: Expand 345 kV Station | Interconnect the Delta load to the Chalybe 345 kV station on the Chalybe to Kingfisher and Chalybe to Palmito 345 kV lines | NEW | Chalybe |  | Conceptual |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2028-06-01 |  | 345 | 46 | 0 | 1350 |  | Cameron |  | Tier 4 |  |  |  |  | 8735, 79500, 79501, 88337 | Y | N |  |  | 81589 | 81588
86240 | AEN_REPLACE_LYTTON__345kV_LYAT1_and_LYAT2_AUTOS_WITH__New_672_MVAs | Replace the two existing 345kV Lytton Autos with two new 672 MVA/345kV autos |  | Lytton 9074 | Lytton 9075 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2028-06-01 |  | 345 | 0 | 0 | 762 |  | Caldwell | Caldwell | Tier 4 |  |  |  |  | 9074, 9075, 9078, 9081 | Y |  |  |  | 86241 | 86240
71408 | Upgrade CKT943 to 3000 amperes | Replace existing 2-795ACSR conductors with 2-795 ACSS conductors and the upgrade the terminal equipment to 3000 amperes. |  | Lytton Springs | Pilot Knob | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2028-06-01 |  | 138 | 0 | 11.13 | 0 |  | Caldwell | Travis | Tier 4 |  |  |  |  | 9075, 9259 | Y |  |  |  | 71409 | 71408
14TPIT0038 | Northland to Mag Plant Circuit 979 Upgrade | Reconductor the existing Northland to Mag Plant circuit from single 795SCAR to bundle 795 ACSR Drake and increase rating to 3000 Amp |  | Northland Substation | Mag Plant Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | NEW | 2028-06-01 |  | 138 | 0 | 4.11 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9128, 9238 | Y | N |  | Will add the project to the base case | 9723 | 2443
86838 | AEN_JustinLane_KoenigLane_Ckt__conversion_to_138kV | Justin Lane Koenig Lane convert to 138kV |  | 9225 | 9227 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2028-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9225, 9227 | Y |  |  |  | 86839 | 86838
86315 | AEN_Barton_Vega_Ckt_928_Reconductor |  |  | 9158 | 9285 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2028-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9158, 9285 | Y |  |  |  | 86316 | 86315
81302 | Rockhound - Midland East 345 kV Line Rebuild | Rebuild the existing 345 kV line and add a second circuit to the new line |  | Rockhound | Midland East | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3025 | 2028-06-15 |  | 345 | 0 | 24.2 | 0 |  | Midland | Midland | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1021, 10062 | Y |  |  |  | 81303 | 81302
90029 | Dupont Switch to Dupont PP1 Circuit 2: Rebuild 138 kV Line | Rebuild the Dupont Switch to Dupont PP1 Circuit 2 138 kV line | NEW | Dupont Switch | Dupont PP1 | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 | TP2024138 | 2028-06-30 |  | 138 | 0 | 1.52 | 0 |  | San Patricio | San Patricio | Tier 4 | [5 empty] | Y |  |  |  | 90030 | 90029
90012 | Lumos: Construct New 345 kV Station | Interconnect Ross Solar & Storage to the new Lumos 345 kV station on the Angstrom to Static 345 kV line | CANCEL | Lumos |  | Planned |  | AEP TCC | Doug Evans deevans@aep.com 918-599-2938 | TP2024105 | 2028-06-30 |  | 345 | 0 | 0 | 0 |  | Refugio |  | Tier 4 |  |  |  |  | 8249, 8676, 80082 | Y | N |  |  | 90013 | 90012
90016 | Dupont Switch to Dupont PP1 Circuit 1: Rebuild 138 kV Line | Rebuild the Dupont Switch to Dupont PP1 Circuit 1 138 kV line | NEW | Dupont Switch | Dupont PP1 | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 | TP2024138 | 2028-06-30 |  | 138 | 0 | 1.46 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  |  | 8422, 8817, 8819 | Y |  |  |  | 90017 | 90016
90025 | Festin: Construct New 345 kV Station | Interconnect Sunscape Renewable Solar and Storage to the new Festin 345 kV station on the Lon Hill to Reforzar 345 kV line | NEW | Festin |  | Planned |  | AEP TCC | Doug Evans deevans@aep.com 918-599-2938 | TP2024111 | 2028-07-31 |  | 345 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 8455, 80078, 80085 | Y | N |  |  | 90026 | 90025
91623 |  |  |  | Lillian | Highpoint | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2028-09-01 |  | 138 |  | 5.5 | 0 |  | Johnson | Johnson | Tier 4 |  |  |  |  | 419, 439 | Y |  |  |  | 91624 | 91623
61224 | AEN_Decker_SH_ckt_1008__reconductor | Upgrade the 7.04 mile Decker to Sand Hill 138 kV transmission line (Ckt 1008) with bundled 795 ACSS Drake conductor rated for 3000 amps |  | Decker [9187] | Sandhill [9216] | Planned |  | AEN | Shirley Mathew shirley.mathew@austinener 512-322-6103 |  | 2028-09-01 |  | 138 | 0 | 7.04 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9187, 9216 | Y |  |  |  | 61225 | 61224
91615 |  |  |  | Concord | Crowley | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2028-09-01 |  | 138 | 0 | 9.3 | 0 |  | Johnson | Johnson | Tier 4 |  |  |  |  | 394, 398, 399 | Y |  |  |  | 91616 | 91615
66492D | Chico West - Grindstone Switch 69 kV Line rebuild | Upgrade Chico West - Chico City Services 69 kV Line |  | Chico City Services | Chico West | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3006 | 2028-09-15 |  | 69 | 0 | 6 | 0 |  | Jack | Jack | Tier 4 |  |  |  |  | 1553, 1554 | Y |  |  |  | 76368 | 66492
90043 | Kelvin to Eneus: Construct New 345 kV Line | Interconnect the new Eneus load station to the expanded Kelvin 345 kV station on the Gulch to La Palma 345 kV line | NEW | Kelvin | Eneus | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 | TP2024073 | 2028-09-30 |  | 345 | 1 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  |  | 8013, 8317, 8704, 80113 | Y |  |  |  | 90044 | 90043
91483 | New REC station cutting into Ray Raymond to Explorer line and new 12.35 mile from new REC station to Rand |  |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2028-10-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 2 |  |  |  |  | 6802, 6833, 6906, 6907 | Y |  |  |  | 91484 | 91483
93831 | New substation to replace Loma Alta |  |  | Stillman, Waterport, and also future Nimzo Substations | Cronus (Loma Alta) | Planned |  | BPUB | Luis Martinez lugmartinez@brownsville-pub.com 956-983-6212 |  | 2028-10-02 |  | 138 | 0 | 0 | 0 | 0,50 |  |  | Tier 3 |  |  |  |  | 5943, 5944, 5962, 59450, 59510, 59551, 79601 | Y |  |  |  | 93832 | 93831
76131 | Pendulo: Build New 345 kV terminal | Interconnect Inertia Solar and BESS 2 to the Pendulo 345 kV Station on the Clear Crossing to Smoky Hill line | Owner, Contact, and In-Service Date Update | Pendulo |  | Planned |  | ETT | Lance Price twang1@aep.com 918-599-2635 |  | 2028-10-31 |  | 345 | 0 | 0 | 0 |  | Haskell |  | Tier 4 |  |  |  |  | 60507 | Y | N |  |  | 76132 | 76131
90061 | Poisson: Construct New 345 kV Station | Interconnect Short Creek Solar to the new Poisson 345 kV station on the Riley to Fisher Road 345 kV line |  | Poisson |  | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | TP2024154 | 2028-10-31 |  | 345 | 0 | 0 | 0 |  | Wichita |  | Tier 4 |  |  |  |  | 1425, 6101, 60136 | Y | N |  |  | 91151 | 90061
70673 | Clairmont Sun Oil Tap: Rebuild 69 kV Line | Rehab Clairmont Sun Oil Tap 69 kV Line | Contact and In-Service Date Update | Clairmont | Sun Clairmont | Planned |  | AEP TNC | Dewey Peters twang1@aep.com 918-599-2635 | TA2021233 | 2028-10-31 |  | 69 | 0 | 0 | 0 |  | Kent | Kent | Tier 4 |  |  |  |  | 6197, 6198 | Y |  |  |  | 70674 | 70673
5889 | MIRAGE - 138kV Substation Removal | Remove 138kV MIRAGE customer-owned substation from CEHE service. |  | MIRAGE | MCCABE/BIMONT | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2028-10-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40200, 40209, 42351, 42360 | N | N |  |  | 13606 | 5889
55617 | Campwood to Rocksprings: Rebuild 69 kV Line | Rebuild the Campwood to Rocksprings 69 kV line | Contact Update | Campwood | Rocksprings | Planned | 1102 - 1280 | AEP TCC | Greg Crane jlsolis@aep.com 361-881-5574 | 3820 | 2028-11-30 |  | 69 | 0 | 27.2 | 0 |  | Edwards | Edwards | Tier 4 | 24RPG009 | 2024-03-21 | 2024-04-12 |  | 8365, 8633 | Y |  |  |  | 65573 | 55617
69277 | Cangrejo to Carbide: Rebuild 138 kV Line | Rebuild 138 kV Line from Cangrejo to Carbide |  | Cangrejo | Carbide | Planned |  | AEP TCC | Lorraine Timmerman mlforcum@aep.com 918-599-2674 |  | 2028-11-30 |  | 138 | 0 | 11 | 0 |  | Calhoun | Calhoun | Tier 1 | 21RPG002 | 2021-02-01 | 2021-09-16 | 2021-10-22 | 8140, 8155, 8190, 8723 | Y |  |  |  | 69278 | 69277
55470 | Bison to Ozona: Rebuild 69 kV Line | Rehab 69 kV line from Bison to Ozona |  | Bison | Ozona | Planned | 1095 - 1273 | AEP TNC | Robert Younger twang1@aep.com 918-599-2635 | 1863 | 2028-11-30 |  | 69 | 0 | 27 | 0 |  | Reagan | Crockett | Tier 4 |  |  |  |  | 6549, 6560, 60395 | Y | N |  |  | 65570 | 55470
50876 | Victoria to Port Lavaca: Retire 69 kV Line | Retire 69 kV Line on Victoria to Port Lavaca |  | Port Lavaca | Victoria | Planned | 1054 - 1227 | AEP TCC | Lorraine Timmerman mlforcum@aep.com 918-599-2674 | 3782 | 2028-11-30 |  | 69 | 0 | 29 | 0 |  | Calhoun | Victoria | Tier 1 | 21RPG002 | 2021-02-01 | 2021-09-16 | 2021-10-22 | 8135, 8136, 8169 | Y | N |  |  | 50877 | 50876
78545 | Brookhollow to Cangrejo: Rebuild 69 kV Line | Rebuild 69 kV line from Brookhollow to Cangrejo | Contact, In-Service Date, and RPG Update | Brookhollow | Cangrejo | Planned |  | AEP TCC | Lorraine Timmerman deevans@aep.com 918-599-2938 |  | 2028-11-30 |  | 69 | 0 | 2.15 | 0 |  | Calhoun | Calhoun | Tier 1 | 21RPG002 | 2021-02-01 | 2021-09-16 | 2021-10-22 | 8133, 8135, 8720, 8723, 8756, 88133 | Y |  |  |  | 78546 | 78545 | 2019-C2
55605 | Rebuild 69 kV line from Campwood to Rocksprings | New Barksdale to Rocksprings: Rebuild 69 kV line | RPG Update | New Barksdale | Rocksprings | Planned | 1102 - 1280 | AEP TCC | Greg Crane jlsolis@aep.com 361-881-5574 | 3819 | 2028-11-30 |  | 69 | 0 | 19.51 | 0 |  | Edwards | Edwards | Tier 3 | 24RPG009 | 2024-03-21 | 2024-04-12 |  | 8238, 8365 | Y |  |  |  | 65572 | 55605
92354 | Wren: Construct New 345 kV Station | Interconnect the Eolic load to the new Baltic 345 kV station on the Gulch to Kelvin 345 kV line | NEW | Wren |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 | TP2025127 | 2028-11-30 |  | 345 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  |  | 8013, 8704, 8759 | Y | N |  |  | 92355 | 92354
76696 | Construct a new Border - Shifting Sands 138 kV Line | Construct a new Border – Shifting Sands 138 kV Line |  | Atchison | Shifting Sands | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8628 | 2028-12-01 |  | 138 | 64.6 | 0 | 0 |  | Loving | Winkler | Tier 2 |  |  |  |  | 1074, 10157, 11089, 11391, 18672, 18705 | Y |  |  |  | 92338 | 76696
3818 | Rebuild Calallen to Robstown | Rebuild 4-0 ACSR 69 kV to higher rated and 138 kV capable line, as originally recommended in 2013 RTP. |  | Calallen | Robstown | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2028-12-01 |  | 69 | 0 | 6.26 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 5626, 5634 | Y | N |  |  | 11275 | 3818 | 2014-S2
84902 | Rebuild Spruce to Pawnee into a double circuit |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2028-12-01 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  |  | 5400, 5725 | Y |  |  |  | 84903 | 84902
71910C | Rebuild the Hillsboro - Elm Mott 69 kV Line | Rebuild the Abbott - Hillsboro Switch 69 kV Line |  | Abbott 69 kV Substation | Hillsboro 69 kV Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6221 | 2028-12-15 |  | 69 | 0 | 10.1 | 0 |  | Hill | Hill | Tier 3 |  |  |  |  | 3523, 3524, 3525, 13525 | Y |  |  |  | 91607 | 71910
89918 | GVEC Gonzales substation | Rebuild existing substation, 138 kV bus, new PWT, new Control House, new HV and LV structures, containment foundations, bus, panels, etc |  | Gonzales |  |  |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2028-12-15 | 2958101 | 138 | 0 | 0 | 0 |  | Gonzales | Gonzales | Tier 4 | [5 empty] | Y |  |  |  | 89919 | 89918
87705 | Pepper Creek - Temple Elm Creek 138 kV Double-Circuit Line | Reconductor the Pepper Creek - Temple Elm Creek 138 kV Double-Circuit Line |  | Pepper Creek | Temple Elm Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6198 | 2028-12-15 |  | 138 | 0 | 6.2 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 3484, 3608, 13608, 13662 | Y |  |  |  | 87706 | 87705 | 2023-NC51
87703 | Belton - Killeen 138 kV Line via Nolanville | Reconductor the Belton - Killeen 138 kV Line via Nolanville |  | Belton | Killeen | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6347 | 2028-12-15 |  | 138 | 0 | 24.8 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 3366, 3423, 3429, 3444, 3610, 3616, 3617, 3618, 3619, 13426, 13427 | Y |  |  |  | 87704 | 87703 | 2023-NC22, 2023-NC36, 2023-NC50
87711 | Watercrest - Killeen 138 kV Line | Upgrade the Watercrest - Killeen 138 kV Line |  | Watercrest | Killeen | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6355 | 2028-12-15 |  | 138 | 0 | 7 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 3423, 3428, 13628 | Y |  |  |  | 87712 | 87711
87709 | Belton - Temple 138 kV Line | Rebuild the Belton - Temple 138 kV Line |  | Belton | Temple | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6199 | 2028-12-15 |  | 138 | 0 | 9.6 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 3415, 3602, 3610, 3611, 3612 | Y |  |  |  | 87710 | 87709 | 2023-NC5, 2023-NC17
87695 | Establish a new Oncor-owned Bell County 138 kV Switch | Establish a new Oncor-owned Bell County 138 kV Switch |  | Bell County | Bell County | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6363 | 2028-12-15 |  | 138 | 0 | 0 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 132, 3493, 3598, 3640 | Y |  |  |  | 87696 | 87695
81240 | Consavvy – Odessa EHV 345 kV Double Circuit Line Rebuild | Rebuild the existing 345 kV Double-Circuit Line |  | Consavvy | Odessa EHV | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3027 | 2028-12-15 |  | 345 | 0 | 40 | 0 |  | Midland | Ector | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1125, 11016, 11028, 11387, 18540, 18548 | Y |  |  |  | 81241 | 81240
81268 | Longshore – Consavvy 345 kV Double-Circuit Line Rebuild | Rebuild existing 345 kV Double-Circuit Line |  | Cattleman | Longshore | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3027 | 2028-12-16 |  | 345 | 0 | 66.8 | 0 |  | Howard | Midland | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1058, 11387, 18548 | Y |  |  |  | 81388 | 81268
87697 | Bell County - Poage - Seaton 69 kV Line Conversion to 138 kV | Bell County - Poage - Seaton 69 kV Line Conversion to 138 kV |  | Bell County | Seaton | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6367 | 2028-12-16 |  | 138 | 0 | 17.8 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 126, 130, 131, 133, 3598, 3636, 3735, 33126 | Y |  |  |  | 87698 | 87697
87648 | Carver to Poblano: Convert 69 kV Line to 138 kV | Convert the Sonora to Uvalde 69 kV line to 138 kV and reterminate at Carver and Poblano | Contact Update | Carver | Poblano | Planned |  | AEP TCC/AEP TNC, ETT | Charity Kreher deevans@aep.com 918-599-2938 | TP2024058 | 2028-12-29 |  | 138 | 1 | 107.5 | 0 |  | Sutton | Uvalde | Tier 4 | 24RPG009 | 2024-03-21 | 2024-04-12 |  | 6513, 6570, 8009, 8230, 8231, 8238, 8365, 8633, 60039, 60119, 60120, 60121, 60210, 60412, 80073, 80074, 80075, 80081 | Y | Y |  |  | 87649 | 87648
85953 | Camp Wood - Leakey Transmission Line Conversion | LCRATSC will perform a voltage conversion on Camp Wood – Leakey (T269) 69-kV transmission line. This project will increase the reliability of transmission facilities by converting the substation equipment at Camp Wood and Leakey substation to operate at 138-kV. |  | Bandera 7438 | Leakey 7426 | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2028-12-30 | 2958101 | 138 | 0 | 0 | 0 |  | Bandera | Real | Tier 4 | 24RPG009 | 2024-03-21 | 2024-04-12 |  | 7426, 7428, 7438, 7439, 7440, 8633, 80074 | Y |  |  |  | 87789 | 85953 | 2023-W14
91487A | Austrop - Sim Gideon Transmission Line Upgrade |  |  |  |  | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 | PLC-8100 | 2028-12-31 |  | 138 | 0 | 0 | 0 |  | Travis | Bastrop | Tier 4 |  |  |  |  | 7310, 7322, 7327, 7328, 7329, 9328 | Y |  |  |  | 91488 | 91487
55217 | Putnam to Leon: Rebuild 138 kV line | Rehab the Putnam to Leon (Oncor) 138 kV line | In-Service Date Update | Putnam | Leon | Planned | 1042 - 1269 | AEP TNC | LaRissa Lundry twang1@aep.com 918-599-2635 | 1859 | 2028-12-31 |  | 138 | 0 | 20.81 | 0 |  | Callahan | Eastland | Tier 4 |  |  |  |  | 1624, 6310 | Y | N |  |  | 55218 | 55217
59394 | Pointer to Rule: Rebuild 69 kV Line | Rehab the Pointer to Rule 69 kV Line |  | Pointer | Rule | Planned | 1122 - 1300 | AEP TNC | Dewey Peters twang1@aep.com 918-599-2635 | 1867 | 2028-12-31 |  | 69 | 0 | 14.78 | 0 |  | Haskell | Knox | Tier 4 |  |  |  |  | 763, 6014, 6115, 6120, 60346 | Y | N |  |  | 59395 | 59394
45015 | Barnhart to Cassava: Rebuild 69 kV line | Rebuild the Barnhart to Cassava 69 kV line |  | Barnhart | Cassava | Planned | 942 - 1120 | AEP TNC | LaRissa Lundry twang1@aep.com 918-599-2635 | 2756 | 2028-12-31 01:00 |  | 69 | 0 | 6.021 | 0 |  | Irion | Irion | Tier 4 |  |  |  |  | 6530, 6532, 6537, 60359 | Y | N |  |  | 65525 | 45015
91487B | Austrop - Sim Gideon Transmission Line Upgrade |  |  |  |  | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 | PLC-8100 | 2029-01-01 |  | 138 | 0 | 0 | 0 |  | Travis | Bastrop | Tier 4 |  |  |  |  | 7310, 7316, 7320, 7327, 7329 | Y |  |  |  | 93482 | 91487
76133 | West Childress: Station Rehab | Rehab the West Childress station |  | West Childress |  | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | TA2020223 | 2029-01-31 |  | 138 | 0 | 0 | 0 |  | Childress |  | Tier 4 |  |  |  |  | 6030, 6135 | Y | N |  |  | 76134 | 76133
73116 | Install new Cedar Port Mobile (CDM) 138kV Distribution Substation | Install new Cedar Port Mobile (CDM) 138kV Distribution Substation. Loop from existing Ckt.03B to create new Ckt.03B Trinity Bay to Cedar Port Mobile to KENNY tap. |  | Cedar Port Mobile | Trinity | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2029-01-31 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  |  | 40921, 41610, 48360 | N | N |  |  | 73120 | 73116
50645 | CPSE_Rafter 138kV Cap Bank | [6 empty] | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2029-01-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5355 | Y |  |  |  | 50646 | 50645
86802 | Saragosa: Construct New 138 kV Terminal | Interconnect Cantaloupe Solar to the Saragosa 138 kV station | Project Description and Contact Update | Saragosa |  | Planned | TP2024067 | AEP TNC | Damian Raab twang1@aep.com 918-599-2635 |  | 2029-02-28 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  |  | 60716 | Y | N |  |  | 86803 | 86802
86884 | Saragosa: Construct New 138 kV Terminal | Interconnect Bracero Pecan Storage to the Saragosa 138 kV station | Contact and In-Service Date Update | Saragosa | Bracero Pecan | Planned | TP2024091 | AEP TNC | Nathan Cowan twang1@aep.com 918-599-2635 |  | 2029-02-28 |  | 138 | 0.5 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  | 2024-03-21 | 2024-04-12 |  | 60716 | Y | N |  |  | 86885 | 86884
80346 |  |  |  | SANDY SWITCH | CRUTCHFIELD | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2029-03-15 |  | 138 | 0 | 3.2 | 0 |  | Grimes | Grimes | Tier 4 |  |  |  |  | 5, 8 | Y |  |  |  | 80347 | 80346
80373 |  |  |  | IOLA | CRUTCHFIELD | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2029-03-15 |  | 138 | 0 | 5.5 | 0 |  | Grimes | Grimes | Tier 4 |  |  |  |  | 4, 8 | Y |  |  |  | 80374 | 80373
80579 | La Palma to Stewart Road: Convert to 138 kV | Convert the La Palma to Stewart Road 69 kV line to 138 kV | Contact Update | La Palma | Stewart Road | Planned | TA2020071 | AEP TCC | Robert Younger deevans@aep.com 918-599-2938 |  | 2029-03-30 |  | 138 | 0 | 37.5 | 0 |  | Cameron | Hidalgo | Tier 3 | 23RPG005 | 2023-03-01 | 2023-03-23 |  | 5778, 8040, 8310, 8314, 8701, 8703, 8748, 8751, 8949, 8951, 80104, 80229 | Y | N |  |  | 80580 | 80579
91562 |  |  |  | Gainesville | Sivells Bend | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2029-04-01 |  | 138 | 0 | 7.3 | 0 |  | Cooke | Cooke | Tier 4 |  |  |  |  | 716, 719, 721, 725, 726, 727, 735, 11722, 33726 | Y |  |  |  | 91563 | 91562
90000 | Upgrade San Diego - Orange Grove SW | Upgrade San Diego - Orange Grove SW to 795 ACSR. 2024 RTP |  | San Diego | Orange Grove SW | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2029-05-01 |  | 69 | 0 | 21.56 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 5654, 5658 | Y |  |  |  | 90001 | 90000
89991 | Upgrade Sargent - Bay City | Upgrade Sargent - Bay City line to 795ACSR. 2024 RTP |  | Sargent | Bay City | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2029-05-01 |  | 69 | 0 | 18.5 | 0 |  | Matagorda |  | Tier 4 |  |  |  |  | 5560, 5564 | Y |  |  |  | 89992 | 89991
91567 |  |  |  | New station Rhew | New station Rhew | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2029-05-01 |  | 345 | 0 | 0 | 0 |  | Wilson | Wilson | Tier 4 |  |  |  |  | 3, 5133, 5901 | Y |  |  |  | 91568 | 91567
90022 | Upgrade Sam Rayburn to Warburton | Upgrade Sam Rayburn to Warburton to 795 ACSR conductor. 2024 RTP. |  | Sam Rayburn | Warburton | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2029-05-01 |  | 69 | 0 | 22.63 | 0 |  | Victoria | Victoria | Tier 4 |  |  |  |  | 5500, 5605, 5606 | Y |  |  |  | 90023 | 90022
92734 | Construct Clearfork - Drill Hole 345 kV DCKT Line | Construct Clearfork - Drill Hole 345 kV DCKT Line |  | Clearfork | Drill Hole | Planned | R8792 R8801 R8802 R8803 | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2029-05-01 |  | 345 | 196.8 | 0 | 0 |  | Andrews | Culberson | Tier 1 |  |  |  |  | 10073, 18718, 23876 | Y |  |  |  | 92735 | 92734
91312C | Austrop - Zorn Transmission Line Upgrade |  |  | 9074 | 7042 |  |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG | PLC-8063, PLC-8139, PLC-8140 | 2029-05-15 |  | 345 | 0 | 46.2 | 0 |  | Caldwell | Guadalupe | Tier 1 |  |  |  |  | 7040, 7042, 9074 | Y |  |  |  | 91315 | 91312 | 2024-SC19
93306 | Bastrop_Mesquite_Utley_Transmission_Line_Addition | Provide looped transmission service for BBEC-member load at 138-kV Utley Substation |  | 7320 | 7317 | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2029-05-15 |  | 138 | 0 | 0 | 0 |  | Bastrop | Bastrop | Tier 3 |  |  |  |  | 7317, 7320 | Y |  |  |  | 93307 | 93306
12TPIT0004 | Sulpher Springs - New 138kV Substation | Loop new 138kV substation into the existing 138kV OW Sommers to Kirby line |  | Sulpher Springs | OW Sommers-Kirby | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0385 | 2029-05-15 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5250, 5395, 5416 | Y | N |  | There are no transformers associated with this project | 10365 | 3021
81551 | Dos Rios 138 kV Switch | Establish Dos Rios 138 kV Switch |  | Dos Rios Switch | Dos Rios Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6231 | 2029-05-15 |  | 138 | 0 | 0 | 0 |  | Milam | Milam | Tier 4 |  |  |  |  | 32, 3707, 3725 | Y |  |  |  | 81552 | 81551
93661 | New BPUB substation needed to service new load. Will require 6 miles of 138kV transmission line. |  |  | Nimzo | DEMETER | Planned |  | BPUB | Luis Martinez lugmartinez@brownsville-pub.com 956-983-6212 |  | 2029-05-29 |  | 138 | 12 | 0 | 0 |  |  |  | Tier 2 |  |  |  |  | 59551, 59555 | Y |  |  |  | 93662 | 93661
72051 | Twinwood Mobile (TWM) 138kV Distribution Substation | Install new Twinwood Mobile (TWM) 138kV Distribution Substation. Loop from existing Ckt.25E to create new Ckt.25E Foster to Twinwood Mobile to Peters |  | Twinwood | Foster | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2029-05-30 |  | 138 | 0 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 4 |  |  |  |  | 44256, 44861, 46220 | N | N |  |  | 72052 | 72051
91903 | Iowa: Construct New Distribution Station | Construct new distribution station on the Bates to Liston 138 kV line | NEW | Iowa |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2029-05-30 |  | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  |  | 8392, 8394, 80180 | Y | N |  |  | 91904 | 91903
54120 | Rebuild Tejas-Commanche (Bundled 795 ACSS) | Rebuild Tejas - Commanche 138 kV line with Bundled 795 ACSS conductor. |  | Tejas 138 kV Substation (Bus # 38530) | Commanche 138 kV Substation (Bus # 38560) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 | STE07318 | 2029-05-31 |  | 138 | 0 | 0.95 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 38530, 38560 | Y |  |  |  | 54121 | 54120
76348 | Reconductor Foxtail-PIGCreek-1926ACSS-138KV |  |  | Foxtail | PIG Creek | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2029-05-31 |  | 138 | 0 | 0.68 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  |  | 38294, 60393 | Y |  |  |  | 76349 | 76348
70796 | El Campo to Corichi: Rebuild 138 kV Line | Rehab the El Campo to Corichi 138 kV line |  | El Campo | Corichi | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 | TA2018020 | 2029-05-31 |  | 138 | 0 | 13.26 | 0 |  | Wharton | Wharton | Tier 4 |  |  |  |  | 8099, 8102 | Y |  |  |  | 70797 | 70796
66204 | Rebuild Hidden Lakes-PH Robinson with bundled 795 ACSS |  |  | TNMP Hidden Lakes (bus # 38900) | CenterPoint PH Robinson (bus # 42015) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2029-05-31 |  | 138 | 0 | 3.15 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 38900, 42015 | Y |  |  |  | 66205 | 66204
60526 | Rebuild West Columbia Local-Angleton with 795 ACSS | [6 empty] | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2029-05-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 39530, 39560 | Y |  |  |  | 60527 | 60526
93217 | Update Topology in Brownsville Area per Approved RPG Project | Adding in 345 kV topology for LRGV Brownsville area (new 345 kV Chalybe station with two (2) 675 MVA autos being fed from Sharyland's Kingfisher and Palmito stations) per the BOD approved RPG project. Also added additional 138 kV feed from Stillman to AEP's Chalybe 138 kV | Added two (2) 675 MVA Autotransformers to serve load on 138 kV system | Chalybe |  | Planned | 77144 | SLU | Charles Aleman caleman@huntutility.com 682-406-9656 |  | 2029-05-31 |  | 345 | 47 | 0 | 1350 |  | Cameron |  | Tier 1 | 24RPG008 | 2024-06-11 | 2024-09-25 | 2024-12-03 | 8735, 79500, 79501, 79502, 79596, 79597, 79601 | Y | N |  |  | 94231 | 93217
60504 | Rebuild Caddo-Apache with bundled 795 ACSS | [6 empty] | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2029-05-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 38710, 38720 | Y |  |  |  | 60505 | 60504
60502 | Rebuild Apache-Amoco with bundled 795 ACSS | [6 empty] | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2029-05-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 38620, 38720 | Y |  |  |  | 60503 | 60502
87427 | Rebuild Magnolia to Seminole 138kV line. | Replacement for recently committed PMCR # 4010. |  | Magnolia Sub | Seminole Sub | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2029-05-31 |  | 138 | 0 | 3.3 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 38950, 38990 | Y |  |  |  | 87428 | 87427
93134 | Minnesota: Construct New Distribution Station | Construct new distribution station on the North Edinburg to Pharr 138 kV line between McColl Road and Pharr |  | Minesota |  | Planned |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2029-05-31 |  | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  |  | 8085, 8372, 8908 | Y |  |  |  | 93135 | 93134
60522 | Rebuild Hidden Lakes-League City with 795 ACSS | [6 empty] | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2029-05-31 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 38900, 38920 | Y |  |  |  | 60523 | 60522
84898 | New Eastside Switching Station |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2029-06-01 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  |  | 5035, 5110, 5250, 5294, 5295, 5371, 5400, 5416, 5485 | Y |  |  |  | 84899 | 84898
87693 | Rebuild Spruce to Eastside Double Circuit |  |  |  |  | Planned | T-0398 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2029-06-01 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 3 |  |  |  |  | 5295, 5400 | Y |  |  |  | 87694 | 87693
86329 | AEN_PilotKnob_CarsonCreek_Ckt_944_RECONDUCTOR |  |  | 9175 | 9259 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2029-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9175, 9259 | Y |  |  |  | 86330 | 86329
86836 | AEN_Northland_KoenigLane_Ckt__conversion_to_138kV | Northland to Koenig Lane convert_to_138kV |  | 9129 | 9227 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2029-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9129, 9227 | Y |  |  |  | 86837 | 86836
86275 | AEN_REPLACE_DUNLAP_345kV_DLAT1_and_DLAT2_AUTOS_WITH__New_672_MVAs | Replace Autos with new 672 MVA |  | 9044 | 9045 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2029-06-01 |  | 345 | 0 | 0 | 672 |  | Travis | Travis | Tier 4 |  |  |  |  | 9044, 9045, 90001, 90007 | Y |  |  |  | 86276 | 86275
6687 | Rebuild Rio Hondo to East Rio Hondo | Rebuild the 138 kV line from Rio Hondo to East Rio Hondo. |  | Rio Hondo | East Rio Hondo | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2029-06-01 |  | 138 | 0 | 8.19 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  |  | 5764, 8319 | Y | N |  |  | 14458 | 6687
86273 | AEN_REPLACE_AUSTROP_345kV_AUAT1_and_AUAT2_AUTOS_WITH__New_672_MVAs_PMCR | Autos to be upgraded to 672 MVAs |  | 7040 | 9328 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2029-06-01 |  | 345 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 7040, 9328, 9329, 9330 | Y |  |  |  | 86274 | 86273
6666 | BRYN_6666_Steele_Store_to_Cooks_Point | Construct 138kV line from BTU Steele Store to LCRA Cooks Point (Bundled 1033 ACSR - Curlew & 959 ACSS Suwannee) |  | 32852 | 7569 | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2029-06-30 |  | 138 | 7.2 | 0 | 0 |  | Brazos | Burleson | Tier 4 |  | 2025-01-10 | 2025-07-05 |  | 7569, 32852 | Y |  |  |  | 91617 | 6666
86857 | Blessing: Install New 345 kV Cap Bank | Install new capacitor bank at the Blessing 345 kV station | In-Service Date Update | Blessing |  | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 | TP2023803 | 2029-06-30 |  | 345 | 0 | 0 | 0 | 0,130.9 | Matagorda |  | Tier 4 |  |  |  |  | 8123 | Y |  |  |  | 86858 | 86857
81238 | Zoisite: Construct New 345 kV Station and 345 kV Lines to STP | Interconnect the HIF load to the new Zoisite 345 kV station and construct two new STP to Zoisite 345 kV lines | Project Title, Description, Terminal, In-Service Date, Cost, and Mileage Update | STP | Zoisite | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 | TP2023803 | 2029-06-30 |  | 345 | 1.6 | 0 | 0 | 0,261.8 | Matagorda | Matagorda | Tier 4 |  |  |  |  | 5915, 8754 | Y |  |  |  | 81239 | 81238
73053 | Wimberley Loop to New Substation | Adds new 138 kV branch (219 MVA) from Wimberley to a new three terminal ring bus substation between Dripping Springs and Rutherford. |  | Wimberley | Cebolla Creek | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2029-08-01 |  | 138 | 13.44 | 0 | 0 |  | Hays | Hays | Tier 2 | 22RPG026 | 2022-08-29 | 2023-02-03 |  | 70496, 70509, 70511, 70512 | Y | N |  |  | 73054 | 73053
92432 |  |  |  | Reno | New Station Nofoul | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2029-11-15 |  | 138 | 0 | 0 | 0 |  | Parker | Parker | Tier 4 |  |  |  |  | 534, 541, 542 | Y |  |  |  | 92433 | 92432
57910 | Uvalde to West Batesville: Rebuild 138 kV Line | Rebuild the Uvalde to West Batesville 138 kV line | Contact and In-Service Date Update | Uvalde | West Batesville | Planned | 1117 - 1295 | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 | 3836 | 2029-11-30 |  | 138 | 0 | 20.6 | 0 |  | Uvalde | Zavala | Tier 4 |  |  |  |  | 8234, 8236 | Y | N |  |  | 65580 | 57910
6685 | Van Vleck substation loop | Replaces single circuit radial line connected to a pole mounted switch with a double circuit transmission loop to the Van Vleck substation and upgrades the 4/0 ACSR to 795 ACSR on 138 kV capable poles. |  | Van Vleck Substation | Van Vleck Switch | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2029-12-01 |  | 69 | 2 | 2 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  |  | 5556, 5557, 5558, 5560 | Y | N |  |  | 14456 | 6685
84900 | Rebuild Pawnee to Tango into a double circuit |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2029-12-01 |  | 345 | 0 | 0 | 0 |  |  |  | Tier 1 |  |  |  |  | 5725, 8689 | Y |  |  |  | 84901 | 84900
59260 | Mason Phillips Tap to Mason Phillips: Rebuild 69 kV Line | Rehab the Mason Phillips Tap to Mason Phillips 69 kV Line |  | Seaquist | Mason Phillips | Planned | 1127 - 1305 | AEP TNC | Christopher Carroll twang1@aep.com 918-599-2635 | 1872 | 2029-12-01 |  | 69 | 0 | 13.7 | 0 |  | Mason | Mason | Tier 4 |  |  |  |  | 6395, 6407, 60458 | Y | N |  |  | 65588 | 59260
93624 | L7C Add a new Creosote - Toyah Creek 345-kV double-circuit line | AEP and Oncor joint project to add the 23-mile L7C Creosote - Toyah Creek 345-kV double-circuit transmission line part of the local common projects approved as part of the Permian Basin Reliability Plan |  | Creosote | Toyah Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 |  | 2029-12-31 |  | 345 | 46 | 0 | 0 |  | Ward | Pecos | Tier 1 |  | 2023-05-18 | 2023-06-09 |  | 18669, 60141, 60145 | Y |  |  |  | 93625 | 93624
66118 | Reconductor TI-Lakepointe with 959 ACSS/TW | Project ISD anticipated in 2025. |  | Lakepoint (bus # 37010) | TI (bus # 37080) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2029-12-31 |  | 138 | 0 | 2.78 | 0 |  | Denton | Denton | Tier 4 |  |  |  |  | 37010, 37080 | Y |  |  |  | 66119 | 66118
61550 | East Munday to Lake Pauline: Rebuild 138 kV Line | Rehab East Munday to Lake Pauline 138 kV line |  | East Munday | Lake Pauline | Planned | 1129 - 1307 | AEP TNC | Greg Crane twang1@aep.com 918-599-2635 | 1874 | 2030-04-30 |  | 138 | 0 | 59.97 | 0 |  | Knox | Hardeman | Tier 4 | 20RPG018 |  |  |  | 6037, 6050, 6110 | Y | N |  |  | 65594 | 61550
81277 | Midland East – Midland County NW 345 kV Line Rebuild | Rebuild the existing 345 kV line and add a second circuit to the new line |  | Midland East | Midland County Northwest | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8729 | 2030-05-01 |  | 345 | 0 | 42.6 | 0 |  | Midland | Midland | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1021, 1185 | Y |  |  |  | 81278 | 81277
6304 | Shamburger North - Shamburger 345 kV Line | Upgrade existing 345 kV Line | Project Deferral | Shamburger North | Shamburger | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6085 | 2030-05-15 |  | 345 | 10 | 10 | 0 |  | Smith | Smith | Tier 3 |  |  |  |  | 3103, 3223 | Y | N |  |  | 14033 | 6304
5981 | Shamburger North 345/138 kV Sw. Sta. | Establish Shamburger North 345/138 kV Sw. Sta. | Project Deferral | Shamburger North | Shamburger North | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6083 | 2030-05-15 |  | 345 | 0 | 0 | 600 |  | Smith | Smith | Tier 3 |  |  |  |  | 2485, 3103, 3201, 3206, 3217, 3223, 3226 | Y | N |  |  | 13696 | 5981
5982 | Shamburger North - Shamburger 138 kV Line | Upgrade Shamburger North - Shamburger 138 kV Line | Project Deferral | Shamburger North | Shamburger | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6084 | 2030-05-15 |  | 138 | 10 | 0 | 0 |  | Smith | Smith | Tier 4 |  |  |  |  | 3104, 3206, 3226 | Y | N |  |  | 13697 | 5982
6287 | Sherry Sw. - Webb/Kennedale 345 kV DCKT Line | Upgrade the existing 345 kV Line |  | Sherry | Webb/Kennedale | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4252 | 2030-05-15 |  | 345 | 0 | 11.2 | 0 |  | Tarrant | Tarrant | Tier 3 |  |  |  |  | 1911, 1918, 1929, 1930, 1932, 1934 | Y |  |  |  | 14016 | 6287
17TPIT0031 | Elkton 345/138 kV autotransformer | Replace existing autotransformer |  | Elkton | Elkton | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6032-E | 2030-05-15 |  | 345 | 0 | 0 | 600 |  | Smith | Smith | Tier 3 |  |  |  |  | 3105, 3106, 29150 | Y | N |  |  | 10501 | 3155
93088 | Cattleman - Champion Creek/Bitter Creek - Sweetwater East 345-kV Double-Circuit Line Rebuild 345 kV Double-Circuit Line Rebuild | AEP and Oncor joint project to add L24A Upgrade the existing Cattleman - Champion Creek/Bitter Creek - Sweetwater East 345-kV double-circuit line |  | Cattleman | Longshore | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | PB_L24_A | 2030-05-15 |  | 345 | 0 | 83.22 | 0 |  | Nolan | Mitchell | Tier 1 |  | 2023-09-29 |  |  | 1414, 10053, 11420, 71050 | Y |  |  |  | 93089 | 93088
91399 | Bitter_Creek_Substation_Upgrade | Oncor will upgrade the existing 345-kV double-circuit transmission lines Bitter Creek - Morgan Creek (Cattleman) and Bitter Creek - Sweetwater East. Part of the Permian Basin Reliability Plan released by ERCOT, under transmission upgrades L24 |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-8256 | 2030-05-15 |  | 345 | 0 | 0 | 0 |  | Nolan | Nolan | Tier 4 |  |  |  |  | 11420, 71050 | Y |  |  |  | 91400 | 91399
52070 | Carver to Maxwell: Rebuild 138 kV line | Rehab Carver to Maxwell 138 kV Line |  | Carver | Maxwell | Planned | 1079 - 1252 | AEP TCC/AEP TNC | Damian Raab twang1@aep.com 918-599-2635 | 3804 | 2030-05-31 | 2958101 | 138 | 0 | 60.24 | 0 |  | Sutton | Val Verde | Tier 3 | 22RPG042 | 2022-12-02 | 2022-12-28 |  | 8259, 8261, 8991, 8998, 60412, 60440 | Y | N |  |  | 65562 | 52070
16TPIT0007 | McNeil to MagPlant Ckt 977 Upgrade | Reconductor existing McNeil to MagPlant circuit from 2000 to 3000 Amp. Relocate McNeil to Summit Circuit 907 and McNeil to MagPlant Circuit 977 to separate structures. Kramer Lane (KA) substation will be cut-into this line in 2023 |  | McNeil Substation | Mag Plant Substation | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 | P396 | 2030-06-01 |  | 138 | 0 | 3.24 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9077, 9238, 9276 | Y | N |  | Will add the ptoject to the base case. | 8207 | 1031
92282 | Faulkner - Cryo 138kV - Part of Upgrade L4 2024 Permian Basin Study |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2030-06-01 |  | 138 | 22.8 | 0 | 0 |  | Reeves | Reeves | Tier 2 |  |  |  |  | 38124, 60721 | Y |  |  |  | 92283 | 92282
92280 | Alamo St - Bottlebrush 138kV - Upgrade L12 2024 Permian Basin Study |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2030-06-01 |  | 138 | 1.6 | 28.51 | 0 |  | Pecos | Pecos | Tier 2 |  |  |  |  | 38310, 38320, 38331, 38360, 38365, 38381, 38383, 38439 | Y |  |  |  | 92281 | 92280
92274 | Whitebaker 345kV - Part of Upgrade L13 2024 Permian Basin Study |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2030-06-01 |  | 345 | 22 | 0 | 1500 |  |  |  | Tier 1 |  |  |  |  | 38430, 38435, 38436, 38437, 76002 | Y |  |  |  | 92275 | 92274
92278 | Faulkner 345kV - Part of Upgrade L5 2024 Permian Basin Study |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2030-06-01 |  | 345 | 79.28 | 0 | 1500 |  | Pecos | Reeves | Tier 1 |  |  |  |  | 38124, 38125, 38126, 38127, 60404 | Y |  |  |  | 92279 | 92278
92276 | Bottlebrush 345kV - Part of Upgrade L13 2024 Permian Basin Study |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2030-06-01 |  | 345 | 174.84 | 29.81 | 1500 |  | Pecos | Pecos | Tier 1 |  |  |  |  | 38430, 38431, 38432, 38435, 38439, 38441, 38442, 38443, 38455, 60404 | Y |  |  |  | 92277 | 92276
89920 | GVEC Nixon substation | Rebuild existing substation, 138 kV bus, new PWT, new Control House, new HV and LV structures, containment foundations, bus, panels, etc |  | Gonzales |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2030-10-25 | 2958101 | 138 | 0 | 0 | 0 |  | Gonzales | Gonzales | Tier 4 | [5 empty] | Y |  |  |  | 89921 | 89920
67915 | Asherton to West Batesville: Rebuild 138 kV Line | Rehab Asherton to West Batesville 138 kV line | In-Service Date Update | Asherton | West Batesville | Planned |  | AEP TCC/ETT | John Solis jlsolis@aep.com 361-881-5574 |  | 2030-11-30 |  | 138 | 0 | 36.09 | 0 |  | Dimmit | Zavala | Tier 3 |  |  |  |  | 8236, 8283, 8285 | Y |  |  |  | 67916 | 67915
1549 | Devine Switch breaker addition | Adds breakers to Devine Switch to allow closing of normally open Devine Switch to Devine. Creates 3- terminal switching station |  | Devine Switch |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2030-12-01 |  | 69 | 0 | 0 | 0 |  | Medina |  | Tier 4 | [5 empty] | Y | N |  |  | 8754 | 1549
92340 |  |  |  | New 138 KV station "Warg" | New 138 KV station "Warg" | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2030-12-01 |  | 138 | 4 | 0 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  |  | 173, 176, 177 | Y |  |  |  | 92341 | 92340
91939 | Solstice to Bottlebrush: Construct New 345 kV Double Circuit Line | Construct a new 345 kV double circuit line from Solstice to Bottlebrush | NEW | Solstice | Bottlebrush | Planned |  | AEP TNC/TNMP | Tong Wang twang1@aep.com 918-599-2635 | TP2024076 | 2030-12-31 |  | 345 | 31 | 0 | 0 |  | Pecos | Reeves | Tier 1 | [5 empty] | Y | N |  |  | 91940 | 91939
91937 | Cryo to Faulkner: Construct New 138 kV Line | Construct a new 138 kV single circuit line from Cryo to Faulkner | NEW | Cryo | Faulkner | Planned |  | AEP TNC/TNMP | Tong Wang twang1@aep.com 918-599-2635 | TP2025146 | 2030-12-31 |  | 138 | 11.5 | 0 | 0 |  | Reeves | Reeves | Tier 2 | [5 empty] | Y | N |  |  | 91938 | 91937
91853 | Fort Stockton Plant to Solstice: Rebuild 138 kV Line | Rebuild the Fort Stockton Plant to Solstice 138 kV line and retire the PST at Solstice | NEW | Fort Stockton Plant | Solstice | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | TP2025145 | 2030-12-31 |  | 138 | 0 | 25 | 0 |  | Pecos | Pecos | Tier 3 |  |  |  |  | 6630, 60384, 60385 | Y | N |  |  | 91854 | 91853
91941 | Solstice to Faulkner: Construct New 345 kV Double Circuit Line | Construct a new 345 kV double circuit line from Solstice to Faulkner | NEW | Solstice | Faulkner | Planned |  | AEP TNC/TNMP | Tong Wang twang1@aep.com 918-599-2635 | TP2024165 | 2030-12-31 |  | 345 | 40 | 0 | 0 |  | Pecos | Reeves | Tier 1 | [5 empty] | Y | N |  |  | 91942 | 91941
91906 | Carver to Friend Ranch: Rebuild 138 kV Line | Rebuild the Carver to Friend Ranch 138 kV line | NEW | Carver | Friend Ranch | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | TP2025168 | 2030-12-31 |  | 138 | 0 | 33 | 0 |  | Sutton | Crockett | Tier 3 |  |  |  |  | 6562, 60412 | Y | N |  |  | 91907 | 91906
71877 | CPSE_Cagnon to Shepherd Rebuild (Phase B) |  |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | T-0281 | 2031-01-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5054, 5230, 5378, 5465 | Y |  |  |  | 71878 | 71877
5479 | Trinidad - Tri Corner 345 kV Double-Circuit Line | Upgrade existing DCKT line |  | Trinidad Sw. Sta | TriCorner/Watermill | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4045 | 2031-05-15 |  | 345 | 0 | 92.1 | 0 |  | Henderson | Dallas | Tier 3 |  |  |  |  | 2432, 3123, 3124 | Y | N |  |  | 13184 | 5479
45068 | Merida to Harlandale Rebuild | CPSE_Merida to Harlandale Rebuild |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | T-0233 | 2031-05-15 |  | 138 | 0 | 10 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5190, 5310, 5385, 5395 | Y |  |  |  | 45069 | 45068
72956 | Bellville South - Prairie View Transmission Line Upgrade | the proposed project converts the existing 69kV transmission line T283 from Bellville South- Quanex Sw - Sunnyside - Prarie View substation to 138kV. The proposed project improves the reliabiltiy of transmission facilities on the 26.1 mile transmission line and increases the line capacity for long term system growth. |  | Bellville South | Prairie View | Conceptual | Project transitioned to STEC from LCRA . Previous Mod Project #47428 | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2031-05-15 |  | 69 | 0 | 0 | 0 |  | Austin | Waller | Tier 3 |  |  |  |  | 7269, 57660, 57664, 57666 | N | N |  |  | 72957 | 72956
64065 | Alice to Kingsville 138 kV Line Rebuild | Rehab the Alice to Kingsville 138 kV line | In-Service Date Update | Alice | Kingsville | Conceptual |  | AEP TCC | Charity Kreher deevans@aep.com 918-599-2938 | TA2021079 | 2031-05-31 |  | 138 | 0 | 22.48 | 0 |  | Jim Wells | Kleberg | Tier 4 |  |  |  |  | 8503, 8518 | Y |  |  |  | 66649 | 64065
3595 | Bevo to AEP Carrizo Springs 69 kV line | Add 2 mile line by double circuiting two existing circuits, as recommended in 2013 RTP. |  | Bevo | Carrizo Springs | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2031-06-01 |  | 69 | 0 | 2 | 0 |  | Dimmit | Dimmit | Tier 1 |  | 2012-04-12 | 2012-08-12 | 2012-09-12 | 5871, 8244 | N | N |  | This new line was part of Karnes and Medina Electric Cooperatives Project that was approved in 2012. This also helped voltage on AEP transmission under contingencies. While much of the projected load is now on the system, not all of the projected load materialized. Studies with newer load projections have not shown the need for this line. STEC recommends evaluating this project as an option when studies show the need for a project in this area of the transmission system. | 10984 | 3595 | 2013-R104
90330 |  |  |  | Red River | JSR1 | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2031-09-02 |  | 69 | 1.2 | 0 | 0 |  | Cooke | Cooke | Tier 4 |  |  |  |  | 715, 719, 735 | Y |  |  |  | 90331 | 90330
14TPIT0098 | Cost Substation Addition | Upgrade the existing 69-kV substation |  | Cost |  | Planned |  | GVEC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2031-10-26 |  | 69 | 0 | 0 | 0 |  | Gonzales |  | Tier 4 |  |  |  |  | 7622 | Y | N |  |  | 78325 | 3321
73001 | Truscott Humble Tap: Rebuild 69 kV Line | Rehab Truscott Humble Tap 69 kV line | In-Service Date Update | Moorhouse | Truscott Humble | Planned |  | AEP TNC | Craig Tabor twang1@aep.com 918-599-2635 |  | 2031-11-30 |  | 69 | 0 | 13.92 | 0 |  | Knox | Knox | Tier 4 |  |  |  |  | 6080, 6082, 6084, 6085, 60023 | Y | N |  |  | 73002 | 73001
50898 | Alamito Creek to Paisano to Alpine: Rebuild 69 kV line | Rehab Alamito Creek to Paisano to Alpine 69 kV line | In-Service Date Update | Alamito Creek | Alpine | Planned | 1045 - 1218 | AEP TNC | Brooks Dow twang1@aep.com 918-599-2635 | 2793 | 2031-12-31 |  | 69 | 0 | 22.26 | 0 |  | Presidio | Brewster | Tier 4 | 20RPG017 |  |  |  | 6666, 6667, 6672 | Y | N |  |  | 50899 | 50898
50647 | CPSE_Merida to Westside MLSE | Upgrade terminal at Merida to ensure a 2000 A rating. |  | Merida | Westside | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0773 | 2032-01-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5310, 5490 | Y |  |  |  | 50648 | 50647
76790 | Upgrade Pearsall Auto | Upgrade Pearsall Auto |  | Pearsall | Pearsall | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2032-05-01 |  | 138 | 0 | 0 | 0 |  | Frio | Frio | Tier 4 |  |  |  |  | 5893, 5895 | Y |  |  |  | 76791 | 76790
87653 | Bluff Creek to Scurry Chevron Line Rebuild | Rebuild Bluff Creek to Scurry Chevron |  | Bluff Creek | Scurry Chevron | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R9002 | 2032-05-15 |  | 138 | 0 | 16 | 0 |  | Scurry | Scurry | Tier 3 |  |  |  |  | 1309, 1310, 1312 | Y |  |  |  | 87654 | 87653
15TPIT0033 | Randolph - 138 kV Substation Equipment Upgrade | Upgrade the Weiderstein and Tuttle terminals and ensure a 2000 A rating (minimum). Reconfigure and-or upgrade the main bus to ensure a 2000 A rating (minimum). |  | Randolph | Tuttle-Weiderstein | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0645b | 2032-06-01 12:00 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5360, 5435 | Y | N |  | There are no transformers associated with this project | 9557 | 2306
4425 | New TR-AW Ckt 1032 AW-MR Ckt 1039 MR-JV Ckt 961 | Old Description in Planbook Add 2nd Ckt from TR to HL to tie-in to HL-JV Ckt 1032 (part of old CKT 961), bypassing HL and creating TR-AW-MR-JV Ckt. New description Ckt 1032 from TR-AW, Ckt 1039 from MR-AW and CKT 961 from MR - JV |  | Techridge 9190 AshtonWoods 9224 | AshtonWoods 9226 Jollyville 9223 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2032-08-01 |  | 138 | 1.7 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9190, 9223, 9224, 9226, 9230, 9231 | Y | N |  |  | 11984 | 4425
4084 | Barton-Vega: Upgrade Ckt 928 | Reconductor to 2000 amps |  | Barton | Vega | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2032-08-10 |  | 138 | 0 | 4.05 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9158, 9285 | Y |  |  |  | 11609 | 4084
3334 | Fort Sam to Kirby and Fort Sam to Tenth Street MLSE Upgrade | Upgrade entire bus and terminals at Fort Sam and ensure a rating of 2000 A. |  | Fort Sam | Kirby/Tenth Street | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0744 | 2032-12-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5160, 5250, 5420 | Y | N |  | There are no transformers associated with this project | 10692 | 3334

## Completed Projects
JUNE BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 6/1/2025
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar ) (-Reactor, +Capacitor ) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | RPG Number | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number | RTP Project Number
59409 | Centralia 138 kV Capacitors | Add Centralia 138 kV Capacitors |  | Centralia | Centralia | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8568 | 2022-05-15 | 2024-06-24 | 138 | 0 | 0 | 0 | 0,55.2 | Upton | Upton | Tier 4 |  |  |  |  | 11209 | Y |  |  |  | 59534 | 59409
78339 | [7 empty] | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2023-04-13 | 2024-10-01 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 2625, 6795, 6999 | Y |  |  |  | 78340 | 78339
72564 | Buttercup Bus Upgrade | Upgrade the Buttercup bus from operate/transfer to double-bus double-breaker. Replaces Project ID 51740. |  | Buttercup |  | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2023-05-15 | 2024-04-01 | 138 | 0 | 0 | 0 |  | Williamson |  | Tier 4 |  |  |  |  | 70531 | Y | N |  |  | 72565 | 72564
61400 | Esperanza-Fair Oaks Transmission Line Upgrade | This project will increase the reliability and capacity of transmission facilities on the 4.3-mile T503 Esperanza to Fair Oaks Ranch 138-kV and T656 Bergheim to Kendall 345-kV double-circuit transmission line between Esperanza Substation and existing structure #173 and the 0.12-mile T506 Fair Oaks to Fair Oaks Ranch 138-kV and T656 double-circuit transmission line between Fair Oaks Substation and structure #173B by replacing the aging conductors. |  | Esperanza | Fair Oaks | Planned | 61406, 61358, 61392, 61350, 61234, 61362, 61356, 61402, 61404 | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2023-11-30 | 2024-02-29 | 345 | 0 | 4.42 | 0 |  | Kendall | Kendall | Tier 3 | 22RPG005 | 2022-03-04 | 2022-09-09 |  | 5470, 7046, 7169, 7710, 7770 | Y | N |  |  | 78303 | 61400
7013 | NASA Substation Upgrades | Upgrade substation equipment at NASA on Ckt.06 NASA to Webster to increase thermal limits |  | NASA | NASA | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2023-11-30 | 2024-10-31 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 42610, 42970, 43500 | Y | N |  |  | 14835 | 7013
75901 | Upgrade Ckt.90D Garrott to Midtown to increase thermal limits | Upgrade Ckt.90D Garrott to Midtown to increase thermal limits |  | Garrott | Midtown | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2023-11-30 | 2024-04-23 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47660, 47661, 47707, 47709 | Y | N |  |  | 75902 | 75901
72570 | PEC_HeroWay_Substation_Addition | Add new three terminal ring bus substation to 138 kV line between Nameless and Leander and install 46.7 MVA distribution transformer. The new substation will be located approximately 3.1 miles (45% of existing line length) from Leander substation. Replaces Project ID 63906. |  | Nameless | Leander | Planned | 61279 | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2023-12-01 | 2024-03-01 | 138 | 0 | 0 | 0 |  | Williamson |  | Tier 4 |  |  |  |  | 70525, 70526, 70536 | Y | N |  |  | 72571 | 72570
72582B | Nameless to Leander Transmission Line Upgrade | Rebuild and upgrade Leander to Hero Way with double-circuit capable structures. Install 1 ckt with bundled 795 kcmil conductor (440 MVA).(Replaces ERCOT Project # 61279B) |  | Leander | Hero Way | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2023-12-15 | 2024-03-01 | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 70525, 70536 | Y | N |  |  | 72584 | 72582
69552A | Teal 345/138 kV Switch connected to LCRA POI (Limmer) | Teal 138 kV Switch (Oncor) | Hard Tap POI to be complete in May 2024 | Teal | Teal | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6165 | 2023-12-15 | 2024-05-15 | 345 | 0 | 0 | 600 |  | Williamson | Williamson | Tier 3 | 22RPG027 | 2022-08-15 | 2022-09-15 |  | 3362, 3363, 3364, 3666, 3673, 13364 | Y |  |  |  | 69553 | 69552
57412 | GENRAL Substation Removal | Remove 69kV GENRAL substation from CNP service |  | GENRAL | Garden Villas | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2023-12-31 | 2024-01-22 | 69 | 0 | 9.91 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 42690, 47540, 47670 | Y | N |  |  | 61869 | 57412
76620 | This is a duplicate project. Correct project is MOD78457 | This is a duplicate project. Correct project is MOD78457 |  |  |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-01-01 | 2024-04-26 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 | [5 empty] | Y |  |  |  | 76621 | 76620
71193 | Blue Acres - Yosemite 138 kV Line | Upgrade the existing 138 kV line |  | Blue Acres | Yosemite | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8638 | 2024-01-15 | 2024-02-09 | 138 | 0 | 5.9 | 0 |  | Midland | Midland | Tier 4 | [5 empty] | Y |  |  |  | 80828 | 71193
61438 | Sim Gideon - Tahitian Village Transmission Line Storm Hardening | LCRA TSC will perform a Storm Hardening on the 5.1-mile Sim Gideon ¿ Tahitian Village (T648) 138-kV transmission line. This project will increase both the reliability and safety of the structures and conductor by ensuring that the transmission line meets or exceeds current NESC and LCRA TSC design standards and will be in compliance with PUCT storm hardening requirements for this circuit. |  | Sim Gideon | Tahitian Village | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2024-01-21 | 2024-05-09 | 138 | 0 | 0 | 0 |  | Bastrop | Bastrop | Tier 4 |  |  |  |  | 7310, 7575 | Y | N |  |  | 61439 | 61438
64774 |  | Loop new 138kV Donop substation into existing 138kV Southton to Braunig transmission line. |  |  |  | Planned | T-0311 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0963 | 2024-01-25 | 2024-02-01 | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5030, 5128, 5394 | Y |  |  |  | 64775 | 64774
48587 | Tesoro 345/138 kV Switch | Construct a new 345/138 kV switch (formerly known as Quail East) |  | Consavvy | Quail/Midessa South | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8634 | 2024-01-30 | 2024-02-05 | 345 | 0 | 0 | 1200 |  | Midland | Midland | Tier 3 | 22RPG032 | 2022-10-11 | 2022-11-07 |  |  | Y |  |  |  | 80829 | 48587
69888B | Deepwater to Clinton Ckts.33B-33C Line Upgrades | Rebuild-Reconductor portions of Ckt.33C Clinton to Harrisburg ahead of future 138kV conversions. |  | Clinton | Harrisburg | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-01-31 | 2024-01-11 | 69 | 0 | 4.7 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40352, 40800 | Y | N |  | Cost included in other phase. | 91909 | 69888
77146 | Reconducter WNK-AAT-MDT-FSH |  |  | Wink (37900) | Fishhook (38180) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2024-01-31 | 2024-01-19 | 138 | 0 | 13.18 | 0 |  | Winkler | Ward | Tier 4 |  |  |  |  | 37900, 38135, 38140, 38180 | Y |  |  |  | 77147 | 77146
63495 | Cedar Canyon to Noelke 2nd circuit | Add the 2nd circuit to CREZ Cedar Canyon to Noelke 345 kV line |  | Cedar Canyon | Noelke | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2024-01-31 | 2024-02-13 | 345 | 16 | 0 | 0 |  | Crockett | Crockett | Tier 2 |  | 2021-02-04 | 2021-06-11 |  | 7053, 76015 | Y | N |  |  | 63496 | 63495
66532 | Grey Well Draw - Pronghorn 138 kV Line Rebuild | Add Grey Well Draw - Pronghorn 138 kV Line Rebuild |  | Grey Well Draw | Pronghorn | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8606 | 2024-01-31 | 2024-02-05 | 138 | 9.9 | 0 | 0 |  | Midland | Midland | Tier 4 | [5 empty] | Y |  |  |  | 80769 | 66532
71196 | Grey Well Draw - Pecan Grove 138 kV Line | Rebuild existing 138 kV line |  | Grey Well Draw | Pecan Grove | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8640 | 2024-01-31 | 2024-02-05 | 138 | 0 | 7.8 | 0 |  | Midland | Midland | Tier 4 |  |  |  |  | 23860, 23861 | Y |  |  |  | 71198 | 71196
67217A | Addicks to Campbell Ckts 09 & 21 Upgrades | Upgrade Ckt.09I Addicks to Campbell tap to increase thermal limits |  | Addicks | Campbell | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-01-31 | 2024-01-04 | 138 | 0 | 3.53 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 45610, 48056 | Y | N |  |  | 67218 | 67217
67217B | Addicks to Campbell Ckts 09 & 21 Upgrades | Upgrade Ckt.21H Addicks to Campbell tap to increase thermal limits |  | Addicks | Campbell | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-01-31 | 2024-01-04 | 138 | 0 | 3.53 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 45610, 46610, 48057, 48349 | Y | N |  | Cost included in Phase A | 67219 | 67217
70623C | Cottonwood Bayou - Related Upgrades | Upgrade Ckt.04 Danbury to Liverpool to Snug to increase thermal limits |  | Liverpool | Danbury/Snug | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-01-31 00:02 | 2024-05-24 | 138 | 0 |  | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42870, 42875, 44890 | Y | N |  |  | 70626 | 70623
66221E | Galena Park Area Conversion Project | De-energize Ckt.20C Galena Park to Greens Bayou |  | Galena Park | Greens Bayou | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-01-31 00:04 | 2024-02-08 | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 3 | 21RPG020 | 2021-11-30 | 2021-12-22 | 2021-12-22 | 40611, 40725 | Y | N |  | Cost included in main entry | 86744 | 66221
64941B | PETSON to MONSAN Ckt.04D Upgrade | Upgrade Ckt 04D PETSON to MONSAN to increase thermal limits. Upgrade PETSON equipment to 4000A. |  | PETSON | MONSAN | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-01-31 12:00 | 2024-01-07 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42940, 43070 | Y | N |  |  | 75898 | 64941
6931 | New Tres Lagos Substation | Adds new station and short line from W Edinburg-Alton line |  | West Edinburg | Alton | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2024-02-01 | 2024-05-15 | 138 | 1.8 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  |  | 5770, 5771, 5772 | Y | N |  |  | 14750 | 6931
61457 | Nada - Ricebird Transmission Line Overhaul | LCRA TSC will perform an overhaul on the 13.1-mile Nada ¿ Ricebird (T588) 138-kV transmission line. This project will increase reliability of the structures and conductor by ensuring that the transmission line meets or exceeds current NESC and LCRA TSC design standards. |  | Nada | Ricebird | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2024-02-02 | 2024-02-02 | 138 | 0 | 0 | 0 |  | Colorado | Wharton | Tier 4 |  |  |  |  | 78103, 78104 | Y | N |  |  | 61458 | 61457
68974 | Second circuit from San Miguel to Fowlerton 345 kV | String the second circuit on existing towers from San Miguel to Fowlerton |  | San Miguel | Fowlerton | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2024-02-08 | 2024-05-01 | 345 | 36.4 | 0 | 0 |  | Atascosa | McMullen | Tier 1 |  |  |  |  | 5709, 5901 | Y | N |  |  | 68975 | 68974
75514 | Rising Star Area Conversions | This project converts the voltage from Holder (292) to Nimrod (289) to 138 KV |  | Holder (292) | Nimrod (289) | Under Construction |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2024-02-12 | 2024-02-29 | 138 | 0 | 28.5 | 0 |  | Brown | Comanche | Tier 4 |  |  |  |  | 285, 289, 292 | Y |  |  |  | 75515 | 75514
66124 | Prarie Swiitch Wind Interconnect | Connect Crawfish to El Campo to Lane City 138 kV Line | IN-SERVICE | EL CAMPO | LANE CITY PUMP | In-Service |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 | TP2021286 | 2024-02-14 | 2024-02-14 | 138 | 0 | 0 | 0 |  | Wharton | Wharton | Tier 4 |  |  |  |  | 8102, 8104, 8679 | Y |  |  |  | 66125 | 66124
64310 | Cumby-Cumby Tap Line Conversion | Cumby - Cumby Tap Radial Line 69 to 138 kV Conversion. Project requires coordination with RCEC and TNMP. |  | Cumby Tap | Cumby Substation | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R944 | 2024-02-16 | 2024-03-11 | 138 | 0 | 0 | 0 |  | Hopkins | Hopkins | Tier 4 |  |  |  |  | 1812, 1813, 1815, 6861 | Y | N |  |  | 66059 | 64310
52147 | Rising Star Area Conversions | Converts voltage to 138 KV from Holder to Nimrod to Rising Star. |  | Holder |  | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2024-02-22 | 2024-02-29 | 138 | 0 | 0 | 0 |  | Brown | Comanche | Tier 4 |  |  |  |  | 289, 292, 293 | Y |  |  |  | 52148 | 52147
65003 | WA Parish to Nash Ckt.02B Upgrades | Upgrade Ckt.02B WA Parish to Nash to replace aging infrastructure and to address line clearance concerns |  | WA Parish | Nash | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-02-28 | 2024-02-06 | 138 | 0 | 18.02 | 0 |  | Fort Bend | Brazoria | Tier 4 | 21RPG013 | 2021-08-08 | 2021-09-10 |  | 42410, 42980, 44010, 48364, 48365 | Y | N |  |  | 65004 | 65003
66221A | Galena Park Area Conversion Project | Remove Galena Park Auto A1. Remove Galena Park 69kV facilities. Remove Galena Park 138kV ring bus. Rebuild Galena Park substation for double-tap 138kV service. |  | Galena Park |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-02-28 | 2024-02-08 | 69 | 0 | 0 | -200 |  | Harris | Harris | Tier 3 | 21RPG020 | 2021-11-30 | 2021-12-22 | 2021-12-22 | 40610, 40611, 40752, 49015 | Y | N |  |  | 86746 | 66221
66221B | Galena Park Area Conversion Project | De-energize Ckt.38A Galena Park to GYPSUM |  | Galena Park | GYPSUM | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-02-28 00:01 | 2024-02-08 | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 3 | 21RPG020 | 2021-11-30 | 2021-12-22 | 2021-12-22 | 40611, 40619, 40720, 40751 | Y | N |  | Cost included in main entry | 86747 | 66221
66221C | Galena Park Area Conversion Project | De-energize Ckt.17A Galena Park to Greens Bayou |  | Galena Park | Greens Bayou | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-02-28 00:02 | 2024-02-08 | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 3 | 21RPG020 | 2021-11-30 | 2021-12-22 | 2021-12-22 |  | Y | N |  | Cost included in main entry | 86748 | 66221
66221D | Galena Park Area Conversion Project | De-energize Ckt.38B Clinton to Greens Bayou |  | Clinton | Greens Bayou | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-02-28 00:03 | 2024-02-08 | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 3 | 21RPG020 | 2021-11-30 | 2021-12-22 | 2021-12-22 | 40352, 40720 | Y | N |  | Cost included in main entry | 86749 | 66221
66221F | Galena Park Area Conversion Project | Rebuild Galena Park substation for double tap service. Bypass Galena Park breakers with Ckt.94 and tap Galena Park to create new Ckt.94M CITFIL to Normandy tap to Galena Park tap to TANKER |  | CITFIL | TANKER | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-02-28 00:05 | 2024-02-15 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 3 | 21RPG020 | 2021-11-30 | 2021-12-22 | 2021-12-22 | 40610, 40611, 40612, 40613, 40614, 40615, 40630, 48130, 48261, 48613 | Y | N |  | Cost included in main entry | 90300 | 66221
66221H | Galena Park Area Conversion Project | Join 69kV Greens Bayou buses 40720 & 40725 at a Minimum 40KAIC |  | Greens Bayou |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-02-28 00:07 | 2024-02-08 | 69 | 0 | 0 | 0 |  | Harris |  | Tier 3 | 21RPG020 | 2021-11-30 | 2021-12-22 | 2021-12-22 | 40720, 40725, 41570, 41681 | Y | N |  | Cost included in main entry | 86751 | 66221
62712 | Driver - Skywest 138 kV Line Rebuild | Rebuild the existing Driver - Skywest 138 kV Line |  | Driver | Skywest | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8564 | 2024-03-15 | 2024-06-01 | 138 | 0 | 11.9 | 0 |  | Upton | Upton | Tier 4 |  |  |  |  | 23863, 71210 | Y |  |  |  | 62716 | 62712
75516 | Rising Star Area Conversions | This converts from NImrod (289) to Rising Star (285) to 138 KV service |  | Nimrod (289) | Rising Star (285) | Under Construction |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2024-03-20 | 2024-03-11 | 138 | 0 | 0 | 0 |  | Eastland | Comanche | Tier 4 |  |  |  |  | 281, 285, 289 | Y |  |  |  | 75517 | 75516
70964 | WETT 345 kV Volta witch | Construct new 345 kV Volta Switch and two approximately 0.15-mile 345 kV lines between WETT-owned Volta 345 kV Switch and Oncor-owned Expanse |  | Howard | Martin | Planned |  | WETT | Chris Ramirez cramirez@wettllc.com 737-218-4525 |  | 2024-03-25 | 2024-06-04 | 345 | 0.3 | 0 | 0 |  | Howard | Martin | Tier 3 | 22RPG007 | 2022-03-06 | 2022-04-04 |  | 11366, 11369, 59900, 59901, 59910 | Y |  |  |  | 80004 | 70964
81396 |  |  |  | RUCKER | RUCKER | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2024-03-26 | 2024-05-09 | 69 | 0 | 0 | 0 |  | Comanche | Comanche | Tier 4 |  |  |  |  | 287, 1663 | Y |  |  |  | 81397 | 81396
71190 | Einstein - St Lawrence 138 kV Line | Upgrade the existing 138 kV line |  | Einstein | St. Lawrence | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8646 | 2024-03-28 | 2024-03-18 | 138 | 0 | 4.6 | 0 |  | Glasscock | Glasscock | Tier 4 |  |  |  |  | 23852, 23854 | Y |  |  |  | 71192 | 71190
66635 | Lamesa 69 kV Substation Conversion to 138 kV | Add Lamesa 69 kV Substation Conversion to 138 kV |  | Lamesa 69 kV | Lamesa 138 kV | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8595 | 2024-03-30 | 2024-03-09 | 69 | 0 | 0 | 0 |  | Dawson | Dawson | Tier 4 | [5 empty] | Y |  |  |  | 80849 | 66635
55464 | Adds new Morrow sub near Pearsall | Adds new Morrow substation and short line from Morrow to the Pearsall substation |  | Pearsall | Morrow | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2024-03-31 | 2024-06-18 | 138 | 0.91 | 0 | 0 |  | Frio | Frio | Tier 4 |  |  |  |  | 5895, 5896 | Y | N |  |  | 55465 | 55464
70665A | Danek (DNK) CEHE Substation for Remy Jade - 23INR0339 | New 138kV Danek (DNK) substation for generator interconnection to Remy Jade. Loop Ckt.08G into substation to create new Ckt.08 Crosby to Danek to Highlands tap Install generator lead from Danek (DNK) substation to JADE/Remy Jade. |  | Danek | Crosby/Highlands | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-03-31 | 2024-03-14 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  |  | 40390, 40396, 40890, 48141, 113219 | Y | N |  |  | 75840 | 70665
67422H | Greens Bayou to Clinton 138kV Conversion | Rebuild-Reconductor Ckt.61A Greens Bayou (TEXWAL LOCATION) to Wallisville to Prepare for 138kV Conversion |  | Greens Bayou | Wallisville | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-03-31 00:01 | 2024-03-31 | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40720, 41682 | Y | N |  |  | 87574 | 67422
52169 | Rising Star Area Conversions | This converts the voltage to 138 following Rising Star Substation Voltage Conversion |  | Rising Star | Downing | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2024-04-10 | 2024-05-16 | 138 | 0 | 0 | 0 |  | Comanche | Comanche | Tier 4 |  |  |  |  | 281, 285, 294 | Y |  |  |  | 52170 | 52169
68229 | Penumbra: Build new 345 kV Station | Interconnect Montgomery Ranch Wind to the Avogadro to Edith Clarke 345 kV line | IN-SERVICE | Penumbra |  | In-Service |  | AEP TNC | Zach Lachiusa twang1@aep.com 918-599-2635 |  | 2024-04-11 | 2024-04-11 | 345 | 0 | 0 | 0 |  | Foard |  | Tier 4 |  |  |  |  | 60059, 60500, 60506, 60722 | Y | N |  |  | 68230 | 68229
81726 | Mobile substation | Project is to add a mobile substation next to Airport Substation tapping into the Transmission line that is Filter Plant to Airport Substation. Then connecting lines South Plant to Southmost by passing Airport Substation. This is due to Airport Substation being decommissioned in April. |  | 59420 Filter Plant, 59500 South Plant | Mobile substation, 5789 Southmost | Planned |  | BPUB | Luis Martinez lugmartinez@brownsville-pub.com 956-983-6212 |  | 2024-04-15 | 2024-04-15 | 138 | 0 | 0 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  |  | 5789, 5946, 59420, 59430, 59460, 59500 | Y |  |  |  | 81727 | 81726
57169 | Rebuild Redgate to N Edinburg 138 kV | Rebuild Redgate to N Edinburg 138kV and opens Redgate tap |  | Redgate | Faysville Switch | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2024-04-27 | 2024-05-22 | 138 | 0 | 3.45 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  |  | 5779, 5784, 8380, 88380 | Y | N |  |  | 63733 | 57169
70961A | Crosby Sub Exp for HOLY/Citadel BESS and Upgrades | Expand Crosby substation for HOLY/Citadel BESS generator interconnection (24INR0147). Reposition Ckt.08H to a new breaker position. |  | Crosby |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-04-30 | 2024-02-05 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  |  | 40390, 113333 | Y | N |  |  | 70962 | 70961
72649A | Add_Celina_Load | Connecting Rayburn Celina switch to ONCOR Wilson Creek 138 kV substation. Adding CPR substation and load. |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2024-04-30 | 2024-04-30 | 138 | 0 | 0 | 0 |  | Collin | Collin | Tier 4 |  |  |  |  | 2350, 6790, 6793, 6825 | Y |  |  |  | 78608 | 72649
72596A | PEC_MarshallFord_Paleface_StormHardening | Rebuild single circuit section of Paleface to Marshal Ford and reconductor with Single 959 ACSS Conductor, 380 MVA; (Replaces ERCOT Project # 61274A) | 1/10/2023: Changes to description based on final design. | Paleface | Marshall Ford | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2024-04-30 | 2024-05-01 | 138 | 0 | 3.65 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 70477, 77356 | Y | N |  |  | 72598 | 72596
69894 | HO Clarke Substation Expansion for Callisto Energy Center (22INR0490 & 22INR0491) | Expand HO Clarke substation for Callisto Energy Center generator interconnection (22INR0490 & 22INR0491) |  | HO Clarke |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-04-30 | 2024-05-01 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  |  | 47150, 113105 | Y | N |  |  | 69895 | 69894
67604 | Stafford Reconfigurations Ckt.05D | Reconfigure Stafford loads served from Ckt.05D. Create Ckt.05D Westchase tap to Stafford loop to Stafford TR4 tap to Missouri City tap |  | Stafford | Missouri City | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-04-30 | 2024-02-06 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 44015, 44020, 44670, 44673, 44674, 44676, 44760, 44761, 48162, 48351, 48352, 48358, 49911 | Y | N |  |  | 86917 | 67604
55572 | Burma to Sterling City: Rebuild 69 kV Line | Rehab the Burma to Sterling City 69 kV Line | IN-SERVICE | Burma | Sterling City | In-Service | 1096 - 1274 | AEP TNC | Forrest Farson twang1@aep.com 918-599-2635 | 1864 | 2024-05-01 | 2024-05-01 | 69 | 0 | 32 | 0 |  | Tom Green | Sterling | Tier 3 | 20RPG021 | 2020-10-01 | 2020-11-01 |  | 6435, 6439, 6445, 6446, 6460, 6461, 60411, 61016, 61017 | Y | N |  |  | 55573 | 55572
68055 | Rio Colorado substation | Adds new Rio Colorado load serving station between Bay City and Tin Top |  | Rio Colorado |  | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2024-05-01 | 2024-02-01 | 69 | 3.8 | 0 | 0 |  | Matagorda |  | Tier 4 |  |  |  |  | 5560, 5563, 5569 | Y | N |  |  | 68056 | 68055
72596B | PEC_MarshallFord_Paleface_StormHardening | Reconductor triple circuit section in conjunction with LCRA TSC Storm Hardening project (ERCOT Project #62068) with Single Suwanee Conductor. (Replaces ERCOT Project # 61274B) | 1/10/2023: Changes to description based on final design. | Paleface | Marshall Ford | Planned |  | PEC/LCRATSC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2024-05-01 | 2024-05-01 | 138 | 0 | 11.5 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 70477, 77356 | Y | N |  |  | 72597 | 72596
72878 | LCRATSC_Leesville_Substation_Addition | This project provides a point of interconnection for a new 95 MW Solar Farm and 33 MW Battery Energy Storage System via a new 138-kV Leesville Substation on T605 between Deer Creek and LCRA Nixon substations. |  | Leesville | Leesville | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2024-05-09 | 2024-05-09 | 138 | 0 | 0 | 0 |  | Gonzales |  | Tier 4 |  |  |  |  | 7595, 7599, 7621 | Y | N |  |  | 72879 | 72878
56350B | Burnett - Bowie 69 kV Line | Rebuild Burnett-Ringgold Magnolia Tap Line |  | Burnett | Ringgold Magnolia Tap | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R4015 | 2024-05-14 | 2024-06-15 | 69 | 0 | 20.1 | 100 |  | Wichita | Clay | Tier 3 | 21RPG008 | 2021-04-23 | 2021-05-18 |  | 1452, 1491, 1543, 1544, 1545 | Y | N |  |  | 73039 | 56350
56350C | Burnett - Bowie 69 kV Line | Establish Old lake switch and convert Fisher Road - Old Lake Switch (FKA Burnett-Ringgold Magnolia Tap) Line from 69 kV to 138 kV |  | Burnett | Ringgold Magnolia Tap | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R4015 | 2024-05-14 | 2024-06-15 | 138 | 0 |  | 100 |  | Wichita | Clay | Tier 3 | 21RPG008 | 2021-04-23 | 2021-05-18 |  | 775, 1426, 1452, 1491, 1524, 1543, 1544, 1545, 11540, 11541, 33770 | Y | N |  |  | 73040 | 56350
71172 | Luther - Vealmoor 138 kV Line | Upgrade the existing 138 kV line |  | Luther | Vealmoor | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8636 | 2024-05-15 | 2024-06-12 | 138 | 0 | 10 | 0 |  | Borden | Howard | Tier 4 |  |  |  |  | 23831, 23835 | Y |  |  |  | 71174 | 71172
72863 | Delaware River 138 kV Switch | Establish Delaware River 138 kV Switch for merchant plant |  | Horseshoe Springs | Riverton | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8621 | 2024-05-15 | 2024-05-07 | 138 | 0 | 0 | 0 |  | Culberson | Reeves | Tier 4 |  |  |  |  | 11112, 11190, 11272 | Y |  |  |  | 72865 | 72863
73443 | Utilize Melton POI via Navarro 345 kV Switch for Project Lefty | Utilize Melton POI via Navarro 345 kV Switch for Project Lefty |  | Navarro | Navarro | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6338 | 2024-05-15 | 2024-04-15 | 345 | 0.2 | 0 | 0 |  | Navarro | Navarro | Tier 4 |  |  |  |  | 3373, 68091 | Y |  |  |  | 73444 | 73443
71898 | Install two additional 9.2 Mvar stages at Carroll Springs 69 kV Cap Bank | Install two additional 9.2 Mvar stages at Carroll Springs 69 kV Cap Bank |  | Carroll Springs | Carroll Springs | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6241 | 2024-05-15 | 2024-06-15 | 69 | 0 | 0 | 0 | 0,18.4 | Anderson | Anderson | Tier 4 |  |  |  |  | 3270 | Y |  |  |  | 71899 | 71898
72572 | Highway 32 capacitor bank addition | Install 31.3 Mvar capacitor bank at Highway 32. Replaces Project ID 70363. |  | Highway 32 |  | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2024-05-15 | 2024-10-10 | 138 | 0 | 0 | 0 | 0,31.2 | Hays |  | Tier 4 |  |  |  |  | 70546 | Y | Y |  |  | 72573 | 72572
71940 | LCRATSC_Saxet_Substation_Addition | LCRA TSC will provide two transmission points of interconnection by installing taps on the LCRA TSC owned 138-kV transmission lines T522 Weil – Lon Hill and T437 Lon Hill – Nueces Bay to serve AEP customer load. |  | Saxet |  | Planned |  | LCRATSC/AEP TCC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2024-05-15 | 2024-05-15 | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 8441, 8452, 8482, 78568, 78569 | Y | Y |  |  | 72407 | 71940
71948 | LCRATSC_Copperas_Copperas_TL_Overhaul | LCRA TSC will perform an overhaul on the 2.4-mile portion of Copperas Cove Oncor – Copperas Cove PEC (T393) 138-kV transmission line between Copperas Cove PEC Substation and Oncor Tie existing structure #35/8. |  | Copperas (ONCOR) | Copperas (PEC) | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2024-05-15 | 2024-05-15 | 138 | 0 | 3 | 0 |  | Coryell | Coryell | Tier 4 |  |  |  |  | 3630, 7061 | Y | N |  |  | 71949 | 71948
71973 | Morgan Creek - Barber Lake Rebuild West Ckt | Rebuild the existing 138 kV line |  | Morgan Creek | Barber Lake | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8623 | 2024-05-15 | 2024-05-22 | 138 | 0 | 4.75 | 0 |  | Mitchell | Mitchell | Tier 4 |  |  |  |  | 1032, 1190 | Y |  |  |  | 81360 | 71973
73417 | LCRATSC_Schumansville_SheriffsPosse_StormHardening | Perform storm hardening on the 5.6 mile Schumansville - Sheriff's Posse (T307) transmission line. T307 shares ROW with de-energized T409 Comal - Sheriff's Posse between structure #5 and Sheriff's Posse. Design of T307 should allow for the future addition of circuit T409 on double-circuit structures between Sheriff's Posse and structure #5. |  | Schumansville | Sheriff's Posse | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@lcra.org 512-578-4514 |  | 2024-05-15 | 2024-05-15 | 138 | 0 | 6 | 0 |  | Guadalupe | Comal | Tier 4 |  |  |  |  | 7460, 7609 | Y | N |  |  | 73418 | 73417
73434 | Shaw 138 kV POD | Add Shaw 138 kV POD |  | Midkiff | Shaw POD | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8697 | 2024-05-15 | 2024-06-30 | 138 | 0 | 0 | 0 | 0,55.2 | Reagan | Glasscock | Tier 4 |  |  |  |  | 11222, 18664 | Y |  |  |  | 73435 | 73434
70977 | Ozark Trail 345 kV Switch | Establish Ozark Trail 345 kV Switch to provide a POI for Hornet Solar |  | Ogallala | Tule Canyon | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8027 | 2024-05-15 | 2024-05-17 | 345 | 0 | 0 | 0 |  | Castro | Swisher | Tier 4 |  |  |  |  | 23901, 23912, 23914 | Y |  |  |  | 70980 | 70977
71175 | Tall City - Pecan Grove 138 kV Line | Upgrade the existing 138 kV line |  | Tall City | Pecan Grove | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8635 | 2024-05-15 | 2024-06-01 | 138 | 0 | 11.6 | 0 |  | Midland | Martin | Tier 4 |  |  |  |  | 23840, 23855, 23861 | Y |  |  |  | 71177 | 71175
67377 | Upgrade Bowman Autotransfomer 2 | Upgrade existing Bowman Auto #2 300 MVA to 600 MVA. |  | Bowman | Bowman | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R4026 | 2024-05-15 | 2024-05-15 | 345 | 0 | 0 | 600 |  | Archer | Archer | Tier 3 | 22RPG008 | 2022-03-29 | 2022-04-15 |  | 1422, 1424, 29050 | Y | N |  |  | 67378 | 67377
5940B | Mountain Home Substation and Transmission Line Addition | Cut-in the existing Gillespie to Fredericksburg 138-kV transmission line (T379) at Peach substation (converted to 138-kV, located adjacent to Live Oak substation), re-terminate and convert the existing 69-kV Harper to Live Oak transmission line to form 138-kV Headwaters to Peach transmission line, and connect the existing 69-kV Gillespie to Live Oak (T131) and existing Live Oak to Goehman Tap (T287) transmission lines to create a continuous 69-kV circuit from Gillespie to Goehman Tap. |  | Headwater | Goehman Tap. | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1017394 | 2024-05-15 | 2024-05-15 | 138 | 0 | 22.5 | 0 |  | Kerr | Gillespie | Tier 1 | 16RPG015 | 2016-11-18 |  |  | 7130, 7410, 7412, 7413 | Y | N |  |  | 78336 | 5940
45084A | Braunig to Highland Rebuild | Rebuild approximately six circuit miles of 138kV transmission from Braunig to Highland Hills/Brooks. This rebuild is between 'Highland Hills to Schillers Tap'. |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | T-0194, T-0238 | 2024-05-15 | 2024-05-03 | 138 | 0 | 6 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5030, 5095, 5205 | Y |  |  |  | 45085 | 45084
50954 | Whitepoint: Add Second Auto | Whitepoint: Add Second Auto | IN-SERVICE | Whitepoint |  | In-Service | 1085 - 1258 | AEP TCC | Dave Goetz mlforcum@aep.com 918-599-2674 | 3805 | 2024-05-15 | 2024-05-15 | 345 | 0 | 0 | 500 |  | San Patricio |  | Tier 4 | [5 empty] | Y | N |  |  | 50955 | 50954
70900A | Roanoke Area Upgrades | Establish Kingsridge 138 kV Switch |  | Kingsridge | Kingsridge | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5281 M5144 M5146 M5148 | 2024-05-15 | 2024-05-15 | 138 | 0 | 0 | 0 |  | Tarrant | Tarrant | Tier 1 | 21RPG008 | 2022-02-15 | 2022-03-15 | 2022-08-15 | 566, 1856, 2027, 2033, 2034, 2036, 2037, 2038, 12033, 12034, 12036, 12043, 12044, 12045, 12046 | Y | N |  |  | 72013 | 70900
68797 | Morgan Creek - Barber Lake East 138 kV Line | Upgrade the existing 138 kV Line |  | Morgan Creek | Barber Lake | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8624 | 2024-05-15 | 2024-05-22 | 138 | 0 | 4.83 | 0 |  | Mitchell | Mitchell | Tier 4 |  |  |  |  | 1032, 11393 | Y |  |  |  | 81361 | 68797
76680 | Add Capacitor Bank at East Stiles | Add Capacitor Bank at East Stiles |  |  |  | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8693 | 2024-05-15 | 2024-07-08 | 138 | 0 | 0 | 0 | 0,55.2 |  |  | Tier 4 |  |  |  |  | 23869 | Y |  |  |  | 76681 | 76680
76684 | Add Centralia 138 kV Capacitors | Add Centralia 138 kV Capacitors |  |  |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8700 | 2024-05-15 | 2024-06-05 | 138 | 0 | 0 | 0 | 0,55.2 |  |  | Tier 4 |  |  |  |  | 1209 | Y |  |  |  | 76685 | 76684
61465 | Starcke - Wirtz Transmission Line Storm Hardening | LCRA TSC will perform a Storm Hardening on the 6.7-mile Starcke - Wirtz (T654) 138-kV transmission line. This project will increase both the reliability and safety of the structures and conductor by ensuring that the transmission line meets or exceeds current NESC and LCRA TSC design standards and will be in compliance with PUCT storm hardening requirements for this circuit. |  | Starcke | Wirtz | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2024-05-15 | 2024-05-15 | 138 | 0 | 0 | 0 |  | Burnet | Burnet | Tier 4 |  |  |  |  | 7104, 7351 | Y | N |  |  | 61466 | 61465
76431 | Establish 345 kV Bale Switch | Establish 345 kV Bale Switch |  | 345 kV St John Switch | 345 kV Jewett Switch | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6256 | 2024-05-15 | 2024-05-15 | 345 | 0 | 0 | 0 |  | Falls | Falls | Tier 4 |  |  |  |  | 3384, 3390, 3711, 153733 | Y |  |  |  | 76432 | 76431
78683A | POI for Connolly Storage (Denton Creek Switch) | Establish Connolly Storage POI |  | Bennett Road Switch | Krum Tap Switch | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3500 | 2024-05-15 | 2024-05-15 | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  |  | 1510, 1566, 1568 | Y |  |  |  | 79645 | 78683
61463 | Marshall Ford - McNeil Transmission Line Storm Hardening | LCRA TSC will perform a Storm Hardening on the 14.2-mile Marshall Ford ¿ McNeil (T197) 138-kV transmission line. This project will increase both the reliability and safety of the structures and conductor by ensuring that the transmission line meets or exceeds current NESC and LCRA TSC design standards and will be in compliance with PUCT storm hardening requirements for this circuit. |  | Marshall Ford | McNeil | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2024-05-15 | 2024-05-15 | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 | 22RPG018 | 2022-06-15 | 2022-07-08 |  | 7334, 7356, 7542 | Y | N | 22RPG018 reclassified as Teir 4 neutral by REPG review on 1/08/2022 |  | 61464 | 61463
61402 | Boerne-Esperanza Transmission Line Upgrade | This project will increase the reliability and capacity of transmission facilities on the 1.7-mile T657 Boerne to Esperanza 138-kV and T656 Bergheim to Kendall 345-kV double-circuit transmission line between Boerne Split and Esperanza Substation and the 2.2-mile T657 Boerne to Esperanza 138-kV and T228 Boerne to Welfare double-circuit transmission line between Boerne Substation and Boerne Split by replacing the aging conductors. |  | Boerne | Esperanza | Planned | 61406, 61358, 61392, 61350, 61234, 61362, 61356, 61400, 61404 | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2024-05-15 | 2024-05-10 | 345 | 0 | 3.9 | 0 |  | Kendall | Kendall | Tier 4 | 22RPG005 | 2022-03-04 | 2022-09-09 |  | 7046, 7153, 7168, 7710, 7770 | Y | N |  |  | 61403 | 61402
57726 | Commerce - Royse 69 kV Line Conversion to 138 kV | Convert existing 69 kV Line to 138 kV |  | Commerce Switch | Royse | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R985 | 2024-05-15 01:00 | 2024-05-23 | 138 | 0 | 38.3 | 0 |  | Hunt | Rockwall | Tier 3 | 20RPG023 | 2020-12-23 | 2021-01-19 |  |  | Y | N |  |  | 81830 | 57726 | 2020-NC5
70204 | LCRATSC_McCarty_Rattler_TL_Upgrade | LCRA plans to upgrade T725 McCarty Lane - Rattler 138-kV transmission line to obtain a higher operational rating. |  | McCarty Lane | Rattler | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2024-05-17 | 2024-02-26 | 138 | 0 | 1.27 | 0 |  | Hays | Hays | Tier 4 |  |  |  |  | 7182, 7184 | Y | N |  |  | 78307 | 70204
70351 | LCRATSC_Rattler_Redwood_TL_Upgrade | Upgrade T262 Rattler - Redwood 138-kV transmission line to obtain a higher operational rating. |  | Rattler | Redwood | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2024-05-17 | 2024-05-15 | 138 | 0 | 1.07 | 0 |  | Hays | Hays | Tier 4 |  |  |  |  | 7184, 7188 | Y | N |  |  | 70352 | 70351
82210 | PMCR for LEAGUE CITY STATION REBUILD | [6 empty] | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2024-05-31 | 2025-01-24 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 38920 | Y |  |  |  | 82211 | 82210
76212 | Model Coachwhip Sub |  |  | From Mivida PSSE bus# 38152 | To Fishhook PSSE Bus# 38180 | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2024-05-31 | 2024-07-19 | 138 | 0 | 0 | 0 |  | Ward | Ward | Tier 4 |  |  |  |  | 38152, 38170, 38180 | Y |  |  |  | 76213 | 76212
77148 | Coryell Rebuild |  |  |  |  | Under Construction |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2024-05-31 | 2024-05-15 | 69 | 0 | 0 | 0 |  | Coryell | Coryell | Tier 4 |  |  |  |  | 37520, 37530, 37570, 37580 | Y |  |  |  | 77149 | 77148
75835B | Upgrade Ckt.66B Stone Lake to Tomball to increase thermal limits. Install 40 MVAR cap bank at Hockley substation and tapped on Ckt.66B Hockley to Stone Lake. | Install 40 MVAR cap bank at Hockley substation and tapped on Ckt.66B Hockley to Stone Lake. |  | Hockley |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 | 2024-05-09 | 138 | 0 | 0 | 0 | 0,40 | Harris | Harris | Tier 3 | 23RPG012 | 2023-05-04 | 2023-05-26 | 2023-05-26 | 45880 | Y | N |  |  | 75837 | 75835
75932 | Village Creek Distribution Transformer Addition | Expand Village Creek substation with addition of 3rd distribution transformer. Transformer expected at Ckt.09K Zenith to Village Creek to Franz. |  | Village Creek | Zenith/ Franz | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 | 2024-05-10 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 44272 | Y | N |  |  | 80705 | 75932
75936 | Galena Park Distribution Transformer Addition | Expand Galena Park substation with addition of 3rd distribution transformer. Transformer expected at Ckt.94M Normandy tap to Galena Park tap to TANKER. |  | Galena Park |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 | 2024-04-08 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 | [5 empty] | Y | N |  |  | 75937 | 75936
69900B | Eastgate (EAS) 138kV CNP Substation for XE Murat Solar (22INR0354) | Install generator lead from Eastgate (EAS) substation to ADLONG/XE Murat Solar |  | Eastgate | ADLONG | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 | 2024-05-13 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 | [5 empty] | Y | N |  |  | 86050 | 69900
69900A | Eastgate (EAS) 138kV CNP Substation for XE Murat Solar (22INR0354) | New 138kV Eastgate (EAS) substation for generator interconnection to XE Murat Solar. Loop Ckt.66E into substation to create new Ckt.66 Crosby to Eastgate to Atascocita. |  | Eastgate | Atascocita/Crosby | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 | 2024-05-13 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40130, 40390, 40690 | Y | N |  | Loop Ckt.66E into new substation to create new Ckt.66 Crosby to Eastgate to Atascocita. | 86051 | 69900
67422B | Greens Bayou to Clinton 138kV Conversion | Reduce existing Greens Bayou cap bank CB1 from 120 MVAR to 100 MVAR |  | Greens Bayou | 0 | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 | 2024-03-01 | 138 | 0 | 0 | 0 | -20,0 | Harris | Harris | Tier 4 |  |  |  |  | 40717 | Y | N |  |  | 87575 | 67422
69896 | Singleton Expansion for Limousin Oak Storage (22INR0338) | Expand Singleton 345kV substation and install one generator lead for new interconnection to Limousin Oak Storage |  | Singleton |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 | 2024-05-03 | 345 | 0 | 0 | 0 |  | Grimes |  | Tier 4 |  |  |  |  | 40090, 40942, 44645, 48214, 120742 | Y | N |  |  | 69897 | 69896
66009B | SNUG (SNU) 138kV CEHE Station for Cottonwood Bayou Solar (21INR0228 | Install one generator lead for new interconnection to COTTON/Cottonwood Bayou Solar |  | SNUG | COTTON | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 00:01 | 2024-03-21 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 44890, 113435 | Y | N |  |  | 75723 | 66009
67422C | Greens Bayou to Clinton 138kV Conversion | Convert Wallisville substation from double-tap service to loop service on Ckt.10A. Remove TEXWAL substation from Ckt.10 service. Resulting in Ckt.10A Clinton to CASTEN tap to Wallisville loop to Greens Bayou |  | Clinton | Greens Bayou | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 00:01 | 2024-02-07 | 69 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 40352, 40720, 41570, 41680, 41681, 41682, 48299, 48372, 48412, 48413 | Y | N |  |  | 87576 | 67422
67422D | Greens Bayou to Clinton 138kV Conversion | Rebuild TEXWAL substation as 138kV breakered station. Rebuild Wallisville substation as 138kV loop-tap station. Expand Greens Bayou 138kV 'West' bus and Clinton 138kV station with new line positions. Reconfigure and connect new 138kV stations to create new 138kV Ckt.xx Greens Bayou to TEXWAL to Wallisville to Clinton. |  | Greens Bayou | Clinton | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 00:02 | 2024-02-07 | 138 | 2.17 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40350, 40715, 41575 | Y | N |  | Cost included in Phase C | 87577 | 67422
73371I | BP24 Sub Upgrades | Upgrade Jefferson to South Channel Ckt.06E to increase thermal limits |  | Jefferson | South Channel | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 00:08 | 2024-02-06 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 41240, 41370 | Y | N |  |  | 89973 | 73371
66009A | SNUG (SNU) 138kV CEHE Station for Cottonwood Bayou Solar (21INR0228 | Loop new CEHE 138kV substation SNUG (SNU) into Ckt.04 Liverpool to PETSON to create new Ckt.04 Liverpool to SNUG to PETSON. |  | SNUG | Liverpool/PETSON | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-05-31 12:00 | 2024-03-21 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42870, 43070, 44890 | Y | N |  |  | 66010 | 66009
63902 | Bakersfield: Build New 345 kV Terminal | Interconnect Hydra BESS to the Bakersfield 345 kV Station | IN-SERVICE | Bakersfield |  | In-Service | 1136 - 1314 | ETT | Rasa Ansari twang1@aep.com 918-599-2635 | 1881 | 2024-06-12 | 2024-05-01 | 345 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  |  | 76002, 135602 | Y | N |  |  | 63903 | 63902
68970 | Lobo: Build (2) 345 kV terminals | Construct new terminals at Cenizo, Del Sol, Lobo, and Pomelo for the ETT 2nd circuits project | Transmission Status, In-Service Date, Planning Tier, RPG Number, and RPG Dates Update | Lobo |  | In-Service |  | ETT | James Weaver mlforcum@aep.com 918-599-2674 | TP2021704 | 2024-06-12 | 2024-05-01 | 345 | 0 | 0 | 0 |  | Webb |  | Tier 1 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 80219 | Y | Y |  |  | 68971 | 68970
54811 | Winecup: Build 69 kV station | Construct new 69 kV box bay on the North San Angelo to San Angelo Grape Creek Tap 69 kV line | IN-SERVICE | Winecup |  | In-Service | 1041 - 1268 | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 | 1858 | 2024-06-12 | 2024-07-01 | 69 | 0 | 0 | 0 |  | Tom Green |  | Tier 4 |  |  |  |  | 6459, 6465, 60796 | Y | N |  |  | 54812 | 54811
61398 | Whitepoint 138 kV Station: Upgrade Pelican Terminal | Upgrade the Pelican terminal at the Whitepoint 138 kV station | IN-SERVICE | Whitepoint |  | In-Service |  | AEP TCC | Wade Weller deevans@aep.com 918-599-2938 | TP2020040 | 2024-06-12 | 2024-11-27 | 138 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 | 19RPG0016 |  |  |  | 8961, 80259 | Y |  |  |  | 61399 | 61398
66386 | Albany to Throckmorton: Rebuild 69 kV line | Rehab 69 kV line from Albany to Throckmorton | IN-SERVICE | Albany | Throckmorton | In-Service |  | AEP TNC | Raza Ansari twang1@aep.com 918-599-2635 |  | 2024-06-12 | 2024-05-15 | 69 | 0 | 32.36 | 0 |  | Shackelford | Throckmorton | Tier 4 | 21RPG015 | 2022-08-21 | 2022-09-21 |  | 6205, 6206, 6207 | Y | N |  |  | 66387 | 66386
70225 | Junction: Install capacitor bank | Install Capacitor Bank at Junction Station | IN-SERVICE | Junction |  | In-Service |  | AEP TNC | Damian Raab twang1@aep.com 918-599-2635 |  | 2024-06-12 | 2024-08-20 | 69 | 0 | 0 | 0 | 0,7.7 | Kimble |  | Tier 4 |  |  |  |  | 6400 | Y | N |  |  | 70226 | 70225
50710 | Quartz Sand 138 kV Switch | Construct a new 138 kV switch |  | Spraberry | Polecat Creek | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8670 | 2024-06-13 | 2024-06-22 | 138 | 0 | 0 | 0 |  | Glasscock | Glasscock | Tier 4 |  |  |  |  | 1328 | Y |  |  |  | 73335 | 50710
68780 | Triangle - Yosemite 138 kV Line | Upgrade the existing 138 kV Line |  | Triangle | Yosemite | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8626 | 2024-06-13 | 2024-09-15 | 138 | 0 | 11.2 | 0 |  | Midland | Midland | Tier 4 |  |  |  |  | 11390, 23858 | Y |  |  |  | 85995 | 68780
71968 | Midkiff - Pemkiff 138 kV Line | Rebuild the existing 138 kV line |  | Midkiff | Pemkiff | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8641 | 2024-06-13 | 2024-06-21 | 138 | 0 | 0.31 | 0 |  | Upton | Upton | Tier 4 |  |  |  |  | 1210, 23871 | Y |  |  |  | 71970 | 71968
66216 | Upgrade and convert Waco West - Temple 69 kV Line to 138 kV | Upgrade and convert Waco West - Temple 69 kV Line to 138 kV |  | Waco West | Temple | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6191 | 2024-06-15 | 2024-12-26 | 138 | 0.7 | 6.7 | 0 |  | McLennan | Bell | Tier 4 | 22RPG046 | 2022-12-01 | 2023-01-01 |  | 147, 3361, 3417, 3437, 3446, 3544, 3578, 3580, 3581, 3644, 13662 | Y |  |  |  | 67582 | 66216
71901 | Install 110.4 Mvar 138 kV capacitor bank at Thorndale North | Install 110.4 Mvar 138 kV capacitor bank at Thorndale North |  | Thorndale North | Thorndale North | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6236 | 2024-06-15 | 2024-06-28 | 138 | 0 | 0 | 0 | 0,110.4 | Milam | Milam | Tier 4 | [5 empty] | Y |  |  |  | 71902 | 71901
66522 | Andrews North - Paul Davis Tap 138 kV Line Rebuild | Add Andrews North - Paul Davis Tap 138 kV Line Rebuild |  | Andrews North | Paul Davis Tap | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8596 | 2024-06-15 | 2024-06-01 | 138 | 0 | 25 | 0 |  | Andrews | Dawson | Tier 4 | 21RPG012 | 2021-08-03 | 2021-08-26 |  | 1159, 1167, 11206 | Y |  |  |  | 87117 | 66522
71873 | CPSE_Hill Country Auto# 2 Impedance Upgrade |  |  |  |  | Planned | S-0769 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2024-06-20 | 2024-08-22 | 345 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 3 |  |  | 2022-07-09 |  | 5210, 5211, 5213 | Y |  |  |  | 71874 | 71873
61350 | Antler-Highway 46 Transmission Line Upgrade | This project will increase the reliability and capacity of transmission facilities on the T610 Antler to Highway 46 138-kV and T389 Bergheim to Hays Energy 345-kV 10.4-mile double-circuit transmission line by replacing the aging conductors from Antler to Highway 46 substations. |  | Antler | Highway 46 | Planned | 61406, 61358, 61392, 61234, 61362, 61356, 61400, 61402, 61404 | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2024-06-21 | 2024-06-21 | 345 | 0 | 10.4 | 0 |  | Comal | Comal | Tier 3 | 22RPG005 | 2022-03-04 | 2022-09-09 |  | 7043, 7171, 7177, 7770 | Y | N |  |  | 78332 | 61350
52670 | Rising Star Area voltage conversion | This portion of the project connects Green Creek Switch |  | Stephenville | Carlton Switch | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2024-06-24 | 2024-10-18 | 138 | 0 | 0 | 0 |  | Erath | Erath | Tier 4 |  |  |  |  | 286, 294, 33286 | Y |  |  |  | 52671 | 52670
61230 | Altair - Garwood Transmission Line Overhaul | LCRA TSC will perform an overhaul on the 9.4-mile Altair ¿ Garwood (T542) (including all the tap lines) 69-kV transmission line. This project will increase reliability of the structures and conductor by ensuring that the transmission line meets or exceeds current NESC and LCRA TSC design standards. |  | Altair | Garwood | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2024-06-28 | 2024-06-24 | 69 | 0 | 0 | 0 |  | Colorado | Colorado | Tier 4 |  |  |  |  | 78106, 78530 | Y | N |  |  | 61231 | 61230
51225 | Driver - Hadacol Corner 138 kV Line | Upgrade the existing 138 kV line |  | Driver Tap | Hadacol Corner | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8637 | 2024-06-30 | 2024-06-27 | 138 | 0 | 3.2 | 0 |  | Midland | Reagan | Tier 4 |  |  |  |  | 23863, 23867 | Y |  |  |  | 71134 | 51225
76676 | Roadrunner 138 kV Capacitors | Add Capacitor at Roadrunner. |  |  |  | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8677 | 2024-06-30 | 2024-06-27 | 138 | 0 | 0 | 0 | 0,55.2 |  |  | Tier 4 |  |  |  |  | 11199 | Y |  |  |  | 76679 | 76676
61513 | New RELLIS Substation |  |  | Steele Store | Smetana | Under Construction |  | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2024-06-30 | 2024-10-30 | 138 | 0 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  |  | 32780, 32852, 32853 | Y |  |  |  | 80552 | 61513
70961B | Crosby Sub Exp for HOLY/Citadel BESS and Upgrades | Upgrade Ckt.66F Baytown to Baytown TR1 tap to increase thermal limits |  | Baytown | Baytown | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-06-30 | 2024-09-27 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  |  | 40170, 44630 | Y | N |  |  | 70963 | 70961
70200 | LCRATSC_ChiefBrady_RoundRock_TL_Upgrade | LCRA TSC will upgrade T378 Chief Brady - Round Rock 138-kV transmission line to achieve a higher operational rating. |  | Chief Brady | Round Rock | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2024-07-01 | 2024-07-01 | 138 | 0 | 5.1 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | 3668, 7366 | Y | N |  |  | 70201 | 70200 | 2023-SC17
66120 | Rebuild Freeway Park-Dickinson with bundled 795 ACSS |  |  | Freeway Park (bus # 38820) | Dickinson (bus # 38820) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2024-07-01 | 2024-04-01 | 138 | 0 | 6.25 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 38820, 38850 | Y |  |  |  | 66121 | 66120
18TPIT0001 | Wiederstein Substation Transformer Replacement | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Wiederstein |  | Planned |  | GVEC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2024-07-09 | 2024-07-09 | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  |  | 7461 | Y | N |  |  | 10675 | 3319
75520 | Rising Star Area Conversions |  |  | Green Creek | Carlton | Under Construction |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2024-07-10 | 2024-08-23 | 69 | 0 | 0 | 0 |  | Erath | Erath | Tier 4 |  |  |  |  | 298, 299, 33286 | Y |  |  |  | 75521 | 75520
70742B | Pleak 35kV Distribution Substation | Convert Needville to a breakered substation. |  | Needville |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-07-31 | 2024-04-17 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42370, 42380, 42390, 43380 | Y | N |  |  | 86079 | 70742
78457 | Pledger Distibution Substation | Rebuild Pledger distribution substation from tap to loop-tap service. |  | Pledger |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-07-31 | 2024-04-26 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 43110, 43120, 43121, 43340, 48281 | Y | N |  |  | 80967 | 78457
75522 | Rising Star Area Conversions |  |  | Stephenville | Stephenville | Under Construction |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2024-08-10 | 2024-10-23 | 138 | 0 | 0 | 0 |  | Erath | Erath | Tier 4 |  |  |  |  | 286, 295, 299 | Y |  |  |  | 75523 | 75522
52179 | Rising Star Area Conversions | This converts Hasse to Downing to 138 KV |  | Downing | Hasse | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2024-08-10 | 2024-05-17 | 138 | 0 | 0 | 0 |  | Comanche | Comanche | Tier 4 |  |  |  |  | 277, 278, 281, 1649, 33281 | Y |  |  |  | 52180 | 52179
72596D | PEC_MarshallFord_Paleface_StormHardening | Align Impedances and ratings on line to current delays and project status. Future phases were also adjusted. |  |  |  | In-Service |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2024-08-15 | 2024-05-01 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 70477, 77356 | Y |  |  |  | 87546 | 72596
78683B | POI for Connolly Storage (Denton Creek Switch) | Establish Denton Creek Switch tie line to Connolly storage |  | Bennett Road Switch | Krum Tap Switch | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3500 | 2024-08-16 | 2024-05-15 | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  |  | 1510, 154272 | Y |  |  |  | 79646 | 78683
76618 | Expand 345kV Refuge substation for Peyton Creek Wind II (20INR0155) | Expand 345kV Refuge substation for Peyton Creek Wind II (20INR0155) |  |  |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-08-31 | 2024-05-13 | 345 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  |  | 42400, 111383 | Y | N |  |  | 76619 | 76618
63497 | Bakersfield to Cedar Canyon 2nd circuit | Add the 2nd circuit to CREZ Bakersfield to Cedar Canyon 345 kV line |  | Bakersfield | Cedar Canyon | In-Service |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2024-09-01 | 2024-09-12 | 345 | 21.1 | 0 | 0 |  | Pecos | Crockett | Tier 2 |  | 2021-02-04 | 2021-06-11 |  | 76002, 76015 | Y | N |  |  | 63498 | 63497
52175 | Rising Star Area Conversions | This continues the Rising Star Area Conversions with Downing to Mountary | Carlton to Downing 138 kV Conversion | Carlton | Downing | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2024-09-10 | 2024-06-06 | 138 | 0 | 0 | 0 |  | Erath | Comanche | Tier 4 |  |  |  |  | 281, 294, 297 | Y |  |  |  | 52176 | 52175
77035 | New Mathis Substation | Remove Mathis substation, construct new Mathis substation | IN-SERVICE | Mathis |  | In-Service |  | AEP TCC | Chase Isaac deevans@aep.com 918-599-2938 | DP20X0003 | 2024-09-12 | 2024-09-12 | 69 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  |  | 5666, 5668, 8107, 8407, 8424, 8671 | Y |  |  |  | 77036 | 77035
66200B | Upgrade Taylor - Holland 69 kV Line | Rebuild the Bartlett Tap - Bartlett 69 kV Line |  | Taylor | Holland | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6173 | 2024-09-15 | 2024-12-04 | 69 | 0 | 5.3 | 0 |  | Bell | Williamson | Tier 4 | 22RPG036 |  |  |  | 3647, 13647 | Y |  |  |  | 71895 | 66200
45693 | Rocky Road - Stiles 138 kV Line | Upgrade the existing 138 kV line |  | Rocky Road | Stiles | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8599 | 2024-09-15 | 2024-09-20 | 138 | 0 | 6.6 | 0 |  | Reagan | Reagan | Tier 4 |  |  |  |  | 23864, 23868 | Y |  |  |  | 71171 | 45693
72588B | Trading Post to Cedar Valley Storm Hardening | Terminal Equipment upgrade on this facility before project completion that increases rating on the line. |  | Trading Post | Cedar Valley | Planned |  | PEC | Charles Dewitt Charles.Dewitt@peci.com 830-868-5041 |  | 2024-09-16 | 2024-09-01 | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 70505, 70506 | Y | N |  |  | 87525 | 72588
5167 | Poesta to Tuleta: Build new double circuit 138/69 kV line | Construct a new 138/69 kV Poesta station and install a 138/69 kV autotransformer with 130 MVA capacity at Poesta station. Rebuild and convert Beeville - Three Rivers 69 kV line to 138 kV and reterminate into Poesta. Construct the new 138/69 kV double circuit transmission line from Tuleta - Beeville. | IN-SERVICE | Poesta | Tuleta | In-Service | 742 - 0925 | AEP TCC | Dave Goetz mlforcum@aep.com 918-599-2674 | 2916 | 2024-09-17 | 2024-09-17 | 138 | 23.5 | 23.5 | 0 |  | Bee | Bee | Tier 1 | 15RPG004 | 2015-03-01 | 2015-09-01 | 2015-10-01 | 8195, 8196, 8197, 8198, 8584, 8585, 8586, 8590, 8592, 8593, 8629, 85851, 88198 | Y | N |  |  | 61033 | 5167 | 2015-S10
70777 | Bunsen: Install Cap Bank | Install a 15.4 MVAR capacitor bank at the Bunsen 138 kV station | IN-SERVICE | Bunsen |  | In-Service |  | AEP TCC | Brooks Dow deevans@aep.com 918-599-2938 | TP2022722 | 2024-09-26 | 2024-09-26 | 138 | 0 | 0 | 0 | 0,15.4 | Nueces |  | Tier 4 |  |  |  |  | 8459 | Y |  |  |  | 70778 | 70777
70190 | LCRATSC_Cuero_Substation_Upgrade | Increase the reliability of substation equipment at the Cuero Substation by converting the station bus layout from single bus single breaker to a breaker and a half configuration, replacing obsolete and/or aged equipment, upgrade facility structures as required, and installing a new control enclosure to adhere to high wind requirements. Contingency Update |  | Cuero | Cuero | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2024-09-28 | 2024-09-24 | 138 | 0 | 0 | 0 |  | DeWitt | DeWitt | Tier 4 | 23RPG015 | 2023-06-02 | 2023-06-26 |  |  | Y | Y |  |  | 70191 | 70190
70742A | Pleak 35kV Distribution Substation | Install new Pleak (PLK) 138/35kV Distribution Substation. Loop from existing Ckt.89A to create new Ckt.89 Big Creek to Pleak to Fort Bend. |  | Pleak | Big Creek/Fort Bend | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-09-30 | 2024-05-14 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42370, 42380, 42390, 44280, 44680 | Y | N |  |  | 86078 | 70742
88058 | Upgrade the existing 55.2 MVAR capacitor bank to a 110.4 MVAR capacitor bank | Upgrade the existing 55.2 MVAR capacitor bank to a 110.4 MVAR capacitor bank |  | Tex Harvey |  | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8812 | 2024-10-01 | 2024-10-01 | 138 | 0 | 0 | 0 |  | Midland | Midland | Tier 4 |  |  |  |  | 1221 | Y |  |  |  | 88061 | 88058
76694 | Calmont 69 kV line rebuild | Calmont 69 kV line rebuild |  | Calmont | Calmont | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5137 | 2024-10-01 | 2024-12-28 | 69 | 0 | 2.9 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  |  | 11956, 12089 | Y |  |  |  | 76695 | 76694
75567 | Create_Magness_Bus |  |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2024-10-01 | 2024-09-19 | 138 | 0 | 0 | 0 |  | Hunt | Hunt | Tier 4 |  |  |  |  | 6817, 6879, 6883 | Y |  |  |  | 75568 | 75567
82304 | Blackjack 138kV-69kV Substation |  |  |  |  | Under Construction |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2024-10-02 | 2024-12-13 | 138 | 0.674 | 0 | 178 |  | Bosque | Bosque | Tier 4 |  |  |  |  | 1646, 1647, 37650, 37680, 37681, 37682 | Y |  |  |  | 87722 | 82304
59093 | Starr Solar Connection | Starr Solar Connection | IN-SERVICE | Roma Tap |  | In-Service |  | AEP TCC | William Lovelace mlforcum@aep.com 918-599-2674 | TP2020209 | 2024-10-09 | 2024-10-09 | 138 | 0.1 | 0 | 0 |  | Starr |  | Tier 4 |  |  |  |  | 8795, 88795 | Y |  |  |  | 59094 | 59093
75518 | Rising Star Area Conversions |  |  | Carlton Switch | Carlton (298) | Under Construction |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2024-10-10 | 2024-10-18 | 69 | 0 | 0 | 0 |  | Erath | Erath | Tier 4 |  |  |  |  | 297, 298, 299 | Y |  |  |  | 75519 | 75518
72586 | Seward Junction capacitor bank addition | Install 31.3 Mvar capacitor bank at Seward Junction. Replaces ERCOT Project # 70361. |  | Seward Junction |  | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2024-10-15 | 2024-12-19 | 138 | 0 | 0 | 0 | 0,31.2 | Williamson |  | Tier 4 |  |  |  |  | 70524 | Y | Y |  |  | 72587 | 72586
66194B | Holliday - Navy Kickapoo 69 kV Line | Idle Holliday-Navy Kickapoo 69 kV line and Demolish Blackwell 69 kV Substation |  | Holliday | Navy Kickapoo | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R4022 | 2024-10-15 | 2024-11-08 | 69 | 0 | 0 | 0 |  | Archer | Archer | Tier 4 |  |  |  |  | 1473, 1525, 1526, 1527 | Y |  |  |  | 78353 | 66194
70798 | Stewart Road: Station work | Kiskadee Storage | IN-SERVICE | Stewart Road | Kiskadee | In-Service |  | AEP TCC | Curtis Brown jlsolis@aep.com 361-881-5574 | TP2022166 | 2024-10-17 | 2024-10-17 | 138 | 1 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 | [5 empty] | Y |  |  |  | 70799 | 70798
48327 | Reconductor 138kV ckt 972 Howard Lane to McNeil to 3000A. |  |  | 9079 | 9217 | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinene 512-322-6740 |  | 2024-10-18 | 2024-01-26 | 138 | 0 | 2.81 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9079, 9217 | Y |  |  |  | 48328 | 48327
6373 | Hamilton Road to Picacho Ckt #2: Rebuild 138 kV Line | Rebuild Hamilton Road to Picacho 138 kV line ckt #2 | IN-SERVICE | Hamilton Road | Picacho | In-Service | 870-1051 | AEP TCC | Jeremy Brazeal jlsolis@aep.com 361-881-5574 | 3660 | 2024-10-18 | 2024-10-18 | 138 | 0 | 8.4 | 0 |  | Val Verde | Val Verde | Tier 4 |  |  |  |  | 8186, 8255, 8684, 8687, 8688, 8690 | Y | N |  |  | 65505 | 6373 | 2017-W1 W2
86962 | Planck: Install New WSL Metering | Interconnect Torrecillas BESS to the existing Planck 345 kV station | IN-SERVICE | Planck |  | In-Service |  | ETT | Michael Forcum mlforcum@aep.com 918-599-2674 | TP2024040 | 2024-10-30 | 2024-10-30 | 345 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  |  | 80219 | Y |  |  |  | 86963 | 86962
57750 | Seabrook 138kV Distribution Substation | Build new 138kV Seabrook distribution substation. Double tap from Ckt.79F PH Robinson to Hanna and Ckt.96A PH Robinson to Bayou. |  | Seabrook |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-10-31 | 2024-12-15 | 138 | 0 | 0 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 42160, 42780, 42851, 42852, 42853, 48282, 48283, 48851, 48852 | Y | N |  |  | 86005 | 57750
57549A | Garden Villas 138kV Load Conversion | Reposition existing Garden Villas dual-voltage transformers TR1/TR2. Reposition one of the transformers with Ckt.06G Garden Villas to Drouet and rename transformer as TR4. |  | Garden Villas | Drouet | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-10-31 | 2024-11-07 | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 42680, 42690 | Y | N |  |  | 79860 | 57549
57549B | Garden Villas 138kV Load Conversion | Reposition existing Garden Villas dual-voltage transformers TR1/TR2. Reposition one of the transformers with Ckt.07A Garden Villas to Chocolate Bayou tap and rename transformer as TR3. |  | Garden Villas | Chocolate Bayou | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-10-31 | 2024-11-07 | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 42042, 42680, 42681, 42683, 42690 | Y | N |  | Cost included in main project | 79859 | 57549
73371A | BP24 Sub Upgrades | Upgrade Bellaire Auto A2 spans and CTs to increase thermal limits |  | Bellaire |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-10-31 | 2024-10-14 | 345 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  |  | 47000, 47010, 49084 | Y | N |  |  | 89974 | 73371
73057 | Basil: Construct New 138 kV Station | Interconnect Tulsita Solar to the new Basil 138 kV station on the Euler to Tuleta 138 kV line | IN-SERVICE | Basil |  | In-Service |  | AEP TCC | Raza Ansari jlsolis@aep.com 361-881-5574 |  | 2024-10-31 | 2024-10-18 | 138 | 0 | 0 | 0 |  | Goliad |  | Tier 4 |  |  |  |  | 8162, 8590, 8595, 8731 | Y |  |  |  | 73058 | 73057
75628 | Poetry 345 kV Switch | Establish Poetry 345 kV Switch |  | Poetry | Poetry | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3228 | 2024-10-31 | 2024-06-04 | 345 | 0 | 0 | 0 |  | Kaufman |  | Tier 4 | [5 empty] | Y |  |  |  | 87875 | 75628
78464 | Refuge 345kV Substation Expansion for Peyton Creek Wind II (20INR0155) | Expand 345kV Refuge substation for Peyton Creek Wind II (20INR0155) |  | Refuge |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-10-31 | 2024-05-13 | 345 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  |  | 42400, 114093 | Y | N |  |  | 78465 | 78464
61358 | Highway 46-River Oaks Transmission Line Upgrade | This project will Increase the reliability of transmission facilities on the T518 Highway 46 to River Oaks 138-kV and T389 Bergheim to Hays Energy 345-kV 8.6-mile double-circuit transmission line by replacing the aging conductor. Project ID 61356 captures the T389 Bergheim - Hays Energy 345-kV conductor upgrade for modeling purposes. |  | Highway 46 | River Oaks | Planned | 61406, 61392, 61350, 61234, 61362, 61356, 61400, 61402, 61404 | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2024-11-13 | 2024-11-13 | 345 | 0 | 8.6 | 0 |  | Comal | Comal | Tier 3 | 22RPG005 | 2022-03-04 | 2022-09-09 |  | 7043, 7173, 7177, 7770 | Y | N |  |  | 78326 | 61358
77648A | Establish Tiger Creek 345 kV Switch for Jaguar Solar/BESS | Establish Tiger Creek 345 kV Switch for Jaguar Solar/BESS |  | Tiger Creek Switch | Tiger Creek Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6223 | 2024-11-14 | 2024-12-01 | 345 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 13401, 13405, 68090 | Y |  |  |  | 77649 | 77648
49572 | Goodlett to Quanah: Build a new portion of 69 kV line | Build new section of 69 kV line between Goodlett and Quanah | IN-SERVICE | Goodlett | Quanah | In-Service | 1022 - 1200 | AEP TNC | Dewey Peters twang1@aep.com 918-599-2635 | 2784 | 2024-11-18 | 2024-11-18 | 69 | 6 | 0 | 0 |  | Hardeman |  | Tier 2 | 19RPG020 | 2019-11-01 | 2020-01-01 |  | 6051, 6052, 60446 | Y | N |  |  | 49573 | 49572
73050 | LCRATSC_JohnDumas_Substation_Addition | Substation addition to provide point interconnection for a new power plant. |  | John Dumas |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2024-11-20 | 2024-11-20 | 345 | 0 | 0 | 0 |  | Caldwell |  | Tier 4 |  |  |  |  | 7041, 7047, 7050 | Y | N |  |  | 73051 | 73050
71011 | Solstice: CT Removal | Remove CTs from Solstice station located along the Solstice to Sand Lake ONCOR and the Solstice to Bakersfield LCRA 345 kV double circuit lines | IN-SERVICE | Solstice |  | In-Service |  | AEP TNC | Chris Caroll twang1@aep.com 918-599-2635 |  | 2024-11-25 | 2024-11-25 | 345 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  |  | 11098, 60404, 76002 | Y | N |  |  | 71012 | 71011
50948 | Angstrom - Grissom: Build New Line | Angstrom - Grissom: Build New Line | IN-SERVICE | Angstrom | Grissom | Planned | 1063 - 1236 | AEP TCC | Teresa Trotman mlforcum@aep.com 918-599-2674 | 3797 | 2024-11-30 | 2024-11-22 | 345 | 17 | 0 | 0 |  | San Patricio | Bee | Tier 1 | 19RPG0016 | 2019-10-07 | 2020-05-19 | 2020-06-09 | 8249, 8624 | Y | N |  |  | 50949 | 50948
50966 | Naismith: Build 345/138 kV Station | Build new 345/138 kV station with two autotransformers | IN-SERVICE | Naismith |  | In-Service | 1063 - 1236 | AEP TCC | Thomas Reynolds mlforcum@aep.com 918-599-2674 | TP2017032 | 2024-11-30 | 2024-12-18 | 345 | 0 | 0 | 1350 |  | San Patricio |  | Tier 1 | 19RPG0016 | 2019-10-07 | 2020-05-19 | 2020-06-15 | 8659, 8660, 8674 | Y | N |  |  | 69279 | 50966
87594 | Rebuild League City-Dickinson 138kV with 2-795 ACSS. |  |  | Dickinson (38850) | League City (38920) | Under Construction |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2024-11-30 | 2024-11-26 | 138 | 0 | 5.6 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 38850, 38920 | Y |  |  |  | 87595 | 87594
72042 | Oasis 345kV Substation Expansion for SMT Ironman BESS (24INR0265) | Expand 345kV Oasis substation for SMT Ironman BESS (24INR0265) |  | Oasis |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-11-30 | 2024-10-09 | 345 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  |  | 43030, 43035, 113613 | Y | N |  |  | 72043 | 72042
73371G | BP24 Sub Upgrades | Upgrade Ckt.27A DOW to Jones Creek to increase thermal limits for Continuous ratings |  | DOW | Jones Creek | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-11-30 00:06 | 2024-12-12 | 345 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42500, 42530 | Y | N |  |  | 89976 | 73371
52728 | Add Foundry 138 kV Switch | Oncor's portion of AEP's Crane Area Transmission Project |  | LCRA Arco Crane | Navajo Tap | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8502 | 2024-12-01 | 2024-12-01 | 138 | 0 | 0 | 0 |  | Crane | Crane | Tier 4 |  | 2019-06-01 | 2019-07-22 |  | 10002, 11202, 60448, 71199 | Y |  |  |  | 52730 | 52728 | 2019-FW2
63579 | Roby to Rotan: Rebuild 69 kV Line | Rebuild the Roby to Rotan 69 kV Line | IN-SERVICE | Roby | Rotan | In-Service | 1130 - 1308 | AEP TNC | Christopher Carroll twang1@aep.com 918-599-2635 | 1875 | 2024-12-11 | 2024-12-11 | 69 | 0 | 8 | 0 |  | Fisher |  | Tier 4 |  |  |  |  | 6194, 6195, 6196 | Y | N |  |  | 63580 | 63579
76145 | Matador: Station Build | Build a new Matador station five breaker ring bus | IN-SERVICE | Matador |  | In-Service |  | AEP TNC | Chris Carrol twang1@aep.com 918-599-2635 | TA2020140 | 2024-12-11 | 2024-12-11 | 69 | 0 | 0 | 0 |  | Motley |  | Tier 4 |  |  |  |  | 6039, 6074, 6140, 6141 | Y | N |  |  | 76146 | 76145
50843 | Heron: Build 138 kV station | Build Heron 138 kV station with a 138/69 kV auto, expand the Kinnison 138 kV station, expand the Sage 69 kV station, rebuild Heron to Ollin and convert to a 138 kV line, and rebuild Kinnison to Sage 69 kV line | IN-SERVICE | Heron |  | In-Service | 1048 - 1221 | AEP TNC | Gregory Crane twang1@aep.com 918-599-2635 | 2796 | 2024-12-12 | 2024-12-12 | 138 | 0 | 0 | 90 |  | Crane |  | Tier 3 |  | 2019-06-21 | 2019-07-22 |  | 6610, 6611, 6614, 60447, 60448 | Y | N |  |  | 50844 | 50843
51010 | Heron to Ollin: Rebuild and convert to 138 kV line | Build Heron 138 kV station with a 138/69 kV auto, expand the Kinnison 138 kV station, expand the Sage 69 kV station, rebuild Heron to Ollin and convert to a 138 kV line, and rebuild Kinnison to Sage 69 kV line | IN-SERVICE | Heron | Ollin | In-Service | 1048 - 1221 | AEP TNC | Gregory Crane twang1@aep.com 918-599-2635 | 2798 | 2024-12-12 | 2024-12-12 | 138 | 0 | 2 | 0 |  | Crane | Crane | Tier 3 |  | 2019-06-21 | 2019-07-22 |  | 60441, 60448 | Y | N |  |  | 51011 | 51010
80956 | Holly: 138 kV Breaker Replacement | Upgrade 138 kV bus tie breaker at the Holly 138 kV station | IN-SERVICE | Holly |  | In-Service | TP2023629 | AEP TCC | Wade Weller deevans@aep.com 918-599-2938 |  | 2024-12-13 | 2024-12-13 | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 8486 | Y | N |  |  | 80957 | 80956
66130 | North Shore Reactive Project | Install 69.2 MVAR capacitor banks at Hecker and Resnik 138 kV stations | IN-SERVICE | Hecker | Resnik | In-Service |  | AEP TCC | Chase Isaac deevans@aep.com 918-599-2938 | TP2021207 | 2024-12-13 | 2024-12-13 | 138 | 0 | 0 | 0 | 0,69.2 | San Patricio | San Patricio | Tier 4 |  |  |  |  | 8565, 8580 | Y |  |  |  | 66131 | 66130
81063 | Progress Park 138 kV Switch | Establish Progress Park 138 kV Switch |  | Progress Park |  | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3076 | 2024-12-15 | 2024-12-17 | 138 | 0 | 0 | 0 |  | Grayson |  | Tier 4 |  |  |  |  | 1699, 12677, 12678 | Y |  |  |  | 81065 | 81063
62693 | Courtney Creek - Yucca Drive 69 kV Line Conversion to 138 kV | Add Courtney Creek - Yucca Drive 69 kV Line Conversion to 138 kV |  | Courtney Creek | Yucca Drive | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8591 | 2024-12-15 | 2024-12-01 | 69 | 0 | 44 | 0 |  | Pecos | Ward | Tier 3 | 22RPG025 | 2022-08-24 | 2022-09-16 |  | 1009, 1015, 1202, 1203, 1204, 1238, 1239, 1240, 1242, 11204, 11238, 11242, 11258, 11262, 60792 | Y |  |  |  | 87202 | 62693
64089 | Raptor: Construct New 345 kV Station | Interconnect Peregrine Solar to the new Raptor 345 kV station on the Coleto Creek to Grissom 345 kV line | IN-SERVICE | Coleto Creek | Grissom | In-Service |  | AEP TCC | Brent Harris deevans@aep.com 918-599-2938 |  | 2024-12-15 | 2024-12-15 | 345 | 0 | 0 | 0 |  | Goliad |  | Tier 4 |  |  |  |  | 8164, 8624, 8673, 88673 | Y |  |  |  | 64090 | 64089
52332 | Lamesa - Paul Davis Tap 138 kV Line Section | Upgrade the existing 138 kV line |  | Lamesa | Paul Davis Tap | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8499, R8475 | 2024-12-15 | 2024-12-15 | 138 | 0 | 17 | 0 |  | Dawson | Dawson | Tier 3 |  |  |  |  | 1163, 1169, 18880 | Y |  |  |  | 87135 | 52332
80550 | Central Park 138 kV Switch | Establish Central Park 138 kV Switch for Graphic Packaging International, LLC |  | Central Park | Central Park | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6273 | 2024-12-15 | 2024-12-15 | 138 | 1.2 | 0 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  |  | 3446, 3474, 3544, 3547 | Y |  |  |  | 87808 | 80550
77650 | Establish Steakley Dam 345 kV Switch for Blevins Solar | Establish Steakley Dam 345 kV Switch for Blevins Solar |  | Steakley Dam | Steakley Dam | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6282 | 2024-12-15 | 2024-12-12 | 345 | 0 | 0 | 0 |  | Falls | Falls | Tier 4 |  |  |  |  | 3404, 3409, 3741 | Y |  |  |  | 77651 | 77650
45640 | Spraberry - Polecat Creek 138 kV Line | Upgrade the existing 138 kV line |  | Spraberry | Polecat Creek | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8645 | 2024-12-15 | 2024-12-15 | 138 | 0 | 32.4 | 0 |  | Midland | Glasscock | Tier 3 |  |  |  |  | 1328, 1329, 1337, 10029, 11337, 11350, 11372, 11394 | Y |  |  |  | 73413 | 45640
5467 | Nacogdoches Southeast_Redland 345kV Line | Establish a new 345kV Line between Nacogdoches Southeast Switch and Redland Switch |  | Nacogdoches Southeast | Redland | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6075 | 2024-12-15 | 2024-12-20 | 345 | 13.4 | 0 | 0 |  | Nacogdoches | Angelina | Tier 2 | 20RPG019 | 2020-10-01 | 2022-04-01 |  | 3119, 3321 | Y | N |  |  | 13171 | 5467
5466 | Redland Switch 345/138 kV Autotransformer | Install new 345/138 kV Autotransformer at Redland Switch previously known as Herty North |  | Redland | Redland | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6076 | 2024-12-15 | 2024-12-20 | 345 | 0 | 0 | 600 |  | Angelina | Angelina | Tier 3 | 20RPG019 | 2020-10-01 | 2022-04-01 |  | 3306, 3321, 3322 | Y | N |  |  | 13170 | 5466
5436 | Morgan Creek - McDonald 138 kV Line | Upgrade existing line | Project Deferral | Morgan Creek | McDonald Rd | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8360 | 2024-12-15 | 2024-12-15 | 138 | 0 | 31.8 | 0 |  | Howard | Mitchell | Tier 3 | 23RPG011 | 2023-05-03 | 2023-05-26 |  | 1032, 1333, 11395 | Y |  |  |  | 73625 | 5436
66289A | Tyler to Athens 138 kV line Conversion | Chandler West to Echols 69 Kv Line Upgrade |  | Chandler | Echols | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6094 | 2024-12-15 | 2024-12-31 | 69 | 0 | 0 | 0 |  | Henderson | Henderson | Tier 3 | 22RPG015 | 2022-06-01 | 2022-07-01 |  | 3108, 3236, 13235 | Y |  |  |  | 87814 | 66289
68955 | Meteor 345 kV Switch | Establish Meteor 345 kV Switch |  | Wolf | Moss | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8619 | 2024-12-15 | 2024-12-27 | 345 | 0 | 0 | 0 |  | Ward | Ector | Tier 4 |  |  |  |  | 1018, 10012, 11010 | Y |  |  |  | 68957 | 68955
66200C | Upgrade Taylor - Holland 69 kV Line | Rebuild the Bartlett - Granger 69 kV Line |  | Taylor | Holland | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6173 | 2024-12-15 | 2024-12-22 | 69 | 0 | 6.9 | 0 |  | Williamson | Williamson | Tier 4 | 22RPG036 |  |  |  | 3647, 3648 | Y |  |  |  | 71896 | 66200
73368 | Grey Well Draw - Buffalo 138 kV Second Circuit | Add Grey Well Draw - Buffalo 138 kV Second Circuit |  | Grey Well Draw | Buffalo | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8692 | 2024-12-15 | 2025-01-01 | 138 | 6 | 26.2 | 0 |  | Midland | Midland | Tier 3 |  |  |  |  | 10061, 11390, 11396, 23837, 23858 | Y |  |  |  | 87790 | 73368
71989 | Big Spring West - Stanton East 138 kV Line | Rebuild the existing 138 kV line |  | Big Spring West | Stanton East | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8303 | 2024-12-15 | 2024-12-15 | 138 | 0 | 17.6 | 0 |  | Martin | Howard | Tier 4 |  |  |  |  | 1322, 1324, 1325, 1326, 10044, 11316, 11324, 11331 | Y |  |  |  | 73334 | 71989
76080 | Laredo VFT North to North Laredo Switch: Rebuild 138 kV Line | Rebuild Mines Road to North Laredo SW 138 kV line | IN-SERVICE | Mines Road | North Laredo | In-Service | 1116 - 1294 | AEP TCC/ETT | William Lovelace jlsolis@aep.com 361-881-5574 | 3835 | 2024-12-15 | 2024-12-15 | 138 | 0 | 5.85 | 0 |  | Webb | Webb | Tier 4 |  |  |  |  | 8643, 8909 | Y |  |  |  | 76081 | 76080
72649B | Add_Celina_Load | Connecting Rayburn Celina tap to ONCOR Outer loop 138kV substation. |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2024-12-15 | 2024-04-30 | 138 | 0 | 0 | 0 |  | Collin | Collin | Tier 4 |  |  |  |  | 2350, 6793, 12351 | Y |  |  |  | 78609 | 72649
71976 | Watermill 138 kV Switch | Rebuild the existing Watermill 138 kV Switch |  | Watermill |  | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3031 | 2024-12-15 | 2024-12-15 | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 3 |  |  |  |  | 2126, 2238, 2427, 2429, 2430, 12430, 12433 | Y |  |  |  | 71977 | 71976
71993 | Tributary - Vincent 138 kV Line Section | Rebuild the existing 138 kV line |  | Tributary | Vincent | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8667 | 2024-12-15 | 2024-12-20 | 138 | 0 | 11.2 | 0 |  | Howard | Howard | Tier 3 |  |  |  |  | 1394, 1397, 10047 | Y |  |  |  | 73300 | 71993
71960 | Upgrade Grady - Expanse 138 kV Line | Rebuild the existing 138 kV line |  | Grady | Expanse | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8639 | 2024-12-15 | 2024-12-13 | 138 | 0 | 6.4 | 0 |  | Martin | Martin | Tier 4 |  |  |  |  | 11368, 23842 | Y |  |  |  | 71962 | 71960
71908 | Install second 345/138 kV Auto at Temple Pecan Creek | Install second 345/138 kV Auto at Temple Pecan Creek and cut in the Temple - Lake Creek 345 kV Line |  | Temple Pecan Creek | Temple Pecan Creek | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6239 | 2024-12-15 | 2024-12-16 | 345 | 0 | 0 | 600 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 3404, 3412, 3414, 3420, 13412 | Y |  |  |  | 71909 | 71908 | 2023-NC60
70900B | Roanoke Area Upgrades | Establish Exchange 345 kV Switch |  | Exchange Switch | Exchange Switch | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5281 M5144 M5146 M5148 | 2024-12-15 | 2024-12-31 | 345 | 0.4 | 0 | 1500 |  | Tarrant | Tarrant | Tier 1 | 21RPG008 | 2022-02-15 | 2022-03-15 | 2022-08-15 | 1845, 1851, 1855, 2081, 12077, 12078, 12079, 12080, 12081 | Y | N |  |  | 87467 | 70900
81378 | Odessa EHV - Edwards Tap 138 kV Line Rebuild | Odessa EHV - Edwards Tap 138 kV Line Rebuild |  | Odessa EHV | Wolf | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8528 | 2024-12-15 | 2024-12-31 | 138 | 0 | 16.6 | 0 |  | Ector | Ward | Tier 3 |  |  |  |  | 1027, 1052, 1053, 1054, 1099, 1110, 10134, 11003, 11281 | Y |  |  |  | 87865 | 81378
87756 | Rowan Creek 138 kV Switch | Establish Rowan Creek 138 kV Switch for Azalea Springs Solar |  | Rowan Creek | Rowan Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6257 | 2024-12-15 | 2024-12-05 | 138 | 0 | 0 | 0 |  | Angelina | Angelina | Tier 4 |  |  |  |  | 3349, 3351, 3760 | Y |  |  |  | 87757 | 87756
77624 | Wallaby Switch 345 kV Switch | Establish Wallaby Switch 345 kV Switch |  | AJ Swope | Windmill | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3021 | 2024-12-15 | 2024-12-19 | 345 | 0 | 0 | 0 |  | Deaf Smith | Deaf Smith | Tier 4 |  |  |  |  | 23906, 23909, 23910 | Y |  |  |  | 77627 | 77624
73043 | Peck - Driver 138 kV Line | Construct a new 138 kV line |  |  |  | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8603 | 2024-12-16 | 2024-12-16 | 138 | 0 | 0 | 0 |  |  |  | Tier 2 | 22RPG047 | 2022-12-27 | 2023-01-20 |  | 1217, 1222, 1223, 1226, 1329, 1330, 10114, 10126, 11222, 11226, 11227, 18664, 23863 | Y |  |  |  | 87662 | 73043
56350D | Burnett - Bowie 69 kV Line | Rebuild Old lake Switch - Smith Creek Line (FKA Ringgold Magnolia tap - Bellevue) |  | Burnett | Ringgold Magnolia Tap | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R4015 | 2024-12-16 | 2024-11-14 | 69 | 0 | 9.8 | 100 |  | Wichita | Clay | Tier 3 | 21RPG008 | 2021-04-23 | 2021-05-18 |  | 11541, 17010, 33770 | Y | N |  |  | 73041 | 56350
3297 | Tezel Road - New 138kV Substation | Loop new 138 kV substation into the existing 138 kV Helotes to Bandera line. |  |  |  | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2024-12-18 | 2024-12-19 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5020, 5200, 5421 | Y |  |  | There are no transformers associated with this project | 10840 | 3297
70717 | LCRATSC_Yarrington_Substation_Addition | Add new three terminal ring bus substation to 138 kV line between Rohr and Goforth and install 46.7 MVA distribution transformer. The new substation will be located approximately 0.17 miles from Rohr substation. |  | Rohr | Goforth | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2024-12-18 | 2024-12-18 | 138 | 0 | 0 | 0 |  | Hays |  | Tier 4 |  |  |  |  | 7501, 7514, 7515 | Y | N |  |  | 70718 | 70717
69281 | Angstrom to Naismith: Build New 345 kV Line | Build New 345 kV Line from Angstrom to Naismith | IN-SERVICE | Angstrom | Naismith | In-Service | TP2020205 | AEP TCC | William Lovelace deevans@aep.com 918-599-2938 |  | 2024-12-18 | 2024-12-18 | 345 | 19 | 0 | 0 |  | San Patricio | San Patricio | Tier 1 | 19RPG0016 | 2019-10-07 | 2020-05-19 | 2020-06-15 | 8249, 8659 | Y | N |  |  | 69282 | 69281
65725 | James Rowe: Construct New Distribution Station | Construct New Distribution Station on the North McAllen to West McAllen 138 kV Line | IN-SERVICE | James Rowe |  | In-Service | 1030 - 1208 | AEP TCC | Alison Scribailo deevans@aep.com 918-599-2938 | 3769 | 2024-12-18 | 2024-12-18 | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  |  | 8041, 8367, 8631 | Y | N |  |  | 65726 | 65725
59099 | Blessing to Celanese: Rebuild 138 kV line | Rebuild the Blessing to Celanese 138 kV line | IN-SERVICE | Blessing | Celanese Bay City | Planned |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 | TP2020227 | 2024-12-18 | 2024-12-18 | 138 | 11.54 | 0 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  |  | 8116, 8121, 8191, 8558 | Y |  |  |  | 65587 | 59099 | 2020-C1
69283 | Naismith to Resnik: Build New 138 kV Line | Build New 138 kV line from Naismith to Resnik | IN-SERVICE | Naismith | Resnik | In-Service | 1063 - 1236 | AEP TCC | Thomas Reynolds mlforcum@aep.com 918-599-2674 | TP2017032 | 2024-12-18 12:00 | 2024-12-18 | 138 | 3 | 0 | 0 |  | San Patricio | San Patricio | Tier 1 | 19RPG0016 | 2019-10-07 | 2020-05-19 | 2020-06-15 | 8580, 8660, 8674 | Y | N |  |  | 69284 | 69283
57797 | Athey: Build 138 kV Station | Build new 138 kV Station on the Ft Stockton to Rio Pecos 138 kV line | IN-SERVICE | Athey |  | In-Service | 1109 - 1287 | AEP TNC | Shawn Ketcher twang1@aep.com 918-599-2635 | 1866 | 2024-12-19 | 2024-12-19 | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  |  | 60718, 60792, 60798 | Y | N |  |  | 65578 | 57797
6934B | Elm Creek - New 345 kV Reactor | Install new 345 kV 60 Mvar Reactor at Elm Creek Substation. | [5 empty] | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0873, S-0893 | 2024-12-19 | 2024-12-19 | 345 | 0 | 0 | 0 | 60,0 | Guadalupe |  | Tier 4 |  |  |  |  | 5133 | Y |  |  |  | 14754 | 6934
70354 | LCRATSC_WolfLane_Substation_Upgrade | Upgrade Wolf Lane Substation to a 3000 A, 138-kV ring bus arrangement. Contingency Update |  | Wolf Lane |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2024-12-20 | 2024-12-20 | 138 | 0 | 0 | 0 |  | Bastrop |  | Tier 4 | [5 empty] | Y | Y |  |  | 70355 | 70354
76719 | Establish Blue Mountain 138 kV Switch | Establish 138 kV Switch |  | Blue Mountain | Blue Mountain | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8702 | 2024-12-23 | 2024-12-01 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 1092, 11070, 11113, 11382, 18680 | Y |  |  |  | 81370 | 76719
70633A | Burke to Eagles Nest Ckt.02J Upgrades | Upgrade Ckt.02J Burke to Eagles Nest as a Hardening upgrade |  | Burke | Eagles Nest | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 | 2024-07-11 | 138 | 0 | 4.59 | 0 |  | Brazoria | Brazoria | Tier 4 | 22RPG037 | 2022-10-31 | 2022-11-22 | 2022-11-22 | 42410, 42430, 42980 | Y | N |  |  | 72452 | 70633
72053 | Oasis 345kV Substation Expansion for SOHO BESS (23INR0419) | Expand 345kV Oasis substation for SOHO BESS (23INR0419). Reposition existing Ckts. 18B and 27B Oasis to Dow and Ckt.99E Meadow to Oasis. |  | Oasis |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 | 2026-02-28 | 345 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 | [5 empty] | Y | N |  |  | 72054 | 72053
73338A | Pythias (PYT) 138kV CNP Station for Second Division Solar (20INR0248) | Loop new CNP 138kV substation Pythias (PYT) into Ckt.60H to create new Ckt.60 San Bernard to Pythias to West Columbia. |  | Pythias | San Bernard/ West Columbia | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 | 2024-09-28 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 43090, 43110, 43380 | Y | N |  |  | 88037 | 73338
75930 | Expand Highlands substation with addition of 3rd distribution transformer. Transformer expected at Ckt.66F Garth to Highlands tap to Haney. |  |  | Highlands | Garth/Haney | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 | 2024-11-02 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40812 | Y | N |  |  | 75931 | 75930
52068 | Coy City Tap to Pleasanton: Convert to 138 kV | Convert Pleasanton to Three Rivers 69 kV line and Coy City Tap to Fashing 69 kV line to 138 kV, reterminate Pleasanton to Three Rivers into 138 kV yards at Pleasanton and Three Rivers, install new terminal for the Trumbo line at Pleasanton, and convert Fashing, Coy City Tap, and Schottky stations to 138 kV | IN-SERVICE | Pleasanton | Three Rivers | In-Service | 1077 - 1250 | AEP TCC | Lorraine Timmerman jlsolis@aep.com 361-881-5574 | 3802 TP2020193 | 2024-12-31 | 2024-12-03 | 138 | 0 | 8.46 | 0 |  | Atascosa | Live Oak | Tier 4 |  |  |  |  | 8142, 8199, 8200, 8203, 8400, 8403, 8406, 8507, 8599, 8600, 84061, 85071, 85991, 86001, 88507 | Y | N |  |  | 65610 | 52068 | 2020-S1/2020
67422E | Greens Bayou to Clinton 138kV Conversion | Rebuild-Reconductor Ckt.10A Wallisville tap to TEXWAL |  | Wallisville | TEXWAL | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 | 2024-01-04 | 69 | 0 | 1.44 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 41570, 41682 | Y | N |  |  | 87578 | 67422
73166 | Whitepoint: Rebuild Station | Rehab Whitepoint 138/69 kV Station | IN-SERVICE | Whitepoint |  | In-Service |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 | TA2018035 | 2024-12-31 | 2024-12-31 | 138 | 0 | 0 | 130 |  | San Patricio |  | Tier 4 |  |  |  |  | 8960, 8961 | Y | N |  |  | 73167 | 73166
76176 | Transmission POI for Dogfish BESS |  |  |  |  | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2024-12-31 | 2024-10-03 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 38331, 38455, 38465 | Y |  |  |  | 76177 | 76176
77046 | AEP_TCC_OdemSandPit | Add Odem Sand station | IN-SERVICE | Edroy | Smith | In-Service |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 | DP22X0029 | 2024-12-31 | 2024-12-31 | 69 | 0 | 0 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  |  | 8408, 8734, 8866 | Y |  |  |  | 77047 | 77046
78420 | Baytown Distribution Transformer | Install third Baytown distribution transformer on Ckt.03B to create new Ckt.03B Kenny tap to Baytown tap to Baytown 138kV. |  | Baytown | KENNY | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 | 2024-08-06 | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  |  | 40170, 40171, 40172, 40173, 44630 | Y | N |  |  | 87362 | 78420
78423 | Bellaire to WAP Ckt.50A Upgrade - WAP Switch 0505 | Upgrade Bellaire to WAP Ckt.50A to increase thermal limits |  | Bellaire | WA Parish | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 | 2024-10-19 | 138 | 0 | 0 | 0 |  | Harris | Fort Bend | Tier 4 |  |  |  |  | 44005, 47000 | Y | N |  |  | 78424 | 78423
77074 | Buda to Turnersville Storm Hardening | Rebuild single circuit section of Buda to Turnersville and reconductor with bundled 795 ACSR Conductor, 439 MVA. |  | Buda | Turnersville | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2024-12-31 | 2025-01-09 | 138 | 0 | 3.8 | 0 |  | Hays | Hays | Tier 4 |  |  |  |  | 7500, 70498 | Y | N |  |  | 77075 | 77074
73476 | Rebuild Kermit #2 as Windblown 69kV Substation. | Rebuild Kermit #2 Substation as Windblown 69kV Substation, and rebuild Wink-Windblown 69kV Line. |  | TNMP Wink (37920) | TNMP Windblown (38270) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2024-12-31 | 2024-12-20 | 69 | 0 | 10.8 | 0 |  | Winkler | Winkler | Tier 4 |  |  |  |  | 37920, 38250, 38260, 38270, 38290 | Y |  |  |  | 87443 | 73476
66567 | Add Wolf - Moss 138 kV Line Rebuild | Add Wolf - Moss 138 kV Line Rebuild |  | Wolf | Moss | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8530 | 2024-12-31 | 2024-12-31 | 138 | 0 | 34.5 | 0 |  | Ward | Ector | Tier 3 | 22RPG013 | 2022-05-11 | 2022-06-03 |  | 1013, 1019, 1292, 11292, 11293 | Y |  |  |  | 87221 | 66567
73352B | PH Robinson Area 138kV Upgrades | Upgrade Ckt.79F PH Robinson to Seabrook to HANNAH to HUNTER to increase thermal limits |  | PH Robinson | Seabrook | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 00:01 | 2025-01-09 | 138 | 0 | 0 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  |  | 42780, 42830, 42852, 48282 | Y | N |  |  | 73354 | 73352
73338B | Pythias (PYT) 138kV CNP Station for Second Division Solar (20INR0248) | Install one generator lead for new interconnection to DAMAZO / Second Division Solar |  |  |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 00:01 | 2024-09-28 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 43090, 113702, 113703 | Y | N |  |  | 88038 | 73338
70633B | Burke to Eagles Nest Ckt.02J Upgrades | Upgrade Ckt.02K Eagles Nest to West Columbia as a Hardening upgrade |  | Eagles Nest | West Columbia | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 00:01 | 2024-12-11 | 138 | 0 | 1.86 | 0 |  | Brazoria | Brazoria | Tier 4 | 22RPG037 | 2022-10-31 | 2022-11-22 | 2022-11-22 | 42430, 43380 | Y | N |  |  | 72451 | 70633
73371C | BP24 Sub Upgrades | Upgrade Crosby to Danek Ckt.08G to increase thermal limits |  | Crosby | Danek | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 00:02 | 2024-11-15 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40390, 40890 | Y | N |  |  | 89978 | 73371
73578H | Heights 138kV Loop Conversion | Install 7.2MVAR cap bank at Dunlavy TR2. |  | Dunlavy |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 00:05 | 2024-10-30 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47580 | Y | N |  |  | 90925 | 73578
73578F | Heights 138kV Loop Conversion | Install 7.2MVAR cap bank at Hyde Park TR3. |  | Hyde Park |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2024-12-31 00:05 | 2024-10-30 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47690 | Y | N |  |  | 90924 | 73578
80462 | Lon Hill to Weil Tract 138 kV(LCRA): Construct Temp Tap | Construct Temp Tap on the Lon Hill to Weil Tract 138 kV line |  | Nueces | Nueces | In-Service |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 |  | 2025-01-07 | 2024-07-17 | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 78569 | Y |  |  |  | 80463 | 80462
72085 |  |  | IN-SERVICE |  |  | In-Service |  | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 |  | 2025-01-07 | 2024-06-01 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 8111, 8127, 8668, 89500 | Y |  |  |  | 72086 | 72085
44854 | Lipton: Build 138 kV Box Bay | New Lipton 138 kV Station, replaces Lipton Hard Tap |  | Lipton |  | In-Service |  | AEP TCC | Jeremy Brazeal mlforcum@aep.com 918-599-2674 | TP2018214 | 2025-01-07 | 2024-05-14 | 138 | 0 | 0 | 0 |  | Zavala |  | Tier 4 |  |  |  |  | 8236, 8283, 8285, 88285 | Y | N |  |  | 44855 | 44854
76141 | Santo Nino: Install cap bank | Install cap banks at Santo Nino, Molina, and Wormser Road |  | Santo Nino |  | In-Service |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 |  | 2025-01-07 | 2024-02-12 | 138 | 0 | 0 | 0 | 0,23.1 | Webb |  | Tier 4 |  |  |  |  | 8653 | Y |  |  |  | 76142 | 76141
76920 | Kingsville to Bunsen: Construct Primavera Tap | Add Tesla Load |  | Bunsen | Kingsville | In-Service |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 | TP2023059 | 2025-01-07 | 2024-01-31 | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 8518, 8749, 8921, 88747 | Y |  |  |  | 76921 | 76920
69226 | Rebuild 69 kV Line from Point Comfort to Carancahua | Rebuild 69 kV Line from Point Comfort to Carancahua |  | Point Comfort | Carancahua | In-Service |  | AEP TCC | Lorraine Timmerman mlforcum@aep.com 918-599-2674 |  | 2025-01-07 | 2024-05-14 | 69 | 0 | 0 | 0 |  | Calhoun | Jackson | Tier 4 |  |  |  |  | 8131, 8132, 8555 | Y |  |  |  | 69227 | 69226
71000 | TCC& TNC Cap Bank Rehab | TCC& TNC Cap Bank Rehab | IN-SERVICE |  |  | In-Service |  | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | TA2022031 | 2025-01-07 | 2024-06-12 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 6216, 6338, 6468, 6615, 8169, 8348, 8427 | Y | N |  |  | 71001 | 71000
50874 | Smith - Mathis: Line Rebuild | Smith - Mathis: Line Rebuild |  | Smith | Mathis | In-Service | 1053 - 1226 | AEP TCC | Joseph Page bcogan@aep.com 918-599-2857 | 3781 | 2025-01-07 | 2024-02-28 | 69 | 0 | 22.47 | 0 |  | San Patricio | San Patricio | Tier 3 | 20RPG001 | 2020-02-15 | 2020-03-24 |  | 8407, 8408, 8424, 8866 | Y | N |  |  | 65547 | 50874
65987 | Gibbs: Build new 138 kV terminal | Interconnect Jackalope Solar to the Gibbs 138 kV station | In-Service Date Update | Gibbs |  | In-Service |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 | TP2021288 | 2025-01-07 | 2024-08-30 | 138 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  |  | 8173, 88173 | Y |  |  |  | 65988 | 65987
68960 | North Edinburg: Expand 345 kV station | Construct new terminals at North Edinburg for the ETT 2nd circuits project | Transmission Status, Planning Tier, RPG Number, and RPG Dates Update | North Edinburg |  | In-Service |  | AEP TCC | James Weaver mlforcum@aep.com 918-599-2674 | TP2021705 | 2025-01-07 | 2024-05-15 | 345 | 0 | 0 | 0 |  | Hidalgo |  | Tier 1 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 8383, 8455, 8901, 8905 | Y |  |  |  | 71132 | 68960
57912 | Champlin to Weil Tract: Rebuild 138 kV Line | Rebuild Champlin to Weil Tract 138 kV Line | IN-SERVICE | Champlin | Weil Tract | In-Service | 1111 - 1289 | ETT | Thomas Naves mlforcum@aep.com 918-599-2674 | 3830 | 2025-01-07 | 2024-04-08 | 138 | 0 | 1.37 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 8476, 8482 | Y | N |  |  | 65581 | 57912
72309 | AEP_TCC_LonHillHaisley | Lon Hill to Structure 25/4: Rebuild 138 kV Line |  | Lon Hill | Haisley | In-Service |  | AEP TCC | Nathan Cowan bcogan@aep.com 918-599-2857 |  | 2025-01-07 | 2024-12-23 | 138 | 0 | 10.2 | 0 |  | San Patricio | San Patricio | Tier 3 |  |  |  |  | 8027, 8046, 8912, 8920 | Y |  |  |  | 72310 | 72309
68972 | Tiempo to Fowlerton: Add Second 345 kV Circuit | Hang conductor to complete a double circuit between Tiempo and Fowlerton for the ETT 2nd circuits project | Project Title, Transmission Status, Owner, In-Service Date, RPG Number, and RPG Dates Update | Tiempo | Fowlerton | In-Service |  | ETT/STEC | Teresa Trotman mlforcum@aep.com 918-599-2674 | TP2021703 | 2025-01-07 | 2024-05-01 | 345 | 63.38 | 0 | 0 |  | Webb | Zapata | Tier 1 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 5709, 80219, 80220, 80221, 80224, 80230 | Y | Y |  |  | 68973 | 68972
50870 | Coleto Creek - Rosata: Line Rebuild | Coleto Creek - Kenedy SS: Line Rebuild | IN-SERVICE | Coleto Creek | Rosata | In-Service | 1052 - 1225 | AEP TCC | Curtis Brown bcogan@aep.com 918-599-2857 | 3778 | 2025-01-07 01:01 | 2024-05-14 | 138 | 0 | 15.3 | 0 |  | Goliad | Goliad | Tier 3 | 20RPG014 | 2020-08-19 | 2020-09-11 |  | 8153, 8162 | Y | N |  |  | 50871 | 50870
68179 | North Edinburg Red Gate | North Edinburg: Install 3 - 138 kV breakers. Re-terminate Falfurrias 138 kV Line. Terminate Redgate (STEC) 138 kV Line. | Status Update | North Edinburg | Redgate (STEC) | Under Construction |  | AEP TCC | Curtis Brown jlsolis@aep.com 361-881-5574 |  | 2025-01-17 | 2024-11-10 | 138 | 0.08 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  |  | 8380, 88380 | Y |  |  |  | 68180 | 68179
90790 | [5 empty] | In-Service |  | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 |  | 2025-01-18 | 2025-01-18 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 8108, 8909, 88000 | Y |  |  |  | 90791 | 90790
78167 | Add 2nd autotransformer at Trumbull | Add 2nd autotransformer at Trumbull |  | Trumbull | Trumbull | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2025-01-23 | 2025-02-20 | 69 | 0 | 0 | 40 |  | Ellis | Ellis | Tier 4 |  |  |  |  | 221, 222 | Y |  |  |  | 78168 | 78167
70704B | Florence Substation Addition | Fixes Florence bus disconnection issue by removing temporary equipment associated with FLORENCE substation cut-in |  |  |  | In-Service |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | PLC-6320 | 2025-01-30 | 2025-05-15 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 7521, 7523, 70522 | Y |  |  |  | 90388 | 70704
64063 | BRP Antlia BESS Interconnection | Connect BRP Antlia BESS to the Maxwell 138 kV station | Status and In-Service Date Update | Maxwell | Antlia | Under Construction |  | AEP TCC | Joseph Isaac mlforcum@aep.com 918-599-2674 |  | 2025-01-31 | 2025-01-31 | 138 | 0 | 0 | 0 |  | Val Verde | Val Verde | Tier 4 |  |  |  |  | 8998, 88999 | Y |  | TP2021260 |  | 64064 | 64063
87389 | Friendswood Energy GENCO GT (24INR0456) | Friendswood Energy GENCO GT at HO Clarke substation. Utilize existing HO Clarke to Friendswood Energy generator lead. |  | HO Clarke |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-01-31 | 2024-12-31 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 | [5 empty] | Y | N |  |  | 87390 | 87389
76682 | Add Capacitor Bank at Savanna 138 kV Substation | Add Capacitor Bank at Savanna 138 kV Substation |  | Savanna |  | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8694 | 2025-01-31 | 2025-01-31 | 138 | 0 | 0 | 0 | 0,55.2 |  |  | Tier 4 |  |  |  |  | 10025, 23867, 23870 | Y |  |  |  | 81462 | 76682
73371F | BP24 Sub Upgrades | Upgrade Jeanetta to WA Parish Ckt.64A to increase thermal limits |  | Jeanetta | WA Parish | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-01-31 00:05 | 2025-06-05 | 345 | 0 | 0 | 0 |  | Harris | Fort Bend | Tier 4 |  |  |  |  | 44005, 47300 | Y | N |  |  | 89975 | 73371
73371H | BP24 Sub Upgrades | Upgrade White Oak to Jeanetta Ckt.72B to increase thermal limits |  | White Oak | Jeanetta | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-01-31 00:07 | 2025-02-11 | 345 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 46600, 47300 | Y | N |  |  | 89977 | 73371
67919 | Avanzada: Construct New 345 kV Station | Interconnect Outpost Solar to the Lobo to Fowlerton 345 kV line | IN-SERVICE | Avanzada |  | In-Service |  | ETT | Zachary Lachiusa jlsolis@aep.com 361-881-5574 |  | 2025-02-14 | 2025-02-14 | 345 | 0.1 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  |  | 5709, 80219, 80235 | Y |  |  |  | 67920 | 67919
6216 | Bartlett Switch to Bartlett | Bartlett Switch to Bartlett |  | Bartlett Switch | Bartlett | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2025-02-14 12:00 | 2025-05-12 | 69 | 0 | 2.7 | 0 |  | Bell | Bell | Tier 4 |  |  |  |  | 114, 118 | Y |  |  |  | 13941 | 6216
50725 | Lean Clay 138 kV Switch | Construct a new 138 kV switch |  | Culberson | Sand Lake | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8658 | 2025-02-15 | 2025-02-01 | 138 | 0 | 0 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  |  | 1097, 11078, 11086 | Y |  |  |  | 82894 | 50725
77827 | Reconductor TNMP Cottonwood to Oncor Lean Clay |  |  | Oncor Lean Clay (11078) | TNMP Cottonwood (38099) | Under Construction |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-02-15 | 2025-02-21 | 138 | 0 | 0.33 | 0 |  | Reeves | Reeves | Tier 4 |  |  |  |  | 11078, 38099, 38100 | Y |  |  |  | 87863 | 77827
81605 | Kolb Lake 138 kV POD | Establish Kolb Lake 138 kV POD |  | Kolb Lake POD | Kolb Lake POD | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6229 | 2025-02-15 | 2958101 | 138 | 0 | 0 | 0 |  | Angelina | Angelina | Tier 4 |  |  |  |  | 3307, 3340, 3346, 3347, 3747 | Y |  |  |  | 81606 | 81605
72876 | Provide 138 kV POD for Skybox at Teal Switch | Provide 138 kV POD for Skybox at Teal Switch |  | Teal | Skybox | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6259 | 2025-02-15 | 2958101 | 138 | 0.2 | 0 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | 3362, 3371 | Y |  |  |  | 72877 | 72876
60094 | Convert Waco East - Elm Mott 69 kV Line to 138 kV | Convert Waco East - Elm Mott 69 kV Line to 138 kV and relocate the Waco East Substation to the double circuit line going towards Lake Creek/Waco West |  | Waco East | Elm Mott | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6147 | 2025-02-15 | 2024-05-15 | 138 | 0 | 10 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  |  | 3407, 3408, 3438, 3439, 3443, 3571, 3573, 3708, 13438 | Y |  |  |  | 62645 | 60094
70223 | Mont - Pilot Grove Transmission Line Overhaul | LCRA TSC will perform an overhaul on the 8-mile Mont ¿ Pilot Grove (T140) 138-kV transmission line. |  | Mont | Pilot Grove | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2025-02-17 | 2025-02-21 | 138 | 0 | 8 | 0 |  | Lavaca | Lavaca | Tier 4 |  |  |  |  | 7234, 7235, 7249 | Y | Y |  |  | 70224 | 70223
79683 | Add Branch between Padua and Sommers |  |  | 5395 | 170722 | Planned | S-0969, T-0327 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2025-02-18 | 2025-02-18 | 138 | 2.06 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5395, 170722 | Y |  |  |  | 79684 | 79683
54220 | Brazos' member will build McFarland substation, Brazos will install POI Picard | Brazos' member will build McFarland substation, Brazos will install POI Picard |  | Picard | Picard | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2025-02-23 | 2025-05-18 | 138 | 0 | 0 | 0 |  | Parker | Parker | Tier 4 |  |  |  |  | 483, 485, 486, 527 | Y |  |  |  | 54221 | 54220
72061 | HO Clarke to Kirby Ckt.90A Upgrade to Limiting Section | Upgrade Ckt.90A HO Clarke to Kirby to increase thermal limits. |  | HO Clarke | Kirby | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-02-28 | 2024-04-30 | 138 | 0 | 6.78 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 48157, 48363 | Y | N |  |  | 91107 | 72061
76622 | Expand Peters 138kV substation for Walstrom BESS (22INR0540). | Expand Peters 138kV substation for Walstrom BESS (22INR0540). |  |  |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-02-28 | 2025-02-28 | 138 | 0 | 0 | 0 |  | Austin | Austin | Tier 4 |  |  |  |  | 46220, 171382 | Y | N |  |  | 76623 | 76622
75887 | Add_SteepHollow_Load |  |  | Steep Hollow |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2025-02-28 | 2025-05-19 | 138 | 0 | 0 | 0 |  | Brazos | Brazos | Tier 4 | [5 empty] | Y |  |  |  | 91905 | 75887
69902B | New 345kV Mission (MSS) substation for generator interconnection to Parliament Solar. | Upgrade Ckt.71C TH Wharton to Zenith in order to increase thermal limits |  | TH Wharton | Zenith | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-02-28 | 2958101 | 345 | 0 | 0 | 0 |  | Waller | Waller | Tier 4 |  |  |  |  | 44900, 45500 | Y | N |  |  | 91202 | 69902
78476 | Waterhole 345kV Substation - Gulf Star Storage - Generator Interconnection (23INR0460) | Install Gulf Star Storage at Waterhole 345kV substation… Connect at the same generator lead as Gulf Star Solar (Gulf Star Storage - 23INR0460) |  | Waterhole |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-02-28 | 2958101 | 345 | 0 | 0 | 0 |  | Wharton |  | Tier 4 |  |  |  |  | 44880, 112878 | Y | N |  |  | 89927 | 78476
76369 | BRINE Substation Upgrades | Upgrade substation equipment at BRINE on Ckt.86H DALTON to BRINE to Mont Belvieu. |  | BRINE | DALTON/Mont Belvieu | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-02-28 | 2958101 | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  |  | 40220, 40740 | Y | N |  |  | 89911 | 76369
78425 | Danbury to LONG / Longbow BESS (25INR0328) | Expand facilities at customer-owned LONG substation for Longbow BESS (25INR0328). Utilize existing generator lead LONG to Longbow Solar. |  | Danbury | LONG | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-02-28 | 2958101 | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  |  | 42875, 112662 | Y | N |  |  | 89910 | 78425
86009 | Expand ADLONG substation for XE Murat Storage (24INR0329) | Expand facilities at customer-owned ADLONG substation for XE Murat Storage (24INR0329). Utilize existing generator lead Eastgate to XE Murat Solar. |  | Eastgate | ADLONG | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-02-28 00:02 | 2958101 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 40690, 113542 | Y | N |  |  | 86010 | 86009
78374 | Rockhound 345/138 kV Switch | Construct a new 345/138 kV Switch |  | Falcon Seaboard | Midland East | Under Construction |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8705 | 2025-03-01 | 2025-02-14 | 345 | 0 | 0 | 1200 |  | Midland | Martin | Tier 3 | 24RPG002 | 2024-01-11 |  |  | 1021, 1025, 10062, 10063, 10064, 10065, 11390, 23837, 23843, 23858 | Y |  |  |  | 78375 | 78374
61392 | Bergheim - Fair Oaks Transmission Line Upgrade | This project will Increase the reliability of transmission facilities on the T238 Bergheim to Fair Oaks 138-kV and T656 Bergheim to Kendall 345-kV 4.1-mile double-circuit transmission line by replacing the aging conductor. |  | Bergheim | Fair Oaks Ranch/Kendall | Planned | 61406, 61358, 61350, 61234, 61362, 61356, 61400, 61402, 61404 | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2025-03-12 | 2025-03-12 | 345 | 0 | 4.1 | 0 |  | Comal | Kendall | Tier 4 | 22RPG005 | 2022-03-04 | 2022-09-09 |  | 7046, 7169, 7170, 7770 | Y | N |  |  | 61393 | 61392
45501 | Eldorado Live Oak to Sonora: Rebuild 69 kV line | Rehab Eldorado Live Oak to Sonora 69 kV line | IN-SERVICE | Eldorado Live Oak | Sonora | In-Service | 982 - 1160 | AEP TNC | David Baker twang1@aep.com 918-599-2635 | 2769 | 2025-03-12 01:00 | 2025-03-12 | 69 | 0 | 23.92 | 0 |  | Schleicher | Sutton | Tier 3 | 18RPG012 | 2018-12-18 | 2019-01-17 |  | 6054, 6498, 6503, 6505, 6509, 6510, 6513 | Y | N |  |  | 65530 | 45501
88063 | Install new POI | Install new POI |  | Valley South |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3069 | 2025-03-15 | 2025-05-15 | 345 | 0 | 0 | 0 |  | Fannin |  | Tier 4 | [5 empty] | Y |  |  |  | 88064 | 88063
72500 | Rio Lago - New 138kV Substation | Loop new 138kV substation into the existing 138kV Bandera to Verde Creek line and install 40MVA distribution transformer. The new substation will be located approximately 1.64 miles from Bandera substation (23INR0078) |  | Bandera | Verde Creek | Planned |  | BEC | Jhonatan Guerrero Rivera j.rivera@banderaelectric. 830-612-0048 |  | 2025-03-17 | 2025-03-21 | 138 | 0.1 | 0 | 0 |  | Bandera | Bandera | Tier 4 |  |  |  |  | 7146, 7436, 7438 | Y | N |  |  | 72501 | 72500
47541 | Crane Circuit Breaker Addition | Provide transmission service to American Electric Power at Crane Substation. Adding one (1) breaker and associated equipment needed to connect the AEP-owned Crane to Kinnison 138-kV transmission line. |  | Crane Substation | Crane Substation | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2025-03-17 02:00 | 2025-02-26 | 138 | 0 | 0 | 0 |  | Crane | Crane | Tier 4 |  |  |  |  | 76615 | Y | N |  |  | 78402 | 47541
73895 | Sunglow Substation Addition | This project provides a point of interconnection for a new battery energy storage resource at a new 138-kV Sunglow Substation between LCRA TSC T627 and LCRA Rosita Creek Substation. |  | Sunglow |  | Planned |  | LCRATSC | Dylan PReas dylan.preas@lcra.org 512-578-4514 |  | 2025-03-28 | 2025-03-12 | 138 | 0 | 0 | 0 |  | Maverick |  | Tier 4 |  |  |  |  | 8260, 78015, 78016 | Y | N |  |  | 73896 | 73895
75889 | Add_Wellborn_Load |  |  | Wellborn |  | Planned |  | BRYN | Clay Lindstrom clindstrom@btutilities.com 979-821-5763 |  | 2025-03-28 | 2025-05-14 | 138 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  |  | 32895 | Y |  |  |  | 89951 | 75889
70660 | Plaza to Grant Ckt.08I Upgrade | Install parallel underground portion of Ckt.08I Plaza to Grant to increase thermal limits. |  | Plaza | Grant | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-03-30 00:10 | 2958101 | 138 | 0 | 0.44 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47110, 47350 | Y | N |  |  | 70661 | 70660
76078 | Laredo VFT North to North Laredo Switch: Rebuild 138 kV Line | Rebuild Mines Road to Milo 138 kV line |  | Mines Road | Milo | Planned | 1116 - 1294 | AEP TCC/ETT | William Lovelace mlforcum@aep.com 918-599-2674 | 3835 | 2025-03-31 | 2024-12-30 | 138 | 0 | 2.95 | 0 |  | Webb | Webb | Tier 4 |  |  |  |  | 8643, 8918 | Y |  |  |  | 76079 | 76078
69890 | Bailey 345kV Substation Expansion for Ray Gulf Wind (22INR0517) | Expand 345kV Bailey substation for Ray Gulf Wind generator interconnection (22INR0517) |  | Bailey |  | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-03-31 | 2958101 | 345 | 0 | 0 | 0 |  | Wharton |  | Tier 4 |  |  |  |  | 44040, 114215 | Y | N |  |  | 69891 | 69890
87477 | [5 empty] | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2025-04-01 | 2025-04-01 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 3275, 3278, 6935, 6939 | Y |  |  |  | 87478 | 87477
71954 | Adds new Talitha substation and short line from Talitha to Orange Grove 138 | Adds new Talitha substation and short line from Talitha to Orange Grove 138 |  | Orange Grove | Talitha | Under Construction |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-04-01 | 2025-04-01 | 138 | 0.73 | 0 | 0 |  | Jim Wells | Jim Wells | Tier 4 |  |  |  |  | 5660, 5661 | Y |  |  |  | 71955 | 71954
71982 | Upgrade Orange Grove station | Upgrade Orange Grove stationto ring bus |  | Orange Grove | Orange Grove | Under Construction |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-04-01 | 2025-04-01 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 | [5 empty] | Y |  |  |  | 71983 | 71982
61234 | Antler - Bergheim Transmission Line Upgrade | This project will increase the reliability and capacity of transmission facilities on the T493 Antler to Bergheim 138-kV and T389 Bergheim to Hays Energy 345-kV 7.2-mile double-circuit transmission line by replacing the aging conductors from Antler to Bergheim substations. |  | Antler | Bergheim | Planned | 61406, 61358, 61392, 61350, 61362, 61356, 61400, 61402, 61404 | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2025-04-01 | 2025-02-24 | 345 | 0 | 7.2 | 0 |  | Comal | Comal | Tier 3 | 22RPG005 | 2022-03-04 | 2022-09-09 |  | 7043, 7170, 7171, 7770 | Y | N |  |  | 78331 | 61234
78395 | Switching Structure – FY 2023 System Upgrade | Replace switching structure and load-serving power transformer at Thompsonville station. |  | Thompsonville |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 | 1026926 | 2025-04-04 | 2024-08-19 | 69 | 0 | 0 | 0 |  | Gonzales |  | Tier 4 | [5 empty] | Y |  |  |  | 78396 | 78395
79990 | Add new Yellow Wolf station for 21INR0428 |  |  | Limestone | Gibbons Creek | Under Construction |  | CTT | Christina Minchew cminchew@lspower.com 636-698-8443 |  | 2025-04-08 | 2025-04-23 | 345 | 0 | 0 | 0 |  | Leon |  | Tier 4 |  |  |  |  | 967, 46020, 79007 | Y | N |  |  | 79991 | 79990
72576A | Lago Vista to Nameless Transmission Line Upgrade | Rebuild and upgrade Nameless to Lago Vista with double-circuit capable structures. Install 1 ckt with bundled 795 kcmil conductor (440 MVA). Final span of conductor and terminal equipment at Nameless will be upgraded to 440 MVA with ERCOT project #72576B. (Replaces ERCOT Project # 61277A) | 1/10/2023: Added information to clarify timing for final circuit rating upgrade. | Lago Vista | Nameless | Planned |  | PEC | Charles Dewitt Charles.Dewitt@peci.com 830-868-5041 |  | 2025-04-15 | 2025-04-01 | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 70352, 70526 | Y | N |  |  | 72577 | 72576
70922 | Chief Brady - Georgetown Transmission Line Upgrade | LCRA TSC will upgrade T355 Chief Brady - Georgetown 138-kV transmission line to achieve a higher operational rating. |  | Chief Brady | Georgetown | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2025-04-18 | 2025-04-18 | 138 | 0 | 3 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  |  | 7343, 7366 | Y | N |  |  | 70923 | 70922 | 2023-SC17
13TPIT0070 | Nash Creek Substation | Rebuild existing substation, and replace existing PWT with new 69kVx13.09 kV, new Control House, CSW, structures, containment foundations, bus, panels, etc |  | Nash Creek |  | Planned |  | GVEC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2025-04-23 | 2025-07-30 | 69 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  |  | 7596 | Y | N |  |  | 78324 | 3322
71956 | Elgin Switch Substation Upgrade | LCRATSC will install a new three-breaker ring bus substation at Elgin Switch. Oncor will relocate its facilities from Elgin Switch to Brushy Creek. Install a temporary shoo-fly between T668 and T260 to maintain through-path during construction. |  | Elgin Switch |  | Planned |  | LCRATSC | Dylan Preas Dylan.Preas@LCRA.ORG 512-578-4514 |  | 2025-04-24 | 2025-05-14 | 138 | 0 | 0 | 0 |  | Williamson |  | Tier 4 |  |  |  |  | 3541, 3650, 7321, 7324, 7338 | Y | N |  |  | 73564 | 71956
1275 | Hawkins to Gainesville | Hawkins to Gainesville |  | Hawkins | Gainesville | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2025-04-28 | 2026-11-01 | 69 | 0 | 6.72 | 80 |  | Cooke | Cooke | Tier 4 |  |  |  |  | 705, 706, 707, 726, 33705, 33726 | Y |  |  |  | 67891 | 1275
85975 | Carrizo Springs Substation 69-kV Breaker Installation and Power Transformer Upgrade | Carrizo Springs Substation 69-kV Breaker Installation and Power Transformer Upgrade | [5 empty] | RGEC | Larry T. Powell lpowell@rgec.coop 830-563-6178 |  | 2025-04-30 | 2024-10-09 | 69 | 0 | 0 | 0 |  | Dimmit | Dimmit | Tier 4 | [5 empty] | Y |  | Install 69-kV breaker at R3021T fuse and replace existing power transformer with 25/33 MVA transformer. |  | 85976 | 85975
89905 | Addition of facilities installed at OCI ALAMO 1 substation to install a Gen-Tie to Power Soportar Battery Energy Storage System (BESS). |  |  | 5007 | 171082 | Planned | S-1023, T-0363 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2025-05-01 | 2025-05-07 | 138 | 0.06 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 5007, 171082 | Y |  |  |  | 89906 | 89905
81148 | Lago Vista T3 addition | T3 addition with bus tie breakers |  | LAGO VISTA 70352 |  | Planned |  | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2025-05-01 | 2024-06-01 | 138 | 0 | 0 | 0 |  | Travis |  | Tier 4 |  |  |  |  | 70352 | Y |  |  |  | 81149 | 81148
80753 | LST_Claytonville to Camp Springs 138 kV line additions | LST_Claytonville to Camp Springs 138 kV line additions |  | Claytonville 138 |  | Planned |  | LST | Chenyan Guo Chenyan.guo@lonestar-transmission.com 305-972-0663 |  | 2025-05-01 | 2025-03-31 | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 68009, 68012 | Y |  |  |  | 80754 | 80753
72588A | Trading Post to Cedar Valley Storm Hardening |  |  | Trading Post | Cedar Valley | Planned |  | PEC | Charles Dewitt Charles.Dewitt@peci.com 830-868-5041 |  | 2025-05-05 | 2025-05-01 | 138 | 0 | 6.8 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 70505, 70506 | Y | N |  |  | 72589 | 72588
80913 | Establish Sloan 138 kV Switch. | Establish new 138/345 kV Switch. |  | Midessa South Switch | Odessa/Midland East Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8659 | 2025-05-08 | 2025-05-14 | 138 | 0 | 0 | 0 |  | Midland | Midland | Tier 4 |  |  |  |  | 1059, 1124, 1138, 11137, 11138, 11143, 11165 | Y |  |  |  | 90314 | 80913
4645 | Rebuild of Myra to Spring | Rebuild of Myra to Spring |  | Myra | Spring | Planned |  | BEPC | Brian Hithersay bhithersay@brazoselectric.com 254-750-6795 |  | 2025-05-09 | 2025-08-01 | 138 | 0 | 13.9 | 0 |  | Cooke | Cooke | Tier 4 |  |  |  |  | 684, 690, 691 | Y |  |  |  | 12221 | 4645
67992D | CPSE_345KV_Howard_Switching_Station,CPSE_Hamilton_to_MedCtr_Upgrade | Upgrade Hamilton to Medical Center 138KV Line to 469MVA |  | 5187 | 5300 | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2025-05-09 | 2025-04-16 | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 3 |  |  | 2021-12-16 |  | 5187, 5300 | Y |  |  |  | 67994 | 67992
69552B | Teal 345/138 kV Switch connected to LCRA POI (Limmer) | Teal 345 kV Switch, Autotransformers, and 345 kV Tie Lines to Limmer (LCRA) |  | Teal | Teal | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6165 | 2025-05-15 | 2958101 | 345 | 0 | 0 | 600 |  | Williamson | Williamson | Tier 3 | 22RPG027 | 2022-08-15 | 2022-09-15 |  | 3362, 3363, 3364, 3696, 7341, 13363, 13364, 25090 | Y |  |  |  | 88554 | 69552
71199 | Yucca Drive - Moss 138 kV Line | Rebuild existing 138 kV line |  | Yucca Drive | Moss | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R9047 | 2025-05-15 | 2025-05-30 | 138 | 0 | 35.2 | 0 |  | Ector | Winkler | Tier 4 |  |  |  |  | 1009, 1019, 11015, 11128, 18663 | Y |  |  |  | 76384 | 71199
70538 | Pilot Grove - Yoakum Gartner Road Transmission Line Overhaul | Perform an overhaul on the 7.8 mile T614 Pilot Grove (structure #8/2) - Yoakum Gartner Road 138-kV transmission line. Structure #8/2 and the remaining portion of T614 will be overhauled as part of the FY23 Mont - Pilot Grove Transmission Line Overhaul project. |  | Pilot Grove | Yoakum Gartner | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2025-05-15 | 2025-05-15 | 138 | 0 | 0 | 0 |  | Lavaca | DeWitt | Tier 4 |  |  |  |  | 7234, 7242 | Y | N |  |  | 70539 | 70538
82806 | Establish Long Hollow 345 kV Switch (POI for Pinnington Solar) | Establish Long Hollow 345 kV Switch (POI for Pinnington Solar) |  | Graham Plant Switch | Parker Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3509 | 2025-05-15 | 2025-06-30 | 345 | 0 | 0 | 0 |  | Young | Parker | Tier 4 |  |  |  |  | 1430, 1436, 1506 | Y |  |  |  | 82807 | 82806
72007 | Ranger Camp 345/138/69 kV Switch | Construct a new 345/138/69 kV Switch to replace existing Morgan Creek Switch |  | Ranger Camp 345/138 kV Switch | Ranger Camp 345/138 kV Switch | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3024 | 2025-05-15 | 2025-04-16 | 345 | 0 | 0 | 1200 |  | Mitchell | Mitchell | Tier 1 | 23RPG029 | 2023-09-29 |  |  | 1025, 1030, 1032, 1033, 1064, 1189, 1190, 1348, 1378, 10049, 10050, 10051, 10052, 10134, 11004, 11035, 11332, 11342, 11393 | Y |  |  |  | 81363 | 72007
71980 | Watermill 345 kV Switch | Rebuild the existing Watermill 345 kV Switch |  | Watermill |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4012 | 2025-05-15 | 2958101 | 345 | 0 | 0 | 600 |  | Dallas |  | Tier 3 |  |  |  |  | 2398, 2427, 2428, 2429, 2432, 2435, 2466, 2847, 2997, 3159, 12429 | Y |  |  |  | 76731 | 71980
72870 | Soda Lake Generator Circuit Breaker Addition | This project provides a point of interconnection for a new 202.99 MW Solar Energy at the 138-kV Soda Lake Substation by reconfiguring the Soda Lake Substation to breaker-and-a-half to add new 138-kV line terminal and one POI structure to accommodate the new interconnection. Update contingencies |  | Soda Lake |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2025-05-15 | 2025-06-09 | 138 | 0 | 0 | 0 |  | Crane |  | Tier 4 | [5 empty] | Y | N |  |  | 78298 | 72870
81383 | Edwards Tap - Sandhills Tap 138 kV Line Rebuild | Edwards Tap - Sandhills Tap 138 kV Line Rebuild |  | Odessa EHV | Wolf | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8528 | 2025-05-15 | 2025-05-15 | 138 | 0 | 11.71 | 0 |  | Ector | Ward | Tier 3 |  |  |  |  | 1102, 1103, 1110 | Y |  |  |  | 81384 | 81383
77041 | Leon Switch - Putnam Transmission Line Overhaul | LCRA TSC will perform an overhaul on the 8.9-mile Leon Switch – Putnam (T727) 138-kV transmission line between Leon Switch existing structure #1/1 and Putnam existing structure #9/10. This project will increase reliability of the structures and conductor by ensuring that the transmission line meets or exceeds current NESC and LCRA TSC design standards. |  | Leon Switch | Putnam | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2025-05-15 | 2025-05-21 | 138 | 0 | 8.95 | 0 |  | Eastland | Eastland | Tier 4 |  |  |  |  | 1624, 6310 | Y | Y |  |  | 77042 | 77041
82810 | Olympus 138 kV Switch | Establish Olympus 138 kV Switch |  | Olympus Switch | Olympus Switch | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6330 | 2025-05-15 | 2025-05-08 | 138 | 0 | 0 | 0 |  | Navarro | Navarro | Tier 4 |  |  |  |  | 3125, 3127, 3454, 3466, 3723 | Y |  |  |  | 82811 | 82810
73838 | Redwood - San Marcos Transmission Line Upgrade | LCRA TSC will upgrade T200 Redwood - San Marcos 138-kV transmission line to obtain a higher operational rating. |  | Redwood | San Marcos | Planned |  | LCRATSC | Dylan PReas dylan.preas@lcra.org 512-578-4514 |  | 2025-05-15 | 2025-05-13 | 138 | 0 | 0 | 0 |  | Hays | Hays | Tier 4 |  |  |  |  | 7188, 7192 | Y | N |  |  | 73839 | 73838
72004 | Cat Claw 138 kV Dynamic Reactive Device (formerly Midkiff) | Install a new Dynamic Reactive Device at Cat Claw (formerly Midkiff) |  | Cat Claw | Cat Claw | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8675 R8680 R8695 | 2025-05-15 | 2025-05-12 | 138 | 0 | 0 | 0 | -250250 | Upton | Upton | Tier 3 |  |  |  |  | 1210, 1217, 10058, 10059, 10060, 11218, 11345, 23870, 23871 | Y |  |  |  | 73345 | 72004
81358 | Grindstone 138 kV Switch | Establish Grindstone 138 kV Switch |  | Grindstone Switch | Grindstone Switch | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R1754 | 2025-05-15 | 2025-05-15 | 138 | 0 | 0 | 0 |  | Palo Pinto | Palo Pinto | Tier 4 |  |  |  |  | 1569, 1571, 1575, 1592, 1599, 154402 | Y |  |  |  | 81359 | 81358
87760 | Full House 138 kV Switch | Establish Full House 138 kV Switch for Lucky Bluff BESS |  | Full House | Full House | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6327 | 2025-05-15 | 2025-05-08 | 138 | 0 | 0 | 0 |  | Erath | Erath | Tier 4 |  |  |  |  | 1636, 1641, 1652, 153852 | Y |  |  |  | 87761 | 87760
87846 | Bradberry 138 kV Switch | Bradberry 138 kV Switch |  | Bradberry |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4015 | 2025-05-15 | 2958101 | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 3064, 3065, 3066 | Y |  |  |  | 87847 | 87846
62666A | Upgrade and convert McGregor - Waco West Line | Rebuild and Upgrade McGregor Phillips - Waco West Switch 69 kV Line |  | Waco West | McGregor Phillips | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6172 | 2025-05-15 | 2958101 | 69 | 0 | 17.5 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  |  | 3370, 3437, 3584 | Y |  |  |  | 93105 | 62666
62643 | Rebuild Waco East 138 kV Switch | Rebuild Waco East 138 kV Switch |  | Waco East | Waco East | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6146 | 2025-05-15 | 2958101 | 138 | 0 | 0 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  |  | 3434, 3438, 3439, 3443, 3452, 3481, 3482, 3551, 3559, 3708, 13438 | Y |  |  |  | 62664 | 62643
52247 | Marrs - Handley 69 kV Line Conversion to 138 kV | Convert the existing Marrs-Handley 69 kV line to 138 kV operation |  | Marrs SW | Handley | Under Construction |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5222 | 2025-05-15 | 2025-05-30 | 138 | 2.2 | 13 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  |  | 1951, 1952, 1967, 1968, 1969, 2158, 2159, 2160, 2162, 11950, 11951, 11952, 11967 | Y |  |  |  | 86795 | 52247
91060 | Establish Flying Tiger 138 kV Switch | Establish Flying Tiger 138 kV Switch |  | Flying Tiger 138 kV Switch |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3302 | 2025-05-15 | 2025-05-15 | 138 | 0 | 0 | 0 |  | Lamar | Lamar | Tier 4 |  |  |  |  | 1693, 1700, 2163 | Y |  |  |  | 91061 | 91060
85959 | San Marcos - Strahan Transmission Line Upgrade | LCRA TSC will upgrade T230 San Marcos - Strahan 138-kV transmission line to achieve a higher operational rating. |  | San Marcos (7192) | Strahan (7193) | Planned |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2025-05-15 | 2025-04-30 | 138 | 0 | 1.25 | 0 |  | Hays | Hays | Tier 4 |  |  |  |  | 7192, 7193 | Y |  |  |  | 85960 | 85959
78371 | Richardson East Switch – Richardson Spring Creek 138 kV Line Section | Upgrade Richardson East Switch – Richardson Spring Creek 138 kV Line Section |  | Richardson East | Richardson Spring Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4402 | 2025-05-15 | 2958101 | 138 | 0 | 2.1 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 2689, 2690 | Y |  |  |  | 78372 | 78371
78382 | Adds Capacitor Bank at White Dune | Adds Capacitor Bank at White Dune |  | White Dune |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8669 | 2025-05-15 | 2025-05-30 | 138 | 0 | 0 | 0 | 0,110.4 | Winkler | Winkler | Tier 4 |  |  |  |  | 18692 | Y |  |  |  | 80906 | 78382
73793 | McCarty Lane - Zorn Transmission Line Storm Hardening | Perform storm hardening on the 4.2 mile McCarty Lane - Zorn (T202) 138-kV transmission line. T202 is double-circuited with McCarty Lane - Beback - Zorn (T201) 138-kV transmission line. |  | McCarty Lane East | Zorn | Planned |  | LCRATSC | Dylan PReas dylan.preas@lcra.org 512-578-4514 |  | 2025-05-15 | 2025-05-01 | 138 | 0 | 8.58 | 0 |  | Hays | Guadalupe | Tier 4 |  |  |  |  | 7180, 7182, 7187 | Y | N |  |  | 73794 | 73793
76578 | Upgrade the Temple Pecan - Temple Elm 138 kV Double-Circuit Line | Upgrade the 5-mile Temple Pecan - Temple Elm 138 kV Double-Circuit Line |  | Temple Pecan Creek | Temple Elm Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6234 | 2025-05-15 | 2958101 | 138 | 0 | 10 | 0 |  | Bell | Bell | Tier 1 | 24RPG001 |  |  |  | 3420, 13662 | Y |  |  |  | 76579 | 76578 | 2023-NC61
91455 | Establish Dorsett 345 kV Switch |  |  | Dorsett 345 kV Switch | Dorsett 345 kV Switch | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6323 | 2025-05-15 | 2025-05-08 | 345 | 0 | 0 | 0 |  | Rusk | Rusk | Tier 4 |  |  |  |  | 3100, 3105, 3339, 121043 | Y |  |  |  | 91529 | 91455
82808 | Stranger 345 kV Switch | Establish Stranger 345 kV Switch |  | Stranger Switch | Stranger Switch | In-Service |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6320 | 2025-05-15 | 2025-05-15 | 345 | 0 | 0 | 0 |  | Limestone | Limestone | Tier 4 |  |  |  |  | 3390, 3711, 3721, 154063 | Y |  |  |  | 82809 | 82808
89982 | Wrangler 345 kV Switch | Establish 345 Switch |  | Cottonwood | White River | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R3032 | 2025-05-15 | 2025-05-16 | 345 | 0 | 0 | 0 |  | Motley | Motley | Tier 4 |  |  |  |  | 23919, 23922, 59904 | Y |  |  |  | 89983 | 89982
78365 | Fryers Creek 138/69 kV Switch | Construct the new Fryers Creek 138/69 kV Switch |  | Boggy Creek | Boggy Creek | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6295 | 2025-05-15 | 2958101 | 138 | 5 | 0 | 0 |  | Bell | Bell | Tier 1 |  |  |  |  | 132, 3415, 3493, 3496, 3607, 3643, 3644, 3645, 3689, 3726 | Y |  |  |  | 81558 | 78365
67992C | CPSE_345KV_Howard_Switching_Station,CPSE_Hamilton_to_MedCtr_Upgrade | Looping of 345KV Howard Rd switching station into existing Cagnon to AVR and Cagnon to Spruce 34KV lies. The switching station will have 2 600MVA 345KV/138KV autotransformers. |  | 5056 | 5400 and 5475 | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2025-05-29 | 2025-04-07 | 345 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 3 |  |  | 2021-12-16 |  | 5056, 5230, 5231, 5400, 5475 | Y |  |  |  | 67993 | 67992
67992A | CPSE_345KV_Howard_Switching_Station,CPSE_Hamilton_to_MedCtr_Upgrade | Shepherd Rd to Valley Rd 138kV line Reconfiguration. |  | 5378, 5465 | 5320 | Planned |  | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2025-05-29 | 2025-04-07 | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 3 |  |  | 2021-12-16 |  | 5230, 5378, 5465 | Y |  |  |  | 72403 | 67992
78485A | Britmoore to Bellaire Ckt.24B Upgrades | Upgrade Ckt.24B Westchase to Hayes to Britmoore to increase thermal limits. Upgrade Ckt.24 Bellaire equipment and relay limits. |  | Westchase | Britmoore | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-30 | 2025-02-07 | 138 | 0 | 6.21 | 0 |  | Harris | Harris | Tier 3 | 23RPG025 | 2023-09-06 | 2023-09-28 | 2023-09-28 | 48159, 48420 | Y | N |  |  | 90166 | 78485
6719A | Twelvemile Substation Addition | Cuts into first circuit |  | Bakersfield | Schneeman Draw | In-Service |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018769 | 2025-05-30 | 2025-06-17 | 345 | 0 | 0 | 0 |  | Pecos | Crockett | Tier 4 |  |  |  |  | 7053, 76008, 76015 | Y | N |  |  | 58408 | 6719
6719B | Twelvemile Substation Addition | Cuts into the second circuit |  |  |  | Planned |  | LCRATSC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 | 1018769 | 2025-05-30 | 2025-06-17 | 345 | 0 | 0 | 0 |  | Pecos | Crockett | Tier 4 |  |  |  |  | 7053, 76008, 76015 | Y |  |  |  | 90722 | 6719
69902A | New 345kV Mission (MSS) substation for generator interconnection to Parliament Solar. | New 345kV Mission (MSS) substation for generator interconnection to Parliament Solar. Loop Ckt.18E into Mission substation to create new Ckt.18 Gibbons Creek to Mission to Zenith. (Ckt.18 Gibbons Creek to Mission tie-line). |  | MISSION | Zenith | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 | 2025-05-07 | 345 | 0 | 0 | 0 |  | Waller | Waller | Tier 4 |  |  |  |  | 967, 44900, 44920 | Y | N |  |  | 91203 | 69902
66221L | Galena Park Area Conversion Project | De-energize Ckt.20 Greens Bayou to GYPSUM. |  | Greens Bayou | GYPSUM | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 | 2025-04-11 | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 3 | 21RPG020 | 2021-11-30 | 2021-12-22 | 2021-12-22 | 40619, 40725, 40751, 48131 | Y | N |  |  | 90301 | 66221
66221K | Galena Park Area Conversion Project | Rebuild GYPSUM customer substation for 138kV loop-tap service. Tap new GYPSUM substation (Spear Stone) from Ckt.94 between TANKER and new Galena Park tap to create new Ckt.94M CITFIL to Normandy tap to Galena Park tap to Spear Stone to TANKER |  | CITFIL | Tanker | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 | 2958101 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 3 | 21RPG020 | 2021-11-30 | 2021-12-22 | 2021-12-22 | 40590, 40612, 40630, 40731, 40739, 41172, 48130, 48261, 48402, 48613 | Y | N |  |  | 90302 | 66221
78485E | Britmoore to Bellaire Ckt.24B Upgrades | Upgrade Ckt.24B Westchase to Hayes to Britmoore to increase thermal limits. Upgrade Ckt.24 Bellaire equipment and relay limits. |  | Westchase | Britmoore | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 | 2025-06-03 | 138 | 1.2 | 6.21 | 0 |  | Harris | Harris | Tier 3 | 23RPG025 | 2023-09-06 | 2023-09-28 | 2023-09-28 | 44120, 48159 | Y | N |  |  | 90170 | 78485
69902C | New 345kV Mission (MSS) substation for generator interconnection to Parliament Solar. | Install generator lead from Mission (MSS) substation to Parliament/Parliament Solar |  | MISSION | Parliament | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 00:01 | 2025-05-07 | 345 | 0 | 0 | 0 |  | Waller | Waller | Tier 4 |  |  |  |  | 44920, 113925 | Y | N |  |  | 91204 | 69902
73578K | Heights 138kV Loop Conversion | Convert Eureka to double-tap service. Tap Ckt.09D to create new Ckt.09D San Felipe to Eureka TR2/TR3 tap to White Oak. Reconductor Ckt.09D Eureka TR2/TR3 tap to White Oak to increase thermal limits. Upgrade San Felipe line relaying Ckt.09D San Felipe to White Oak. |  | San Felipe | White Oak | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 00:02 | 2025-05-14 | 138 | 0 | 1.57 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 45750, 45752, 46615, 47382, 47685 | Y | N |  |  | 90929 | 73578
73578C | Heights 138kV Loop Conversion | Convert Eureka to double-tap service. Tap Ckt.81J to create new Ckt.81J White Oak to Eureka TR1 tap to Wirt. |  | Wirt | White Oak | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 00:02 | 2025-05-14 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 44656, 45750, 45751, 46615 | Y | N |  |  | 90928 | 73578
73578J | Heights 138kV Loop Conversion | Reconfigure Ckt.40A Dunlavy to HO Clarke with a temporary (BP25 to BP26) configuration. Remove the Dunlavy TR3 tap section from Ckt.40A and install tap section to Ckt.90A. |  | Dunlavy | HO Clarke | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 00:04 | 2025-05-08 | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47160, 47850 | Y | N |  |  | 90927 | 73578
73578I | Heights 138kV Loop Conversion | Install 7.2MVAR cap bank at Hyde Park TR2. |  | Hyde Park |  | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 00:05 | 2024-10-30 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47690 | Y | N |  |  | 90926 | 73578
73578G | Heights 138kV Loop Conversion | Tap existing Ckt.90A Kirby to Garrott near Tower 34720 to serve Dunlavy transformer TR3 load. Create Ckt.90A Kirby tap to DN-TR3 tap to Garrott. |  | Kirby | Garrott | Planned |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 00:05 | 2025-05-08 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  |  | 47580, 47593, 47660, 48363 | Y | N |  |  | 90930 | 73578
66221G | Galena Park Area Conversion Project | Rebuild Galena Park substation for double tap service. Tap Galena Park TR2 on Ckt.21K between Fidelity and Witter. |  | Fidelity | Witter | In-Service |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2025-05-31 00:06 | 2024-02-15 | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 3 | 21RPG020 | 2021-11-30 | 2021-12-22 | 2021-12-22 | 40590, 40610, 40611, 40612, 40630, 40710, 48402, 48610, 48613 | Y | N |  | Cost included in main entry | 90303 | 66221
91578A | buffalo_clover_substation_addition | Installing temporary 69 kV transformer to serve PEC load | [5 empty] | PEC | Joshua Rivers joshua.rivers@peci.com 830-330-4192 |  | 2025-06-01 | 2958101 | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 124, 70000 | Y |  |  |  | 91579 | 91578
11TPIT0011 | East_Village138kV Substation | East_Village 138kV Substation |  | Techridge | East_Village SUB | Planned |  | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2025-06-01 | 2025-05-14 | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  |  | 9045, 9190, 9195 | Y |  |  |  | 13043 | 5357

## Cancelled Projects
JUNE BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 6/1/2025
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar ) (-Reactor, +Capacitor ) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | RPG Number | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number | RTP Project Number
55603 | Big Foot to Pearsall: Rebuild 69 kV line | Rebuild 69 kV line from Big Foot to Dilley | Cancelled, incorrectly submitted prior to RPG submission. | Big Foot | Pearsall | Planned | 1104 - 1282 | AEP TCC | Bill Roberts bcogan@aep.com 918-599-2857 | 3821 | 2022-11-30 | 2025-05-12 | 69 | 0 | 14.79 | 0 |  | Frio | Frio | Tier 3 |  |  |  |  | 8216, 8218 | N |  |  |  | 65571 | 55603
69487 | Wahpekute: Build new 69 kV tap | Build new 69 kV tap along the Jayton to Rotan 69 kV line | CANCELLED | Wahpekute |  | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 |  | 2024-01-31 |  | 69 | 0 | 0 | 0 |  | Fisher |  | Tier 4 |  |  |  |  | 6162, 6196, 60057 | N |  |  |  | 69488 | 69487
63633 | Tribute: Build 138 kV Temorary Tap | Build new 138 kV temporary tap on the San Angelo Power to Red Creek 138 kV line | CANCELLED | Tribute |  | Planned | 1131 - 1309 | AEP TNC | Larry Brown twang1@aep.com 918-599-2635 | 1876 | 2024-03-01 |  | 138 | 0 | 0 | 0 |  | Tom Green |  | Tier 4 |  |  |  |  | 6442, 6473, 60008 | N | N |  |  | 63634 | 63633
06TPIT0143 | Temple Switch - Temple SE 138 kV line | Upgrade existing 138 kV line |  | Temple Switch | Temple SE | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R448-E | 2024-05-15 |  | 138 | 0 | 4.4 | 0 |  | Bell | Bell | Tier 4 |  |  |  |  | 3415, 3612 | N | N |  |  | 8521 | 1342
08TPIT0007 | Austin Ranch - Hebron 138 kV line | Upgrade existing 138 kV line |  | Austin Ranch | Hebron | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3002-E | 2024-05-15 |  | 138 | 0 | 0.7 | 0 |  | Denton | Denton | Tier 4 | [5 empty] | N | N |  |  | 10541 | 3195
73613 | LCRATSC_DraftHorse_Substation_Addition | Substation addition to accommodate new BBEC load. |  | Draft Horse |  | Conceptual |  | LCRATSC | Dylan Preas dylan.preas@lcra.org 512-578-4514 |  | 2024-05-15 |  | 138 | 0 | 0 | 0 |  | Washington |  | Tier 4 |  |  |  |  | 7286, 7289, 7295 | N | N |  |  | 73614 | 73613
5645 | Hamilton Road to Picacho, rebuild 138 kV line | Rebuild Hamilton Road to Picacho 138 kV line | CANCELLED | Hamilton Road | Picacho | Conceptual |  | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 |  | 2024-06-01 |  | 138 | 0 | 8.8 | 0 |  | Val Verde | Val Verde | Tier 4 |  |  |  |  | 8255, 8684 | N | N |  |  | 13379 | 5645
44419 | Load serving |  |  | Mayhill | Denton Steam/Brinker | Planned |  | DME | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2024-07-01 | 2024-07-01 | 138 | 5.1 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  |  | 927, 929, 982 | N | N |  |  | 44420 | 44419
49926 | Brinker-DentonSteam Ckt1 Upgrade |  |  | Brinker | Denton Steam | Planned |  | DME | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2024-07-01 | 2024-07-01 | 138 | 0 | 0.63 | 0 |  | Denton | Denton | Tier 4 |  |  |  |  | 927, 982 | N | N |  |  | 49929 | 49926
15TPIT0049 | Permian Basin 345 kV Switching Station | Construct 345 kV switching station and install 345/138 kV autotransformer |  | Permian Basin |  | Conceptual | R8100C-E & R8100B-E | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R8100B-E | 2024-07-15 |  | 345 | 0 | 0 | 600 |  | Ward |  | Tier 1 |  | 2013-02-15 |  | 2013-09-15 | 1010, 11010 | N | N |  | Estimated cost is included in total estimated cost for 15TPIT0047. | 10184 | 2836
69485 | Wahpekute: Build new 69 kV station | Build new 69 kV station with a capacitor bank along the Jayton to Rotan 69 kV line | CANCELLED | Wahpekute |  | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 |  | 2024-10-31 |  | 69 | 0 | 0 | 0 | 0,3.8 | Fisher |  | Tier 4 |  |  |  |  | 6162, 6196, 60057, 60066 | N |  |  |  | 69486 | 69485
3901 | Lobo to Freer: Rebuild 69 kV line | Rebuild Lobo to Freer 69 kV line with 795 ACSS | Description Update | Lobo | Freer | Planned | 677 - 0846 | AEP | Brandon Cogan bcogan@aep.com 918-599-2857 | 2596 | 2025-01-07 |  | 69 | 0 | 49.8 | 0 |  | Webb | Duval | Tier 3 |  |  |  |  | 8505, 80222 | N | N |  |  | 11371 | 3901 | 2013-R90
65723 | Riedel: Build New Distribution Station | Construct new distribution station on the Magnolia Tap to Nixon 138 kV line | CANCELLED | Riedel |  |  | 1032 - 1210 | AEP TCC/LCRA | Michael Forcum mlforcum@aep.com 918-599-2674 | 3771 | 2025-01-07 |  | 138 | 0 | 0 | 0 |  | Karnes |  | Tier 4 |  |  |  |  | 8583 | N | Y |  |  | 65724 | 65723
69469 | Equinox Solar Project | Equinox Solar Project | CANCELLED | Cenizo | Del Sol |  |  | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 |  | 2025-01-07 |  | 345 | 0 | 0 | 0 |  | Starr | Starr | Tier 4 |  |  |  |  | 80355, 88355 | N |  |  |  | 69470 | 69469
64021 | Texana Solar Interconnection | Connect the Texana Solar to the El Campo to Victoria 138 kV line | CANCELLED | El Campo | Victoria | Planned |  | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | TP2020888 | 2025-01-07 |  | 138 | 0 | 0 | 0 |  | Wharton | Victoria | Tier 4 |  |  |  |  | 8099, 8102, 8117, 8192, 8675 | N |  |  |  | 64022 | 64021
81573 | Oklaunion: Construct New 345 kV Terminal | Interconnect the Alpha load to the existing Oklaunion 345 kV station | CANCEL | Oklaunion |  | Conceptual |  | AEP TNC/ETT | Tong Wang twang1@aep.com 918-599-2635 |  | 2025-03-11 |  | 345 | 0 | 0 | 0 |  | Wilbarger |  | Tier 4 |  |  |  |  | 6100 | N |  |  |  | 81574 | 81573
61467 | Merrilltown Substation Addition | New 138 kV station - Oncor load | [5 empty] | AEN | Reza Ebrahimian reza.ebrahimian@austinenergy.com 512-322-6740 |  | 2025-03-14 |  | 138 | 0 | 0 | 0 | 0,31.2 | Williamson | Williamson | Tier 4 |  |  |  |  | 9223, 9224, 9230, 9231 | N |  |  |  | 61468 | 61467
07TPIT0069 | Sterrett - Sardis 138 kV line | Upgrade existing 138 kV line |  | Sterrett | Sardis | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M361-E | 2025-05-15 |  | 138 | 0 | 2 | 0 |  | Ellis | Ellis | Tier 4 | [5 empty] | N | N |  |  | 10446 | 3102
61451 | La Vernia Substation | Replace T2, 20 MVA with a 40MVA dual high-dual low |  | La Vernia | La Vernia | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.or |  | 2025-05-16 |  | 138 | 0 | 0 | 0 |  | Wilson | Wilson | Tier 4 |  |  |  |  | 7614 | N | N |  |  | 61452 | 61451
48854 | Adds Annova and Port South Bus and lines | Adds Annova and Port South buses, lines to connect Annova to Port South, line from HWY 511 to Port South, and reconnects line from S Carbide to HWY 511 into Port South |  | Annova LNG | Port South | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2025-06-01 |  | 138 | 22.1 | 0 | 0 | 0,120 | Cameron | Cameron | Tier 4 |  |  |  |  | 5767, 5775, 5776, 8337 | N | N |  |  | 48855 | 48854
70943 | Double circuit 138kV tie between Pyote and Coyanosa | Project resubmitted as PMCR ID # 77805 |  | Pyote (bus # 38001) | Coyanosa (bus # 38380) | Conceptual |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2025-06-01 |  | 138 | 15 | 0 | 0 |  | Ward | Reeves | Tier 2 |  |  |  |  | 38001, 38380 | N |  |  |  | 70944 | 70943
76174 | Origin 138 kV Interconnection | Interconnect Callon Petroleum on the Saragosa to Solstice 138 kV line | CANCELLED | Origin |  | Planned |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 |  | 2025-06-30 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  |  | 60206, 60207, 60208, 60209, 60211, 60716 | N | N |  |  | 76175 | 76174
78627 | RCEC_SherwoodShores_AddCap |  |  |  |  | Planned |  | RCEC | Stephen Geiger sgeiger@rayburnelectric.com 469-402-2112 |  | 2025-10-01 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  |  | 6806 | N |  |  |  | 78628 | 78627
76288 | Hecker to McCampbell: Rebuild 138 kV Line | Rebuild the Hecker to McCampbell 138 kV Line | CANCELLED | Hecker | McCampbell | Planned |  | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | TP2023507 | 2025-11-30 |  | 138 | 0 | 0 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  |  | 8565, 80470 | N | N |  |  | 76289 | 76288
76280 | Reforzar: Build new 345 kV station - stage 2 | Build new 345 kV station on the Lon Hill to North Edinburg 345 kV line | CANCELLED | Reforzar |  | Planned |  | AEP TCC | Michael Forcum mlforcum@aep.com 918-599-2674 | TP2022035 | 2026-01-30 |  | 345 | 0 | 0 | 0 |  | Brooks |  | Tier 1 | 21RPG017 | 2020-09-15 | 2021-11-29 | 2021-12-10 | 80078 | N |  |  |  | 76281 | 76280
16TPIT0068 | Venus - Chaparral Steel Tap 138 kV Line | Upgrade existing line |  | Venus | Chaparral Steel Tap | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4113-E | 2026-05-15 |  | 138 | 0 | 5.5 | 0 |  | Ellis | Ellis | Tier 4 |  |  |  |  | 1908, 2300 | N | N |  |  | 10426 | 3082 | 2013-R50
5496 | Forney Switch 345 kV Terminal Equipment | Upgrade the terminal equipment at Forney 345 kV Switch |  | Royse |  | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M3022 | 2026-05-15 |  | 345 | 0 | 0 | 0 |  | Rockwall |  | Tier 4 |  |  |  |  | 2437, 2478 | N |  |  |  | 62442 | 5496
16TPIT0064 | Simpson Stuart - Lancaster Witt 138 kV Line | Upgrade existing line |  | Simpson Stuart | Lancaster Witt | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4112-E | 2026-05-15 |  | 138 | 0 | 3 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | 2988, 3068 | N | N |  |  | 10416 | 3072 | 2013-R25
3276 | JT Deely to Martinez MLSE Upgrade | Upgrade terminal at JT Deely to ensure a rating of 2386 A (minimum). |  | JT Deely | Martinez | Planned | S-0759 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 |  | 2026-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5110, 5294 | N | N |  | There are no transformers associated with this project | 10627 | 3276
81581 | Riley: Construct New 345 kV Terminal | Interconnect the Gamma load to the existing Riley 345 kV station | CANCEL | Riley |  | Conceptual |  | AEP TNC/ETT | Tong Wang twang1@aep.com 918-599-2635 |  | 2026-06-30 |  | 345 | 0 | 0 | 0 |  | Wilbarger |  | Tier 4 |  |  |  |  | 6111 | N |  |  |  | 81582 | 81581
81647 | Dupont Switch to Sardinia: Construct New 138 kV Line | Interconnect the Epsilon load to the new Sardinia 138 kV station out of the existing Dupont Switch 138 kV station | CANCEL | Dupont Switch | Sardinia | Conceptual |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 |  | 2026-06-30 |  | 138 | 2 | 0 | 0 |  | Victoria | Victoria | Tier 4 |  |  |  |  | 8143, 81433 | N |  |  |  | 81648 | 81647
81657 | Verhalen: Construct New 138 kV Terminal | Interconnect the Eta load to the existing Verhalen 138 kV station | CANCEL | Verhalen |  | Conceptual |  | AEP TNC | Tong Wang twang1@aep.com 918-599-2635 |  | 2026-12-31 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  |  | 60207 | N |  |  |  | 81658 | 81657
81825 | Houdini: Construct New 345 kV Station | Interconnect the Xi load to the new Houdini 345 kV station on the STP to WAP 345 kV line | CANCEL | Houdini |  | Conceptual |  | AEP TCC | Doug Evans deevans@aep.com 918-599-2938 |  | 2026-12-31 |  | 345 | 0 | 0 | 0 |  | Matagorda |  | Tier 4 |  |  |  |  | 43990, 44000, 88800 | N |  |  |  | 81826 | 81825
81799 | Four Corners: Construct New 345 kV Station | Interconnect the Nu load to the new Four Corners 345 kV station on the Edith Clarke to Tesla 345 kV line | CANCEL | Four Corners |  | Conceptual |  | AEP TNC/ETT | Tong Wang twang1@aep.com 918-599-2635 |  | 2026-12-31 |  | 345 | 0 | 0 | 0 |  | Hardeman |  | Tier 4 |  |  |  |  | 60501, 60505, 61616 | N | N |  |  | 81800 | 81799
78473A | Odin (ODI) 138kV CEHE Substation | (In terms of completed Waterfowl substation) Loop new CEHE 138kV substation Odin (ODI) into Ckt.36 to create new Ckt.36 COPPER to Odin to Booster tap to Jones Creek. |  | Odin | Brazosport/ Booster | Conceptual |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-04-30 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 |  |  |  |  | 42199, 42215, 42280 | N | N |  |  | 87133 | 78473
78473B | Odin (ODI) 138kV CEHE Substation | Install one generator lead from CEHE 138kV substation Odin (ODI) to VALHAL (VAL) / Valhalla Solar (26INR0042) |  | Odin | VALHAL | Conceptual |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2027-04-30 00:02 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 |  |  |  |  | 42280, 113811 | N | N |  |  | 87134 | 78473
5525 | Forney - Lake Hubbard 345 kV Line | Construct new 345 kV line |  | Forney | Lake Hubbard | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4233 | 2027-05-15 |  | 345 | 0 | 7.5 | 0 |  | Kaufman | Dallas | Tier 2 |  |  |  |  | 2455, 2467 | N | N |  |  | 13252 | 5525
5522 | Lake Hubbard 345/138 kV Switching Station | Construct new 345/138 kV switching station |  | Lake Hubbard |  | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4139 | 2027-05-15 |  | 345 | 0 | 0 | 600 |  | Dallas |  | Tier 3 |  |  |  |  | 2401, 2402, 2455, 12455, 12456 | N | N |  |  | 13249 | 5522
87770 | Establish a 110.4 MVAR Capacitor Bank at Midnight 138 kV Substation | Establish a 110.4 MVAR Capacitor Bank at Midnight 138 kV Substation |  | Midnight Substation | Midnight Substation | Planned |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | R6346 | 2027-05-15 |  | 138 | 0 | 0 | 0 | 0,110.4 | Williamson | Williamson | Tier 4 |  |  |  |  | 3677 | N |  |  |  | 87771 | 87770
73540 | LCRATSC_Carlson_Substation_Addition | Substation addition to provide Point of Interconnection for Oncor Lund substation addition. |  | Carlson |  | Conceptual |  | LCRATSC | Dylan Preas dylan.preas@lcra.org |  | 2027-05-15 |  | 138 | 0 | 0 | 0 |  | Travis |  | Tier 4 |  |  |  |  | 3650, 7337, 7338 | N | N |  |  | 73541 | 73540
81556 | Haber: Construct New 345 kV Terminal | Interconnect the Crunch load to the new Haber 345 kV station | CANCEL | Haber |  | Conceptual |  | AEP TCC | Doug Evans deevans@aep.com 918-599-2938 |  | 2027-05-30 |  | 345 | 1 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  |  | 81003, 81004 | N |  |  |  | 81557 | 81556
81553 | Haber: Construct New 345 kV Terminal | Interconnect the Theta load to the new Haber 345 kV station | CANCEL | Haber |  | Conceptual |  | AEP TCC | Doug Evans deevans@aep.com 918-599-2938 |  | 2027-05-31 |  | 345 | 1 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  |  | 81003, 81005 | N |  |  |  | 81554 | 81553
81655 | Candela: Construct New 345 kV Station | Interconnect the Zeta load to the new Candela 345 kV station | CANCEL | Candela |  | Conceptual |  | AEP TCC | John Solis jlsolis@aep.com 361-881-5574 |  | 2027-06-01 |  | 345 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  |  | 8317, 8704, 8755 | N |  |  |  | 81656 | 81655
50282 | Adds new Jaguar sub near Twin Pines Switch | Adds new Jaguar sub between Twin Pines Switch and Highlands Sub. For AEP load. | AEP is looking at another location to serve the load. | Highlands Sub | Twin Pines Switch | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2027-06-01 |  | 69 | 0 | 0 | 0 |  | Victoria | Victoria | Tier 4 |  |  |  |  | 5602, 5604, 5609 | N | N |  |  | 50283 | 50282
81746 | Calabaza: Construct New 138 kV Terminal | Interconnect the Lambda load to the new Calabaza 138 kV station | CANCEL | Calabaza |  | Conceptual |  | AEP TCC | Doug Evans deevans@aep.com 918-599-2938 |  | 2027-06-02 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  |  | 80380 | N | N |  |  | 81747 | 81746
89993 | STP to Zoisite: Construct New 345 kV Line | Interconnect the HIF load to the new Zoisite 345 kV station on the STP to Zoisite 345 kV line | CANCEL | STP | Zoisite | Planned |  | AEP TCC | Douglas Evans deevans@aep.com 918-599-2938 |  | 2027-06-30 |  | 345 | 1.6 | 0 | 0 |  | Matagorda | Matagorda | Tier 4 | [5 empty] | N | N |  |  | 89994 | 89993
44870 | Charlotte 69 kV Station | Charlotte 69 kV Station: Add Cap Bank |  | Charlotte | - | Planned | 976 - 1154 | AEP TCC | Michael Glueck bcogan@aep.com 918-599-2857 | 3734 | 2027-07-01 |  | 69 | 0 | 0 | 0 | 0,7.2 | Atascosa |  | Tier 3 | [5 empty] | N | N |  |  | 44871 | 44870
4490 | LaPalma: Add 2nd 345/138 kV autotransformer | Add 345/138 kV autotransformer capacity at LaPalma | CANCELLED | LaPalma |  |  | 710 - 0880 | AEP TCC | Teresa Trotman bcogan@aep.com 918-599-2857 | 2904 | 2027-09-30 |  | 345 | 0 | 0 | 675 |  | Cameron |  | Tier 4 |  |  |  |  | 8314, 8317, 8356 | N | N |  |  | 12067 | 4490 | 2014-S15, S16
72457 | AddKiowaToQuinlanLine | Add 138kV line from Kiowa to Quinlan |  | Kiowa | Quinlan | Planned |  | RCEC | Scott Donhamsdonham@rayburnelectric.com 469-402-2024 |  | 2028-01-01 | 2025-06-01 | 138 | 8 | 0 | 0 |  | Hunt | Hunt | Tier 2 |  |  |  |  | 6796, 6884 | N |  |  |  | 72458 | 72457
4834 | Cresson - Rocky Creek 138 kV Line | Construct new line | Project Deferral | Cresson | Rocky Creek | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M5228 | 2028-05-15 |  | 138 | 3 | 0 | 0 |  | Tarrant | Parker | Tier 2 |  |  |  |  | 1881, 2202 | N | N |  |  | 12436 | 4834
6930 | New Paloma Substation | Adds new station and short line from Midstream |  | Midstream | Paloma | Planned |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2029-06-01 |  | 138 | 0.9 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 5643, 5644 | N | N |  |  | 14749 | 6930
6743 | Magellan Tank Farm: LCRA Interconnect | Add 138kV Tie Line between Navigation 138kV substation and Magellan's 138kV substation. Add Metering at Magellan's Substation. | Cancelled | Navigation | Magellan |  | 905 - 1083 | AEP TCC/LCRA | Michael Glueck bcogan@aep.com 918-599-2857 | 3689 | 2029-07-01 |  | 138 | 0 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  |  | 78460 | N | Y |  |  | 14536 | 6743
65648 | Interconnects Faulkner Data Center | Project has been cancelled. |  | TNMP Faulkner (bus # 38124) | Customer substation (bus # 38125) | Planned |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com 281-581-4733 |  | 2029-10-01 |  | 138 | 0.15 | 0 | 0 | 0,160 | Reeves | Reeves | Tier 4 |  |  |  |  | 38124, 38125 | N |  |  |  | 65649 | 65648
5524 | Royse South 345/138 kV Switching Station | Establish new 345/138 kV switching station |  | Royse | Forney | Conceptual |  | ONCOR | Jared Gurley Jared.Gurley@oncor.com 817-215-6079 | M4234 | 2030-05-15 12:00 |  | 345 | 0 | 0 | 0 |  | Rockwall |  | Tier 3 |  |  |  |  | 2437, 2467, 2469, 2470, 2471, 2472, 2474, 2478, 2485, 2702, 2710, 12471 | N | N |  |  | 49918 | 5524 | 2017-NC34
19TPIT0000 | Weser Substation | Replace 5.6 MVA with 69-13.09 kV, 20 MVA transformer |  | Weser |  | Planned |  | GVEC | Dylan Preas dylan.preas@LCRA.org 512-578-4514 |  | 2030-12-17 |  | 69 | 0 | 0 | 0 |  | Goliad |  | Tier 4 |  |  |  |  | 7239 | N | N |  |  | 10694 | 3336
5220 | Move Orange Grove load to 138 kV bus | Move load from the 69 KV to the 138 KV instead of replacing auto. 2015 RTP |  | Orange Grove |  | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2031-06-01 |  | 138 | 0 | 0 | 0 |  | Jim Wells |  | Tier 4 |  |  |  |  | 5660 | N | N |  |  | 12887 | 5220
13TPIT0124 | Airport 69 kV Substation | Build new load serving station in the 69 kV line from Lone Tree to Twin Pines Switch. |  | Airport |  | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2031-06-01 |  | 69 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  |  | 5600, 5601, 5602 | N | N |  |  | 8729 | 1538
3822 | San Miguel to Sigmor 138 kV line upgrade | Upgrade San Miguel to Sigmor 138 kV line as recommended in 2013 RTP. Will investigate re-conductoring on existing structures with ACCC and other high temperature conductors. |  | San Miguel | Sigmor | Conceptual |  | STEC | Teddi Flessner tflessner@stec.org 361-485-6119 |  | 2031-06-01 |  | 138 | 0 | 26.3 | 0 |  | Atascosa | Live Oak | Tier 3 |  |  |  |  | 5689, 5902, 8404 | N | N |  | Studies after the 2013 RTP have shown that AEP's approved project to rebuild the 69 kV Beeville to Three Rivers to 138 kV, TPIT 5166, reduces the loading on this line. STEC believes that rebuilding San Miguel to Sigmor is likely to be justified in the future by load growth and or generation additions. STEC recommends evaluating this project as an option when studies show the need for a project in this area of the transmission system. | 11279 | 3822 | 2013-R102
15TPIT0004 | Converse - New 138kV Substation | Loop new 138kV substation into future 138kV Martinez to Skyline transmission line |  | Converse | Martinez-Skyline | Planned | T-0177 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0601 | 2032-06-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5098, 5294, 5368 | N | N |  | There are no transformers associated with this project | 8143 | 967
12TPIT0009 | Masterson Rd - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to Howard line. |  | Masterson Rd. | Cagnon-Howard | Planned | T-0910 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | S-0538 | 2032-06-05 |  | 138 | 8 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  |  | 5054, 5230, 5296 | N | N |  | There are no transformers associated with this project | 9466 | 2218
44963 | USAA Rebuild 138 kV Station | CPSE_USAA 138 kV Substation Rebuild and Line Reconfiguration. |  |  |  | Planned | S-0896 | CPS | Omer Mohammed omohammed@cpsenergy.com 210-353-2035 | T-0285 | 2032-07-01 |  | 138 | 0.6 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  | 2019-01-10 |  |  | 5125, 5170, 5208, 5300, 5450, 5451, 5452, 5453 | N |  |  |  | 44964 | 44963

## RTPProjects
Project Number | Project Name | Transmission Owner | ERCOT Proposed in-service year | TSP MOD in-service year | Status of Project | Associated TPIT ERCOT Project Number(s) | Notes
2022-C1 | Cap bank Addition at AIRPRO Station | CNP | 2025 min
2016-N1 | Kiamichi Energy Facility (140077) 345-kV Reactor Addition | KIOWA POWER PARTNERS LLC (RE) | 2025 min
2021-N2 | City View (1483) – Ceramic (1485) 138-kV Line Terminal Equipment Upgrade | Oncor | 2024
2020-NC19 | Cedar Crest (2493) to Dealey (2842) to West Levee (2400) 138-kV Line Upgrades | Oncor | 2024
2021-NC9 | Sargant – Saint Augustine 138-kV Line Upgrade | Oncor | 2024
2022-NC1 | Waco Northeast Tap (3551) to Waco North (3552) 138-kV Line Upgrade | Oncor | 2024
2022-NC2 | Brand (827) to Ben Davis (968) 138-kV Line Upgrade | GPL | 2024 |  |  | 67170
2022-NC3 | Argyle - Corinth 138-kV Line Upgrade | ONCOR | 2024
2022-NC4 | Wilmer - Southside Filtration Tap East - Kleberg - Seagoville - Seagoville Switch 138-kV Line Upgrade | Oncor | 2024 |  |  | 71178
2022-NC5 | New International Airport Switch 345/138-kV Station | Oncor | 2024
2022-NC6 | Hackberry - DFW D-East 138-kV Line Upgrades | Oncor | 2024
2022-NC7 | Liggett Switch- DFW Area 138-kV Line Upgrades | Oncor | 2024
2022-NC8 | Lake Creek - Elm Mott 138-kV Line Upgrades | Oncor | 2024
2022-NC9 | Tin Roof 345-kV Expansion | Oncor | 2024
2022-NC10 | Randol Mill Tap East - Randol Mill 138-kV Line Upgrade | Oncor | 2024
2021-FW2 | Yucca Drive Switch - Wolfcamp - Courtney Creek 69-kV to 138-kV Line Conversion | Oncor | 2024
2021-FW4 | Rio Pecos - Rankin - Texon Tap - Atlantic Best Tap - Kemper Tap - Big Lake 69-kV to 138-kV Line Conversion | AEP | 2024
2021-FW5 | Caymus TNP - Gas Pad and Caymus TNP - Caymus Compressor TNP 138-kV Line Terminal Equipment Upgrade | TNMP, AEP | 2024
2021-FW6 | Monument Draw TNP to Monument Draw Gray Oak TNP 138-kV Line Terminal Equipment Upgrade | TNMP | 2027
2021-FW7 | TNMP Flat Top 138/25-kV Transformer Upgrade | TNMP | 2024
2021-FW8 | Wink TNP - California TNP 69-kV to 138-kV Line Conversion | TNMP | 2027
2021-FW12 | Moss Switch - Ector Harper - Red Lakes Switch - Penwell POD - Wolf Switching Station 138-kV Line Upgrade | Oncor | 2024
2021-FW16 | 16th Street TNP - Fort Stockton TNP 69-kV Line Upgrade | TNMP | 2024
2021-FW19 | Morgan Creek SES - Longshore Switch 345-kV Line Upgrade | ONCOR | 2027
2021-FW20 | Lamesa - Key Sub - Gail Sub - Willow Valley Switch 138-kV Line Upgrade | Oncor | 2024
2021-FW23 | Big Spring West - Stanton East 138-kV Line Upgrade | Oncor | 2024
2021-FW24 | Adobe Meadow - Midland East 138-kV Line Upgrade | Oncor | 2025 min
2022-FW1 | Lynx - Tombstone - Fort Stockton Plant - Leon Creek TNP 138-kV Line Upgrade | AEP, TNMP | 2024
2022-FW2 | Cedarvale 345-kV Subtation Expansion | TNMP, Oncor | 2024
2022-FW3 | New Reiter 345/138-kV Substation and Quail East 345-kV Substation | Oncor | 2024
2022-FW4 | New Opyote to Pyote 138-kV Line Addition | TNMP, Oncor | 2024
2022-FW5 | New Load Bus 900012 - New Load Bus 900021 138-kV Line Addition | Oncor | 2024
2022-FW6 | Far West Reactive Power Support Device Additions | TNMP, Oncor, AEP | 2024 |  |  | 65648, 63661, 65642
2022-FW7 | Leon Creek TNP - Airport TNP 138-kV Line Limiting Element Upgrade | TNMP | 2024
2022-FW8 | New Load Bus 900080 - New Load Bus 900032 138-kV Line Addition | Oncor | 2024
2022-FW9 | Cholla 345/138-kV Station Addition | TNMP, Oncor | 2024
2022-FW10 | Dollarhide - Dollarhide Unocal 138-kV Line Upgrade | Oncor | 2024
2022-FW11 | Pecos TNP - Faulkner Toyah TNP 138-kV Line Addition | TNMP | 2024
2022-FW12 | Tarbush TNP - Pig Creek 138-kV Line Upgrade | TNMP, AEP | 2024
2022-FW13 | Yarbrough Sub - Pecos Trails POD - Monahans Tap 2 - Wolf Switching Station 138-kV Line Upgrade | Oncor | 2024
2022-FW14 | Odessa EHV Switch - Rexall - General Tire Switch - Southwestern Portland Tap - Edwards Tap - Judkins - Sandhills Tap - Wolf Switching Station 138-kV Line Upgrade | Oncor | 2024
2022-FW15 | Holt Switch - Turnbaugh Corner Switch - Scharbauer POI - Oncor 900053 Tap - Notrees Southeast POI - Blockline POD - Amburguey - Yucca Drive Switch 138-kV Line Upgrade | Oncor | 2024
2022-FW16 | Moss Switch - Shin Oak POD - Yucca Drive Switch 138-kV Line Upgrade | Oncor | 2024
2022-FW17 | Moss Switch - Trigas Odessa Southwest - Big Three Odessa Tap 138-kV Line Upgrade | Oncor | 2024
2022-FW18 | Odessa EHV Switch - Trigas Odessa Tap 138-kV Line Upgrade | Oncor | 2024
2022-FW19 | Lamesa - Jim Payne POI - Paul D Tap 138-kV Line Upgrade | Oncor | 2024
2022-FW20 | Spraberry Switch - CRMWD 7 Tap - Meyers Draw - Dewey Lake Tap - Polecat Creek Switch 138-kV Line Upgrade | Oncor | 2025 min |  |  | 45640
2022-FW21 | Midland East – Midland County NW 345-kV Line Rebuild and Second Circuit Addition | Oncor | 2025 min
2022-FW22 | Midessa South 345/138-kV Transformer Upgrade and Second 345/138-kV Transformer Addition | Oncor | 2025 min
2022-FW23 | Consavvy South 345/138-kV Station Addition | Oncor | 2024
2022-FW24 | Faraday - Lamesa - Clearfork - Riverton 345-kV Double Circuit Line Addition | Oncor, WETT | 2024
2022-FW25 | Cedarvale Third 345/138-kV Transformer Addition | TNMP | 2024
2022-FW26 | Tarbush TNP - Leon Creek TNP and Woodward - Airport TNP - Leon Creek TNP 138-kV Line Additions | TNMP | 2024
2021-W1 | Cassava - San Angelo Concho 69-kV to 138-kV Line Conversion | AEP | 2025 min
2021-W2 | Morgan Creek - McDonald 138-kV Line Upgrade | Oncor | 2024
2021-W7 | San Angelo Highland Street - San Angelo South Tap - San Angelo Power Station 138-kV Line Upgrade | AEP | 2025
2021-W9 | San Angelo Paulann - San Angelo North 138-kV Line Upgrade | AEP | 2027
2021-W10 | San Angelo Red Creek - San Angelo Coke Street - Rusthill 138-kV Line Upgrade | AEP | 2025
2021-W12 | Cap Bank Addition at 138-kV Hargrove Substation | AEP | 2027
2022-W1 | China Grove - Getty Tap 138-kV Line Upgrade | ONCOR | 2028
2022-W2 | Morgan Creek SES - Tonkawa 345-kV Line Rebuild and Second Circuit Addition | ONCOR | 2025
2022-W3 | Colorado City - Plowboy 69-kV to 138-kV Line Conversion | ONCOR | 2025
2022-W4 | Abilene Northwest - Abilene Mulberry Creek - Abilene Industrial Park - Abilene Elmcreek 138-kV Line Upgrade | AEP | 2024
2022-W5 | Scurry Chevron - Kndrsacrc - New Load Bus 900041 Tap - Knapp 138-kV Line Upgrade | Oncor | 2027
2022-W6 | Morgan Creek - Westbrook - Latan Howard Tap 69-kV Line Upgrade | Oncor | 2024
2022-W7 | Knapp - Bluff Creek Switch - Exxon Sharon Ridge 138-kV Line Upgrade | Oncor | 2027
2021-WFW1 | Big Lake - Barnhart - Cassava 69-kV to 138-kV Line Conversion | AEP | 2027
2022-WFW1 | Twin Buttes - Hargrove - Pumpjack - Jerry - Russek Street - Big Lake 138-kV line Upgrade | AEP, LCRA TSC | 2024
2022-WFW2 | Midessa South SW - Consavvy - Longshore Switch - Morgan Creek SES 345-kV Line Upgrades | Oncor | 2025 min
2022-WFW3 | Morgan Creek SES - Falcon Seaboard - Midland East 345-kV Line Rebuild and Second Circuit Addition | Oncor | 2025 min
2022-SC1 | Sim Gideon - Bastrop City - Swiftex 138-KV Line Upgrade | LCRA TSC | 2027
2022-SC2 | San Marcos - Camp Gray - Robert Brown Jr - Clear Fork - Lockhart 69-kV to 138-kV Line Conversion | LCRA TSC | 2028
2022-SC3 | Pintail and Mallard 138-kV Substation and Line Additions | Oncor | 2025
2022-SC4 | Samsung 345-kV Substation and Line Addition | Oncor | 2028
2022-SC5 | Sandow Switch 345/138-kV Substation Expansion | Oncor | 2024
2022-SC6 | Howard - San Miguel 345-kV Double Circuit Line Addition and Beck Road 345/138-kV Substation Expansion | CPS, STEC | 2027
2022-SC7 | Decker 138-kV Bus Tie Breaker Upgrade | AEN | 2027
2022-SC8 | Lytton Substation 345/138-kV Transformer Addition | AEN | 2027
2022-S1 | Corpus Christi Sub 138/69-kV Transformer Addition and New 138-kV (8462) Substation and Line Additions | AEP, STEC | 2024
2022-S2 | Fannisub - Goliad 69-kV Line Upgrade | AEP, STEC | 2024
2022-S3 | Pearsall 138/69-kV Transformer Upgrade | STEC | 2027
2022-S4 | Cap Bank Addition at 138-kV Wormser Road Substation | AEP | 2025
2022-S5 | Reactor Addition at 345-kV NSub Substation | AEP | 2027
2022-S6 | San Diego - Freer 69-kV Line Upgrade | AEP | 2024
2022-S7 | Rincon - Gregory 69-kV Line Upgrade | AEP | 2024
2022-S8 | Rio Hondo - Burns - Heidelburg 138-kV Line Upgrade | STEC | 2024
2022-S9 | LA Palma – Haine Dr 138-kV Line Upgrade | AEP | 2025
2022-S10 | Wesmer - Pantera 138-kV Line Upgrade | AEP | 2024
2022-S11 | North Laredo- Unitec - Gateway West Tap 138-kV Line Upgrade | AEP | 2025

## TransmissionOwnerProjContac
TRANSMISSION OWNER | TPIT DISTRIBUTION | Primary Contact | Primary Email Address | Primary Phone | Secondary Contacts | Secondary Email Addresses | Secondary PHONE
AEP | Primary & Secondary | Cindy Miller | Camiller2@aep.com | Cindy Miller: 918 599 2891 | Glen Reed; Brandon Cogan; Mike Forcum; Jeff Ellis; Mina Turner; Lisa Kelso; | gareed@aep.com; bcogan@aep.com; mlforcum@aep.com; dnlyons@aep.com; jlellis@aep.com; myturner@aep.com; lokelso@aep.com; | Michael Forcum: 918 599 2674 Glen Reed: 918 599 2664 Brandon Cogan: 918 599 2857 Jeff Ellis: 918 599 3458
AUSTIN ENERGY | Primary & Secondary | Reza Ebrahimian | Reza.Ebrahimian@austinenergy.com; | Reza: (512) 322-6740 | Hunt, Dandy; Brion Ryan | dandy.hunt@austinenergy.com; Ryan, Brion <Brion.Ryan@austinenergy.com> | Reza:512 322 6740 Dandy:512 322 6748 Brion: 512-322-6879
BPUB | Primary | Luis Martinez | lugmartinez@brownsville-pub.com; | Luis: 956 983 6212 | Javier Martinez Jr. | jamartinez@brownsville-pub.com; | Javier: 956 983 6530
BEPC (BRAZOS ELECTRIC) | Primary & Secondary | Brian Hithersay | bhithersay@brazoselectric.com | Brian: 254-750-6795 | David Albers | dalbers@brazoselectric.com | David: 254 750 6358
BTU | Primary & Secondary | Edward Lopez | elopez@btutilities.com | Edward: 979 821 5697 | David Hering | dhering@btutilities.com | David: 979 821 5652
CNP | Primary & Secondary | Wesley Woitt | wesley.woitt@centerpointenergy.com | Wesley Woitt: 713-207-2760 | Samuel Whisler; Raja Sekhar Kakarla; Cody Mann | samuel.whisler@centerpointenergy.com; rajasekhar.kakarla@centerpointenergy.com; cody.mann@centerpointenergy.com | Samuel Whisler: 713-207-2767 Raja Sekhar Kakarla: 713-207-3614 Cody Mann: 713-207-3149
COCS | Primary | Glenn Gavit | ggavit@cstx.gov | Glenn: 979 764 3682 | Timothy Crabb, Stacy Engelmann | tcrabb@cstx.gov; sengelmann@cstx.gov; | Timothy Crabb 979 764 3439 Stacy Engelmann 979 764 3681
CPS | Primary & Secondary | William Robertson | wrobertson@cpsenergy.com | William: 210 353 4147 | Kenneth Bowen Marcos Terrazas Zuber Vohra Eduardo Olivarez | kbowen@cpsenergy.com; mterrazas1@cpsenergy.com; ZMVohra@cpsenergy.com; EJOlivarez@cpsenergy.com | Kenneth: 210 353 4142 Marcos: 210 353 2451 Zuber: 210 353 4262 Eduardo: 210 353 2357
CTT (Cross Texas Transmission) | Primary & Secondary | Christina Minchew | cminchew@lspower.com | Christina: 636:698:8443 | Ramya Nagarajan | RNagarajan@lspower.com | Ramya: 737-881-5008
DENTON | Primary & Secondary | Mark Zimmerer | Mark.Zimmerer@cityofdenton.com | Mark: 940 349 7169 | Cody Tenorio | Cody.Tenorio@cityofdenton.com | Cody: 940 349 7532
GARLAND | Primary & Secondary | Danh Huynh | Dhuynh@gpltexas.org | Danh: 972 205 3826 | David Grubbs Kevin Sills | Dgrubbs@gpltexas.org; ksills@gpltexas.org | David: 972-205-2664 Kevin: 972-205-2603
Golden Spread EC | Primary & Secondary | Chris Koenig | ckoenig@gsec.coop | Chris: 806 349 5201 | Shane McMinn, Mark Reinart | smcminn@gsec.coop; mreinart@gsec.coop | Shane: 806 379 7766 Mark: 806 349 6562
LCRA TSC; BEC (Bandera); BBEC; CTEC; GVEC; NBU; SBEC; RGEC | Primary & Secondary | Dylan Preas | dylan.preas@lcra.org | Dylan: 512-578-4514 | Naved Khan | naved.khan@lcra.org | Naved: 512-578-4176
Lone Star | Primary & Secondary | Chenyan Guo | chenyan.guo@fpl.com | Chenyan: 561-304-5692 | Matt Gomes | Matthew.Gomes@LONESTAR-TRANSMISSION.COM | Matt - 512-236-3133
Oncor | Primary & Secondary | Jared Gurley | Jared.Gurley@oncor.com | Jared: 817-215-6079 | Zahra Jianpanah | Zahra.Jianpanah@oncor.com
PEC | Primary & Secondary | Charles DeWitt | charles.dewitt@peci.com | Charles: 830-225-0673 | Joshua Rivers | joshua.rivers@peci.com | Joshua: 830-330-4192
Rayburn | Primary | Stephen Geiger | sgeiger@rayburnelectric.com | Stephen: 469-402-2112 | Scott Donham | Sdonham@rayburnelectric.com | Scott: 469-402-2024
Sharyland Utilities | Primary & Secondary | Brad Schwarz | bschwarz@huntpower.com | Brad: 512-289-7425 | Mark Caskey | mcaskey@sharyland.com | Mark: 214 978 8243
STEC | Primary & Secondary | Teddi Flessner Long Tran | tflessner@stec.org long.tran@stec.org | Teddi: 361 485 6119 Long: 361 485 6318 | Paul Person Loretta Gonzalez | pperson@stec.org; lgonzalez@stec.org; | Paul: 361 485 6151 Loretta: 956 377 7120
TMPA | Primary & Secondary | Danh Huynh | Dhuynh@gpltexas.org | Danh: 972 205 3826 | Kevin Sills | Ksills@gpltexas.org | Kevin: 972-205-2603
TNMP | Primary & Secondary | Ross Cloninger | ross.cloninger@tnmp.com | Ross: 281-581-4733 | Xia, Tao Roberts, Vincent Gerety, Chris | Tao.Xia@tnmp.com; Vincent.Roberts@tnmp.com; Christopher.Gerety@tnmp.com; | Tao: 281-581-4764 Vincent:409-949-5608 Chris:409-949-5605
Wind Energy Texas Transmission (WETT) | Primary | Chris Ramirez | cramirez@wettllc.com | Chris: 737-218-4525 | Yang Zhang | yzhang@wettllc.com | Yang: 737-218-4542

## TSPResponsibility
Field Name | Required/ Optional
ERCOT Project Number | Required
RTP Project Number | Required if in RTP
RPG Project Number | Required for submitted Tier 1, 2, and 3 projects
Project Title | Required
Project Description | Optional
Comments/Reasons for Delays/Cancellations/Speedup | Optional
Terminal "from" Location | Optional
Terminal "to" Location | Optional
Transmission Status | Optional
Associated Projects (project number) | Optional
Transmission Owner | Required
TSP/Company Contact | Required
Transmission Owner Project Number | Optional
Projected In-Service Date (Month/Yr) | Required
Actual In-Service Date (Month/Yr) | Required once energized in the field
CONFIDENTIAL Total Project Estimated Cost | Required
Service Level kV | Required
Trans Circuit Miles New | Optional
Trans Circuit Miles Rebuilt or Upgraded | Optional
Autotransformer Capacity (MVA) | Optional
Reactive Capability Added | Optional
County Location for Substation or for a Line | Optional
County Location for Ending Point for a Line | Optional
Planning Charter Tier | Required
Date Submitted TO ERCOT for RPG Review | Required for submitted Tier 1, 2, and 3 projects
Date RPG Review Completed (Month/Yr) | Required for submitted Tier 1, 2, and 3 projects, if RPG review has been completed.
Date ERCOT BOD Review Completed | -Required for submitted Tier 1 projects, if ERCOT BOD review completed.
SSWG Base Case Related Bus Numbers | Required
Is the project reflected in SSWG Base Cases? | Required
Part of Interface (Y/N) | Required
Requested Additional Information | Optional

## Cost Summary Info
Net Effective Date | Actual In-Service Date | Tab | Cost Summary
past < effective < TPIT | past < actual < TPIT | Complete | Year Completed
past < effective < TPIT | TPIT < actual < future | Planned | Current Year Planned
past < effective < TPIT | actual == NULL | Planned | Current Year Planned
TPIT < effecitve < Current Year end | past < actual < future | Planned | Current Year Planned
TPIT < effecitve < Current Year end | actual == NULL | Planned | Current Year Planned
Current Year end < effective < future | past < actual < future | Future | Year
Current Year end < effective < future | actual == NULL | Future | Year