## Summary
Release Date: March 17, 2022
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Spring 2022
SUMMARY
The ERCOT region is expected to have sufficient installed generating capacity to serve peak demands in the upcoming spring season, March – May 2022, under normal system conditions and most of the reserve capacity risk scenarios examined. The spring capacity planning reserve margin is forecasted at 52.5%, which is intended to cover resource outages, lower-than-expected renewable output, and higher-than-expected customer demand.
Based on expected spring peak weather conditions, the peak demand for Spring 2022 is forecasted to be 64,729 MW.
A total of 94,394 MW of resource capacity is expected to be available for the spring season. Since the start of winter 2021-22, 31 units have been approved for synchronization to the ERCOT Grid. These units are comprised of wind, solar, and energy storage projects1 that total 1,027 MW based on the expected capacity contribution for wind and solar at the time of peak demand, and spring-rated capacity for thermal resources. An additional 367 MW of planned resource capacity constituting gas-fired and wind units are expected to be available to meet the spring peak demand.
Report Design Changes
For the reserve capacity risk scenarios, the ERCOT Spring Season has been divided into two separate periods with their respective base/moderate and extreme reserve capacity risk scenarios: the peak maintenance season (March-April), and the peak demand month (May). Additional scenario assumption values specific to these time periods have been introduced for wind and solar output. A total of 14 scenarios are presented.
As part of the reorganization of the scenario information, the scenario assumption descriptions were moved to their own tab ("Scenario Assumption Details") to make the scenario tables more compact and allow easier comparison of the assumption descriptions. Planning reserve margins for the two spring time periods have also been moved to their own tab.
___________________________
1 Energy Storage Resources (ESRs) continue to be assigned a zero MW capacity contribution because nearly all of them are short-duration systems assumed to provide Ancillary Services rather than sustained capacity available to meet system peak loads. Also, there is insufficient operational history for longer-duration ESRs to determine the expected capacity contribution during peak load hours.

## Forecasted Capacity
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2022
Release Date: March 17, 2022
Forecasted Capacity and Demand, MW
Resources, MW
| Thermal Resources, Installed Spring-rated Capacity | 65626.3 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
| Hydroelectric, Peak Average Capacity Contribution | 437.495 | Based on 77% of installed capacity for hydro resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Switchable Capacity Total | 3691 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
| Less Switchable Capacity Unavailable to ERCOT | -558 | Based on survey responses of Switchable Resource owners
| Available Mothballed Capacity | 378 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
| Capacity from Private Use Networks | 2775 | Average grid injection during the top 20 spring peak load hours over the last three years, plus the forecasted net change in generation capacity available to the ERCOT grid pursuant to Nodal Protocol Section 10.3.2.4.
| Coastal Wind, Peak Average Capacity Contribution | 3288.128 | Based on 64% of installed capacity for coastal wind resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Panhandle Wind, Peak Average Capacity Contribution | 1612.91 | Based on 38% of installed capacity for panhandle wind resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Other Wind, Peak Average Capacity Contribution | 9385.884 | Based on 36% of installed capacity for other wind resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Solar Utility-Scale, Peak Average Capacity Contribution | 6671.021 | Based on 61% of rated capacity for solar resources (spring season) per Nodal Protocols Section 3.2.6.2.2
| Storage, Peak Average Capacity Contribution | 0 | Based on 0% of rated capacity (spring season); resources assumed to provide regulation reserves rather than sustained capacity available to meet peak loads
| RMR Capacity to be under Contract | 0
| Capacity Pending Retirement | 0 | Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2
| Non-Synchronous Ties, Capacity Contribution | 719.8 | Based on net imports during winter 2020/2021 (Winter Storm Uri) Energy Emergency Alert (EEA) intervals
| Planned Thermal Resources with Signed IA, Air Permits and Adequate Water Supplies | 360.8 | Based on in-service dates provided by developers
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution | 0 | Based on in-service dates provided by developers and 64% spring capacity contribution for coastal wind resources
| Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution | 0 | Based on in-service dates provided by developers and 38% spring capacity contribution for panhandle wind resources
| Planned Other Wind with Signed IA, Peak Average Capacity Contribution | 5.76 | Based on in-service dates provided by developers and 36% spring capacity contribution for other wind resources
| Planned Solar Utility-Scale, Peak Average Capacity Contribution | 0 | Based on in-service dates provided by developers and 61% spring capacity contribution for solar resources
| Planned Storage, Peak Average Capacity Contribution | 0 | Based on in-service dates provided by developers and 0% spring capacity contribution for storage resources
[a] Total Resources, MW |  | 94394.098

## Base & Moderate Risk Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2022_DRAFT
Release Date: March 17, 2022
Base & Moderate Reserve Capacity Risk Scenarios, MW
Spring Maintenance Season, March - April
| Forecasted April Peak Load / Typical Unplanned Outages / Typical Renewable Output | High April Peak Load / Typical Unplanned Outages / Typical Renewable Output | Forecasted April Peak Load / High Unplanned Outages / Typical Renewable Output | Forecasted April Peak Load / Typical Unplanned Outages / Low Renewable Output
Scenario Assumptions
[a] Peak Load Forecast (Baseline) | 58305 | 58305 | 58305 | 58305
[b] Rooftop PV Forecast Reduction, MW | -342 | -342 | -342 | -342
[c] Adjusted Peak Load Forecast, [a+b] | 57963 | 57963 | 57963 | 57963
[d] Total Resources (from Forecast Capacity tab) | 94394.098 | 94394.098 | 94394.098 | 94394.098
Uses of Reserve Capacity
Peak Load Increase, High | 0 | 4781 | - | 0
Typical Planned Outages, Thermal | 6155.0288 | 6155.0288 | 6155.0288 | 6155.0288
Typical Unplanned Outages, Thermal | 12791.1797 | 12791.1797 | 12791.1797 | 12791.1797
High Unplanned Outage Adjustment, Thermal | 0 | 0 | 5379.45 | 0
Low Wind Output Reduction to 3,602 MW | 0 | 0 | 0 | 10690.682
Low Solar Output Reduction to 3,398 MW | 0 | 0 | 0 | 3273.021
[e] Total Uses of Reserve Capacity | 18946.2085 | 23727.2085 | 24325.6585 | 32909.9115
Capacity Available For Operating Reserves
[f] Capacity Available for Operating Reserves, Normal Operating Conditions, [d-c-e] | 17484.8894 | 12703.8894 | 12105.4394 | 3521.1864
Less than 2,300 MW indicates risk of EEA1
[g] Emergency Resources deployed by ERCOT (An amount is only shown if Capacity Available for Operating Reserves is at or below 2,300 MW) | 0 | 0 | 0 | 0
[h] Capacity Available for Operating Reserves, Emergency Conditions [f+g], MW | 17484.8894 | 12703.8894 | 12105.4394 | 3521.1864
Less than 1,000 MW indicates risk of EEA3 Load Shed
Spring Peak Load Month, May
| Forecasted May Peak Load / Typical Unplanned Outages / Typical Renewable Output | High May Peak Load / Typical Unplanned Outages / Typical Renewable Output | Forecasted May Peak Load / High Unplanned Outages / Typical Renewable Output | Forecasted May Peak Load / Typical Unplanned Outages / Low Renewable Output
Scenario Assumptions
[a] Peak Load Forecast (Baseline) | 65159 | 65159 | 65159 | 65159
[b] Rooftop PV Forecast Reduction, MW | -430 | -430 | -430 | -430
[c] Adjusted Peak Load Forecast, [a+b] | 64729 | 64729 | 64729 | 64729
[d] Total Resources (from Forecast Capacity tab) | 94394.098 | 94394.098 | 94394.098 | 94394.098
Uses of Reserve Capacity
Peak Load Increase, High | 0 | 5642 | 0 | 0
Typical Planned Outages, Thermal | 1625.7257 | 1625.7257 | 1625.7257 | 1625.7257
Typical Unplanned Outages, Thermal | 12791.1797 | 12791.1797 | 12791.1797 | 12791.1797
High Unplanned Outage Adjustment, Thermal | 0 | 0 | 5379.45 | 0
Low Wind Output Adjustment to 3,772 MW | 0 | 0 | 0 | 10520.682
Low Solar Output Adjustment to 5,115 MW | 0 | 0 | 0 | 1556.021
[e] Total Uses of Reserve Capacity | 14416.9054 | 20058.9054 | 19796.3554 | 26493.6084
Capacity Available For Operating Reserves
[f] Capacity Available for Operating Reserves, Normal Operating Conditions, [d-c-e] | 15248.1925 | 9606.1925 | 9868.7425 | 3171.4895
Less than 2,300 MW indicates risk of EEA1
[g] Emergency Resources deployed by ERCOT (An amount is only shown if Capacity Available for Operating Reserves is at or below 2,300 MW) | 0 | 0 | 0 | 0
[h] Capacity Available for Operating Reserves, Emergency Conditions [f+g], MW | 15248.1925 | 9606.1925 | 9868.7425 | 3171.4895
Less than 1,000 MW indicates risk of EEA3 Load Shed

## Extreme Risk Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2022
Release Date: March 17, 2022
Extreme Reserve Capacity Risk Scenarios, MW (One or a combination of extreme risk assumptions resulting in low probability, high impact outcomes)
Spring Maintenance Season, March - April
| Extreme April Peak Load / Typical Unplanned Outages / Typical Renewable Output | Extreme April Peak Load / Extreme Unplanned Outages / Typical Renewable Output | Forecasted April Peak Load / Extreme Unplanned Outages / Extreme Low Wind Output
Scenario Assumptions
[a] Peak Load Forecast (Baseline) | 58305 | 58305 | 58305
[b] Rooftop PV Forecast Reduction, MW | -342 | -342 | -342
[c] Adjusted Peak Load Forecast, [a+b] | 57963 | 57963 | 57963
[d] Total Resources (from Forecast Capacity tab) | 94394.098 | 94394.098 | 94394.098
Uses of Reserve Capacity
April Extreme Load Increase | 7931 | 7931 | 0
Typical Planned Outages, Thermal | 6155.0288 | 6155.0288 | 6155.0288
Typical Unplanned Outages, Thermal | 12791.1797 | 12791.1797 | 12791.1797
Extreme Unplanned Outage Adjustment, Thermal | 0 | 7703 | 7703
Extreme Low Wind Output Adjustment to 564 MW | 0 | 0 | 13728.682
[e] Total Uses of Reserve Capacity | 26877.2085 | 34580.2085 | 40377.8905
Capacity Available For Operating Reserves
[f] Capacity Available for Operating Reserves, Normal Operating Conditions, [d-c-e] | 9553.8894 | 1850.8894 | -3946.7926
Less than 2,300 MW indicates risk of EEA1
[g] Emergency Resources deployed by ERCOT (An amount is only shown if Capacity Available for Operating Reserves is at or below 2,300 MW) | 0 | 2815 | 2815
[h] Capacity Available for Operating Reserves, Emergency Conditions [f+g], MW | 9553.8894 | 4665.8894 | -1131.7926
Less than 1,000 MW indicates risk of EEA3 Load Shed
Spring Peak Load Month, May
| Extreme May Peak Load / Typical Unplanned Outages / Typical Renewable Output | Extreme May Peak Load / Extreme Unplanned Outages / Typical Renewable Output | Forecasted May Peak Load / Extreme Unplanned Outages / Extreme Low Wind Output
Scenario Assumptions
[a] Peak Load Forecast (Baseline) | 65159 | 65159 | 65159
[b] Rooftop PV Forecast Reduction, MW | -430 | -430 | -430
[c] Adjusted Peak Load Forecast, [a]+[b] | 64729 | 64729 | 64729
[d] Total Resources (from Forecast Capacity tab) | 94394.098 | 94394.098 | 94394.098
Uses of Reserve Capacity
May Extreme Load Increase | 6188 | 6188 | 0
Typical Planned Outages, Thermal | 1625.7257 | 1625.7257 | 1625.7257
Typical Unplanned Outages, Thermal | 12791.1797 | 12791.1797 | 12791.1797
Extreme Unplanned Outage Adjustment, Thermal | 0 | 7703 | 7703
Extreme Low Wind Output Adjustment to 510 MW | 0 | 0 | 13782.682
[e] Total Uses of Reserve Capacity | 20604.9054 | 28307.9054 | 35902.5874
Capacity Available For Operating Reserves
[f] Capacity Available for Operating Reserves, Normal Operating Conditions, [d-c-e] | 9060.1925 | 1357.1925 | -6237.4895
Less than 2,300 MW indicates risk of EEA1
[g] Emergency Resources deployed by ERCOT (An amount is only shown if Capacity Available for Operating Reserves is at or below 2,300 MW) | 0 | 2815 | 2815
[h] Capacity Available for Operating Reserves, Emergency Conditions [f+g], MW | 9060.1925 | 4172.1925 | -3422.4895
Less than 1,000 MW indicates risk of EEA3 Load Shed

## Planning Reserve Margins
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2022
Release Date: March 17, 2022
Planning Reserve Margins
|  | April | May
| Peak Demand Forecast, MW | 58305 | 65159
| Rooftop PV Forecast Reduction, MW | -342 | -430
| Adjusted Peak Load Forecast, MW | 57963 | 64729
| Total Resources, MW | 94394.098 | 94394.098
| Emergency Resources Deployed by ERCOT, MW 1 | 2815 | 2815
| Planning Reserve Margin 2 | 71.17% | 52.46%
Formula: PRM = (Total Resources / (Adjusted Peak Demand - Emergency Resources)) - 1
1 The derivation of the emergency resource amount is described in the Scenario Assumptions Details tab.
2 The Planning Reserve Margin (PRM) is the forecasted capacity reserve that can cover higher-than-expected peak demand and lower-than-expected resource availability when looking at months or longer in the future. This is in contrast to operating reserve measures that focus on actual available capacity during real-time and hour-ahead operating periods. Consequently, the PRM is not an appropriate measure of capacity reserves when operations timeframes are being considered.

## Scenario Assumption Details
| Base & Moderate Risk Scenarios | Extreme Risk Scenarios
Adjusted Peak Load Forecast | Based on average weather conditions from 2006 – 2020 at the time of the April and May peaks. Data for spring 2021 is not used in the forecast model because the model estimation process depends on using full calendar-year data. Given the timing of forecast preparation in November of each year, the estimation data set extends to the end of the previous calendar-year; for this load forecast, the end date is thus December 31, 2020. These baseline forecasts are adjusted downwards to account for peak load reductions from rooftop solar installations that are not already accounted for in the baseline forecasts. The rooftop solar load reductions for March/April and May are 342 MW and 430 MW, respectively.
April High Load Adjustment | The High April Peak Load is the 90th percentile of forecasted April peaks based on weather conditions from 2006 - 2020. | Based on the most extreme weather conditions from 2006 – 2020 at the time of the April peak (2006). Can also be thought of as representing the forecasted peak if typical May weather occurs in April.
May High Load Adjustment | The 90th percentile of forecasted May peaks based on weather conditions from 2006 - 2020. | Based on the most extreme weather conditions from 2006 – 2020 at the time of the May peak for 2011. Can also be thought of as representing the forecasted peak if typical June weather occurs in May.
Typical Planned Outages, Thermal | Based on the historical average of planned outages for weekdays, hours ending 15 - 22 (3 pm - 10 pm), for the last three spring seasons (2018 - 2020). Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators. Spring 2021 outages were excluded to avoid including Winter Storm Uri-related outages that extended into the spring season.
Typical Unplanned Outages, Thermal | Based on historical average of Unplanned outages for March through May weekdays, hours ending 15 - 22 (3 pm - 10 pm), for the last three spring seasons (2018 - 2020). Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators. Spring 2021 outages were excluded to avoid including Winter Storm Uri-related outages that extended into the spring season.
Unplanned Outage Adjustments, Thermal | Based on the 95th percentile of historical Unplanned outages for March through May weekdays, hours ending 15 - 22 (3 pm - 10 pm), for the last five spring seasons (2016 -2020); the adjustment is the 95th percentile value, 18,170 MW, less the typical Unplanned outage amount of 12,791 MW. The outages include those from Private Use Network (PUN) generators. See the Background tab for more information on the treatment of PUN capacity. Spring 2021 outages were excluded to avoid including Winter Storm Uri-related outages in this calculation. | Based on the Maximum historical Unplanned outages for March through May weekdays, hours ending 15 - 22 (3 pm - 10 pm), for the last five spring seasons (2016 -2020); the adjustment is the Maximum value of 20,494 MW, less the typical Unplanned outage amount of 12,791 MW. The outages include those from PUN generators. See the Background tab for more information on the treatment of PUN capacity. Spring 2021 outages were excluded to avoid including Winter Storm Uri-related outages that extended into the spring season.
Wind Output Adjustments | The adjustments are based on the 5th percentile of hourly wind capacity factors (output as a percentage of installed capacity) for the daily period hour-ending 15 - 18 (3 pm - 7 pm). The capacity factors are derived from annual hourly simulated wind output profiles for the period 1980 - 2020. The profiles reflect hourly weather conditions for each of the 41 simulated weather years. A profile is developed for each current operational wind site as well as each planned wind site included in the Final 2021 Summer SARA. For the March/April period, hourly capacity factors are developed for all days in March and April, resulting in 10,004 capacity factors from which the 5th percentile is computed (41 profiles x 61 days x 4 hours). For the May period, hourly capacity factors are developed for all days in May, resulting in 5,084 capacity factors from which the 5th percentile is computed (41 profiles x 31 days x 4 hours). For the March/April period, this low wind output level is 3,602 MW (CF = 10.4%), while the low output level for May is 3,772 MW (CF = 10.9%). The adjustments are the Peak Average Capacity Contribution, 14,196 MW, less 3,602 MW and 3,772 MW, respectively. The methodology report for profile development is available at: https://www.ercot.com/files/docs/2021/12/07/Report_ERCOT_1980-2020_WindSolarDGPVGenProfiles.pdf | The adjustments are based on the minimum wind capacity factors (output as a percentage of installed capacity) for the daily period hour-ending 15 - 18 (3 pm - 7 pm). The capacity factors are derived from annual hourly simulated wind output profiles for the period 1980 - 2020 as described to the left. For the March/April period, this extreme-low wind output level is 564 MW (CF = 1.6%), while the extreme-low output level for May is 510 MW (CF = 1.6%). The adjustments are the Peak Average Capacity Contribution, 14,196 MW, less 564 MW and 510 MW, respectively. Note that a scenario with a combined extreme peak load and extreme-low renewables output is not provided because an extreme peak load is associated with high solar output due to minimal cloud cover serving as a driver for both system conditions.
Solar Output Adjustments | The adjustments are based on the 5th percentile of hourly solar photovoltaic (PV)capacity factors (output as a percentage of installed capacity) for the daily period hour-ending 15 - 18 (3 pm - 7 pm). The capacity factors are derived from annual hourly simulated solar output profiles for the period 1980 - 2020 as described above. For the March/April period, this low solar PV output level is 3,398 MW (CF = 31.1%), while the low output level for May is 5,115 MW (CF = 46.8%). The adjustments are the Peak Average Capacity Contribution, 6,671 MW, less 3,398 MW and 5,115 MW respectively. | The adjustments are based on the minimum solar PV capacity factors (output as a percentage of installed capacity) for the daily period hour-ending 15 - 18 (3 pm - 7 pm). The capacity factors are derived from annual hourly simulated wind output profiles for the period 1980 - 2020 as described to the left. For the March/April period, this extreme-low solar output level is 37 MW (CF = 0.3%), while the extreme-low output level for May is 1,433 MW (13.1%). The adjustments are the Peak Average Capacity Contribution, 6,671 MW, less 37 MW and 1,433 MW, respectively. Note that a scenario with a combined extreme peak load and extreme-low renewables output is not provided because an extreme peak load is associated with high solar output due to minimal cloud cover serving as a driver for both system conditions.
Emergency Resources deployed by ERCOT | An amount is only shown if Capacity Available for Operating Reserves, line item [g], is at or below 2,300 MW. Consists of the sum of expected Load Resources Available for Responsive Reserves for the spring season (1,591 MW), Emergency Response Service (1,122 MW), and TDSP Voltage Reduction (102 MW). Each of these amounts reflect a 2% gross-up to account for avoided transmission losses. Other resources that may be available include voluntary customer Demand Response (including customer installation of backup generators), switchable generation resources currently serving the Eastern Interconnection, and additional DC tie imports subject to availability.

## SpringCapacities
Unit Capacities - Spring
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1227
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1214
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1323.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1310
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 608
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 608
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 448
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 855
21 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
22 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 932.6
23 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 155
24 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 155
25 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 664
26 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 663
27 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 577
28 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 610
29 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS-CC | SOUTH | 2000 | 164
30 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS-CC | SOUTH | 2000 | 164
31 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS-CC | SOUTH | 2000 | 190
32 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS-GT | NORTH | 1973 | 19
33 | BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS-CC | COASTAL | 2010 | 161
34 | BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS-CC | COASTAL | 2010 | 161
35 | BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS-ST | COASTAL | 1974 | 292
36 | BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS-CC | COASTAL | 1976 | 322
37 | BASTROP ENERGY CENTER CTG 1 | 21INR0541 | BASTEN_GTG1100 | BASTROP | GAS-CC | SOUTH | 2002 | 157
38 | BASTROP ENERGY CENTER CTG 2 | 21INR0541 | BASTEN_GTG2100 | BASTROP | GAS-CC | SOUTH | 2002 | 157
39 | BASTROP ENERGY CENTER STG | 21INR0541 | BASTEN_ST0100 | BASTROP | GAS-CC | SOUTH | 2002 | 236
40 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS-CC | NORTH | 2000 | 161.8
41 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS-CC | NORTH | 2000 | 161.8
42 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS-CC | NORTH | 2001 | 160.6
43 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS-CC | NORTH | 2001 | 83.6
44 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS-CC | NORTH | 2009 | 222.4
45 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS-CC | HOUSTON | 2003 | 169
46 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS-CC | HOUSTON | 2003 | 169
47 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS-CC | HOUSTON | 2003 | 270
48 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS-CC | WEST | 1987 | 77
49 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS-CC | WEST | 1987 | 77
50 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS-CC | WEST | 1988 | 71
51 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS-GT | COASTAL | 2017 | 46.7
52 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS-GT | COASTAL | 2017 | 46.7
53 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS-GT | HOUSTON | 2017 | 46.7
54 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS-GT | HOUSTON | 2017 | 46.7
55 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 168
56 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 168
57 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 182
58 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS-ST | HOUSTON | 1970 | 745
59 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS-ST | HOUSTON | 1972 | 749
60 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS-CC | SOUTH | 2007 | 83.9
61 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS-CC | SOUTH | 2007 | 76.9
62 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS-CC | SOUTH | 2008 | 82.9
63 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS-CC | SOUTH | 2008 | 77.9
64 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS-CC | SOUTH | 2007 | 103
65 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS-CC | SOUTH | 2008 | 107
66 | COLORADO BEND II CTG 7 | 18INR0077 | CBECII_CT7 | WHARTON | GAS-CC | SOUTH | 2017 | 332.1
67 | COLORADO BEND II CTG 8 | 18INR0077 | CBECII_CT8 | WHARTON | GAS-CC | SOUTH | 2017 | 337.8
68 | COLORADO BEND II STG 9 | 18INR0077 | CBECII_STG9 | WHARTON | GAS-CC | SOUTH | 2017 | 482.3
69 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS-CC | HOUSTON | 2008 | 181
70 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS-CC | HOUSTON | 2008 | 178
71 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS-CC | HOUSTON | 2008 | 178
72 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS-CC | HOUSTON | 2008 | 144
73 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS-GT | NORTH | 2004 | 46.5
74 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS-GT | NORTH | 2010 | 48.5
75 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS-ST | NORTH | 1978 | 108.5
76 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS-GT | SOUTH | 1989 | 50
77 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS-GT | SOUTH | 1989 | 50
78 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS-GT | SOUTH | 1989 | 50
79 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS-GT | SOUTH | 1989 | 50
80 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS-GT | NORTH | 1990 | 71
81 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS-GT | NORTH | 1990 | 70
82 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS-GT | NORTH | 1990 | 70
83 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS-GT | NORTH | 1990 | 71
84 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS-CC | HOUSTON | 2002 | 190
85 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS-CC | HOUSTON | 2002 | 202
86 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS-CC | HOUSTON | 2002 | 190
87 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS-CC | HOUSTON | 2002 | 202
88 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS-CC | HOUSTON | 2014 | 174
89 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS-CC | HOUSTON | 2002 | 290
90 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS-IC | NORTH | 2018 | 56.5
91 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS-IC | NORTH | 2018 | 56.5
92 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS-IC | NORTH | 2018 | 56.5
93 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS-IC | NORTH | 2018 | 56.5
94 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS-GT | WEST | 2015 | 153.6
95 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS-GT | WEST | 2015 | 153.6
96 | ELK STATION IC 3 |  | AEEC_ELK_3 | HALE | GAS-IC | PANHANDLE | 2016 | 195
97 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS-CC | NORTH | 2002 | 209
98 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS-CC | NORTH | 2002 | 116
99 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS-GT | HOUSTON | 2009 | 36
100 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS-GT | HOUSTON | 2009 | 36
101 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS-GT | HOUSTON | 2009 | 36
102 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS-GT | HOUSTON | 2009 | 36
103 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS-CC | SOUTH | 2014 | 176
104 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS-CC | SOUTH | 2014 | 176
105 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS-CC | SOUTH | 2014 | 189
106 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS-CC | NORTH | 2003 | 167
107 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS-CC | NORTH | 2003 | 159
108 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS-CC | NORTH | 2003 | 159
109 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS-CC | NORTH | 2003 | 167
110 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS-CC | NORTH | 2003 | 159
111 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS-CC | NORTH | 2003 | 159
112 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS-CC | NORTH | 2003 | 408
113 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS-CC | NORTH | 2003 | 408
114 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS-CC | NORTH | 2002 | 156.2
115 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS-CC | NORTH | 2002 | 156.2
116 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS-CC | NORTH | 2002 | 156.5
117 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS-CC | NORTH | 2002 | 156.5
118 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS-CC | NORTH | 2002 | 178
119 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS-CC | NORTH | 2002 | 177.1
120 | FRIENDSWOOD G CTG 1 (FORMERLY TEJAS POWER GENERATION) |  | FEGC_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2018 | 119
121 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS-ST | WEST | 1960 | 239
122 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 390
123 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
124 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
125 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
126 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 50
127 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
128 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
129 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS-IC | NORTH | 2010 | 8.2
130 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS-IC | NORTH | 2010 | 8.2
131 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS-IC | NORTH | 2010 | 8.2
132 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
133 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
134 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
135 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
136 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS-CC | SOUTH | 2000 | 200
137 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS-CC | SOUTH | 2000 | 200
138 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS-ST | NORTH | 1963 | 395
139 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS-ST | NORTH | 1976 | 435
140 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS-ST | NORTH | 1977 | 435
141 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS-CC | SOUTH | 2002 | 213
142 | HAYS ENERGY FACILITY CSG 2 | 22INR0586 | HAYSEN_HAYSENG2 | HAYS | GAS-CC | SOUTH | 2002 | 214
143 | HAYS ENERGY FACILITY CSG 3 | 21INR0527 | HAYSEN_HAYSENG3 | HAYS | GAS-CC | SOUTH | 2002 | 213
144 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS-CC | SOUTH | 2002 | 216
145 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS-CC | SOUTH | 2000 | 143
146 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS-CC | SOUTH | 2000 | 143
147 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS-CC | SOUTH | 2000 | 172
148 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS-CC | NORTH | 2006 | 150
149 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS-CC | NORTH | 2006 | 150
150 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS-CC | NORTH | 2011 | 150
151 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS-CC | NORTH | 2011 | 150
152 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS-CC | NORTH | 2006 | 285
153 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS-CC | NORTH | 2011 | 285
154 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS-CC | NORTH | 1997 | 163
155 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS-CC | NORTH | 1997 | 106
156 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS-ST | NORTH | 1970 | 392
157 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS-ST | NORTH | 1973 | 523
158 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS-CC | NORTH | 2000 | 161
159 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS-CC | NORTH | 2000 | 153
160 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS-CC | NORTH | 2000 | 153
161 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS-CC | NORTH | 2000 | 161
162 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS-CC | NORTH | 2000 | 204
163 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS-CC | NORTH | 2000 | 204
164 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS-GT | SOUTH | 2008 | 92.9
165 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS-GT | SOUTH | 2008 | 90.1
166 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS-GT | SOUTH | 2004 | 46
167 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS-GT | SOUTH | 2004 | 46
168 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS-GT | SOUTH | 2004 | 46
169 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS-GT | SOUTH | 2004 | 46
170 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS-CC | SOUTH | 2001 | 183
171 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS-CC | SOUTH | 2001 | 175
172 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS-CC | SOUTH | 2001 | 192
173 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS-CC | SOUTH | 2001 | 213.6
174 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS-CC | SOUTH | 2001 | 213.6
175 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS-CC | SOUTH | 2001 | 255.5
176 | MIDLOTHIAN ENERGY FACILITY CTG 1 |  | MDANP_CT1 | ELLIS | GAS-CC | NORTH | 2001 | 232
177 | MIDLOTHIAN ENERGY FACILITY CTG 2 | 21INR0534 | MDANP_CT2 | ELLIS | GAS-CC | NORTH | 2001 | 230
178 | MIDLOTHIAN ENERGY FACILITY CTG 3 | 22INR0543 | MDANP_CT3 | ELLIS | GAS-CC | NORTH | 2001 | 229
179 | MIDLOTHIAN ENERGY FACILITY CTG 4 | 22INR0523 | MDANP_CT4 | ELLIS | GAS-CC | NORTH | 2001 | 232
180 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS-CC | NORTH | 2002 | 244
181 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS-CC | NORTH | 2002 | 246
182 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS-GT | WEST | 1988 | 67
183 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS-GT | WEST | 1988 | 66
184 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS-GT | WEST | 1988 | 66
185 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS-GT | WEST | 1988 | 67
186 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS-GT | WEST | 1988 | 68
187 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS-GT | WEST | 1988 | 68
188 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS-ST | NORTH | 1956 | 122
189 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS-ST | NORTH | 1958 | 118
190 | MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | DALLAS | GAS-ST | NORTH | 1967 | 568
191 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS-CC | COASTAL | 2010 | 161
192 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS-CC | COASTAL | 2010 | 161
193 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS-CC | COASTAL | 1972 | 322
194 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS-ST | SOUTH | 1972 | 420
195 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS-ST | SOUTH | 1974 | 410
196 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS-CC | WEST | 2001 | 164.6
197 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS-CC | WEST | 2001 | 156.1
198 | ODESSA-ECTOR POWER CTG 21 | 20INR0282 | OECCS_CT21 | ECTOR | GAS-CC | WEST | 2001 | 164.6
199 | ODESSA-ECTOR POWER CTG 22 | 20INR0282 | OECCS_CT22 | ECTOR | GAS-CC | WEST | 2001 | 156.1
200 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS-CC | WEST | 2001 | 206.4
201 | ODESSA-ECTOR POWER STG 2 | 20INR0282 | OECCS_UNIT2 | ECTOR | GAS-CC | WEST | 2001 | 206.4
202 | OLD BLOOMINGTON ROAD CTG 1 (VICTORIA PORT 2) |  | VICTPRT2_UNIT1 | VICTORIA | GAS-GT | SOUTH | 2022 | 46.7
203 | OLD BLOOMINGTON ROAD CTG 2 (VICTORIA PORT 2) |  | VICTPRT2_UNIT2 | VICTORIA | GAS-GT | SOUTH | 2022 | 46.7
204 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS-CC | NORTH | 2014 | 218
205 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS-CC | NORTH | 2014 | 217
206 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS-CC | NORTH | 2014 | 308
207 | PANDA TEMPLE I POWER CTG 1 | 22INR0533 | PANDA_T1_TMPL1CT1 | BELL | GAS-CC | NORTH | 2014 | 218.5
208 | PANDA TEMPLE I POWER CTG 2 | 22INR0533 | PANDA_T1_TMPL1CT2 | BELL | GAS-CC | NORTH | 2014 | 218.5
209 | PANDA TEMPLE I POWER STG 1 | 22INR0533 | PANDA_T1_TMPL1ST1 | BELL | GAS-CC | NORTH | 2014 | 353.1
210 | PANDA TEMPLE II POWER CTG 1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS-CC | NORTH | 2015 | 218.5
211 | PANDA TEMPLE II POWER CTG 2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS-CC | NORTH | 2015 | 218.5
212 | PANDA TEMPLE II POWER STG 1 |  | PANDA_T2_TMPL2ST1 | BELL | GAS-CC | NORTH | 2015 | 353.1
213 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS-CC | NORTH | 1989 | 86
214 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS-CC | NORTH | 1989 | 86
215 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS-CC | NORTH | 1990 | 87
216 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS-CC | HOUSTON | 2000 | 170
217 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS-CC | HOUSTON | 2000 | 170
218 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS-CC | HOUSTON | 2000 | 168
219 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS-IC | SOUTH | 2012 | 50.6
220 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS-IC | SOUTH | 2012 | 50.6
221 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS-IC | SOUTH | 2012 | 50.6
222 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS-IC | SOUTH | 2012 | 50.6
223 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS-GT | WEST | 1988 | 64
224 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS-GT | WEST | 1988 | 64
225 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS-GT | WEST | 1988 | 64
226 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS-GT | WEST | 1990 | 64
227 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS-GT | WEST | 1990 | 65
228 | PROENERGY SOUTH 1 (PES1) CTG 1 |  | PRO_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.1
229 | PROENERGY SOUTH 1 (PES1) CTG 2 |  | PRO_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.1
230 | PROENERGY SOUTH 1 (PES1) CTG 3 |  | PRO_UNIT3 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.1
231 | PROENERGY SOUTH 1 (PES1) CTG 4 |  | PRO_UNIT4 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.1
232 | PROENERGY SOUTH 1 (PES1) CTG 5 |  | PRO_UNIT5 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.1
233 | PROENERGY SOUTH 1 (PES1) CTG 6 |  | PRO_UNIT6 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.1
234 | PROENERGY SOUTH 2 (PES2) CTG 7 |  | PRO_UNIT7 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.1
235 | PROENERGY SOUTH 2 (PES2) CTG 8 |  | PRO_UNIT8 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.1
236 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS-GT | HOUSTON | 2018 | 61
237 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS-GT | HOUSTON | 2018 | 62
238 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS-GT | HOUSTON | 2018 | 52
239 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS-GT | HOUSTON | 2018 | 56
240 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS-GT | HOUSTON | 2018 | 56
241 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS-GT | HOUSTON | 2018 | 54
242 | POWERLANE PLANT STG 1 |  | STEAM1A_STEAM_1 | HUNT | GAS-ST | NORTH | 1966 | 17.5
243 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS-ST | NORTH | 1967 | 23.5
244 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS-ST | NORTH | 1978 | 39.5
245 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS-CC | WEST | 2007 | 80
246 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS-CC | WEST | 2007 | 80
247 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS-CC | WEST | 2008 | 80
248 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS-CC | WEST | 2008 | 80
249 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS-CC | WEST | 2007 | 98
250 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS-CC | WEST | 2008 | 98
251 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS-GT | NORTH | 1994 | 104
252 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS-GT | NORTH | 1994 | 104
253 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS-ST | NORTH | 1968 | 75
254 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS-ST | NORTH | 1972 | 120
255 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS-ST | NORTH | 1975 | 208
256 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS-GT | NORTH | 2001 | 90
257 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS-ST | NORTH | 1971 | 107
258 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS-ST | NORTH | 1975 | 146
259 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
260 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
261 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
262 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
263 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 162
264 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS-CC | SOUTH | 2002 | 162
265 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS-CC | SOUTH | 2002 | 162
266 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 306
267 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS-CC | SOUTH | 2003 | 50
268 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS-CC | SOUTH | 2003 | 51
269 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS-CC | SOUTH | 2003 | 50
270 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS-CC | SOUTH | 2003 | 40
271 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS-GT | HOUSTON | 1995 | 83
272 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS-GT | HOUSTON | 1995 | 83
273 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
274 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
275 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
276 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
277 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS-CC | SOUTH | 2004 | 151
278 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS-GT | SOUTH | 2010 | 47
279 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS-GT | SOUTH | 2010 | 47
280 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS-CC | SOUTH | 2004 | 148
281 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS-GT | COASTAL | 2004 | 46
282 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS-CC | COASTAL | 1996 | 40
283 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS-CC | COASTAL | 1962 | 20
284 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS-ST | SOUTH | 1965 | 130
285 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS-ST | SOUTH | 1968 | 133
286 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS-ST | SOUTH | 1972 | 336
287 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS-IC | SOUTH | 2016 | 26.7
288 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS-IC | SOUTH | 2016 | 26.7
289 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS-ST | NORTH | 1966 | 57
290 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS-ST | NORTH | 1973 | 61
291 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS-ST | NORTH | 1958 | 167
292 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS-ST | NORTH | 1965 | 502
293 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS-GT | HOUSTON | 1967 | 14
294 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
295 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
296 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
297 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
298 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
299 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
300 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS-CC | HOUSTON | 1974 | 56
301 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS-CC | HOUSTON | 1974 | 56
302 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
303 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
304 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
305 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
306 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
307 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
308 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS-CC | HOUSTON | 1974 | 109
309 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS-CC | HOUSTON | 1974 | 109
310 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS-CC | HOUSTON | 2000 | 100.6
311 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS-CC | HOUSTON | 2000 | 100.6
312 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS-CC | HOUSTON | 2000 | 100.6
313 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS-CC | HOUSTON | 2000 | 131.5
314 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS-ST | NORTH | 1965 | 235
315 | TOPAZ POWER PLANT U1 |  | TOPAZ_UNIT1 | GALVESTON | GAS-GT | HOUSTON | 2021 | 45.1
316 | TOPAZ POWER PLANT U2 |  | TOPAZ_UNIT2 | GALVESTON | GAS-GT | HOUSTON | 2021 | 45.1
317 | TOPAZ POWER PLANT U3 |  | TOPAZ_UNIT3 | GALVESTON | GAS-GT | HOUSTON | 2021 | 45.1
318 | TOPAZ POWER PLANT U4 |  | TOPAZ_UNIT4 | GALVESTON | GAS-GT | HOUSTON | 2021 | 45.1
319 | TOPAZ POWER PLANT U5 |  | TOPAZ_UNIT5 | GALVESTON | GAS-GT | HOUSTON | 2021 | 45.1
320 | TOPAZ POWER PLANT U6 |  | TOPAZ_UNIT6 | GALVESTON | GAS-GT | HOUSTON | 2021 | 45.1
321 | TOPAZ POWER PLANT U7 |  | TOPAZ_UNIT7 | GALVESTON | GAS-GT | HOUSTON | 2021 | 45.1
322 | TOPAZ POWER PLANT U8 |  | TOPAZ_UNIT8 | GALVESTON | GAS-GT | HOUSTON | 2021 | 45.1
323 | TOPAZ POWER PLANT U9 |  | TOPAZ_UNIT9 | GALVESTON | GAS-GT | HOUSTON | 2021 | 45.1
324 | TOPAZ POWER PLANT U10 |  | TOPAZ_UNIT10 | GALVESTON | GAS-GT | HOUSTON | 2021 | 45.1
325 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS-GT | SOUTH | 2009 | 48
326 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS-GT | SOUTH | 2009 | 48
327 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS-GT | SOUTH | 2009 | 48
328 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS-GT | SOUTH | 2009 | 47
329 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS-ST | SOUTH | 1966 | 217
330 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS-ST | SOUTH | 1968 | 230
331 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS-ST | SOUTH | 1970 | 412
332 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2020 | 46.7
333 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2020 | 46.7
334 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2019 | 46.7
335 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2019 | 46.7
336 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS-CC | SOUTH | 2009 | 171
337 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS-CC | SOUTH | 2009 | 132
338 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 13
339 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 169
340 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 169
341 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 246
342 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 536
343 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS-CC | WEST | 1987 | 20
344 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS-CC | WEST | 1987 | 20
345 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS-CC | WEST | 1987 | 20
346 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS-CC | WEST | 1987 | 17
347 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
348 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
349 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
350 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
351 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS-CC | NORTH | 2004 | 244.4
352 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS-CC | NORTH | 2004 | 244.4
353 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS-CC | NORTH | 2004 | 298
354 | WOLF HOLLOW 2 CTG 4 | 18INR0076 | WHCCS2_CT4 | HOOD | GAS-CC | NORTH | 2017 | 330.6
355 | WOLF HOLLOW 2 CTG 5 | 18INR0076 | WHCCS2_CT5 | HOOD | GAS-CC | NORTH | 2017 | 331.1
356 | WOLF HOLLOW 2 STG 6 | 18INR0076 | WHCCS2_STG6 | HOOD | GAS-CC | NORTH | 2017 | 456.9
357 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS-CC | NORTH | 2002 | 240.4
358 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS-CC | NORTH | 2002 | 234.4
359 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS-CC | NORTH | 2002 | 270
360 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
361 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
362 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
363 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2
364 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
365 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2
366 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
367 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
368 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
369 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
370 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
371 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 65558.3
372
373 | Operational Resources - Synchronized but not Approved for Commercial Operations (Thermal)
374 | BRANDON (LP&L) (DGR) | 21INR0201 | BRANDON_UNIT1 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 20
375 | R MASSENGALE (LP&L) | 21INR0202 | MASSENGL_G6 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 18
376 | R MASSENGALE CTG 2 (LP&L) | 21INR0202 | MASSENGL_G7 | LUBBOCK | GAS | PANHANDLE | 2021 | 18
377 | R MASSENGALE STG (LP&L) | 21INR0202 | MASSENGL_G8 | LUBBOCK | GAS | PANHANDLE | 2021 | 38
378 | TY COOKE CTG 1 (LP&L) | 21INR0506 | TY_COOKE_GT2 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 14
379 | TY COOKE CTG 2 (LP&L) | 21INR0506 | TY_COOKE_GT3 | LUBBOCK | GAS | PANHANDLE | 2021 | 17
380 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 125
381
382 | Operational Capacity Thermal Unavailable due to Extended Outage or Derate |  | THERMAL_UNAVAIL |  |  |  |  | -57
383 | Operational Capacity Thermal Total |  | THERMAL_OPERATIONAL |  |  |  |  | 65626.3
384
385 | Operational Resources (Hydro)
386 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
387 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
388 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
389 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
390 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
391 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
392 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
393 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 49.5
394 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 49.5
395 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
396 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
397 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
398 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
399 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
400 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
401 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
402 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
403 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
404 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
405 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
406 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
407 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36
408 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 22
409 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 22
410 | Operational Capacity Total (Hydro) | [6 empty] | 557.4
411 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 427
412
413 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
414 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4
415 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
416 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
417 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
418 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
419 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 19.7
420 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) |  | DG_HYDRO_CAP_CONT |  |  |  |  | 15.0913
421
422 | Operational Capacity Hydroelectric Unavailable due to Extended Outage or Derate |  | HYDRO_UNAVAIL |  |  |  |  | -4.5963
423 | Operational Capacity Hydroelectric Total (Wind) |  | HYDRO_OPERATIONAL |  |  |  |  | 437.495
424
425 | Operational Resources (Switchable)
426 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS-IC | PANHANDLE | 2016 | 56
427 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS-IC | PANHANDLE | 2016 | 56
428 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS-IC | PANHANDLE | 2016 | 56
429 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS-GT | PANHANDLE | 2016 | 195
430 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS-GT | PANHANDLE | 2016 | 195
431 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS-CC | NORTH | 2000 | 180
432 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS-CC | NORTH | 2000 | 180
433 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS-CC | NORTH | 2000 | 180
434 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS-CC | NORTH | 2000 | 400
435 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 162
436 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179
437 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 178
438 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 389
439 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS-CC | NORTH | 2003 | 162
440 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS-CC | NORTH | 2003 | 158
441 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS-CC | NORTH | 2003 | 322
442 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 159
443 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 161
444 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 323
445 | Switchable Capacity Total | [6 empty] | 3691
446
447 | Switchable Capacity Unavailable to ERCOT
448 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
449 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
450 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
451 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -195
452 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -195
453 | Switchable Capacity Unavailable to ERCOT Total | [6 empty] | -558
454
455 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  |  |  |  | 378
456
457 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 2920
458 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | -145
459
460 | Operational Resources (Wind)
461 | WESTERN TRAIL WIND (AJAX WIND) |  | AJAXWIND_UNIT1 | WILBARGER | WIND-O | WEST | 2022 | 225.6
462 | WESTERN TRAIL WIND (AJAX WIND) U2 |  | AJAXWIND_UNIT2 | WILBARGER | WIND-O | WEST | 2022 | 141
463 | AMADEUS WIND 1 U1 |  | AMADEUS1_UNIT1 | FISHER | WIND-O | WEST | 2021 | 36.7
464 | AMADEUS WIND 1 U2 |  | AMADEUS1_UNIT2 | FISHER | WIND-O | WEST | 2021 | 35.8
465 | AMADEUS WIND 2 U1 |  | AMADEUS2_UNIT3 | FISHER | WIND-O | WEST | 2021 | 177.7
466 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.8
467 | AVIATOR WIND U1 |  | AVIATOR_UNIT1 | COKE | WIND-O | WEST | 2021 | 180.1
468 | AVIATOR WIND U2 |  | AVIATOR_UNIT2 | COKE | WIND-O | WEST | 2021 | 145.6
469 | AVIATOR WIND U3 |  | DEWOLF_UNIT1 | COKE | WIND-O | WEST | 2021 | 199.3
470 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100
471 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102
472 | BARROW RANCH (JUMBO HILL WIND) 1 |  | BARROW_UNIT1 | ANDREWS | WIND-O | WEST | 2021 | 90.2
473 | BARROW RANCH (JUMBO HILL WIND) 2 |  | BARROW_UNIT2 | ANDREWS | WIND-O | WEST | 2021 | 70.5
474 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120
475 | BLUE SUMMIT WIND 1 A | 22INR0550 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 8.8
476 | BLUE SUMMIT WIND 1 B | 22INR0550 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 124.3
477 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 89.7
478 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 6.7
479 | BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WILBARGER | WIND-O | WEST | 2020 | 13.4
480 | BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WILBARGER | WIND-O | WEST | 2020 | 182.4
481 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2020 | 162
482 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.8
483 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120
484 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108
485 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9
486 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7
487 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6
488 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5
489 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117
490 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2
491 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 88
492 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 90
493 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2
494 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4
495 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 123.1
496 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165
497 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 130.5
498 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 120
499 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1
500 | CAPRICORN RIDGE WIND 1 | 17INR0054 | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 231.7
501 | CAPRICORN RIDGE WIND 2 | 17INR0054 | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5
502 | CAPRICORN RIDGE WIND 3 | 17INR0054 | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 200.9
503 | CAPRICORN RIDGE WIND 4 | 17INR0061 | CAPRIDG4_CR4 | COKE | WIND-O | WEST | 2008 | 121.5
504 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 75
505 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 75
506 | CHALUPA WIND |  | CHALUPA_UNIT1 | CAMERON | WIND-C | COASTAL | 2021 | 173.3
507 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5
508 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6
509 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4
510 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4
511 | CRANELL WIND |  | CRANELL_UNIT1 | REFUGIO | WIND-C | COASTAL | 2022 | 220
512 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5
513 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5
514 | DESERT SKY WIND 1 A | 17INR0070 | DSKYWND1_UNIT_1A | PECOS | WIND-O | WEST | 2022 | 64.5
515 | DESERT SKY WIND 2 A | 17INR0070 | DSKYWND1_UNIT_1B | PECOS | WIND-O | WEST | 2022 | 23.4
516 | DESERT SKY WIND 1 B | 17INR0070 | DSKYWND2_UNIT_2A | PECOS | WIND-O | WEST | 2022 | 64.5
517 | DESERT SKY WIND 2 B | 17INR0070 | DSKYWND2_UNIT_2B | PECOS | WIND-O | WEST | 2022 | 14.4
518 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
519 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
520 | EAST RAYMOND WIND (EL RAYO) U1 |  | EL_RAYO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 98
521 | EAST RAYMOND WIND (EL RAYO) U2 |  | EL_RAYO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 96
522 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 121.9
523 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2017 | 98.9
524 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2017 | 131.1
525 | ESPIRITU WIND |  | CHALUPA_UNIT2 | CAMERON | WIND-C | COASTAL | 2021 | 25.2
526 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200
527 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8
528 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6
529 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.5
530 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8
531 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2
532 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80
533 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6
534 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6
535 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82
536 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76
537 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4
538 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8
539 | GREEN MOUNTAIN WIND (BRAZOS) U1 | 21INR0532 | BRAZ_WND_WND1 | SCURRY | WIND-O | WEST | 2003 | 99
540 | GREEN MOUNTAIN WIND (BRAZOS) U2 | 21INR0532 | BRAZ_WND_WND2 | SCURRY | WIND-O | WEST | 2003 | 61
541 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
542 | GRIFFIN TRAIL WIND U1 |  | GRIF_TRL_UNIT1 | KNOX | WIND-O | WEST | 2021 | 98.7
543 | GRIFFIN TRAIL WIND U2 |  | GRIF_TRL_UNIT2 | KNOX | WIND-O | WEST | 2021 | 126.9
544 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2021 | 141.6
545 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2021 | 141.6
546 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.9
547 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 163.5
548 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
549 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 99.9
550 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 100
551 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REAGAN | WIND-O | WEST | 2018 | 152.5
552 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REAGAN | WIND-O | WEST | 2018 | 147.5
553 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52
554 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98
555 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100
556 | HIDALGO II WIND |  | MIRASOLE_MIR13 | HIDALGO | WIND-O | SOUTH | 2021 | 50.4
557 | HIGH LONESOME W 1A |  | HI_LONE_WGR1A | CROCKETT | WIND-O | WEST | 2021 | 46
558 | HIGH LONESOME W 1B |  | HI_LONE_WGR1B | CROCKETT | WIND-O | WEST | 2021 | 52
559 | HIGH LONESOME W 1C |  | HI_LONE_WGR1C | CROCKETT | WIND-O | WEST | 2021 | 25.3
560 | HIGH LONESOME W 2 |  | HI_LONE_WGR2 | CROCKETT | WIND-O | WEST | 2021 | 122.5
561 | HIGH LONESOME W 2A |  | HI_LONE_WGR2A | CROCKETT | WIND-O | WEST | 2021 | 25.3
562 | HIGH LONESOME W 3 |  | HI_LONE_WGR3 | CROCKETT | WIND-O | WEST | 2021 | 127.6
563 | HIGH LONESOME W 4 |  | HI_LONE_WGR4 | CROCKETT | WIND-O | WEST | 2021 | 101.6
564 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 131.1
565 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 98.9
566 | HORSE HOLLOW WIND 1 | 17INR0052 | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230
567 | HORSE HOLLOW WIND 2 | 17INR0053 | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184
568 | HORSE HOLLOW WIND 3 | 17INR0053 | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4
569 | HORSE HOLLOW WIND 4 | 17INR0053 | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115
570 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95
571 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102
572 | INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.8
573 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.7
574 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230
575 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96
576 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74
577 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30
578 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.2
579 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.6
580 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
581 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
582 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.4
583 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2015 | 110
584 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND-O | WEST | 2001 | 79.7
585 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND-O | WEST | 2001 | 79.7
586 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND-O | WEST | 2001 | 40.5
587 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND-O | WEST | 2001 | 79.7
588 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 160
589 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7
590 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.3
591 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.8
592 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194
593 | LONE STAR WIND 2 (POST OAK) U1 | 22INR0479 | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98
594 | LONE STAR WIND 2 (POST OAK) U2 | 22INR0479 | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100
595 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
596 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
597 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 48
598 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51
599 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5
600 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24
601 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200
602 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200
603 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110
604 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
605 | LOS VIENTOS WIND II |  | LV2_LV2 | WILLACY | WIND-C | COASTAL | 2013 | 201.6
606 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
607 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
608 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
609 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
610 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150
611 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.6
612 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.6
613 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
614 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
615 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8
616 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2018 | 196.6
617 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.6
618 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60
619 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 58.8
620 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2
621 | OVEJA WIND U1 |  | OVEJA_G1 | IRION | WIND-O | WEST | 2021 | 151.2
622 | OVEJA WIND U2 |  | OVEJA_G2 | IRION | WIND-O | WEST | 2021 | 151.2
623 | PALMAS ALTAS WIND |  | PALMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2020 | 144.9
624 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
625 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
626 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.2
627 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6
628 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5
629 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5
630 | PANTHER CREEK WIND 3 A |  | PC_SOUTH_PANTH31 | HOWARD | WIND-O | WEST | 2022 | 106.9
631 | PANTHER CREEK WIND 3 B |  | PC_SOUTH_PANTH32 | HOWARD | WIND-O | WEST | 2022 | 108.5
632 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
633 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
634 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 91.7
635 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 85.8
636 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
637 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
638 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
639 | PEYTON CREEK WIND |  | PEY_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2
640 | PYRON WIND 1 |  | PYR_PYRON1 | NOLAN | WIND-O | WEST | 2008 | 121.5
641 | PYRON WIND 2 |  | PYR_PYRON2 | NOLAN | WIND-O | WEST | 2008 | 127.5
642 | RANCHERO WIND |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150
643 | RANCHERO WIND |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150
644 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 104.3
645 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 103
646 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6
647 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9
648 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.4
649 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114
650 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95
651 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150
652 | RTS 2 WIND (HEART OF TEXAS WIND) U1 |  | RTS2_U1 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9
653 | RTS 2 WIND (HEART OF TEXAS WIND) U2 |  | RTS2_U2 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9
654 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160
655 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64
656 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110
657 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.2
658 | SAND BLUFF WIND | 20INR0296 | MCDLD_SBW1 | GLASSCOCK | WIND-O | WEST | 2008 | 90
659 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150
660 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 78
661 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.2
662 | SHAFFER (PATRIOT WIND/PETRONILLA) |  | SHAFFER_UNIT1 | NUECES | WIND-C | COASTAL | 2021 | 226.1
663 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1
664 | SHERBINO 2 WIND | 19INR0120 | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2011 | 132
665 | SILVER STAR WIND | 18INR0064 | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8
666 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102
667 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98
668 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5
669 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8
670 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 98.2
671 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 161
672 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98
673 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96
674 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 120
675 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201
676 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 211.2
677 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 164.7
678 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 42.5
679 | SWEETWATER WIND 2A | 17INR0068 | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16.8
680 | SWEETWATER WIND 2B | 17INR0068 | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 110.8
681 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 33.6
682 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 118.6
683 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 125
684 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 112
685 | SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | NOLAN | WIND-O | WEST | 2007 | 85
686 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150
687 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150
688 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.7
689 | TEXAS BIG SPRING WIND B |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6
690 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150
691 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23
692 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5
693 | TRENT WIND 1 A | 17INR0069 | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 38.3
694 | TRENT WIND 1 B |  | TRENT_UNIT_1B | NOLAN | WIND-O | WEST | 2018 | 15.6
695 | TRENT WIND 2 |  | TRENT_UNIT_2 | NOLAN | WIND-O | WEST | 2018 | 50.5
696 | TRENT WIND 3 A |  | TRENT_UNIT_3A | NOLAN | WIND-O | WEST | 2018 | 38.3
697 | TRENT WIND 3 B |  | TRENT_UNIT_3B | NOLAN | WIND-O | WEST | 2018 | 13.8
698 | TRINITY HILLS WIND 1 | 20INR0019 | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4
699 | TRINITY HILLS WIND 2 | 20INR0019 | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6
700 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2
701 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 169.5
702 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2017 | 125.6
703 | VENADO WIND U1 |  | VENADO_UNIT1 | ZAPATA | WIND-O | SOUTH | 2021 | 105
704 | VENADO WIND U2 |  | VENADO_UNIT2 | ZAPATA | WIND-O | SOUTH | 2021 | 96.6
705 | VERA WIND 1 |  | VERAWIND_UNIT1 | KNOX | WIND-O | WEST | 2021 | 12
706 | VERA WIND 2 |  | VERAWIND_UNIT2 | KNOX | WIND-O | WEST | 2021 | 7.2
707 | VERA WIND 3 |  | VERAWIND_UNIT3 | KNOX | WIND-O | WEST | 2021 | 100.8
708 | VERA WIND 4 |  | VERAWIND_UNIT4 | KNOX | WIND-O | WEST | 2021 | 22
709 | VERA WIND 5 |  | VERAWIND_UNIT5 | KNOX | WIND-O | WEST | 2021 | 100.8
710 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
711 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.9
712 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.3
713 | WEST RAYMOND (EL TRUENO) WIND U1 |  | TRUENO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 116.6
714 | WEST RAYMOND (EL TRUENO) WIND U2 |  | TRUENO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 123.2
715 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 57
716 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.3
717 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125
718 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125
719 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5
720 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.6
721 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30
722 | WOLF RIDGE WIND | 21INR0511 | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 112.5
723 | Operational Capacity Total (Wind) | [6 empty] | 28847.2
724
725 | Operational Wind Capacity Sub-total (Coastal Counties) |  | WIND_OPERATIONAL_C |  |  |  |  | 4664.9
726 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 64
727
728 | Operational Wind Capacity Sub-total (Panhandle Counties) |  | WIND_OPERATIONAL_P |  |  |  |  | 4244.5
729 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PEAK_PCT_P | % |  |  |  | 38
730
731 | Operational Wind Capacity Sub-total (Other Counties) |  | WIND_OPERATIONAL_O |  |  |  |  | 19937.8
732 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PEAK_PCT_O | % |  |  |  | 36
733
734 | Operational Resources (Wind) - Synchronized but not Approved for Commercial Operations
735 | ANCHOR WIND I | 21INR0387 | ANCHOR_WIND2 | EASTLAND | WIND-O | NORTH | 2022 | 98.9
736 | ANCHOR WIND II A | 21INR0539 | ANCHOR_WIND3 | EASTLAND | WIND-O | NORTH | 2022 | 90
737 | ANCHOR WIND II B | 21INR0539 | ANCHOR_WIND4 | EASTLAND | WIND-O | NORTH | 2022 | 38.7
738 | APOGEE WIND U1 | 21INR0467 | APOGEE_UNIT1 | THROCKMORTON | WIND-O | WEST | 2022 | 25
739 | APOGEE WIND U2 | 21INR0467 | APOGEE_UNIT2 | THROCKMORTON | WIND-O | WEST | 2022 | 14
740 | APOGEE WIND U3 | 21INR0467 | APOGEE_UNIT3 | THROCKMORTON | WIND-O | WEST | 2022 | 30.2
741 | APOGEE WIND U4 | 21INR0467 | APOGEE_UNIT4 | THROCKMORTON | WIND-O | WEST | 2022 | 115
742 | APOGEE WIND U5 | 21INR0467 | APOGEE_UNIT5 | THROCKMORTON | WIND-O | WEST | 2022 | 110
743 | APOGEE WIND U6 | 21INR0467 | APOGEE_UNIT6 | THROCKMORTON | WIND-O | WEST | 2022 | 24
744 | APOGEE WIND U7 | 21INR0467 | APOGEE_UNIT7 | THROCKMORTON | WIND-O | WEST | 2022 | 75
745 | AQUILLA LAKE WIND U1 | 19INR0145 | AQUILLA_U1_23 | HILL | WIND-O | NORTH | 2021 | 13.9
746 | AQUILLA LAKE WIND U2 | 19INR0145 | AQUILLA_U1_28 | HILL | WIND-O | NORTH | 2021 | 135.4
747 | AQUILLA LAKE 2 WIND | 20INR0256 | AQUILLA_U2_23 | HILL | WIND-O | NORTH | 2021 | 7
748 | AQUILLA LAKE 2 WIND U2 | 20INR0256 | AQUILLA_U2_28 | HILL | WIND-O | NORTH | 2021 | 143.8
749 | BAIRD NORTH WIND U1 | 20INR0083 | BAIRDWND_UNIT1 | CALLAHAN | WIND-O | NORTH | 2021 | 195
750 | BAIRD NORTH WIND U2 | 20INR0083 | BAIRDWND_UNIT2 | CALLAHAN | WIND-O | NORTH | 2021 | 145
751 | BLACKJACK CREEK WIND U1 | 20INR0068 | BLACKJAK_UNIT1 | BEE | WIND-O | SOUTH | 2022 | 120
752 | BLACKJACK CREEK WIND U2 | 20INR0068 | BLACKJAK_UNIT2 | BEE | WIND-O | SOUTH | 2022 | 120
753 | CACTUS FLATS WIND U1 | 16INR0086 | CFLATS_U1 | CONCHO | WIND-O | WEST | 2018 | 148.4
754 | COYOTE WIND U1 | 17INR0027b | COYOTE_W_UNIT1 | SCURRY | WIND-O | WEST | 2020 | 90
755 | COYOTE WIND U2 | 17INR0027b | COYOTE_W_UNIT2 | SCURRY | WIND-O | WEST | 2020 | 26.6
756 | COYOTE WIND U3 | 17INR0027b | COYOTE_W_UNIT3 | SCURRY | WIND-O | WEST | 2020 | 126
757 | FOXTROT WIND U1 | 20INR0129 | FOXTROT_UNIT1 | KARNES | WIND-O | SOUTH | 2022 | 130.2
758 | FOXTROT WIND U2 | 20INR0129 | FOXTROT_UNIT2 | KARNES | WIND-O | SOUTH | 2022 | 84
759 | FOXTROT WIND U3 | 20INR0129 | FOXTROT_UNIT3 | KARNES | WIND-O | SOUTH | 2022 | 54
760 | HARALD (BEARKAT WIND B) | 15INR0064b | HARALD_UNIT1 | GLASSCOCK | WIND-O | WEST | 2021 | 162.1
761 | LAS MAJADAS WIND U1 | 17INR0035 | LMAJADAS_UNIT1 | WILLACY | WIND-C | COASTAL | 2020 | 110
762 | LAS MAJADAS WIND U2 | 17INR0035 | LMAJADAS_UNIT2 | WILLACY | WIND-C | COASTAL | 2020 | 24
763 | LAS MAJADAS WIND U3 | 17INR0035 | LMAJADAS_UNIT3 | WILLACY | WIND-C | COASTAL | 2020 | 138.6
764 | EL ALGODON ALTO W U1 | 15INR0034 | ALGODON_UNIT1 | WILLACY | WIND-C | COASTAL | 2022 | 171.6
765 | EL ALGODON ALTO W U2 | 15INR0034 | ALGODON_UNIT2 | WILLACY | WIND-C | COASTAL | 2022 | 28.6
766 | MARYNEAL WINDPOWER | 18INR0031 | MARYNEAL_UNIT1 | NOLAN | WIND-O | WEST | 2020 | 182.4
767 | MAVERICK CREEK WIND WEST U1 | 20INR0045 | MAVCRK_W_UNIT1 | CONCHO | WIND-O | WEST | 2020 | 201.6
768 | MAVERICK CREEK WIND WEST U2 | 20INR0045 | MAVCRK_W_UNIT2 | CONCHO | WIND-O | WEST | 2020 | 11.1
769 | MAVERICK CREEK WIND WEST U3 | 20INR0045 | MAVCRK_W_UNIT3 | CONCHO | WIND-O | WEST | 2020 | 33.6
770 | MAVERICK CREEK WIND WEST U4 | 20INR0045 | MAVCRK_W_UNIT4 | CONCHO | WIND-O | WEST | 2020 | 22.2
771 | MAVERICK CREEK WIND EAST U1 | 20INR0046 | MAVCRK_E_UNIT5 | CONCHO | WIND-O | WEST | 2020 | 71.4
772 | MAVERICK CREEK WIND EAST U2 | 20INR0046 | MAVCRK_E_UNIT6 | CONCHO | WIND-O | WEST | 2020 | 33.3
773 | MAVERICK CREEK WIND EAST U3 | 20INR0046 | MAVCRK_E_UNIT7 | CONCHO | WIND-O | WEST | 2020 | 22
774 | MAVERICK CREEK WIND EAST U4 | 20INR0046 | MAVCRK_E_UNIT8 | CONCHO | WIND-O | WEST | 2020 | 20
775 | MAVERICK CREEK WIND EAST U5 | 20INR0046 | MAVCRK_E_UNIT9 | CONCHO | WIND-O | WEST | 2021 | 76.8
776 | MESTENO WIND | 16INR0081 | MESTENO_UNIT_1 | STARR | WIND-O | SOUTH | 2021 | 201.6
777 | PRAIRIE HILL WIND U1 | 19INR0100 | PHILLWND_UNIT1 | LIMESTONE | WIND-O | NORTH | 2020 | 153
778 | PRAIRIE HILL WIND U2 | 19INR0100 | PHILLWND_UNIT2 | LIMESTONE | WIND-O | NORTH | 2020 | 147
779 | PRIDDY WIND U1 | 16INR0085 | PRIDDY_UNIT1 | MILLS | WIND-O | NORTH | 2021 | 187.2
780 | PRIDDY WIND U2 | 16INR0085 | PRIDDY_UNIT2 | MILLS | WIND-O | NORTH | 2021 | 115.2
781 | RELOJ DEL SOL WIND U1 | 17INR0025 | RELOJ_UNIT1 | ZAPATA | WIND-O | SOUTH | 2020 | 55.4
782 | RELOJ DEL SOL WIND U2 | 17INR0025 | RELOJ_UNIT2 | ZAPATA | WIND-O | SOUTH | 2020 | 48
783 | RELOJ DEL SOL WIND U3 | 17INR0025 | RELOJ_UNIT3 | ZAPATA | WIND-O | SOUTH | 2020 | 83.1
784 | RELOJ DEL SOL WIND U4 | 17INR0025 | RELOJ_UNIT4 | ZAPATA | WIND-O | SOUTH | 2020 | 22.8
785 | SAGE DRAW WIND U1 | 19INR0163 | SAGEDRAW_UNIT1 | LYNN | WIND-O | WEST | 2019 | 169.2
786 | SAGE DRAW WIND U2 | 19INR0163 | SAGEDRAW_UNIT2 | LYNN | WIND-O | WEST | 2019 | 169.2
787 | TG EAST WIND U1 | 19INR0052 | TRUSGILL_UNIT1 | KNOX | WIND-O | WEST | 2021 | 42
788 | TG EAST WIND U2 | 19INR0052 | TRUSGILL_UNIT2 | KNOX | WIND-O | WEST | 2021 | 44.8
789 | TG EAST WIND U3 | 19INR0052 | TRUSGILL_UNIT3 | KNOX | WIND-O | WEST | 2021 | 42
790 | TG EAST WIND U4 | 19INR0052 | TRUSGILL_UNIT4 | KNOX | WIND-O | WEST | 2021 | 207.2
791 | VORTEX WIND U1 | 20INR0120 | VORTEX_WIND1 | THROCKMORTON | WIND-O | WEST | 2022 | 153.6
792 | VORTEX WIND U2 | 20INR0120 | VORTEX_WIND2 | THROCKMORTON | WIND-O | WEST | 2022 | 24.2
793 | VORTEX WIND U3 | 20INR0120 | VORTEX_WIND3 | THROCKMORTON | WIND-O | WEST | 2022 | 158.4
794 | VORTEX WIND U4 | 20INR0120 | VORTEX_WIND4 | THROCKMORTON | WIND-O | WEST | 2022 | 14
795 | WHITE MESA WIND U1 | 19INR0128 | WHMESA_UNIT1 | CROCKETT | WIND-O | WEST | 2021 | 152.3
796 | WHITE MESA 2 WIND | 21INR0521 | WHMESA_UNIT2_23 | COKE | WIND-O | WEST | 2021 | 13.9
797 | WHITE MESA 2 WIND U2 | 21INR0521 | WHMESA_UNIT2_28 | CROCKETT | WIND-O | WEST | 2021 | 183.3
798 | WHITE MESA 2 WIND U3 | 21INR0521 | WHMESA_UNIT3_23 | CROCKETT | WIND-O | WEST | 2021 | 18.6
799 | WHITE MESA 2 WIND U4 | 21INR0521 | WHMESA_UNIT3_28 | CROCKETT | WIND-O | WEST | 2021 | 132.5
800 | WHITEHORSE WIND U1 | 19INR0080 | WH_WIND_UNIT1 | FISHER | WIND-O | WEST | 2019 | 209.4
801 | WHITEHORSE WIND U2 | 19INR0080 | WH_WIND_UNIT2 | FISHER | WIND-O | WEST | 2019 | 209.5
802 | WILDWIND | 20INR0033 | WILDWIND_UNIT1 | COOKE | WIND-O | NORTH | 2020 | 18.4
803 | WILDWIND U2 | 20INR0033 | WILDWIND_UNIT2 | COOKE | WIND-O | NORTH | 2020 | 48
804 | WILDWIND U3 | 20INR0033 | WILDWIND_UNIT3 | COOKE | WIND-O | NORTH | 2020 | 6.3
805 | WILDWIND U4 | 20INR0033 | WILDWIND_UNIT4 | COOKE | WIND-O | NORTH | 2020 | 54.6
806 | WILDWIND U5 | 20INR0033 | WILDWIND_UNIT5 | COOKE | WIND-O | NORTH | 2020 | 52.8
807 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Wind) | [6 empty] | 6606.9
808
809 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Coastal Counties) |  | WIND_SYNCHRONIZED_C |  |  |  |  | 472.8
810 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_SYNC_PEAK_PCT_C | % |  |  |  | 64
811
812 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Panhandle Counties) |  | WIND_SYNCHRONIZED_P |  |  |  |  | 0
813 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_SYNC_PEAK_PCT_P | % |  |  |  | 38
814
815 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Other Counties) |  | WIND_SYNCHRONIZED_O |  |  |  |  | 6134.1
816 | Wind Peak Average Capacity Percentage (Other) |  | WIND_SYNC_PEAK_PCT_O | % |  |  |  | 36
817
818 | Operational Resources (Solar)
819 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
820 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10
821 | ANSON SOLAR U1 |  | ANSON1_UNIT1 | JONES | SOLAR | WEST | 2022 | 100
822 | ANSON SOLAR U2 |  | ANSON1_UNIT2 | JONES | SOLAR | WEST | 2022 | 100
823 | ARAGORN SOLAR |  | ARAGORN_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 185
824 | AZURE SKY SOLAR U1 |  | AZURE_SOLAR1 | HASKELL | SOLAR | WEST | 2021 | 74.9
825 | AZURE SKY SOLAR U2 |  | AZURE_SOLAR2 | HASKELL | SOLAR | WEST | 2021 | 153.5
826 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1
827 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 49.1
828 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
829 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
830 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30
831 | BLUEBELL SOLAR II 1 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV1 | STERLING | SOLAR | WEST | 2021 | 100
832 | BLUEBELL SOLAR II 2 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV2 | STERLING | SOLAR | WEST | 2021 | 15
833 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6
834 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50
835 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5
836 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5
837 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5
838 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5
839 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5
840 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5
841 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180
842 | CATAN SOLAR |  | DG_CS10_CATAN | KARNES | SOLAR | SOUTH | 2020 | 10
843 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10
844 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5
845 | CONIGLIO SOLAR |  | CONIGLIO_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 125.7
846 | CORAZON SOLAR PHASE I |  | CORAZON_UNIT1 | WEBB | SOLAR | SOUTH | 2021 | 202.6
847 | EAST BLACKLAND SOLAR (PFLUGERVILLE SOLAR) |  | E_BLACK_UNIT_1 | TRAVIS | SOLAR | SOUTH | 2021 | 144
848 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10
849 | EUNICE SOLAR U1 |  | EUNICE_PV1 | ANDREWS | SOLAR | WEST | 2021 | 189.6
850 | EUNICE SOLAR U2 |  | EUNICE_PV2 | ANDREWS | SOLAR | WEST | 2021 | 237.1
851 | FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6
852 | FOWLER RANCH |  | FWLR_SLR_UNIT1 | CRANE | SOLAR | WEST | 2020 | 150
853 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22
854 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 121.1
855 | GALLOWAY 1 SOLAR |  | GALLOWAY_SOLAR1 | CONCHO | SOLAR | WEST | 2021 | 250
856 | GREASEWOOD SOLAR 1 |  | GREASWOD_UNIT1 | PECOS | SOLAR | WEST | 2021 | 124.6
857 | GREASEWOOD SOLAR 2 |  | GREASWOD_UNIT2 | PECOS | SOLAR | WEST | 2021 | 130.4
858 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLENNAN | SOLAR | NORTH | 2019 | 5
859 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3
860 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6
861 | HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | NOLAN | SOLAR | WEST | 2020 | 102.2
862 | HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | NOLAN | SOLAR | WEST | 2020 | 102.3
863 | IMPACT SOLAR |  | IMPACT_UNIT1 | LAMAR | SOLAR | NORTH | 2021 | 198.5
864 | JUNO SOLAR PHASE I |  | JUNO_UNIT1 | BORDEN | SOLAR | WEST | 2021 | 162.1
865 | JUNO SOLAR PHASE II |  | JUNO_UNIT2 | BORDEN | SOLAR | WEST | 2021 | 143.5
866 | KELLAM SOLAR |  | KELAM_SL_UNIT1 | VAN ZANDT | SOLAR | NORTH | 2020 | 59.8
867 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | WEST | 2019 | 7.5
868 | LAPETUS SOLAR |  | LAPETUS_UNIT_1 | ANDREWS | SOLAR | WEST | 2020 | 100.7
869 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10
870 | LILY SOLAR |  | LILY_SOLAR1 | KAUFMAN | SOLAR | NORTH | 2021 | 147.6
871 | LONG DRAW SOLAR U1 |  | LGDRAW_S_UNIT1_1 | BORDEN | SOLAR | WEST | 2021 | 98.5
872 | LONG DRAW SOLAR U2 |  | LGDRAW_S_UNIT1_2 | BORDEN | SOLAR | WEST | 2021 | 128.3
873 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3
874 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10
875 | MISAE SOLAR U1 |  | MISAE_UNIT1 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 121.4
876 | MISAE SOLAR U2 |  | MISAE_UNIT2 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 118.6
877 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2
878 | OBERON SOLAR |  | OBERON_UNIT_1 | ECTOR | SOLAR | WEST | 2020 | 180
879 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
880 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
881 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
882 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
883 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 100
884 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2
885 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112
886 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.1
887 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 128.1
888 | PHOENIX SOLAR |  | PHOENIX_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 83.9
889 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6
890 | PROSPERO SOLAR 1 U1 |  | PROSPERO_UNIT1 | ANDREWS | SOLAR | WEST | 2020 | 153.6
891 | PROSPERO SOLAR 1 U2 |  | PROSPERO_UNIT2 | ANDREWS | SOLAR | WEST | 2020 | 150
892 | PROSPERO SOLAR 2 U1 |  | PRSPERO2_UNIT1 | ANDREWS | SOLAR | WEST | 2021 | 126.5
893 | PROSPERO SOLAR 2 U2 |  | PRSPERO2_UNIT2 | ANDREWS | SOLAR | WEST | 2021 | 126.4
894 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5
895 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5
896 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR3 | UPTON | SOLAR | WEST | 2020 | 97.5
897 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR4 | UPTON | SOLAR | WEST | 2020 | 107.5
898 | RAMBLER SOLAR |  | RAMBLER_UNIT1 | TOM GREEN | SOLAR | WEST | 2020 | 200
899 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8
900 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8
901 | REDBARN SOLAR 1 (RE MAPLEWOOD 2A SOLAR) |  | REDBARN_UNIT_1 | PECOS | SOLAR | WEST | 2021 | 222
902 | REDBARN SOLAR 2 (RE MAPLEWOOD 2B SOLAR) |  | REDBARN_UNIT_2 | PECOS | SOLAR | WEST | 2021 | 28
903 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2
904 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 150
905 | RIPPEY SOLAR |  | RIPPEY_UNIT1 | COOKE | SOLAR | NORTH | 2020 | 59.8
906 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50
907 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5
908 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10
909 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
910 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
911 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
912 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
913 | TAYGETE SOLAR 1 U1 |  | TAYGETE_UNIT1 | PECOS | SOLAR | WEST | 2021 | 125.9
914 | TAYGETE SOLAR 1 U2 |  | TAYGETE_UNIT2 | PECOS | SOLAR | WEST | 2021 | 128.9
915 | TITAN SOLAR (IP TITAN) U1 |  | TI_SOLAR_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 136.8
916 | TITAN SOLAR (IP TITAN) U2 |  | TI_SOLAR_UNIT2 | CULBERSON | SOLAR | WEST | 2021 | 131.1
917 | TPE ERATH SOLAR |  | DG_ERATH_ERATH21 | ERATH | SOLAR | NORTH | 2021 | 10
918 | WAGYU SOLAR |  | WGU_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2021 | 120
919 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10
920 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182
921 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
922 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5
923 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 100
924 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5
925 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5
926 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10
927 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10
928 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5
929 | Operational Capacity Total (Solar) | [6 empty] | 8445.9
930 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 61
931
932 | Operational Resources (Solar) - Synchronized but not Approved for Commercial Operations
933 | BLUE JAY SOLAR I | 21INR0538 | BLUEJAY_UNIT1 | GRIMES | SOLAR | NORTH | 2022 | 69
934 | BLUE JAY SOLAR II | 19INR0085 | BLUEJAY_UNIT2 | GRIMES | SOLAR | NORTH | 2022 | 141
935 | BRIGHTSIDE SOLAR | 18INR0060 | BRIGHTSD_UNIT1 | BEE | SOLAR | SOUTH | 2021 | 50
936 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U1 | 21INR0406 | BCK_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2022 | 217.5
937 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U2 | 21INR0406 | BCK_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2022 | 221.3
938 | ELARA SOLAR | 21INR0276 | ELARA_SL_UNIT1 | FRIO | SOLAR | SOUTH | 2021 | 132.4
939 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 | EGROVESL_UNIT1 | CRANE | SOLAR | WEST | 2022 | 108
940 | NOBLE SOLAR U1 | 20INR0214 | NOBLESLR_SOLAR1 | DENTON | SOLAR | NORTH | 2022 | 146.7
941 | NOBLE SOLAR U2 | 20INR0214 | NOBLESLR_SOLAR2 | DENTON | SOLAR | NORTH | 2022 | 128.3
942 | PLAINVIEW SOLAR (RAMSEY SOLAR) U1 | 20INR0130 | PLN_UNIT1 | WHARTON | SOLAR | SOUTH | 2021 | 257
943 | PLAINVIEW SOLAR (RAMSEY SOLAR) U2 | 20INR0130 | PLN_UNIT2 | WHARTON | SOLAR | SOUTH | 2021 | 257
944 | SAMSON SOLAR 1 U1 | 21INR0221 | SAMSON_1_G1 | LAMAR | SOLAR | NORTH | 2021 | 125
945 | SAMSON SOLAR 1 U2 | 21INR0221 | SAMSON_1_G2 | LAMAR | SOLAR | NORTH | 2021 | 125
946 | SAMSON SOLAR 3 U1 | 21INR0491 | SAMSON_3_G1 | LAMAR | SOLAR | NORTH | 2021 | 125
947 | SAMSON SOLAR 3 U2 | 21INR0491 | SAMSON_3_G2 | LAMAR | SOLAR | NORTH | 2021 | 125
948 | STRATEGIC SOLAR 1 | 20INR0081 | STRATEGC_UNIT1 | ELLIS | SOLAR | NORTH | 2021 | 135
949 | VISION SOLAR 1 | 20INR0082 | VISION_UNIT1 | NAVARRO | SOLAR | NORTH | 2021 | 127
950 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Wind) | [6 empty] | 2490.2
951 | Solar Peak Average Capacity Percentage |  | SOLAR_SYNC_PEAK_PCT | % |  |  |  | 61
952
953 | Operational Resources (Storage)
954 | BAT CAVE |  | BATCAVE_BES1 | MASON | STORAGE | SOUTH | 2021 | 100.5
955 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30
956 | BRP ALVIN (DGR) |  | BRPALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
957 | BRP ANGELTON (DGR) |  | BRPANGLE_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
958 | BRP BRAZORIA (DGR) |  | BRP_BRAZ_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
959 | BRP DICKINSON (DGR) |  | BRP_DIKN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2021 | 10
960 | BRP HEIGHTS (DGR) |  | BRHEIGHT_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10
961 | BRP LOOP 463 (DGR) |  | BRP_4631_UNIT1 | VICTORIA | STORAGE | SOUTH | 2021 | 9.9
962 | BRP LOPENO (DGR) |  | BRP_LOP1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.9
963 | BRP MAGNOLIA (DGR) |  | BRPMAGNO_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10
964 | BRP ODESSA SW (DGR) |  | BRPODESA_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 10
965 | BRP PUEBLO I (DGR) |  | BRP_PBL1_UNIT1 | MAVERICK | STORAGE | SOUTH | 2022 | 9.9
966 | BRP RANCHTOWN (DGR) |  | BRP_RNC1_UNIT1 | BEXAR | STORAGE | SOUTH | 2021 | 9.9
967 | BRP SWEENY (DGR) |  | BRP_SWNY_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
968 | BRP ZAPATA I (DGR) |  | BRP_ZPT1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 10
969 | BRP ZAPATA II (DGR) |  | BRP_ZPT2_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.9
970 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2018 | 9.9
971 | CHISHOLM GRID |  | CHISMGRD_BES1 | TARRANT | STORAGE | NORTH | 2021 | 100
972 | COMMERCE ST ESS (DGR) |  | X443ESS1_SWRI | BEXAR | STORAGE | SOUTH | 2020 | 10
973 | EUNICE STORAGE |  | EUNICE_BES1 | ANDREWS | STORAGE | WEST | 2021 | 40.3
974 | FLAT TOP BATTERY (DGR) |  | FLTBES_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9
975 | FLOWER VALLEY BATTERY (DGR) |  | FLVABES1_FLATU1 | REEVES | STORAGE | WEST | 2021 | 9.9
976 | GAMBIT BATTERY |  | GAMBIT_BESS1 | BRAZORIA | STORAGE | COASTAL | 2021 | 100
977 | HOEFSROAD BESS (DGR) |  | HRBESS_BESS | REEVES | STORAGE | WEST | 2020 | 2
978 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9
979 | JOHNSON CITY BESS (DGR) |  | JC_BAT_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 2.3
980 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5
981 | LILY STORAGE |  | LILY_BESS1 | KAUFMAN | STORAGE | NORTH | 2021 | 51.7
982 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5
983 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 33.7
984 | NORTH FORK |  | NF_BRP_BES1 | WILLIAMSON | STORAGE | SOUTH | 2021 | 100.5
985 | OCI ALAMO 1 |  | OCI_ALM1_ASTRO1 | BEXAR | STORAGE | SOUTH | 2016 | 1
986 | PORT LAVACA BATTERY (DGR) |  | PTLBES_BESS1 | CALHOUN | STORAGE | COASTAL | 2020 | 9.9
987 | PROSPECT STORAGE (DGR) |  | WCOLLDG_BSS_U1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.9
988 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9
989 | RABBIT HILL ENERGY STORAGE PROJECT (DGR) |  | RHESS2_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2020 | 9.9
990 | SNYDER (DGR) |  | SNY_BESS_UNIT1 | SCURRY | STORAGE | WEST | 2021 | 9.9
991 | SWEETWATER BESS (DGR) |  | SWT_BESS_UNIT1 | NOLAN | STORAGE | WEST | 2021 | 9.9
992 | SWOOSE BATTERY (DGR) |  | SWOOSE1_SWOOSEU1 | WARD | STORAGE | WEST | 2021 | 9.9
993 | TOS BATTERY STORAGE (DGR) |  | TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2
994 | TOYAH POWER STATION (DGR) |  | TOYAH_BESS | REEVES | STORAGE | WEST | 2021 | 9.9
995 | TRIPLE BUTTE (DGR) |  | TRIPBUT1_BELU1 | PECOS | STORAGE | WEST | 2021 | 7.5
996 | WESTOVER BESS (DGR) |  | WOV_BESS_UNIT1 | ECTOR | STORAGE | WEST | 2021 | 9.9
997 | WORSHAM BATTERY (DGR) |  | WRSBES_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9
998 | YOUNICOS FACILITY |  | DG_YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 2
999 | Operational Capacity Total (Storage) | [6 empty] | 864.6
1000 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 0
1001
1002 | Operational Resources (Storage) - Synchronized but not Approved for Commercial Operations
1003 | AZURE SKY BESS | 21INR0476 | AZURE_BESS1 | HASKELL | STORAGE | WEST | 2021 | 77.6
1004 | BRP PUEBLO II (DGR) |  | BRP_PBL2_UNIT1 | MAVERICK | STORAGE | SOUTH | 2020 | 10
1005 | CROSSETT POWER U1 | 21INR0510 | CROSSETT_BES1 | CRANE | STORAGE | WEST | 2021 | 100
1006 | CROSSETT POWER U2 | 21INR0510 | CROSSETT_BES2 | CRANE | STORAGE | WEST | 2021 | 100
1007 | DECORDOVA BESS U1 | 21INR0459 | DCSES_BES1 | HOOD | STORAGE | NORTH | 2022 | 66.5
1008 | DECORDOVA BESS U2 | 21INR0459 | DCSES_BES2 | HOOD | STORAGE | NORTH | 2022 | 66.5
1009 | DECORDOVA BESS U3 | 21INR0459 | DCSES_BES3 | HOOD | STORAGE | NORTH | 2022 | 63.5
1010 | DECORDOVA BESS U4 | 21INR0459 | DCSES_BES4 | HOOD | STORAGE | NORTH | 2022 | 63.5
1011 | FLOWER VALLEY II BATT | 21INR0496 | FLOWERII_BESS1 | REEVES | STORAGE | WEST | 2021 | 100
1012 | REPUBLIC ROAD STORAGE | 21INR0460 | RPUBRDS_ESS1 | ROBERTSON | STORAGE | NORTH | 2021 | 50
1013 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Storage) | [6 empty] | 697.6
1014 | Storage Peak Average Capacity Percentage |  | STORAGE_SYNC_PEAK_PCT | % |  |  |  | 0
1015
1016 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  |  |  |  | 0
1017
1018 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0
1019
1020 | Non-Synchronous Tie Resources
1021 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600
1022 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220
1023 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100
1024 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300
1025 | Non-Synchronous Ties Total | [6 empty] | 1220
1026 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 59
1027
1028 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
1029 | AIR PRODUCTS GCA | 21INR0012 |  | GALVESTON | GAS-ST | HOUSTON | 2023 | 0
1030 | RABBS POWER STATION | 20INR0221 |  | FORT BEND | GAS-GT | HOUSTON | 2022 | 360.8
1031 | CHAMON 2 | 19INR0056 |  | HARRIS | GAS-GT | HOUSTON | 2022 | 0
1032 | COLORADO BEND I EXPANSION | 21INR0512 |  | WHARTON | GAS-GT | SOUTH | 2022 | 0
1033 | BEACHWOOD POWER STATION (MARK ONE) | 22INR0369 |  | BRAZORIA | GAS-GT | COASTAL | 2022 | 0
1034 | MIRAGE CTG 1 | 17INR0022 |  | HARRIS | GAS-GT | HOUSTON | 2023 | 0
1035 | Planned Thermal Resources Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 360.8
1036
1037 | Planned Wind Resources with Executed SGIA
1038 | ANCHOR WIND III | 21INR0546 |  | EASTLAND | WIND-O | NORTH | 2022 | 16
1039 | ANCHOR WIND IV | 22INR0562 |  | EASTLAND | WIND-O | NORTH | 2022 | 0
1040 | APPALOOSA RUN WIND_ | 20INR0249 |  | UPTON | WIND-O | WEST | 2023 | 0
1041 | BOARD CREEK WP | 21INR0324 |  | NAVARRO | WIND-O | NORTH | 2022 | 0
1042 | CANYON WIND | 18INR0030 |  | SCURRY | WIND-O | WEST | 2022 | 0
1043 | CAROL WIND | 20INR0217 |  | POTTER | WIND-P | PANHANDLE | 2024 | 0
1044 | CRAWFISH | 19INR0177 |  | WHARTON | WIND-O | SOUTH | 2022 | 0
1045 | LACY CREEK WIND | 18INR0043 |  | GLASSCOCK | WIND-O | WEST | 2022 | 0
1046 | EL SUAZ RANCH | 20INR0097 |  | WILLACY | WIND-C | COASTAL | 2022 | 0
1047 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND-P | PANHANDLE | 2023 | 0
1048 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2023 | 0
1049 | HUTT WIND | 21INR0005 |  | MIDLAND | WIND-O | WEST | 2023 | 0
1050 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2023 | 0
1051 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2023 | 0
1052 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2022 | 0
1053 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND-O | WEST | 2023 | 0
1054 | MONARCH CREEK WIND | 21INR0263 |  | THROCKMORTON | WIND-O | WEST | 2023 | 0
1055 | MONTE ALTO I | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2023 | 0
1056 | SHEEP CREEK WIND | 21INR0325 |  | CALLAHAN | WIND-O | WEST | 2023 | 0
1057 | Planned Capacity Total (Wind) | [6 empty] | 16
1058
1059 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 0
1060 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 64
1061
1062 | Planned Wind Capacity Sub-total (Panhandle Counties) |  | WIND_PLANNED_P |  |  |  |  | 0
1063 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PL_PEAK_PCT_P | % |  |  |  | 38
1064
1065 | Planned Wind Capacity Sub-total (Other counties) |  | WIND_PLANNED_O |  |  |  |  | 16
1066 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PL_PEAK_PCT_O | % |  |  |  | 36
1067
1068 | Planned Solar Resources with Executed SGIA
1069 | 7V SOLAR | 21INR0351 |  | FAYETTE | SOLAR | SOUTH | 2023 | 0
1070 | ANDROMEDA SOLAR | 22INR0412 |  | SCURRY | SOLAR | WEST | 2023 | 0
1071 | ANGELO SOLAR | 19INR0203 |  | TOM GREEN | SOLAR | WEST | 2023 | 0
1072 | ARMADILLO SOLAR | 21INR0421 |  | NAVARRO | SOLAR | NORTH | 2023 | 0
1073 | ARROYO SOLAR | 20INR0086 |  | CAMERON | SOLAR | COASTAL | 2022 | 0
1074 | BIG STAR SOLAR | 21INR0413 |  | BASTROP | SOLAR | SOUTH | 2022 | 0
1075 | BLUE SKY SOL | 22INR0455 |  | CROCKETT | SOLAR | WEST | 2023 | 0
1076 | BPL FILES SOLAR | 20INR0164 |  | HILL | SOLAR | NORTH | 2022 | 0
1077 | BRASS FORK SOLAR | 22INR0270 |  | HASKELL | SOLAR | WEST | 2023 | 0
1078 | BRIGHT ARROW SOLAR | 22INR0242 |  | HOPKINS | SOLAR | NORTH | 2022 | 0
1079 | CACHENA SOLAR | 23INR0027 |  | WILSON | SOLAR | SOUTH | 2023 | 0
1080 | CAROL SOLAR | 21INR0274 |  | POTTER | SOLAR | PANHANDLE | 2024 | 0
1081 | CASTRO SOLAR | 20INR0050 |  | CASTRO | SOLAR | PANHANDLE | 2023 | 0
1082 | CHARGER SOLAR | 23INR0047 |  | REFUGIO | SOLAR | COASTAL | 2023 | 0
1083 | CHILLINGHAM SOLAR | 23INR0070 |  | BELL | SOLAR | NORTH | 2023 | 0
1084 | CONCHO VALLEY SOLAR | 21INR0384 |  | TOM GREEN | SOLAR | WEST | 2022 | 0
1085 | CORAL SOLAR | 22INR0295 |  | FALLS | SOLAR | NORTH | 2023 | 0
1086 | CORAZON SOLAR PHASE II | 22INR0257 |  | WEBB | SOLAR | SOUTH | 2025 | 0
1087 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2023 | 0
1088 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2023 | 0
1089 | DANCIGER SOLAR | 20INR0098 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
1090 | DANISH FIELDS SOLAR I | 20INR0069 |  | WHARTON | SOLAR | SOUTH | 2023 | 0
1091 | DANISH FIELDS SOLAR II | 21INR0016 |  | WHARTON | SOLAR | SOUTH | 2023 | 0
1092 | DANISH FIELDS SOLAR III | 21INR0017 |  | WHARTON | SOLAR | SOUTH | 2023 | 0
1093 | DAWN SOLAR | 20INR0255 |  | DEAF SMITH | SOLAR | PANHANDLE | 2023 | 0
1094 | DELILAH SOLAR 1 | 22INR0202 |  | LAMAR | SOLAR | NORTH | 2022 | 0
1095 | DELILAH SOLAR 2 | 22INR0203 |  | LAMAR | SOLAR | NORTH | 2023 | 0
1096 | DELILAH SOLAR 3 | 23INR0042 |  | LAMAR | SOLAR | NORTH | 2023 | 0
1097 | DELILAH SOLAR 4 | 23INR0060 |  | LAMAR | SOLAR | NORTH | 2023 | 0
1098 | DILEO SOLAR | 22INR0359 |  | BOSQUE | SOLAR | NORTH | 2023 | 0
1099 | DR SOLAR | 22INR0454 |  | CULBERSON | SOLAR | WEST | 2023 | 0
1100 | EIFFEL SOLAR | 22INR0223 |  | LAMAR | SOLAR | NORTH | 2023 | 0
1101 | ELLIS SOLAR | 21INR0493 |  | ELLIS | SOLAR | NORTH | 2022 | 0
1102 | EQUINOX SOLAR 1 | 21INR0226 |  | STARR | SOLAR | SOUTH | 2025 | 0
1103 | ESTONIAN SOLAR FARM | 22INR0335 |  | DELTA | SOLAR | NORTH | 2023 | 0
1104 | FAGUS SOLAR PARK (MISAE SOLAR II) | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2023 | 0
1105 | FENCE POST SOLAR | 22INR0404 |  | NAVARRO | SOLAR | NORTH | 2022 | 0
1106 | FIGHTING JAYS SOLAR | 21INR0278 |  | FORT BEND | SOLAR | HOUSTON | 2022 | 0
1107 | FORT BEND SOLAR | 18INR0053 |  | FORT BEND | SOLAR | HOUSTON | 2022 | 0
1108 | FRYE SOLAR | 20INR0080 |  | SWISHER | SOLAR | PANHANDLE | 2023 | 0
1109 | GALLOWAY 2 SOLAR | 21INR0431 |  | CONCHO | SOLAR | WEST | 2023 | 0
1110 | GOLINDA SOLAR | 21INR0434 |  | FALLS | SOLAR | NORTH | 2023 | 0
1111 | GP SOLAR | 23INR0045 |  | VAN ZANDT | SOLAR | NORTH | 2023 | 0
1112 | GRANDSLAM SOLAR | 21INR0391 |  | ATASCOSA | SOLAR | SOUTH | 2023 | 0
1113 | GREEN HOLLY SOLAR | 21INR0021 |  | DAWSON | SOLAR | WEST | 2023 | 0
1114 | GREYHOUND SOLAR | 21INR0268 |  | ECTOR | SOLAR | WEST | 2023 | 0
1115 | GRIZZLY RIDGE SOLAR | 21INR0375 |  | HAMILTON | SOLAR | NORTH | 2022 | 0
1116 | G-STAR SOLAR | 23INR0111 |  | WHARTON | SOLAR | SOUTH | 2023 | 0
1117 | HAYHURST TEXAS SOLAR | 22INR0363 |  | CULBERSON | SOLAR | WEST | 2023 | 0
1118 | HOPKINS SOLAR | 20INR0210 |  | HOPKINS | SOLAR | NORTH | 2022 | 0
1119 | HORIZON SOLAR | 21INR0261 |  | FRIO | SOLAR | SOUTH | 2023 | 0
1120 | HORNET SOLAR | 23INR0021 |  | SWISHER | SOLAR | PANHANDLE | 2023 | 0
1121 | INDIGO SOLAR | 21INR0031 |  | FISHER | SOLAR | WEST | 2023 | 0
1122 | JACKALOPE SOLAR | 23INR0180 |  | SAN PATRICIO | SOLAR | COASTAL | 2023 | 0
1123 | JADE SOLAR | 22INR0360 |  | SCURRY | SOLAR | WEST | 2023 | 0
1124 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2023 | 0
1125 | LONGBOW SOLAR | 20INR0026 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
1126 | LUNIS CREEK SOLAR 1 | 21INR0344 |  | JACKSON | SOLAR | SOUTH | 2023 | 0
1127 | MALEZA SOLAR | 21INR0220 |  | WHARTON | SOLAR | SOUTH | 2023 | 0
1128 | MARKUM SOLAR | 20INR0230 |  | MCLENNAN | SOLAR | NORTH | 2024 | 0
1129 | MERCURY II SOLAR | 23INR0153 |  | HILL | SOLAR | NORTH | 2022 | 0
1130 | MERCURY SOLAR | 21INR0257 |  | HILL | SOLAR | NORTH | 2022 | 0
1131 | MORROW LAKE SOLAR | 19INR0155 |  | FRIO | SOLAR | SOUTH | 2023 | 0
1132 | MUSTANG CREEK SOLAR | 18INR0050 |  | JACKSON | SOLAR | SOUTH | 2022 | 0
1133 | MYRTLE SOLAR | 19INR0041 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
1134 | NABATOTO SOLAR NORTH | 21INR0428 |  | LEON | SOLAR | NORTH | 2023 | 0
1135 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2023 | 0
1136 | NEBULA SOLAR (RAYOS DEL SOL) | 19INR0045 |  | CAMERON | SOLAR | COASTAL | 2022 | 0
1137 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2023 | 0
1138 | OUTPOST SOLAR | 23INR0007 |  | WEBB | SOLAR | SOUTH | 2023 | 0
1139 | OYSTERCATCHER SOLAR | 21INR0362 |  | ELLIS | SOLAR | NORTH | 2024 | 0
1140 | PEREGRINE SOLAR | 22INR0283 |  | GOLIAD | SOLAR | SOUTH | 2023 | 0
1141 | PINE FOREST SOLAR | 20INR0203 |  | HOPKINS | SOLAR | NORTH | 2024 | 0
1142 | PISGAH RIDGE SOLAR | 22INR0254 |  | NAVARRO | SOLAR | NORTH | 2022 | 0
1143 | PITTS DUDIK SOLAR | 20INR0074 |  | HILL | SOLAR | NORTH | 2022 | 0
1144 | PORTER SOLAR | 21INR0458 |  | DENTON | SOLAR | NORTH | 2023 | 0
1145 | RADIAN SOLAR | 21INR0205 |  | BROWN | SOLAR | NORTH | 2022 | 0
1146 | RED HOLLY SOLAR | 21INR0022 |  | DAWSON | SOLAR | WEST | 2023 | 0
1147 | REDONDA SOLAR | 23INR0162 |  | ZAPATA | SOLAR | SOUTH | 2023 | 0
1148 | RED-TAILED HAWK SOLAR | 21INR0389 |  | WHARTON | SOLAR | SOUTH | 2023 | 0
1149 | ROSELAND SOLAR | 20INR0205 |  | FALLS | SOLAR | NORTH | 2022 | 0
1150 | ROSELAND SOLAR II | 22INR0506 |  | FALLS | SOLAR | NORTH | 2022 | 0
1151 | ROWLAND SOLAR I | 19INR0131 |  | FORT BEND | SOLAR | HOUSTON | 2022 | 0
1152 | ROWLAND SOLAR II | 22INR0482 |  | FORT BEND | SOLAR | HOUSTON | 2023 | 0
1153 | SAMSON SOLAR 2 | 21INR0490 |  | LAMAR | SOLAR | NORTH | 2023 | 0
1154 | SBRANCH SOLAR PROJECT | 22INR0205 |  | WHARTON | SOLAR | SOUTH | 2022 | 0
1155 | SCHOOLHOUSE SOLAR | 22INR0211 |  | LEE | SOLAR | SOUTH | 2023 | 0
1156 | SECOND DIVISION SOLAR | 20INR0248 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
1157 | MCLEAN (SHAKES) SOLAR | 19INR0073 |  | ZAVALA | SOLAR | SOUTH | 2022 | 0
1158 | SIGNAL SOLAR | 20INR0208 |  | HUNT | SOLAR | NORTH | 2023 | 0
1159 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2023 | 0
1160 | SPACE CITY SOLAR | 21INR0341 |  | WHARTON | SOLAR | SOUTH | 2022 | 0
1161 | SPANISH CROWN | 21INR0323 |  | FALLS | SOLAR | NORTH | 2023 | 0
1162 | SPARTA SOLAR | 22INR0352 |  | BEE | SOLAR | SOUTH | 2022 | 0
1163 | STAMPEDE SOLAR | 22INR0409 |  | HOPKINS | SOLAR | NORTH | 2022 | 0
1164 | STARLING SOLAR | 23INR0035 |  | GONZALES | SOLAR | SOUTH | 2023 | 0
1165 | STARR SOLAR RANCH | 20INR0216 |  | STARR | SOLAR | SOUTH | 2023 | 0
1166 | SUN VALLEY | 19INR0169 |  | HILL | SOLAR | NORTH | 2022 | 0
1167 | SUNRAY | 21INR0395 |  | UVALDE | SOLAR | SOUTH | 2023 | 0
1168 | TAYGETE II SOLAR | 21INR0233 |  | PECOS | SOLAR | WEST | 2022 | 0
1169 | TEXANA SOLAR | 18INR0058 |  | WHARTON | SOLAR | SOUTH | 2022 | 0
1170 | TEXAS SOLAR NOVA | 19INR0001 |  | KENT | SOLAR | WEST | 2023 | 0
1171 | TRES BAHIAS SOLAR | 20INR0266 |  | CALHOUN | SOLAR | COASTAL | 2022 | 0
1172 | TYSON NICK SOLAR | 20INR0222 |  | LAMAR | SOLAR | NORTH | 2023 | 0
1173 | VANCOURT SOLAR | 21INR0213 |  | CAMERON | SOLAR | COASTAL | 2022 | 0
1174 | WESTORIA SOLAR | 20INR0101 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
1175 | ZIER SOLAR | 21INR0019 |  | KINNEY | SOLAR | SOUTH | 2023 | 0
1176 | Planned Capacity Total (Solar) | [6 empty] | 0
1177 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 61
1178
1179 | Planned Storage Resources with Executed SGIA
1180 | ANCHOR BESS | 21INR0474 |  | EASTLAND | STORAGE | NORTH | 2022 | 0
1181 | ANEMOI ENERGY STORAGE | 23INR0369 |  | HIDALGO | STORAGE | SOUTH | 2023 | 0
1182 | BIG STAR STORAGE | 21INR0469 |  | BASTROP | STORAGE | SOUTH | 2022 | 0
1183 | BLUE JAY BESS | 23INR0019 |  | GRIMES | STORAGE | NORTH | 2022 | 0
1184 | BRP ANTLIA BESS | 22INR0349 |  | VAL VERDE | STORAGE | WEST | 2023 | 0
1185 | BRP CACHI BESS | 22INR0388 |  | GUADALUPE | STORAGE | SOUTH | 2022 | 0
1186 | BRP CARINA BESS | 22INR0353 |  | NUECES | STORAGE | COASTAL | 2023 | 0
1187 | BRP DICKENS BESS | 22INR0325 |  | DICKENS | STORAGE | PANHANDLE | 2022 | 0
1188 | BRP HYDRA BESS | 22INR0372 |  | PECOS | STORAGE | WEST | 2022 | 0
1189 | BRP PALEO BESS | 22INR0322 |  | HALE | STORAGE | PANHANDLE | 2022 | 0
1190 | BRP PAVO BESS | 22INR0384 |  | PECOS | STORAGE | WEST | 2022 | 0
1191 | BRP TORTOLAS BESS | 23INR0072 |  | BRAZORIA | STORAGE | COASTAL | 2022 | 0
1192 | BYRD RANCH STORAGE | 21INR0281 |  | BRAZORIA | STORAGE | COASTAL | 2022 | 0
1193 | CHILLINGHAM STORAGE | 23INR0079 |  | BELL | STORAGE | NORTH | 2023 | 0
1194 | ENDURANCE PARK STORAGE | 21INR0479 |  | SCURRY | STORAGE | WEST | 2022 | 0
1195 | ESTONIAN ENERGY STORAGE | 22INR0336 |  | DELTA | STORAGE | NORTH | 2023 | 0
1196 | EVAL STORAGE | 22INR0401 |  | CAMERON | STORAGE | COASTAL | 2023 | 0
1197 | FAULKNER BESS (DGR) | 22INR0571 |  | REEVES | STORAGE | WEST | 2022 | 0
1198 | FENCE POST BESS | 22INR0405 |  | NAVARRO | STORAGE | NORTH | 2022 | 0
1199 | GIGA TEXAS ENERGY STORAGE | 23INR0239 |  | TRAVIS | STORAGE | SOUTH | 2023 | 0
1200 | GREEN HOLLY STORAGE | 21INR0029 |  | DAWSON | STORAGE | WEST | 2023 | 0
1201 | GUAJILLO ENERGY STORAGE | 23INR0343 |  | WEBB | STORAGE | SOUTH | 2023 | 0
1202 | HIGH LONESOME BESS | 20INR0280 |  | CROCKETT | STORAGE | WEST | 2022 | 0
1203 | HOUSE MOUNTAIN 2 BATT | 22INR0485 |  | BREWSTER | STORAGE | WEST | 2023 | 0
1204 | IGNACIO GRID | 21INR0522 |  | HIDALGO | STORAGE | SOUTH | 2022 | 0
1205 | MADERO GRID | 21INR0244 |  | HIDALGO | STORAGE | SOUTH | 2022 | 0
1206 | MATTA POWER STATION (DGR) | 22INR0565 |  | REEVES | STORAGE | WEST | 2022 | 0
1207 | NOBLE STORAGE | 22INR0436 |  | DENTON | STORAGE | NORTH | 2022 | 0
1208 | PADUA GRID BESS | 22INR0368 |  | BEXAR | STORAGE | SOUTH | 2022 | 0
1209 | PYRON BESS II | 20INR0268 |  | NOLAN | STORAGE | WEST | 2022 | 0
1210 | QUEEN BESS | 20INR0281 |  | UPTON | STORAGE | WEST | 2022 | 0
1211 | RED HOLLY STORAGE | 21INR0033 |  | DAWSON | STORAGE | WEST | 2023 | 0
1212 | RIVER VALLEY STORAGE 1 | 20INR0290 |  | WILLIAMSON | STORAGE | SOUTH | 2022 | 0
1213 | RIVER VALLEY STORAGE 2 | 20INR0293 |  | WILLIAMSON | STORAGE | SOUTH | 2022 | 0
1214 | ROSELAND STORAGE | 22INR0280 |  | FALLS | STORAGE | NORTH | 2022 | 0
1215 | ROUGHNECK STORAGE | 19INR0176 |  | BRAZORIA | STORAGE | COASTAL | 2022 | 50
1216 | RYAN ENERGY STORAGE | 20INR0246 |  | CORYELL | STORAGE | NORTH | 2023 | 0
1217 | SADDLEBACK BESS (DGR) | 22INR0570 |  | REEVES | STORAGE | WEST | 2022 | 0
1218 | SILICON HILL STORAGE | 20INR0291 |  | TRAVIS | STORAGE | SOUTH | 2022 | 100
1219 | SP TX-12B BESS | 21INR0357 |  | UPTON | STORAGE | WEST | 2022 | 22.7
1220 | STAMPEDE BESS | 22INR0410 |  | HOPKINS | STORAGE | NORTH | 2022 | 0
1221 | SWOOSE II | 21INR0497 |  | WARD | STORAGE | WEST | 2022 | 100
1222 | TIMBERWOLF BESS 2 | 22INR0495 |  | UPTON | STORAGE | WEST | 2023 | 0
1223 | TURQUOISE STORAGE | 22INR0509 |  | HUNT | STORAGE | NORTH | 2022 | 0
1224 | VORTEX BESS | 21INR0473 |  | THROCKMORTON | STORAGE | WEST | 2022 | 0
1225 | WOLF TANK STORAGE | 22INR0551 |  | WEBB | STORAGE | SOUTH | 2022 | 0
1226 | SMALL GENERATORS WITH SIGNED IAs AND 'MODEL READY DATES' PENDING * |  |  |  | STORAGE |  | 2022 | 0
1227 | Planned Capacity Total (Storage) | [6 empty] | 272.7
1228 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 0
1229
1230 | Inactive Planned Resources
1231 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 60
1232 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2024 | 0
1233 | COTTONWOOD BAYOU | 19INR0134 |  | BRAZORIA | SOLAR | COASTAL | 2023 | 0
1234 | COTTONWOOD BAYOU SOLAR II | 21INR0228 |  | BRAZORIA | SOLAR | COASTAL | 2023 | 0
1235 | INERTIA BESS | 22INR0328 |  | HASKELL | STORAGE | WEST | 2022 | 0
1236 | INERTIA BESS 2 | 22INR0375 |  | HASKELL | STORAGE | WEST | 2022 | 0
1237 | INERTIA SOLAR | 22INR0374 |  | HASKELL | SOLAR | WEST | 2022 | 0
1238 | INERTIA WIND | 22INR0326 |  | HASKELL | WIND-O | WEST | 2022 | 0
1239 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 152.5
1240 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 150
1241 | OLD HICKORY SOLAR | 20INR0236 |  | JACKSON | SOLAR | SOUTH | 2023 | 0
1242 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND-P | PANHANDLE | 2022 | 0
1243 | ROADRUNNER CROSSING WIND 1 | 19INR0117 |  | EASTLAND | WIND-O | NORTH | 2022 | 0
1244 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2022 | 0
1245 | RUETER SOLAR | 20INR0202 |  | BOSQUE | SOLAR | NORTH | 2022 | 0
1246 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2024 | 0
1247 | Inactive Planned Capacity Total | [6 empty] | 362.5
1248
1249 | Seasonal Mothballed Resources
1250 | GREGORY POWER PARTNERS GT1 (AS OF 1/1/2022, AVAILABLE 1/1 THROUGH 9/30) |  | LGE_LGE_GT1 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 152
1251 | GREGORY POWER PARTNERS GT2 (AS OF 1/1/2022, AVAILABLE 1/1 THROUGH 9/30) |  | LGE_LGE_GT2 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 151
1252 | GREGORY POWER PARTNERS STG (AS OF 1/1/2022, AVAILABLE 1/1 THROUGH 9/30) |  | LGE_LGE_STG | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 75
1253 | Total Seasonal Mothballed Capacity | [6 empty] | 378
1254
1255 | Mothballed Resources
1256 | RAY OLINGER STG 1 (AS OF 4/5/22) |  | OLINGR_OLING_1 | COLLIN | GAS-ST | NORTH | 1967 | 78
1257 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 430
1258 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420
1259 | Total Mothballed Capacity | [6 empty] | 928
1260
1261 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
1262 | Total Retiring Capacity
Notes:
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of updated resource registration system information. Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational/planned capacity formulae. These resources are assumed to provide Ancillary Services rather than sustained capacity available to meet system peak loads.
Unit Names with a (DGR) suffix are Distribution Generation Resources.
The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation are assumed to be available for the season regardless of their projected Commercial Operations Dates.
Planned projects for which maximum seasonal sustained capacity ratings have been provided are used in lieu of capacities entered into the online Resource Integration and Ongoing Operations - Interconnection Services (RIOO-IS) system.
* ERCOT implemented a new Small Generator interconnection process for projects between one and 10 MW in size. Public disclosure of individual Resource details is only allowed when the Resource has been assigned a Model Ready Date (MRD), or ERCOT has been granted permission to make public the detailed data before MRD assignment. "Model Ready" means that the Resource data has been loaded into the ERCOT Network Operations Model, and the Resource is ready to begin the commissioning process. The aggregate capacity reported in this line item is for Small Generators that do not have a MRD yet.
Note on I382: SPENCER STG U4 (SPNCER_SPNCE_4), -57 MW, from 11/3/2021 to 6/1/2022
Note on I422: Extended outages: GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE (3.6 MW) and 2.4 MW of the 4.8 MW GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP Hydro unit.
Note on I1034: synchronization approval for MIRAGE CTG 1 - 17INR0022 was revoked on 12/9/21 due to an extended outage that is expected to last form 11/16/21 to 6/30/22

## Background
Release Date: March 17, 2022
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a probabilistic reliability standard.
For seasonal assessments that look ahead less than a year, specific information may be available (for example, an anticipated common-mode event such as a system-wide heat wave) which can be used to consider the range of resource adequacy outcomes in a more deterministic manner.
The SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. It uses operating reserve thresholds of 2,300 and 1,000 MW, respectively, to indicate the risk that an Energy Emergency Alert Level 1 (EEA1) and Level 3 (EEA3) may be triggered during the time of the forecasted seasonal peak load. These threshold levels are intended to be roughly analogous to the 2,300 and 1,000 MW Physical Responsive Capability (PRC) thresholds for EEA1 and EEA3 with controlled outages ordered by ERCOT, respectively. However, PRC is a real-time capability measure for Resources that can quickly respond to system disturbances. In contrast, the SARA operating reserve reflects additional capability assumed to be available before energy emergency procedures are initiated, such as from Resources qualified to provide non-spinning reserves. Additionally, the amount of operating reserves available may increase relative to what is included in the SARA report due to the market responding to wholesale market price increases and anticipated capacity scarcity conditions. Given these considerations, ERCOT believes that the 2,300 and 1,000 MW reserve capacity thresholds are reasonable indicators for the risk of Energy Emergency Alerts given the uncertainties in predicting system conditions months in advance.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. It serves as a situational awareness tool for ERCOT operational planning purposes, and helps fulfill the "extreme weather" resource adequacy assessment requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). In addition to a base scenario, several other scenarios are developed by varying the value of load forecast and resource availability parameters. The variations in these parameters are based on historic ranges of the parameter values, known changes expected in the near-term, or reasonable assumptions regarding potential future events.
Thermal Outage Accounting
Directly comparing SARA thermal unplanned (previously "forced") outage scenario capacity with outage amounts listed in ERCOT outage reports — such as the Unplanned Resource Outages Report — will yield misleading results. The reason is that the SARA report consists of multiple resource availability line items, and thermal outages for certain resource types are reflected elsewhere in the SARA reports rather than the thermal outage scenario line items. As a result, the SARA thermal outage scenario amounts will always be less than what is typically shown in other outage reports. The main differences include the following:
• Outages for Private Use Network (PUN) generators are incorporated in the line item called “Capacity from Private Use Networks.” This is an aggregate estimate of the amount of capacity available for the ERCOT grid during the highest 20 seasonal hourly demands for the last three years and incorporates average generator outage amounts over those hourly intervals. Additionally, the aggregate estimate reflects PUN owner decisions to supply power to their industrial loads versus export to the grid. PUN outages are thus already reflected in the SARA available resource capacity estimate. Note that the high and extreme Unplanned scenario assumptions do account for PUN generator outages because the associated adjustments are made directly to outage amounts rather than to the "Capacity from Private Use Networks" amount, thus avoiding capacity double-counting issues.
• Extended outages are reported in the SARA Capacities tab in a line item called “Operational Capacity Unavailable due to Extended Outage or Derate.” Extended Outages are those forced outages that are expected to last a minimum of 180 days as reported by the resource owner via submission of a Notice of Suspension of Operations (NSO) form. These outages are thus already reflected in the SARA available resource capacity estimate.
• The capacity of Switchable Generation Resources (SWGRs) that are assumed to serve a neighboring grid for the season is deducted from available resource capacity, so outages associated with these SWGRs are not reflected anywhere in the SARA report.
To more closely align the SARA with other outage reports based on ERCOT Outage Scheduler data, a modification was made to the treatment of outages classified as Unavoidable Extensions, or UEs. UEs are defined as "a Planned or Maintenance Outage that is not completed within the ERCOT-approved timeframe and extended." For past SARA reports, if the original outage was classified as Planned in the Outage Scheduler, then the UE would continue to be classified as Planned. If the original outage was classified as Forced, then the UE would continue to be classified as Forced. In contrast, for other ERCOT outage reports, UE outages are all classified as Forced (Unplanned). SARA reports now treat all UEs as Unplanned. While this category change does not impact the total base outage amount, it does increase the high and extreme unplanned thermal adjustments used in several risk scenarios.