## Slide 1
NPRR1100 Discussion of Operational Requirements for Transmission Connected Resources
Refer to OWG presentation Jan 22
https://www.ercot.com/files/docs/2022/01/21/OWG%20NPRR1100_discussion_updated_mp01202022_pdf.pdf
and Tesla NPRR1100 Workshop https://www.ercot.com/calendar/event?id=1634567146387
Operations Working Group
Mar 24, 2022

## Slide 2: Possible re-integration options
Open Transition (proposed)
  The application for Operations appears straightforward and involves minimal language changes to define the application and the outage instances which can be quickly implemented.
Closed Transition
  The application involves telemetry, system and display changes to resolve re-integration of an energized load with extended an extended implementation time, so if desired should be addressed in a subsequent NPRR.( refer to issues presented at Jan OWG- see appendix)

## Slide 3: Open transition– Proposed language
6.5.5.1 Changes in Resource Status
(1) Each QSE shall notify ERCOT of a change in Resource Status via telemetry and through changes in the Current Operating Plan (COP) as soon as practicable following the change.
(2) Each QSE shall promptly inform ERCOT when the operating mode of its Generation Resource’s Automatic Voltage Regulator (AVR) or Power System Stabilizer (PSS) is changed while the Resource is On-Line. The QSE shall also provide the Resource’s AVR or PSS status logs to ERCOT upon request.
(3) Each QSE shall immediately report to ERCOT and the TSP any inability of the QSE’s Generation Resource required to meet its reactive capability requirements in these Protocols.
(4) Nothing in these Protocols prohibits a QSE or Resource Entity from using a Generation Resource or Energy Storage Resource to serve customer Load in any circumstance in which the customer and the Resource are both involuntarily disconnected from the ERCOT System due to an Outage of the transmission or distribution system, provided that, for any customer Load greater than 1 MW, the Load must be de-energized at the time it is reconnected to the ERCOT System.

## Slide 4: Open transition– Proposed language (cont’d)
6.5.6 TSP and DSP Responsibilities
(1) Each TSP shall notify ERCOT of any changes in status of Transmission Elements as provided in these Protocols and clarified in the ERCOT procedures.
(2) Each TSP shall as soon as practicable report to ERCOT any short-term inability to meet minimum TSP reactive requirements.
(3) Each DSP shall as soon as practicable report to ERCOT any short-term inability to meet minimum DSP reactive requirements.
(4) A TDSP shall not intentionally disconnect, or direct another TDSP to disconnect, a Generation Resource or Energy Storage Resource from the ERCOT System except in the following circumstances:
an approved or accepted Planned or Maintenance Outage of a Transmission Facility reasonably requires, or would otherwise result in, the disconnection of the Resource from the ERCOT System,
the Resource is a Distribution Generation Resource or Distribution Energy Storage Resource, and disconnection of the Resource is required for distribution system maintenance,
the TDSP’s disconnection of the Resource is necessary to maintain the security of the TDSP’s system or the ERCOT System, or
ERCOT directs the disconnection of the Resource.

## Slide 5: Appendix – Slides Presented at 1/20/22 OWG Meeting

## Slide 6: Discussion of Operations Requirements for Transmission Connected Resources
Limited GR/ESR may serve the load BTM ONLY when transmission system is out. (Not directly related to an ERCOT emergency.)
Pre-approval of procedures, settings and expected behavior by TDSP/ERCOT/QSE/RE:
  Existing procedures only apply to generation, not picking up energized loads
    Relay settings including synchronization
    Switching procedures and timing
    Consider limiting to open transition switching instead. (Refer to Tesla's proposed sequencing presented at their workshop.)
  Modeling simulations validating that GR/ESR will not trip during transition to and from Microgrid Island mode.

## Slide 7: Discussion of Operations Requirements for Transmission Connected Resources (cont.)
Awareness of the island during an event
  Telemetry status of “Out” is not adequate – need an entirely new COPS status with a new Telemetry point to identify “Microgrid” operation for Loads and Generators for Operators.
  Operators will need visual changes to Ops model to highlight islands (new symbol or color).
  Limit GR/ESR Island support to single transmission POI, otherwise too many combinations.
Reconnecting with the transmission system after an event
  Restoration after outage proposes closed transition switching with duration less than 2 seconds.
    Full synchronization capability for Load must be demonstrated and approved in advance.
Reporting after the event
  TDSP and ERCOT required to provide full report on island > 100 MW within 24 hours of event.
    NERC EOP-004
    DOE OE-417