| NOGRR Number | 234 | NOGRR Title | Related to NPRR1098, Direct Current Tie (DC Tie) Reactive Power Capability Requirements |
| --- | --- | --- | --- |
| Date of Decision |  | March 31, 2022 |  |
| Action |  | Approved |  |
| Timeline |  | Normal |  |
| Effective Date |  | Upon implementation of Nodal Protocol Revision Request (NPRR) 1098, Direct Current Tie (DC Tie) Reactive Power Capability Requirements |  |
| Priority and Rank Assigned |  | Not Applicable |  |
| Nodal Operating Guide Sections Requiring Revision |  | 2.7.2, Maintaining Voltage Profile 2.7.3.3, TO/TSP Responsibilities 2.7.3.6, DCTO Responsibilities and DC Tie Requirements (new) |  |
| Related Documents Requiring Revision/Related Revision Requests |  | NPRR1098 |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) revises the Nodal Operating Guide to be consistent with the Reactive Power capability requirements for Direct Current Ties (DC Ties) proposed by NPRR1098. A new Section 2.7.3.6 is proposed to specify Direct Current Tie Operator (DCTO) responsibilities relative to Real-Time operational voltage control. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This NOGRR aligns the Nodal Operating Guide with the proposed revisions included in NPRR1098 and partially addresses Directive 8 from Public Utility Commission of Texas (PUCT) Project No. 46304, Oversight Proceeding Regarding ERCOT Matters Arising Out of PUC Docket No. 45624 Relating to DC Tie Project Proposed by Southern Cross Transmission, LLC. |  |
| ROS Decision |  | On 11/4/21, ROS voted unanimously via roll call to table NOGRR234 and refer the issue to the Operations Working Group (OWG). All Market Segments participated in the vote. On 12/2/21, ROS voted via roll call to recommend approval of NOGRR234 as amended by the 11/29/21 ERCOT comments. There was one abstention from the Cooperative (LCRA) Market Segment. All Market Segments participated in the vote. On 1/6/22, ROS voted unanimously via roll call to endorse and forward to TAC the 12/2/21 ROS Report and the Impact Analysis for NOGRR234. All Market Segments participated in the vote. |  |
| Summary of ROS Discussion |  | On 11/4/21, participants reviewed NOGRR234 and the 11/1/21 Oncor comments. ERCOT Staff requested time to assess the potential impacts of language proposed by Oncor; participants requested further discussion at OWG. On 12/2/21, ERCOT Staff reviewed the 11/29/21 ERCOT comments. On 1/6/22, participants reviewed the Impact Analysis. |  |
| TAC Decision |  | On 1/31/22, TAC voted unanimously via roll call to recommend approval of NOGRR234 as recommended by ROS in the 1/6/22 ROS Report. All Market Segments participated in the vote. |  |
| Summary of TAC Discussion |  | On 1/31/22, TAC reviewed the ERCOT Opinion and ERCOT Market Impact Statement for NOGRR234. |  |
| ERCOT Opinion |  | ERCOT supports approval of NOGRR234. |  |
| ERCOT Market Impact Statement |  | ERCOT Staff has reviewed NOGRR234 and believes the market impact for NOGRR234 is consistent with the TAC-approved proposal in response to Directive 8 of the May 23, 2017 order of the PUCT in Project No. 46304, which requires ERCOT to address a number of issues as a condition for the energization of the DC Tie project proposed by Southern Cross Transmission, LLC. |  |
| Board Decision |  | On 3/7/22, the ERCOT Board voted to recommend approval of NOGRR234 as recommended by TAC in the 1/31/22 TAC Report. |  |
| PUCT Decision |  | On 3/31/22, the PUCT approved NOGRR234 and accompanying ERCOT Market Impact Statement as presented in Project No. 52934, Review of Rules Adopted by the Independent Organization. |  |

| Sponsor |  |
| --- | --- |
| Name | John Bernecker |
| E-mail Address | John.Bernecker@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4274 |
| Cell Number |  |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Oncor 110121 | Proposed revisions to ensure requirements are appropriately split between facility owners and facility operators, similar to existing modeling requirements that apply to Resource Entities as facility owners |
| ERCOT 112921 | Proposed additional clarifying language on Real-Time communications and telemetry requirements related to control systems used to automatically control volage at the Point of Interconnection Bus (POIB) |

Market Rules Notes

Please note the baseline Nodal Operating Guide language in the following section(s) has been updated to reflect the incorporation of the following NOGRR(s) into the Nodal Operating Guide:

- NOGRR212, Related to NPRR1016, Clarify Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs) (unboxed 1/1/22)

  - Section 2.7.3.3

- NOGRR210, Related to NPRR1005, Clarify Definition of Point of Interconnection (POI) and Add Definition Point of Interconnection Bus (POIB) (unboxed 2/1/22)

  - Section 2.7.3.3

Proposed Guide Language Revision

2.7.2	Maintaining Voltage Profile

(1)	ERCOT has the responsibility for monitoring and controlling the Voltage Profile and should use the following:

(a)	Operations Engineering

(i)	All voltage limits must be based on sound engineering studies that use the appropriate Network Operations Model.  TSP study results should be made available to ERCOT; and

(ii)	Transfer limits shall reflect voltage and/or reactive restrictions.

(b)	Coordination

(i)	Entities must coordinate high voltage limits in order to guarantee that the maximum continuous over-voltage of equipment is not exceeded.  TOs shall notify ERCOT of normal operating voltage limits and post-contingency voltage limits for each bus;

(ii)	Low voltage limits must be coordinated in order to prevent one Entity from being a burden to another;

(iii)	Voltage limits shall not be violated during all normal and Credible Single Contingency conditions; and

(iv)	The operation of all Reactive Power devices under the control of a TO, Direct Current Tie Operator (DCTO), or a Qualified Scheduling Entity (QSE) will be coordinated under the direction of ERCOT to maintain transmission voltage levels within normal limits and post-contingency voltages within post contingency limits.  Static reactive devices will be managed to ensure that adequate dynamic reactive reserves are maintained at all times.

(c)	Notification

(i)	Generation Resources with voltage problems shall notify the TO to whom they are directly connected.  TOs shall notify other affected TOs and ERCOT; and

(ii)	ERCOT will monitor events and may direct actions to solve the problem.

[NOGRR204: Replace item (c) above with the following upon system implementation of NPRR989:] (c) Notification (i) Generation Resources or ESRs with voltage problems shall notify the TO to whom they are directly connected. TOs shall notify other affected TOs and ERCOT; and (ii) ERCOT will monitor events and may direct actions to solve the problem.

(d)	Response

(i)	When the voltage levels deviate from established limits, ERCOT or the TO shall take immediate steps to relieve the condition using all available reactive resources.

(e)	Monitoring

(i)	TOs shall provide telemetry to ERCOT on all major transmission bus voltages.

(f)	Controls

(i)	ERCOT must be aware of the location of and availability of reactive capability;

(ii)	ERCOT shall maintain displays to monitor Voltage Profiles and reactive flows; and

(iii)	Controls to maintain Voltage Profiles may include but are not limited to capacitor switching, reactor switching, auto-transformer tap changing, generator and DC Tie reactive dispatch, transmission line switching, and Load shedding.

[NOGRR204: Replace item (f) above with the following upon system implementation of NPRR989:] (f) Controls (i) ERCOT must be aware of the location of and availability of reactive capability; (ii) ERCOT shall maintain displays to monitor Voltage Profiles and reactive flows; and (iii) Controls to maintain Voltage Profiles may include but are not limited to capacitor switching; reactor switching; auto-transformer tap changing; Generation Resource, ESR, and DC Tie reactive dispatch; transmission line switching; and Load shedding.

(g)	Documentation

(i)	Each TO must maintain a voltage/reactive plan for normal and Emergency Conditions and will provide this plan to adjacent TOs as well as ERCOT upon request.

(h)	Emergency or Abnormal Conditions

(i)	Transmission systems shall be designed so that effective reactive reserves shall be available without de-energizing other Facilities or shedding Load under normal conditions;

(ii)	Major transmission lines shall be kept in service during light Load as much as possible.  Lines should only be removed after all applicable reactive controls are implemented and studies show that reliability will not be degraded; and

(iii)	Voltage reduction should not be done on the transmission system unless coordinated with adjacent TOs.

2.7.3.3	TO/TSP Responsibilities

(1)	Each TO shall be responsible for directing Voltage Set Points for each Generation Resource required to provide VSS interconnected to its TSP’s Facilities.  Each TO will adjust the Voltage Set Point by communicating directly with the Resource Entity or QSE responsible for the operation of the Generation Resource.  Normal communication is to request voltage or Reactive Power be raised or lowered at a specified bus by a stated number of kV or MVAr (e.g., +1 kV, +20 MVAr, or -1 kV, -20 MVAr).

(2)	Each TO shall monitor system voltages and shall operate voltage control equipment, including, but not limited to, static Reactive Power resources such as capacitors, reactors and transformer tap changers to maintain system voltages within limits.

(3)	Each TO shall operate static Reactive Power resources within its operating area as required by its criteria while maintaining dynamic reactive reserves, both leading and lagging, provided by Generation Resources.  Except as reasonably necessary to ensure reliability or operational efficiency, TOs should utilize available static reactive devices prior to requesting a Voltage Set Point change from a Generation Resource.

(4)	Each TO shall telemeter to ERCOT via ICCP the Real-Time desired Voltage Set Point and actual voltage at the POIB for each Generation Resource interconnected to its system required to provide VSS.  Each TO shall modify the telemetered Voltage Set Point as soon as practicable in order to match any verbal Voltage Set Point instruction issued.

(5)	Each TO shall know the status of static transmission Reactive Power resources in its operating area and shall provide such information to ERCOT.

(6)	When voltage levels deviate from established limits, the affected TO shall take immediate steps to relieve the condition using available reactive resources under its control.

(7)	Each TSP shall, as soon as practicable, notify ERCOT of any temporary transmission voltage limit changes and shall coordinate with ERCOT to update the Network Operations Model with any permanent or long-term changes to voltage limits that deviate from those identified in Section 2.7.3.1, Operational Guidelines.

[NOGRR177 and NOGRR204: Replace applicable portions of Section 2.7.3.3 above with the following upon system implementation of NPRR857 or NPRR989, respectively:] 2.7.3.3 TO/TSP Responsibilities (1) Each TO shall be responsible for directing Voltage Set Points for each Generation Resource and ESR required to provide VSS interconnected to its TSP’s Facilities. Each TO will adjust the Voltage Set Point by communicating directly with the Resource Entity or QSE responsible for the operation of the Generation Resource or ESR. Normal communication is to request voltage or Reactive Power be raised or lowered at a specified bus by a stated number of kV or MVAr (e.g., +1 kV, +20 MVAr, or -1 kV, -20 MVAr). (2) Each TO shall monitor system voltages and shall operate voltage control equipment, including, but not limited to, static Reactive Power resources such as capacitors, reactors and transformer tap changers to maintain system voltages within limits. (3) Each TO shall operate static Reactive Power resources within its operating area as required by its criteria while maintaining dynamic reactive reserves, both leading and lagging provided by Generation Resources and ESRs. Except as reasonably necessary to ensure reliability or operational efficiency, TOs should utilize available static reactive devices prior to requesting a Voltage Set Point change from a Generation Resource or ESR. (4) Each TO shall telemeter to ERCOT via ICCP the Real-Time desired Voltage Set Point and actual voltage at the POIB for each Generation Resource and ESR interconnected to its system required to provide VSS. Each TO shall modify the telemetered Voltage Set Point as soon as practicable in order to match any verbal Voltage Set Point instruction issued. (5) Each TO shall know the status of static transmission Reactive Power resources in its operating area and shall provide such information to ERCOT. (6) When voltage levels deviate from established limits, the affected TO shall take immediate steps to relieve the condition using available reactive resources under its control. (7) Each TSP Direct Current Tie Operator shall, as soon as practicable, notify ERCOT of any temporary transmission voltage limit changes and shall coordinate with ERCOT to update the Network Operations Model with any permanent or long-term changes to voltage limits that deviate from those identified in Section 2.7.3.1, Operational Guidelines. (8) Each TO designated by a DCTO operating a DC Tie meeting the applicability requirements of paragraph (1) of Section 3.15.4, Direct Current Tie Owner and Direct Current Tie Operator (DCTO) Responsibilities Related to Voltage Support, shall be responsible for directing the operation of reactive power resources operated by that DCTO. Each TO shall telemeter to ERCOT via ICCP and to the DCTO via telemetry, the Real-Time desired target voltage at the DC Tie’s Point of Interconnection Bus (POIB) and the actual voltage at the POIB. Each TO shall modify the telemetered target voltage to match any verbal target voltage instruction issued as soon as practicable. (9) Each TO designated by a DCTO operating a DC Tie meeting the applicability requirements of paragraph (1) of Section 3.15.4 shall for each such DC Tie provide to ERCOT, via ICCP, the status of the DC Tie Facility’s voltage control system. An “On” status will indicate that the control system is on and set to regulate the voltage at the DC Tie’s POIB in automatic voltage control mode, and an “Off” status will indicate that the control system is off or in manual mode. (10) Each TO designated by a DCTO operating a DC Tie meeting the applicability requirements of paragraph (1) of Section 3.15.4 shall, as soon as practicable, notify ERCOT when a DC Tie Facility experiences a change that affects its reactive capability, including any change to the operation mode of the DC Tie Facility’s voltage control system or any temporary transmission voltage limit changes.

#### 2.7.3.6	DCTO Responsibilities and DC Tie Requirements

(1)	Each DCTO operating a DC Tie subject to Protocol Section 3.15.4, Direct Current Tie Owner and Direct Current Tie Operator Responsibilities Related to Voltage Support, shall comply with any instruction from its designated TO with respect to the DC Tie’s Reactive Power capability, including any instruction to maintain a specific voltage at the POIB, subject to the DC Tie’s operating characteristic limits and voltage limits, and within the tolerances identified in paragraph (2) below, and subject to any superseding Dispatch Instruction from ERCOT.

(2)	A DCTO operating a DC Tie subject to Protocol Section 3.15.4 shall maintain the voltage at the POIB within the tolerance band below while operating at less than or equal to the maximum reactive capability of the DC Tie.  A DC Tie’s POIB voltage may be out of the tolerance band if all of its reactive capability has been exhausted.  The tolerance bands are as follows:

| Nominal Voltage | Tolerance Band kV |
| --- | --- |
| 345 | +/- 4kV |
| 230 | +/- 3kV |
| 138 | +/- 2kV |
| 115 | +/- 2kV |
| 69 | +/- 1kV |

(3)	Required reactive capability must be maintained at all times that the DC Tie is not experiencing an Outage.  When a DC Tie experiences a change that affects its reactive capability, the associated DCTO shall notify its TO as soon as practicable, but not longer than 30 minutes, from becoming aware of the change in reactive capability.

(4)	Each DCTO shall, as soon as practicable, notify its TO of any temporary transmission voltage limit changes.  The DC Tie owner shall coordinate with its DCTO on necessary changes to the Network Operations Model.   The DCTO will coordinate with ERCOT to update the Network Operations Model with any permanent or long-term changes to voltage limits that deviate from those identified in Section 2.7.3.1, Operational Guidelines.

(5)	Each DCTO shall provide to its TO, via telemetry, the status of the voltage control system for any DC Tie meeting the applicability requirements of paragraph (1) of Protocols Section 3.15.4.  An “On” status will indicate that the control system is on and set to regulate the voltage at the DC Tie’s POIB in automatic voltage control mode, and an “Off” status will indicate that the control system is off or in manual mode.