## Slide 1
Resource Adequacy Modeling Projects for 2022
Pete Warnken
Resource Adequacy Dept.
April 4, 2022

## Slide 2: Effective Load Carrying Capability (ELCC) Study

## Slide 3: ELCC Overview
ELCC is a probability-based measure of the reliability benefit of a resource type (or combination of resource types) for the system during periods that have the highest risk of capacity reserve shortfalls
  Accounts for:
    The resource production and electricity demand profiles
    The system’s resource mix (types and quantities)
    Synergies between resource types, so-called “diversity benefits”
ELCC estimation is based on probabilistic system simulations, the most common being Monte Carlo
ELCC is forward-looking; the current Peak Average Capacity Contribution approach for the CDR report is based on historical average capacity factors during seasonal peak demand hours

## Slide 4: ELCC Overview
ELCC development procedure is summarized below:
For more details, see the ERCOT 2020 Reserve Margin Study Report: https://www.ercot.com/files/docs/2021/01/15/2020_ERCOT_Reserve_Margin_Study_Report_FINAL_1-15-2021.pdf

## Slide 5: ELCC Study Objectives
Study Objectives: Use SERVM1 Monte Carlo simulations to do the following:
  Determine renewable and battery storage ELCC values for individual high-risk hours by season, to potentially be used as alternatives to seasonal or monthly values
  Conduct sensitivity analysis of ELCC values with respect to resource penetration levels, alternative technology types (solar), and grid location
Intent is to lay the groundwork for specifying the recommended ELCC methodology for resource adequacy and planning studies
Expect up to a 100 unique scenarios to be simulated
1 Strategic Energy & Risk Valuation Model, licensed by Astrape Consulting

## Slide 6: ELCC Study Key Milestones
Project completion targeted for 7/30/2022
  Will keep SAWG apprised of the project
  Study report and SAWG presentation expected in September
Next step is to develop Protocol revision request language to integrate into a broader NPRR on revised CDR methodologies

## Slide 7: Zonal Reliability Impact Study

## Slide 8: Zonal Study Objective and Tasks
Study Objective: Determine the system reliability and reserve margin impacts of a zonal SERVM model as compared to the current single-zone model design
  Focus on renewable resource impacts
  Supports risk scenario requirement for 2022 NERC Probabilistic Assessment
Study tasks:
  Define load zones in the SERVM model and establish zonal transfer limits
  Convert the current ERCOT Long-Term Load Forecast into zonal load profiles and assign generating units to load zones
  Run SERVM simulations for two study years: 2023 and 2026
  Compare reliability and reserve margins results to the original single-zone model

## Slide 9: Topology Bubble Diagram
Transfer limits derived from Regional Transmission Plan (RTP) cases:
  “High Renewables, Coincident Peak with No Curtailment”
  “High Renewables, Coincident Peak with Wind Curtailment”

## Slide 10: Zonal Study Key Milestones
Targeting study completion by mid-to-late June
Will keep SAWG apprised of the study project
Study report and SAWG presentation expected in July

## Slide 11: NERC Probabilistic Assessment (ProbA) Study

## Slide 12: ProbA Study
Complements NERC’s Long Term Reliability Assessment (LTRA) by providing probabilistic reliability statistics of the forecasted resource portfolios reported in the LTRA data submissions
Reliability Statistics include annual and monthly Loss of Load Hours (LOLH, hours/year) and Expected Unsupplied Energy (EUE, MWh)
ProbA conducted every even-numbered year
Two study years: 2024, 2026
NERC Probabilistic Assessment Working Group oversees ProbA scheduling, data submission and reporting procedures

## Slide 13: ProbA Study
The study must include at least one risk scenario
  Use zonal SERVM model developed for the zonal reliability modeling project to simulate year-2026 impacts of West Zone transmission limits on providing Inverter Based Resource (IBR) energy to the rest of ERCOT
Main Milestone Dates:
  Base Case study completion in early August; PAWG peer review of Base Case results completed by 8/23/2022
  Summary of ProbA study and Base Case results to be included in NERC LTRA report to be release in mid-December 2022
  Scenario risk results due 1/11/2023 for all Assessment Areas
  ProbA Risk Scenario report released in June 2023