## Slide 1: IBR TF update to ROS
Chair: Mohammad Albaijat, PhD
Vice-Chair: Julia Matevosyan, PhD
April 07, 2022

## Slide 2: IBR TF meetings
Two meetings
  February 18, 2022
  March 18, 2022
February 18, 2022, meeting
  Odessa Disturbance follow ups
  Similar Inverter Model Assessment
  Smaller unexpected tripping event analysis
  Priorities
March 18, 2022, meeting
  Review of NERC and other IBR WG updates
  IEEE 2800-2022 standards
  Odessa Disturbance and event process draft
  PGRR 075 and 085 updates
  Draft Interconnections Check list
  Discussed priorities and items for the following meeting (April 8th)

## Slide 3: Odessa Disturbance updates
Focused on 5 Follow-up RFIs representing 80% of solar Resources lost during the event
Some plants have implemented mitigations, some couldn’t be due to legacy inverters, further follow ups will be needed with others (to be discussed in next meetings)
Specific issue of inverters tripping on overvoltage and mitigation requires further investigation with OEMs, since such behavior is not meeting ERCOT’s Voltage Ride Through requirements as per NOGs.
Current RFI procedure after disturbances: time consuming for staff and MPs, needs improvement and more streamlined process (to be discussed in the upcoming meetings)
Follow up RFIs for May 9th event (sent 8 out of 10)
Additional follow up RFIs on March 9th mainly on reduction of output by different MW values
Similar Inverter Model Assessment
About 8.3 GW of solar capacity using same or similar models of inverters as the ones that tripped in Odessa event.
ERCOT will follow-up with RFIs to such units requesting to address potential cause of tripping
ERCOT will prioritize communications based on most significant causes.
Smaller unexpected tripping event analysis
Smaller but similar events should be monitored to identify causes of IBR tripping and potentially prevent future larger events.
ERCOT needs to streamline the process and develop events criteria for sending RFIs.

## Slide 4: Review of NERC and other IBRWG updates
NERC IBR performance subcommittee is exploring performance of utility scale inverter resources directly connected to bulk power system
Guidelines and reports on IBR performance
Latest reports include:
Utilizing the excess capability of IBRs for frequency support (NERC paper September 2021)
White paper published December 2021 “Grid Forming Technology”
Follow-ups on NERC disturbance reports and alerts (Several NERC reports covering all major events including Odessa Disturbance)
Ongoing activities related to reliability guidelines
IEEE 2800 Standards
Standard for interconnection and interoperability of IBR interconnecting with transmission systems
Discussed reliability issues with IBR (six major events)
Harmonizes technical minimum capability
A consensus based, voluntary IEEE performance standard
Approved in January 2022 and publication in April/May 2022
In scope: IBR plant, hybrid IBR plant. Out of scope: hybrid plant (multiple IBR and non-IBR resources operated as one by TS operator), co located plant (multiple resources operated separately by TS operator)
ACTION: Gap analysis to be performed on ERCOT rules vs. IEEE 2800

## Slide 5: PGRR 075 and 085 updates
PGRR-075 effective May 1, 2020, and PGRR-085 effective March 2021
PGRR-075 Introduced model quality test(MQT) requirements for PSS/E dynamic model
PGRR-085 introduced MQT and unit model validation requirements for PSCAD model
Both: Unit model validation (Resource interconnection) and Plant model verification (commissioning and operation)
Dynamic model requirements (model quality test for PSS/E, model quality test for PSCAD model, unit model validation for PSCAD model and model parameter verification)
Draft Interconnection Check list
It’s a pre draft questionnaire meant to draw attention of all stakeholders to participate in finalizing formal proposal to ensure reliability in reasonable fashion
Five questions focused on making sure that new IBRs read and implemented relevant NERC guidelines, read and implemented recommendations from NERC event reports, read and implemented if new IBR is going to be connected at a distribution level, read and implemented applicable standards and relevant nodal protocol operating guide requirements
It seems there is a push back on this questionnaire as it is. But again, this was an informal proposal meant to engage stakeholders to participate in formulating a formal proposal

## Slide 6: Priorities and items for next meeting
Gap analysis between ERCOT nodal protocols and guide requirements and IEEE2800 Standard. Specifically, we wanted to know where IEEE2800 exceeds ERCOT rules and where both ERCOT and IEEE2800 meet and where ERCOT exceeds IEEE2800.
Strategy of adoption IEEE2800
Continuous follow up on RFI on the Odessa event
IBR Ride-Thru failures monthly update
Draft interconnection check list discussion
OEM scenarios and simulations