## Slide 1
Public Utility Commission of Texas (PUCT) Oversight Project No. 46304 Relating to DC Tie Project Proposed by Southern Cross Transmission, LLC
Directive #6 : Transmission Upgrades
Directive #8: Voltage Support
APRIL 13, 2022
ERCOT Staff

## Slide 2: Agenda
Background of Project and PUCT Directives
Directive 6: Transmission Upgrades
Directive 8: Voltage Support
Request for Endorsement and Next Steps

## Slide 3: Background of Project and PUCT Directives
Southern Cross Transmission LLC/Pattern Power Marketing LLC received FERC approval (FERC Docket No. TX 11-1-001) to interconnect DC Tie line.
PUCT imposed conditions for interconnection of the SCT DC Tie line in two PUCT proceedings:
  City of Garland docket – Docket No. 45624
  Oversight proceeding arising out of City of Garland docket – Project No. 46304
As part of the oversight proceeding, PUCT issued 14 Directives to ERCOT, requiring certain studies and determinations be made to accommodate the SCT DC Tie.

## Slide 4: Summary of Directive 6 Related to Transmission Upgrades
Directive 6 requires ERCOT to study and determine what transmission upgrades, if any, are necessary to manage congestion resulting from power flows over the Southern Cross DC tie (SCT DC Tie).
Determination (summarized from the whitepaper):
  No transmission system upgrades are ultimately necessary to manage congestion resulting from power flows over the Southern Cross DC Tie.
  ERCOT expects that it may need to redispatch generation and/or limit flows across the Southern Cross DC Tie to manage constraints in real time.
Transmission Analysis Conclusions:
  For imports during summer peak conditions, thermal limits were reached before voltage stability limits. The transmission system was able to accommodate an import level of approximately 547 MW before thermal overloads were observed.
  For high wind, low load conditions, exports across the Southern Cross DC Tie would be limited to 1,289 MW by voltage stability constraints. Without transmission system upgrades, ERCOT expects that exports across the Southern Cross DC Tie would need to be limited to manage the voltage stability constraints identified.
  The cost of transmission upgrades needed to resolve the voltage stability constraint associated with exports was estimated to be $182-205 million.
  Fewer transmission upgrades would be needed to achieve full export capability under the studied conditions if the Southern Cross DC Tie provided the equivalent of 0.95 power factor leading and lagging reactive power capability.
  The transmission system would experience angular instability at assumed full import conditions (2,000 MW). Additionally, under summer peak conditions, the transmission system would experience instability at an import level of 1,375 MW for the contingency loss of a double-circuit transmission line.
  The cost of the incremental transmission upgrades that would resolve the angular stability limits was estimated to be $161-360 million.

## Slide 5: Summary of Directive 6 Related to Transmission Upgrades
Basis for Determination (summarized from the whitepaper):
  ERCOT transmission analysis conducted in 2019 revealed that upgrades would be needed to accommodate the modeled flows over the Southern Cross DC Tie under certain system conditions.
  PGRR077, DC Tie Planning Assumptions, approved by the ERCOT Board in October 2020, requires ERCOT to curtail assumed DC Tie flows in transmission planning analysis when necessary to meet reliability criteria.
  Consequently, ERCOT’s future transmission planning studies will not identify any reliability-based need for transmission upgrades following the interconnection of the SCT DC Tie.
  Additionally, ERCOT’s Directive 7 determination shows that existing operational and market mechanisms can be used to manage congestion due to flows over the SCT DC Tie including ERCOT’s ability to curtail the import or export to the extent necessary to operate the system within its limits.

## Slide 6: Summary of Directive 8 Related to Voltage Support
Directive 8 requires ERCOT to study and determine whether Southern Cross Transmission or any other entity scheduling flows across the Southern Cross DC Tie should be required to provide or procure voltage support service or its technical equivalent.
Determination (summarized from the whitepaper):
  All DC Tie facilities energized after January 1, 2021, and any DC Tie facility that is replaced after that date should be required to have at least 0.95 power factor leading/lagging reactive power capability.
Basis for Determination (summarized from the whitepaper):
  NPRR1098, Direct Current Tie (DC Tie) Reactive Power Capability Requirements and NOGRR234, Related to NPRR1098, Direct Current Tie (DC Tie) Reactive Power Capability Requirements, approved by the PUCT on 3/31/2022 revised the Protocols and Operating Guide to require that new or replaced DC Tie facilities shall have at least 0.95 power factor leading/lagging reactive power capability.
  ERCOT’s study performed pursuant to Directive 6 identified a voltage stability limit for exports of 1,289 MW during high-wind, low-load conditions, which would require the installation of additional reactive capability to accommodate exports in excess of that amount during those conditions.
  ERCOT’s study noted that, if the Southern Cross DC Tie provided the equivalent of 0.95 power factor leading and lagging reactive power capability, fewer transmission upgrades would be needed to achieve full export capability under the studied conditions.

## Slide 7: Next Steps
Request that TAC endorse the Directive 6 Transmission Upgrades and Directive 8 Voltage Support whitepapers as presented and posted with the TAC materials.
ERCOT plans to take the whitepapers to the ERCOT Board for approval at its April 27, 2022 meeting.
ERCOT staff continues to work with stakeholders on the remaining Directives
  http://www.ercot.com/mktrules/puctDirectives/southernCross