## Slide 1
Resource Integration Topics
Jay Teixeira
ERCOT
Resource Integration Working Group
April 19, 2022

## Slide 2: Quarterly Stability Assessment (QSA)
Planning Guide 5.9
Next Deadline for QSA
If a GINR is not included in QSA, its Initial Synchronization date will be automatically delayed to the next quarter
All-Inclusive Generation Resource Initial Synchronization Date | Last Day for an IE to meet prerequisites as listed in paragraph (4) below | Completion of Quarterly Stability Assessment
Upcoming January, February, March | Prior August 1 | End of October
Upcoming April, May, June | Prior November 1 | End of January
Upcoming July, August, September | Prior February 1 | End of April
Upcoming October, November, December | Prior May 1 | End of July

## Slide 3: Quarterly Stability Assessment (QSA)
Planning Guide 5.9, Quarterly Stability Assessment
Issue’s seen in previous QSA’s
  10 day comment period for FIS
    Needs to be complete before QSA deadline
    TSPs need to plan for it
  Dynamic/PSCAD Model Review
    Updated dynamic model dependent on FIS Stability study
    Need to meet PG 6.9 15 to 30 days prior to QSA deadline
PSSE Model Quality Test Required
  TSPs have requested dynamic model MQT report submitted with dynamic model prior to FIS Stability Study
PSCAD Model Quality Test and Unit Model Validation required
TSAT Model Required – If PSSE model is UDM, then TSAT model should be UDM

## Slide 7: Discussion Items
What are Generator Terminals
  As modeled in ERCOT Operations Model
  For non-conventional, usually 34.5 kV
Dissimilar Real Power/Turbine Rating
  Need to study summer and winter with higher turbine ratings in winter
  Use highest sustainable rating regardless of temperature on RARF Unit Info
  HRL at highest seasonal rating value
  SGIA refer to differing seasonal ratings if applicable
  Higher rated seasonal ratings studied in addition to summer peak if necessary

## Slide 8: Active RR’s
None

## Slide 9: Other contact information
ResourceIntegrationDepartment@ercot.com is distribution list for Resource Integration department
Mailing List
  RESOURCE_INTEGRATION@LISTS.ERCOT.COM

## Slide 10: Questions?
Thank you!