| SCR Number | 821 | SCR Title | Voltage Set Point Target Information for Distribution Generation Resource (DGR) or Distribution Energy Storage Resource (DESR) |
| --- | --- | --- | --- |
| Date of Decision |  | April 14, 2022 |  |
| Action |  | Tabled |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | To be determined |  |
| Priority and Rank Assigned |  | To be determined |  |
| Supporting Protocol or Guide Sections/Related Documents |  | Inter-Control Center Communication Protocol (ICCP) Handbook |  |
| System Change Description |  | This System Change Request (SCR) allows, at the option of the Transmission and/or Distribution Service Provider (TDSP), Voltage Set Point target information to be provided to a Distribution Generation Resource (DGR) or a Distribution Energy Storage Resource (DESR) installation. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This change reduces operational risk by clarifying roles and responsibilities related to Voltage Set Point target information. Real-Time notification allows for patterns to be developed and allows for analysis that can feed back into Voltage Profile creation process for continuous improvement. |  |
| PRS Decision |  | On 4/14/22, PRS voted unanimously via roll call to table SCR821 and refer the issue to ROS. All Market Segments participated in the vote. |  |
| Summary of PRS Discussion |  | On 4/14/22, participants noted varying metering accuracy for voltage across devices and requested additional review by ROS. |  |

| Sponsor |  |
| --- | --- |
| Name | Dennis Kunkel |
| E-mail Address | dkkunkel@eap.com |
| Company | American Electric Power Service Corporation |
| Phone Number | 361-289-4003 |
| Cell Number | 361-813-4140 |
| Market Segment | Investor Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

None

Proposed System Change

Issue:

- Distribution Energy Storage Resources (DESRs) will likely need voltage control versus power factor control due to their significant variability in output.  A DESR developer has expressed the need for voltage schedule communication similar to transmission level voltage sites for standardization.

- There is an increasing number of DESRs and other highly variable Distribution Generation Resources (DGRs) on voltage control thus verbal adjustments to a voltage schedule for an area-wide event to many sites will not be feasible.  The need for an application that allows quick adjustment for wide-area events for all DESRs, DGRs and potentially Settlement Only Distribution Generators (SODGs) where the Distribution Service Provider (DSP) has determined a need or benefit for a location using a voltage schedule rather than a power factor profile.  This means the unit would operate with its Automatic Voltage Regulator (AVR) on and in voltage control mode.

Resolution:

- Transmission and/or Distribution Service Provider (TDSP) will provide Real-Time Voltage Set Point target information.  Voltage Set Point notification is to ERCOT via Inter-Control Center Communication Protocol (ICCP) and ERCOT will pass Voltage Set Point target information through to the Qualified Scheduling Entity (QSE).  The DGR/DESR would be expected to follow the Voltage Set Point target information in Real-Time within +/-2% or as indicated by interconnection agreements.

- Optional for any TDSP to use on any distribution connected DGR greater than 1 MW.  The TDSP will determine during interconnection studies if Voltage Set Point instruction will be issued.

- TDSP will include in the Distribution Generation Interconnection Agreement and will notify ERCOT that Voltage Set Point information will be used.

- The DGR/DESR will need to ensure its reactive capability is accurately modeled in Resource Asset Registration Form (RARF) / Resource Integration and Ongoing Operations (RIOO) system and tested as part of reactive testing.

- Look at using similar process of using transmission KVT or KVM parameters

  - Measurements “DGKVT” or “DGKVM”

  - The Distributed Generation (DG) labeling as determined by ERCOT should distinguish between transmission and distribution so that there are no compliance issues created.

  - Modeling should identify the nominal kV to calculate the % delta

  - Modeling should identify the QSE and Resource Entity

  - Modeling should identify any one to many relationships (i.e., one DGKVT and DGKVM for multiple DGR/DESR/SODG units).

- TDSP can provide the Voltage Set Point information via ICCP and/or verbally as they choose.

- Installations must maintain nominal voltage before operation is allowed.

- Distribution systems with this provision should have any voltage reduction processes coordinated to avoid issues during voltage reduction measures.

- Any failure to ride through for any DGR/DESR in voltage control mode to a system disturbance should be evaluated by the TDSP and corrective actions made by the DGR/DESR.

- TDSP will provide ERCOT new ICCP Supervisory Control and Data Acquisition (SCADA) point for the DESR/DGR.

- Process:

  - TDSP will provide ERCOT new ICCP SCADA points for the DGR/DESR.

  - TDSP to determine set point and measurement

  - Transmission Service Provider (TSP) sends set point and measurement to ERCOT

  - ERCOT sends set point and measurement to the appropriate QSE for each distributed connected Generation Resource in voltage control mode

  - QSE provides set point and measurement to DGR/DESR

- ERCOT will need new ICCP SCADA points for the DGR/DESR.

- Communications would leverage existing communication infrastructure

- Process leverages the Wide Area Network (WAN) and ERCOT could have option on how DGR/DESR instruction is provided to the QSE.