## Slide 1
ERCOT Frequency Control Report
March 2022
ERCOT
Operations Planning
PDCWG | April 20th, 2022

## Slide 2: Summary of March 2022
CPS1: 171.07%
Current CPS1 12-Month Rolling Average: 171.65%
0 BAAL Exceedance(s)
3 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2022 RMS1 Statistics
  Mean: 15.17 mHz
  Min: 12.43 mHz
  Max: 19.20 mHz
Energy Statistics
  Total Energy: 30,450,997 MWh
  Wind Energy: 11,016,800 MWh
  Percent Energy from Wind: 36.18 %
  Solar Energy: 1,773,088 MWh
  Percent Energy from Solar: 5.82%
Minimum System Inertia
  Mean: 144,298 MW*s
  Max: 246,062 MW*s on March 8th
  Min: 114,674 MW*s on March 21st

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Chart: Day
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
Q1 | 169.685 | 164.4787 | 151.9903 | 166.0963 | 164.2468 | 170.2797 | 152.3247 | 167.1225 | 171.4898 | 177.1042 | 168.3435 | 167.924 | 172.4493 | 158.9824 | 170.188 | 167.2228 | 161.7987 | 158.3605 | 174.2442 | 177.2563 | 155.0355 | 168.9406 | 159.5061 | 170.9911 | 166.0539 | 166.4468 | 170.9737 | 155.8005 | 158.0036 | 154.9735 | 162.153
Median-Q1 | 7.3621 | 12.1202 | 12.3367 | 8.9629 | 9.2044 | 7.0556 | 18.9615 | 9.6739 | 5.9398 | 3.1042 | 8.0387 | 9.2745 | 6.691 | 13.799 | 7.0852 | 7.8977 | 7.3674 | 7.7201 | 5.9088 | 4.0649 | 6.7414 | 4.3634 | 10.3052 | 6.6948 | 9.9675 | 10.5643 | 5.569 | 12.2962 | 10.6401 | 11.4369 | 8.6288
Q3-Median | 7.1044 | 8.3652 | 13.6292 | 9.156 | 8.603 | 4.0106 | 7.9183 | 5.5818 | 3.5358 | 2.2696 | 4.5677 | 4.7334 | 6.9334 | 5.4846 | 4.7762 | 5.42 | 8.0199 | 9.6232 | 1.4097 | 3.5732 | 14.0459 | 4.8944 | 10.0012 | 4.3839 | 4.2672 | 3.3067 | 2.5069 | 8.7152 | 6.5493 | 9.9632 | 6.6588
Mean | 176.7543 | 174.8477 | 164.9975 | 173.8755 | 171.5085 | 176.0044 | 166.6375 | 172.1169 | 175.657 | 177.4652 | 173.7287 | 174.3584 | 178.0969 | 170.3036 | 172.4192 | 173.634 | 167.4355 | 163.1883 | 174.422 | 180.5426 | 159.1498 | 172.3174 | 163.7533 | 170.1756 | 172.854 | 172.4425 | 173.6897 | 163.9442 | 166.0828 | 161.7623 | 167.4462
Outliers | 123.6289 | 155.7033 | 161.4699 | 152.1784 | 159.5854 | 144.6606 | 135.614 | 100.8467 | 129.0697 | 107.8541 | 124.0512 | 136.8441 | 153.9331 | 165.4318 | 121.9876 | 93.3956 | 141.9781 | 128.5695 | 121.1695 | 92.2313 | 108.9631 | 62.4428 | 134.686 | 133.806 | 115.7607 | 112.7709 | 111.6956
Mar-22 CPS1 (%): 171.07
Notes: 1. 93.4%@ 3/21/2022 HE 14:00
Expected Generation Deviation
Between 1:30-2:00pm the Expected gen dev remained negative. The largest expected gen dev was -2320 MW @ 1:51pm with signification contribution from solar and wind generation.
IRR Ramps
Between 1:45-1:55pm wind ramped down by ~700MW and solar ramped down by ~300MW
Regulation: Regulation up was exhausted during most of the second half of the hour. A 350 MW SCED manual offset was applied and 620 MW of RRS was deployed.
2. 92.2% @ 3/23/2022 HE 21:00
Expected Generation Deviation
Expected gen dev remained negative for the hour. The largest expected gen dev was -2660 MW @ 8:54pm with signification contribution from thermal resources and wind generation.
IRR Ramps
Between 8:40pm to 9:00pm wind ramped down by ~1750 MW.
Regulation: Regulation up was exhausted during the second half of the hour. Multiple SCED offsets were applied, the largest being a 350 MW SCED manual offset.
3. 62.4%@ 3/24/2022 HE 20:00
Expected Generation Deviation
Expected gen dev remained negative for the whole hour. The largest expected gen dev was -4247 MW @ 7:30pm with signification contribution from solar and wind generation.
IRR Ramps
Between 7:00pm and 8:00pm, solar ramped down ~3,900 MW and wind ramped down ~2,000 MW
Regulation: Regulation up was exhausted during first half of the hour. Multiple SCED offsets were applied, the largest being a 500 MW SCED manual offset.

## Slide 5: BAAL Exceedances & Violations
There are 0 BAAL exceedance(s) in March

## Slide 6: 15-Minute Average CPS1%
Mar-22 CPS1 (%): 171.07

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 171.65%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 15.17 mHz
  Min: 12.43 mHz
  Max: 19.2 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: 16.1mHz on avg

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 30,450,997 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 11,016,900 MWh

## Slide 23: % Energy from Wind Generation
Notes: 36.18% %

## Slide 24: Total Energy From Solar Generation
Notes: 1,773,088 MWh

## Slide 25: % Energy from Solar Generation
Notes: 5.82%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia =114,674 MW*s on 3/21/2022
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 144,298 MW*s
Max: 246,062 MW*s on Mar 8th
Min: 114,674 MW*s on Mar 21st

## Slide 28: Questions?
Thank you!