## Slide 1
Next Start Resource Test
BSWG
April 19, 2022

## Slide 2: Next Start Test Overview
Next Start Resource Test
  Established in PRR686 and NPRR019 by BSTF in 2007
  On a physical test, clear the Basic Starting Test, Line Energization Test when required and a Load Carrying Test.
  Ability of a Black Start Resource to start up the next start unit’s largest required motor while continuing to remain stable and controlling voltage and frequency
    Can be completed through a simulation study
  Ability of the Black Start Resource to operate at stable voltage and frequency and controlling voltage for at least 30 minutes.
  The test shall be repeated when a new next start unit is selected
  To be completed once every five years

## Slide 3: Next Start Resource Test
Physical Test vs Simulation
  Only test that allows for simulation
  Physical test can be performed if Next Start Resource is collocated with Black Start Resource or if a dedicated path available.
  Load bank of equal size to Next Start largest motor can be used.
  Simulation option is available if outages needed to isolate path is too extensive.
Three BS Resources have performed a simulation for the Next Start test.
Two BS Resources have used a load bank alternative.