| NPRR Number | 1117 | NPRR Title | Related to SMOGRR025, Modifications to Line Loss Compensation Requirement for EPS Metering |
| --- | --- | --- | --- |
| Date of Decision |  | April 13, 2022 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | Upon implementation of Settlement Metering Operating Guide Revision Request (SMOGRR) 025, Modifications to Line Loss Compensation Requirement for EPS Metering |  |
| Priority and Rank Assigned |  | Not Applicable |  |
| Nodal Protocol Sections Requiring Revision |  | 10.3.2.2, Loss Compensation of EPS Meter Data 11.1.5, Loss Compensation of ERCOT Polled Settlement Meter Data |  |
| Related Documents Requiring Revision/Related Revision Requests |  | SMOGRR025 EPS Metering Design Proposal |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) aligns the Protocols with SMOGRR025 revisions allowing for losses in short runs of connecting lines to be disregarded in instances where the ERCOT-Polled Settlement (EPS) Meter is not physically placed at the Point of Interconnection (POI). |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | Currently all segments of line between the EPS metering point and the POI must be accounted for with loss compensation. The Metering Working Group (MWG) discussed and recognized that there are instances where the losses associated with the distance of line between the POI and the EPS metering points physical location are minimal. SMOGRR025 allows for a calculation to determine whether to require the EPS Meter to be programmed to account for line losses. This NPRR aligns the Protocols with the SMOGRR025 revisions. Changes to the EPS Metering Design Proposal will be made pursuant to Section 3.4, EPS Metering Facility Processes and Forms. |  |
| Credit Work Group Review |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR1117 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |
| PRS Decision |  | On 2/9/22, PRS voted unanimously via roll call to recommend approval of NPRR1117 as submitted. All Market Segments participated in the vote. On 3/9/22, PRS voted unanimously vial roll call to endorse and forward to TAC the 2/9/22 PRS Report and Impact Analysis for NPRR1117. All Market Segments participated in the vote. |  |
| Summary of PRS Discussion |  | On 2/9/22, ERCOT Staff presented NPRR1117. On 3/9/22, participants reviewed the Impact Analysis. |  |
| TAC Decision |  | On 3/30/22, TAC voted unanimously via roll call to table NPRR1117. All Market Segments participated in the vote. On 4/13/22, TAC voted via roll call to recommend approval of NPRR1117 as recommended by PRS in the 3/9/22 PRS Report. There was one abstention from the Independent Generator (Luminant) Market Segment. All Market Segments participated in the vote. |  |
| Summary of TAC Discussion |  | On 3/30/22, participants determined to table NPRR1117 to await the ROS recommendation regarding the related SMOGRR025. On 4/13/22, there was no discussion. |  |
| ERCOT Opinion |  | ERCOT supports approval of NPRR1117. |  |
| ERCOT Market Impact Statement |  | ERCOT Staff has reviewed NPRR1117 and believes the market impact for NPRR1117, in conjunction with SMOGRR025, will facilitate calculations to determine whether to require the EPS Meter to be programmed to account for line losses. |  |

| Sponsor |  |
| --- | --- |
| Name | Don Tucker |
| E-mail Address | Donald.Tucker@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3913 |
| Cell Number |  |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

None

Proposed Protocol Language Revision

10.3.2.2	Loss Compensation of EPS Meter Data

(1)	Where the EPS Meter is not located at the Point of Interconnection (POI) to the ERCOT Transmission Grid, actual metered consumption must be adjusted for line and transformation losses to the POI in accordance with Settlement Meter Operating Guide (SMOG) Section 8, Transformer and Line Loss Compensation Factors.  The preferred method for loss compensation and correction is via internal meter programming.

(2)	Recognizing the fact that some locations may not have the total functionality necessary to perform internal compensation, the Data Aggregation System (DAS) must have the functionality to perform approved loss compensation as necessary.  ERCOT shall retain the discretion to allow or deny the continued use of this type of metering.

(3)	No meter may be compensated internally for losses more than once.  ERCOT may compensate multiple meters prior to netting to the POI.  Pulse communications transfer of data between meters is not allowed.

11.1.5	Loss Compensation of ERCOT Polled Settlement Meter Data

(1)	Adjustments will be made to actual metered consumption to accommodate the energy consumption related to line and transformation losses to the Point of Interconnection (POI) with the ERCOT Transmission Grid in accordance with Section 10.3.2.2, Loss Compensation of EPS Meter Data.  These adjustments are intended specifically to correct the metered consumption when the meter is not located at the POI with the ERCOT Transmission Grid.

(2)	The preferred method for loss compensation and correction is by programming of the meter.  Recognizing that some meters may not have the ability to perform internal compensation computations, ERCOT’s Data Aggregation System (DAS) will have the ability to perform approved loss compensation as necessary.

(3)	TSPs and/or DSPs requesting loss compensation for a specific meter will comply with Section 10, Metering, and the Settlement Metering Operating Guide (SMOG).  ERCOT will provide a compensation mechanism based upon a single percentage value submitted by the TSP and/or DSP and approved by ERCOT.  The loss compensation percentage value will remain in place and will be applied to all intervals of data until such time as the TSP and/or DSP submits, and ERCOT approves, revised loss compensation values.  The loss compensation percentage values should not be changed more than once annually.