## Slide 1
Distribution Voltage Reduction
Alex Lee
ERCOT Grid Analysis
ROS Meeting
May 5, 2022

## Slide 2: Criteria
NPRR 1105 allows ERCOT to direct deployment of distribution voltage reduction measures prior to entering Energy Emergency Alert (EEA).
  Approved in December 2021.
ERCOT Operating Procedures – Transmission and Security Desk Section 4.8.

## Slide 3: Distribution Voltage Reduction (DVR) Capability
Benefit of DVR is less than 1% of ERCOT System Load.
  Less than 30% of ERCOT System Load has existing, in-service DVR.
Benefit of DVR is slightly higher in winter than summer. Better response from resistive load.
Benefit of DVR may have minimal decay at least up to 6 hours.
  Limited tests performed by four TDSPs in 2014.
  Depends on specific load characteristics and outliers did exist.
  https://www.ercot.com/files/docs/2022/04/18/VRTF_Final_Report__07142014.doc
 | System Load MW (Summer) | Summer |  | System Load MW (Winter) | System Load MW (Winter) | 
ERCOT System Load (MW) | 60,000 | 70,000 | 80,000 | 55,000 | 65,000 | 75,000
Estimated Total MW Reduction From DVR | 453 | 551 | 655 | 459 | 564 | 674
i) SCADA Controlled (MW) | 193 | 243 | 298 | 238 | 298 | 363
ii) Manual (MW) | 260 | 308 | 357 | 222 | 266 | 311