## Slide 1
PDCWG Report to ROS
Chair: Jimmy Jackson, CPS
Vice Chair: Vacant
ROS
May 5, 2022

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs and IMFR
    3 FMEs in the month of March
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 4/20/2022
  SCR809 Presentation
  Introduction of Analysis of High Wind Penetration Events
  ERCOT Reports
  TRE Report

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 3 FMEs in March
  3/12/2022 10:21:03
    Loss of 747 MW of generation
    Interconnection Frequency Response: 1,737 MW/0.1 Hz
    53 Resources were evaluated. These includes,
      51 Generation Resources
      2 Controllable Load Resources
      0 Energy Storage Resources
    5 of 51 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    6 of 51 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
There were 3 FMEs in March
  3/14/2022 21:41:14
    Loss of 440 MW of generation
    Interconnection Frequency Response: 1,073 MW/0.1 Hz
    41 Resources were evaluated. These includes,
      39 Generation Resources
      2 Controllable Load Resources
      0 Energy Storage Resources
    9 of 41 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    15 of 41 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Frequency Measurable Events
There were 3 FMEs in March
  3/22/22 04:16:26
    Loss of 703 MW of generation
    Interconnection Frequency Response: 1,192 MW/0.1 Hz
    46 Resources were evaluated. These includes,
      44 Generation Resources
      2 Controllable Load Resources
      0 Energy Storage Resources
    8 of 46 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    6 of 46 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 8: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 412 MW/0.1 Hz
IMFR Performance currently
1271.49 MW/0.1HZ

## Slide 9
Questions?

## Slide 10: Frequency Control Report
March 2022

## Slide 11: CPS1 Performance

## Slide 12: RMS1 Performance of ERCOT Frequency

## Slide 13: Frequency Profile Analysis

## Slide 14: Time Error Corrections

## Slide 15: ERCOT Total Energy
Notes: 31,284,898 MWh

## Slide 16: ERCOT Total Energy from Wind Generation
Notes: 8,261,666 MWh

## Slide 17: ERCOT % Energy from Wind Generation
Notes: 26.41%

## Slide 18: ERCOT Total Energy from Solar Generation
Notes: 1,423,230 MWh

## Slide 19: ERCOT % Energy from Solar Generation
Notes: 4.55 %