## Slide 1: IBR TF update to ROS
Chair: Mohammad Albaijat, PhD
Vice-Chair: Julia Matevosyan, PhD
May 05, 2022

## Slide 2: IBR TF meetings
Three meetings
  February 18, 2022
  March 18, 2022
  April 8, 2022
April 8, 2022, meeting
  OEM: VARS at 0 MW
  Status update on Odessa disturbance
  IBR Ride-Thru failures monthly updates
  Gap analysis between IEEE2800 and ERCOT Nodal Protocols
  Discussed priorities and items for the following meeting (May 23rd)

## Slide 3: Odessa Disturbance updates
Plants identified in NERC Odessa Disturbance report
  10 plants of 1,112 MW reduction
Plant trips due to loss of synchronization
  2 plants cause 389 MW reduction
  Loss of synchronization protection (LSP) setting disabled for both plants
  Additional plants with similar inverters also disabled LSP
  Waiting confirmation from OEM on other inverter types if at risk of tripping
Plant trips on inverter terminal overvoltage
  2 plants cause 269 MW reduction
  Inverter from same OEM related to loss of synch
  Both plants had inverters trip on instantaneous overvoltage above 1.25 pu
  Some plants stated can not relax O/V protection setting but will evaluate reactive power injection
  20 other plants had similar inverter and ERCOT is working on implement same mitigation
  ERCOT to conduct a study comparing Short Circuit Ratios of POIs
Plant trips with OEM#2 Inverters
  2 plants cause 300 MW reduction
  ERCOT scheduled meeting to discuss
Plant Trips due to underfrequency (Follow up on RFI, reach out to relay manufacturer, evaluating potential changes in Voltage/Frequency settings for PRC 024 3 curves
IBR Ride Thru Failures
Five major events in Jan/Feb cause a lost of MW between 98MW to 208 per event
  Follow up by ERCOT
No significant solar event in March
March 22,
  Event #1 in Panhandle cause total lose of 680 MW of wind farms
  Event #2 in Panhandle cause total lose of 440 MW of wind farms
  ERCOT sent RFI for several plants involved (RFI due April 12)
Plant trips for undermined reasons
  2 plants cause 51 MW reduction
  Both plants are using inverters from OEM#3 which is no longer in business
  Both plants had limited availability to data and troubleshooting capabilities
  Discuss capabilities for retrieving data for new events

## Slide 4: OEM: VARS at 0 MW
Reactive power control methods
  Constant power factor or Var set point
  Controlled PF or VAr via communication
  Autonomous Var control depending on voltage
  Autonomous PF control depending on real power output
Q at Night
  Reactive power at night (optional)
  Reactive power up to 60% of nominal power
  Hardware modification required on older inverters
  Can be retrofitted on existing units
  Inverter switch to Q@night when AC power falls below set point (KW)
IEEE 2800 Standards Vs. ERCOT Nodal: Gap Analysis
Work in progress
Voltage Ride Through
  ERCOT nodal operating guide 2.9.1 has default requirements for Renewable and BESS but IEEE 2800 7.2.2.3 details low and high VRT for wind and solar : Raise to 2800
  Restore output after VRT: Raise to 2800
  Transit overvoltage ride through requirements: Raise to 2800
  Voltage Phase angle ride through: Raise to 2800
  Consecutive voltage ride through: Raise to 2800
Reactive Power
  Raise to 2800 and require VArs at night. But discussion of additional cost of providing VArs at 0 MW.
Voltage Support
  ERCOT exceeds 2800
ACTION: continue gap analysis to be performed on ERCOT rules vs. IEEE 2800

## Slide 5: Priorities and items for next meeting
Continue gap analysis between ERCOT nodal protocols and guide requirements and IEEE2800 Standard. Specifically, we wanted to know where IEEE2800 exceeds ERCOT rules and where both ERCOT and IEEE2800 meet and where ERCOT exceeds IEEE2800 and strategy of adoption IEEE2800
Continuous follow up on RFI on the Odessa event
IBR Ride-Thru failures monthly update
NERC IBRWG update
NPRRs, NOGRRs and PGRRS update
Draft interconnection check list discussion