## Summary
Release Date: May 16, 2022
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Summer 2022
SUMMARY
The ERCOT region is expected to have sufficient installed generating capacity to serve peak demands in the upcoming summer season, June - September 2022, under normal system conditions and most of the reserve capacity risk scenarios examined. This SARA report includes seven risk scenarios reflecting alternative assumptions for peak demand, unplanned thermal outages, and renewable generation output.
With continued economic growth across the state, ERCOT anticipates a summer 2022 peak demand of 77,317 MW, which accounts for load reductions based on an incremental rooftop solar capacity forecast. This would be a new system-wide peak demand record for the region.
ERCOT anticipates there will be 91,392 MW of resource capacity available during summer peak demand hours, which includes 473 MW of planned gas-fired, utility-scale solar and wind capacity. Additionally, ERCOT expects to have 2,035 MW of operational battery storage resources, which includes 283 MW of planned additions. While some of these battery storage resources may help meet customer demand, they are not currently included in ERCOT’s capacity contribution for summer because they are not expected to provide sustained capacity for meeting system peak loads.
A noteworthy development is that several operational generation resources are now classified as Private Use Network (PUN) generators. The aggregate installed capacity for these new PUN units is almost 1,700 MW.
The summer capacity planning reserve margin is forecasted at 22.8%, after accounting for forecasted customer demand, emergency demand reduction programs, typical unplanned outages, and typical renewable output.
Report Design Changes
Beginning with this SARA, ERCOT is including the installed capacity ratings of individual generating units, as well as reporting the aggregate installed capacities of the various resource categories on the 'Forecasted Capacity' tab. Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer.

## Forecasted Capacity
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Summer 2022
Release Date: May 16, 2022
Installed and Summer Capacity Ratings, MW
| Resources, MW | Installed Capacity Rating (see note) | Expected Capacity for Summer Peak Demand
| Thermal Resources, Installed Summer-rated Capacity | 71213.6 | 63514.2 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
| Hydroelectric, Peak Average Capacity Contribution | 563.3 | 475.4044 | Based on 83% of installed capacity for hydro resources (summer season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Switchable Capacity Total | 3840.12 | 3490 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
| Less Switchable Capacity Unavailable to ERCOT | -572.12 | -542 | Based on survey responses of Switchable Resource owners
| Available Mothballed Capacity | 470 | 365 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
| Capacity from Private Use Networks | 11249 | 4262 | Average grid injection during the top 20 summer peak load hours over the last three years, plus the forecasted net change in generation capacity available to the ERCOT grid pursuant to Nodal Protocols Section 10.3.2.4.
| Coastal Wind, Peak Average Capacity Contribution | 5137.7 | 2928.489 | Based on 57% of installed capacity for coastal wind resources (summer season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Panhandle Wind, Peak Average Capacity Contribution | 4244.5 | 1273.35 | Based on 30% of installed capacity for panhandle wind resources (summer season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Other Wind, Peak Average Capacity Contribution | 25811.6 | 5162.32 | Based on 20% of installed capacity for other wind resources (summer season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Solar Utility-Scale, Peak Average Capacity Contribution | 11341.6 | 9140.121 | Based on 81% of rated capacity for solar resources (summer season) per Nodal Protocols Section 3.2.6.2.2
| Storage, Peak Average Capacity Contribution | 1751.93 | 0 | Based on 0% of rated capacity (summer season); resources assumed to provide regulation reserves rather than sustained capacity available to meet peak loads
| RMR Capacity to be under Contract | 0 | 0
| Capacity Pending Retirement | 0 | 0 | Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocols Section 3.14.1.2
| Non-Synchronous Ties, Capacity Contribution | 1220 | 849.974 | Based on net imports during summer 2019 Energy Emergency Alert (EEA) intervals
| Planned Thermal Resources with Signed IA, Air Permits and Adequate Water Supplies | 355.6 | 355.6 | Based on in-service dates provided by developers
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution | 0 | 0 | Based on in-service dates provided by developers and 57% summer capacity contribution for coastal wind resources
| Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution | 0 | 0 | Based on in-service dates provided by developers and 30% summer capacity contribution for panhandle wind resources
| Planned Other Wind with Signed IA, Peak Average Capacity Contribution | 16 | 3.2 | Based on in-service dates provided by developers and 20% summer capacity contribution for other wind resources
| Planned Solar Utility-Scale, Peak Average Capacity Contribution | 141.1 | 114.291 | Based on in-service dates provided by developers and 81% summer capacity contribution for solar resources
| Planned Storage, Peak Average Capacity Contribution | 282.6 | 0 | Based on in-service dates provided by developers and 0% summer capacity contribution for storage resources
[a] Total Resources, MW |  | 137066.53 | 91391.9494
Note on Installed Capacities: Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer.

## Base & Moderate Risk Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Summer 2022
Release Date: May 16, 2022
Base & Moderate Reserve Capacity Risk Scenarios, MW
|  | Forecasted Peak Load / Typical Unplanned Outages / Typical Renewable Output | High Peak Load / Typical Unplanned Outages / Typical Renewable Output | Forecasted Peak Load / High Unplanned Outages / Typical Renewable Output | Forecasted Peak Load / Typical Unplanned Outages / Low Renewable Output
Scenario Adjustments
| [a] Peak Load Forecast (Baseline) | 77884 | 77884 | 77884 | 77884
| [b] Rooftop PV Forecast Reduction, MW | -567 | -567 | -567 | -567
| [c] Adjusted Peak Load Forecast, [a+b] | 77317 | 77317 | 77317 | 77317
| [d] Total Resources (from Forecast Capacity tab) | 91391.9494 | 91391.9494 | 91391.9494 | 91391.9494
Uses of Reserve Capacity
| High Peak Load Adjustment | 0 | 1922 | 0 | 0
| Typical Planned Outages, Thermal | 23.6541 | 23.6541 | 23.6541 | 23.6541
| Typical Unplanned Outages, Thermal | 4080.8915 | 4080.8915 | 4080.8915 | 4080.8915
| High Unplanned Outage Adjustment, Thermal | 0 | 0 | 3985 | 0
| Low Wind Output Reduction | 0 | 0 | 0 | 6489.359
| Low Solar Output Reduction | 0 | 0 | 0 | 2229.412
[d] Total Uses of Reserve Capacity |  | 4104.5456 | 6026.5456 | 8089.5456 | 12823.3166
Capacity Available For Operating Reserves
[e] Capacity Available for Operating Reserves, Normal Operating Conditions (Scenarios tab c-d), MW |  | 9970.4037 | 8048.4037 | 5985.4037 | 1251.6327
Less than 2,300 MW indicates risk of EEA1
[f] EEA Resources deployed by ERCOT |  | 0 | 0 | 0 | 2895
[g] Capacity Available for Operating Reserves, Emergency Conditions (e+f), MW |  | 9970.4037 | 8048.4037 | 5985.4037 | 4146.6327
Less than 1,000 MW indicates risk of EEA3 Load Shed

## Extreme Risk Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Summer 2022
Release Date: May 16, 2022
Extreme Reserve Capacity Risk Scenarios, MW (One or a combination of extreme risk assumptions resulting in low probability, high impact outcomes)
|  | Extreme Peak Load / Typical Unplanned Outages / Typical Renewable Output | Extreme Peak Load / Extreme Unplanned Outages / Typical Renewable Output | High Peak Load / Extreme Unplanned Outages / Extreme Low Wind Output
Scenario Adjustments
| [a] Peak Load Forecast (Baseline) | 77884 | 77884 | 77884
| [b] Rooftop PV Forecast Reduction, MW | -567 | -567 | -567
| [c] Adjusted Peak Load Forecast, [a+b] | 77317 | 77317 | 77317
| [d] Total Resources (from Forecast Capacity tab) | 91391.9494 | 91391.9494 | 91391.9494
Uses of Reserve Capacity
| High/Extreme Peak Load Adjustment | 4250 | 4250 | 1922
| Typical Planned Outages, Thermal | 23.6541 | 23.6541 | 23.6541
| Typical Unplanned Outages, Thermal | 4080.8915 | 4080.8915 | 4080.8915
| Extreme Unplanned Outage Adjustment, Thermal | 0 | 9595 | 9595
| Extreme Low Wind Output Reduction | 0 | 0 | 9104.359
[d] Total Uses of Reserve Capacity |  | 8354.5456 | 17949.5456 | 24725.9046
Capacity Available For Operating Reserves
[e] Capacity Available for Operating Reserves, Normal Operating Conditions (Scenarios tab c-d), MW |  | 5720.4037 | -3874.5963 | -10650.9553
Less than 2,300 MW indicates risk of EEA1
[f] EEA Resources deployed by ERCOT |  | 0 | 2895 | 2895
[g] Capacity Available for Operating Reserves, Emergency Conditions (e+f), MW |  | 5720.4037 | -979.5963 | -7755.9553
Less than 1,000 MW indicates risk of EEA3 Load Shed

## SummerCapacities
Unit Capacities - Summer
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | INSTALLED CAPACITY RATING (MW) | SUMMER CAPACITY (MW)
3 | Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1269 | 1205
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1269 | 1195
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1365 | 1293.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1365 | 1280
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 650 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 615 | 604
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 615 | 599
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 460 | 437
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 555 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 922 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 893 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 956.8 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 893 | 800
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 893 | 805
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 893 | 805
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 916.8 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 916.8 | 855
21 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 430 | 391
22 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 1008 | 932.6
23 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 174.6 | 155
24 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 174.6 | 155
25 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 734.1 | 664
26 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 734.1 | 663
27 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 614.6 | 577
28 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 653.99 | 610
29 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS-CC | SOUTH | 2000 | 195 | 164
30 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS-CC | SOUTH | 2000 | 195 | 164
31 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS-CC | SOUTH | 2000 | 222 | 190
32 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS-GT | NORTH | 1973 | 21 | 18
33 | BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 157
34 | BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 157
35 | BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS-ST | COASTAL | 1974 | 352.8 | 292
36 | BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS-CC | COASTAL | 1976 | 351 | 319
37 | BASTROP ENERGY CENTER CTG 1 | 21INR0541 | BASTEN_GTG1100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 150
38 | BASTROP ENERGY CENTER CTG 2 | 21INR0541 | BASTEN_GTG2100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 150
39 | BASTROP ENERGY CENTER STG | 21INR0541 | BASTEN_ST0100 | BASTROP | GAS-CC | SOUTH | 2002 | 242 | 233
40 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 143
41 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 143
42 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS-CC | NORTH | 2001 | 188.7 | 145
43 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS-CC | NORTH | 2001 | 94.95 | 79.5
44 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS-CC | NORTH | 2009 | 254.15 | 213.5
45 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 149.7
46 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 149.7
47 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS-CC | HOUSTON | 2003 | 275.57 | 257.9
48 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS-CC | WEST | 1987 | 75 | 75
49 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS-CC | WEST | 1987 | 75 | 75
50 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS-CC | WEST | 1988 | 62 | 70
51 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 44
52 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 44
53 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 44
54 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 44
55 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 163
56 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 163
57 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 178
58 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS-ST | HOUSTON | 1970 | 765 | 745
59 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS-ST | HOUSTON | 1972 | 765 | 749
60 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 79.9
61 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 71.9
62 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 78.9
63 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 72.9
64 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS-CC | SOUTH | 2007 | 105 | 102
65 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS-CC | SOUTH | 2008 | 108.8 | 107
66 | COLORADO BEND II CTG 7 | 18INR0077 | CBECII_CT7 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 329.3
67 | COLORADO BEND II CTG 8 | 18INR0077 | CBECII_CT8 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 335
68 | COLORADO BEND II STG 9 | 18INR0077 | CBECII_STG9 | WHARTON | GAS-CC | SOUTH | 2017 | 508.5 | 478.4
69 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS-CC | HOUSTON | 2008 | 192.1 | 169
70 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS-CC | HOUSTON | 2008 | 192.1 | 165
71 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS-CC | HOUSTON | 2008 | 192.1 | 165
72 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS-CC | HOUSTON | 2008 | 150 | 144
73 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS-GT | NORTH | 2004 | 48 | 45
74 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS-GT | NORTH | 2010 | 50 | 47
75 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS-ST | NORTH | 1978 | 120 | 107
76 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 48
77 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 48
78 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 48
79 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 48
80 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 69
81 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 69
82 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 68
83 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 69
84 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 172
85 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 182
86 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 172
87 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 182
88 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS-CC | HOUSTON | 2014 | 199 | 156
89 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS-CC | HOUSTON | 2002 | 274.5 | 287
90 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
91 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
92 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
93 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
94 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 147
95 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 147
96 | ELK STATION IC 3 |  | AEEC_ELK_3 | HALE | GAS-IC | PANHANDLE | 2016 | 202 | 190
97 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 204
98 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS-CC | NORTH | 2002 | 140 | 115
99 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36
100 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36
101 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36
102 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36
103 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 169
104 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 169
105 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS-CC | SOUTH | 2014 | 204 | 182
106 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 165
107 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 157
108 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 157
109 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 165
110 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 157
111 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 157
112 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 406
113 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 406
114 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 147
115 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 147
116 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 145
117 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 145
118 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 169
119 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 168
120 | FRIENDSWOOD G CTG 1 (FORMERLY TEJAS POWER GENERATION) |  | FEGC_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2018 | 129 | 119
121 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS-ST | WEST | 1960 | 225 | 239
122 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 387 | 390
123 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 56
124 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 56
125 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 56
126 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 50
127 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 56
128 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 56
129 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
130 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
131 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
132 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 143
133 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 143
134 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 141
135 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 141
136 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 198
137 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 198
138 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS-ST | NORTH | 1963 | 395 | 395
139 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS-ST | NORTH | 1976 | 435 | 435
140 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS-ST | NORTH | 1977 | 435 | 435
141 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 210
142 | HAYS ENERGY FACILITY CSG 2 | 22INR0586 | HAYSEN_HAYSENG2 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 211
143 | HAYS ENERGY FACILITY CSG 3 | 21INR0527 | HAYSEN_HAYSENG3 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 210
144 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 213
145 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 149
146 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 149
147 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS-CC | SOUTH | 2000 | 198.05 | 168
148 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 150
149 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 150
150 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 158
151 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 158
152 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS-CC | NORTH | 2006 | 320.6 | 289
153 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS-CC | NORTH | 2011 | 320.6 | 295
154 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS-CC | NORTH | 1997 | 185 | 163
155 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS-CC | NORTH | 1997 | 107 | 106
156 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS-ST | NORTH | 1970 | 397 | 392
157 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS-ST | NORTH | 1973 | 531 | 523
158 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 153
159 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 145
160 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 145
161 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 153
162 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204
163 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204
164 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 90.1
165 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 87.3
166 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
167 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
168 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
169 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
170 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 170
171 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 170
172 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS-CC | SOUTH | 2001 | 204 | 188
173 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 215
174 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 215
175 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS-CC | SOUTH | 2001 | 258.4 | 236
176 | MIDLOTHIAN ENERGY FACILITY CTG 1 |  | MDANP_CT1 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 229
177 | MIDLOTHIAN ENERGY FACILITY CTG 2 | 21INR0534 | MDANP_CT2 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 227
178 | MIDLOTHIAN ENERGY FACILITY CTG 3 | 22INR0543 | MDANP_CT3 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 227
179 | MIDLOTHIAN ENERGY FACILITY CTG 4 | 22INR0523 | MDANP_CT4 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 227
180 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 241
181 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 243
182 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 66
183 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 65
184 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 65
185 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67
186 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67
187 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67
188 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS-ST | NORTH | 1956 | 122 | 122
189 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS-ST | NORTH | 1958 | 118 | 118
190 | MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | DALLAS | GAS-ST | NORTH | 1967 | 568 | 568
191 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 157
192 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 157
193 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS-CC | COASTAL | 1972 | 351 | 319
194 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS-ST | SOUTH | 1972 | 445 | 420
195 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS-ST | SOUTH | 1974 | 435 | 410
196 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS-CC | WEST | 2001 | 176 | 166.7
197 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS-CC | WEST | 2001 | 176 | 158.2
198 | ODESSA-ECTOR POWER CTG 21 | 20INR0282 | OECCS_CT21 | ECTOR | GAS-CC | WEST | 2001 | 176 | 166.7
199 | ODESSA-ECTOR POWER CTG 22 | 20INR0282 | OECCS_CT22 | ECTOR | GAS-CC | WEST | 2001 | 176 | 158.2
200 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS-CC | WEST | 2001 | 224 | 206
201 | ODESSA-ECTOR POWER STG 2 | 20INR0282 | OECCS_UNIT2 | ECTOR | GAS-CC | WEST | 2001 | 224 | 206
202 | OLD BLOOMINGTON ROAD CTG 1 (VICTORIA PORT 2) |  | VICTPRT2_UNIT1 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 44
203 | OLD BLOOMINGTON ROAD CTG 2 (VICTORIA PORT 2) |  | VICTPRT2_UNIT2 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 44
204 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 199
205 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 199
206 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS-CC | NORTH | 2014 | 353.1 | 287
207 | PANDA TEMPLE I POWER CTG 1 | 22INR0533 | PANDA_T1_TMPL1CT1 | BELL | GAS-CC | NORTH | 2014 | 232 | 223
208 | PANDA TEMPLE I POWER CTG 2 | 22INR0533 | PANDA_T1_TMPL1CT2 | BELL | GAS-CC | NORTH | 2014 | 232 | 220
209 | PANDA TEMPLE I POWER STG 1 | 22INR0533 | PANDA_T1_TMPL1ST1 | BELL | GAS-CC | NORTH | 2014 | 353.1 | 326
210 | PANDA TEMPLE II POWER CTG 1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS-CC | NORTH | 2015 | 232 | 191.2
211 | PANDA TEMPLE II POWER CTG 2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS-CC | NORTH | 2015 | 232 | 191.2
212 | PANDA TEMPLE II POWER STG 1 |  | PANDA_T2_TMPL2ST1 | BELL | GAS-CC | NORTH | 2015 | 353.1 | 334.7
213 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 76
214 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 76
215 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS-CC | NORTH | 1990 | 90 | 87
216 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 164.5
217 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 164.5
218 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS-CC | HOUSTON | 2000 | 195.5 | 170.4
219 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
220 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
221 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
222 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
223 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS-GT | WEST | 1988 | 89.4 | 63
224 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS-GT | WEST | 1988 | 89.4 | 64
225 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS-GT | WEST | 1988 | 89.4 | 64
226 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS-GT | WEST | 1990 | 89.4 | 64
227 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS-GT | WEST | 1990 | 89.4 | 65
228 | PROENERGY SOUTH 1 (PES1) CTG 1 |  | PRO_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
229 | PROENERGY SOUTH 1 (PES1) CTG 2 |  | PRO_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
230 | PROENERGY SOUTH 1 (PES1) CTG 3 |  | PRO_UNIT3 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
231 | PROENERGY SOUTH 1 (PES1) CTG 4 |  | PRO_UNIT4 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
232 | PROENERGY SOUTH 1 (PES1) CTG 5 |  | PRO_UNIT5 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
233 | PROENERGY SOUTH 1 (PES1) CTG 6 |  | PRO_UNIT6 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
234 | PROENERGY SOUTH 2 (PES2) CTG 7 |  | PRO_UNIT7 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
235 | PROENERGY SOUTH 2 (PES2) CTG 8 |  | PRO_UNIT8 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
236 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 59
237 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 61
238 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 49
239 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 54
240 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 54
241 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 52
242 | POWERLANE PLANT STG 1 |  | STEAM1A_STEAM_1 | HUNT | GAS-ST | NORTH | 1966 | 18.75 | 17.5
243 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS-ST | NORTH | 1967 | 25 | 23.5
244 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS-ST | NORTH | 1978 | 43.2 | 39.5
245 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 74
246 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 74
247 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 72
248 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 72
249 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS-CC | WEST | 2007 | 98.1 | 98
250 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS-CC | WEST | 2008 | 98.1 | 98
251 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS-GT | NORTH | 1994 | 115.25 | 100
252 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS-GT | NORTH | 1994 | 115.25 | 100
253 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS-ST | NORTH | 1968 | 74.98 | 70
254 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS-ST | NORTH | 1972 | 113.61 | 118
255 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS-ST | NORTH | 1975 | 216.01 | 208
256 | RABBS POWER STATION (UNITS 3-5) |  | RAB_UNIT3 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6
257 | RABBS POWER STATION (UNITS 3-5) |  | RAB_UNIT4 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6
258 | RABBS POWER STATION (UNITS 3-5) |  | RAB_UNIT5 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6
259 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS-GT | NORTH | 2001 | 88.4 | 80
260 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS-ST | NORTH | 1971 | 113.64 | 107
261 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS-ST | NORTH | 1975 | 156.6 | 146
262 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
263 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
264 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
265 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
266 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 158
267 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 158
268 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 158
269 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 373.16 | 303
270 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50
271 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50
272 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50
273 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS-CC | SOUTH | 2003 | 41.98 | 40
274 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 80
275 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 80
276 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
277 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
278 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
279 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
280 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS-CC | SOUTH | 2004 | 198.9 | 142
281 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 47
282 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 47
283 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS-CC | SOUTH | 2004 | 191 | 139
284 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS-GT | COASTAL | 2004 | 60.5 | 46
285 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS-CC | COASTAL | 1996 | 50 | 38
286 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS-CC | COASTAL | 1962 | 25 | 20
287 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS-ST | SOUTH | 1965 | 136 | 130
288 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS-ST | SOUTH | 1968 | 136 | 135
289 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS-ST | SOUTH | 1972 | 351 | 336
290 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS-IC | SOUTH | 2016 | 25.71 | 26.7
291 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS-IC | SOUTH | 2016 | 25.71 | 26.7
292 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS-ST | NORTH | 1966 | 61 | 57
293 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS-ST | NORTH | 1973 | 65 | 61
294 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS-ST | NORTH | 1958 | 177 | 167
295 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS-ST | NORTH | 1965 | 479 | 502
296 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS-GT | HOUSTON | 1967 | 16.32 | 14
297 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54
298 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54
299 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54
300 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54
301 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54
302 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54
303 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS-CC | HOUSTON | 1974 | 62 | 54
304 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS-CC | HOUSTON | 1974 | 62 | 54
305 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56
306 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56
307 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56
308 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56
309 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56
310 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56
311 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110
312 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110
313 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 80.3
314 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 80.3
315 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 80.3
316 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS-CC | HOUSTON | 2000 | 143.65 | 124.9
317 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS-ST | NORTH | 1965 | 239 | 235
318 | TOPAZ POWER PLANT U1 |  | TOPAZ_UNIT1 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
319 | TOPAZ POWER PLANT U2 |  | TOPAZ_UNIT2 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
320 | TOPAZ POWER PLANT U3 |  | TOPAZ_UNIT3 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
321 | TOPAZ POWER PLANT U4 |  | TOPAZ_UNIT4 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
322 | TOPAZ POWER PLANT U5 |  | TOPAZ_UNIT5 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
323 | TOPAZ POWER PLANT U6 |  | TOPAZ_UNIT6 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
324 | TOPAZ POWER PLANT U7 |  | TOPAZ_UNIT7 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
325 | TOPAZ POWER PLANT U8 |  | TOPAZ_UNIT8 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
326 | TOPAZ POWER PLANT U9 |  | TOPAZ_UNIT9 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
327 | TOPAZ POWER PLANT U10 |  | TOPAZ_UNIT10 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5
328 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
329 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
330 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
331 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 47
332 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS-ST | SOUTH | 1966 | 225 | 217
333 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS-ST | SOUTH | 1968 | 240 | 230
334 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS-ST | SOUTH | 1970 | 420 | 412
335 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 44
336 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 44
337 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 44
338 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 44
339 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS-CC | SOUTH | 2009 | 196.86 | 160
340 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS-CC | SOUTH | 2009 | 180.2 | 125
341 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 16.32 | 13
342 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169
343 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169
344 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 299.2 | 240
345 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 580.5 | 527
346 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
347 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
348 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
349 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS-CC | WEST | 1987 | 20 | 17
350 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
351 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
352 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
353 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
354 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS-CC | NORTH | 2004 | 275 | 241.4
355 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS-CC | NORTH | 2004 | 275 | 241.4
356 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS-CC | NORTH | 2004 | 290 | 298
357 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 238.5
358 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 230.5
359 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS-CC | NORTH | 2002 | 300 | 268
360 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 116.45 | 105
361 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8 | 9.8
362 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6
363 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2 | 3.2
364 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4 | 4
365 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2 | 4.2
366 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4
367 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2
368 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4
369 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2
370 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8
371 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 70937.88 | 63325.4
372
373 | Operational Resources - Synchronized but not Approved for Commercial Operations (Thermal)
374 | BRANDON (LP&L) (DGR) | 21INR0201 | BRANDON_UNIT1 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 25 | 20
375 | R MASSENGALE CTG 1 (LP&L) | 21INR0202 | MASSENGL_G6 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18
376 | R MASSENGALE CTG 2 (LP&L) | 21INR0202 | MASSENGL_G7 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18
377 | R MASSENGALE STG (LP&L) | 21INR0202 | MASSENGL_G8 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 58.9 | 38
378 | RABBS POWER STATION (UNITS 6-8) | 22INR0597 | RAB_UNIT6 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6
379 | RABBS POWER STATION (UNITS 6-8) | 22INR0597 | RAB_UNIT7 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6
380 | RABBS POWER STATION (UNITS 6-8) | 22INR0597 | RAB_UNIT8 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6
381 | TY COOKE CTG 1 (LP&L) | 21INR0506 | TY_COOKE_GT2 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 18.7 | 14
382 | TY COOKE CTG 2 (LP&L) | 21INR0506 | TY_COOKE_GT3 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 26.6 | 17
383 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 350.7 | 258.8
384
385 | Operational Capacity Thermal Unavailable due to Extended Outage or Derate |  | THERMAL_UNAVAIL |  |  |  |  | -74.98 | -70
386 | Operational Capacity Thermal Total |  | THERMAL_OPERATIONAL |  |  |  |  | 71213.6 | 63514.2
387
388 | Operational Resources (Hydro)
389 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 34.7 | 37.9
390 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 34.7 | 37.9
391 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 8
392 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 9
393 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16
394 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16
395 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 18.3 | 17
396 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 50.8 | 49.5
397 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 50.8 | 49.5
398 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6 | 9.6
399 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12
400 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12
401 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12
402 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 27 | 29
403 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 27 | 29
404 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6 | 6
405 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 15 | 14
406 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 19.8 | 21
407 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 19.8 | 20
408 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
409 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
410 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
411 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 21 | 22
412 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 21 | 22
413 | Operational Capacity Total (Hydro) | [6 empty] | 549.6 | 557.4
414 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 549.6 | 464
415
416 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
417 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4 | 1.4
418 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8 | 4.8
419 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7 | 7.7
420 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6 | 3.6
421 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2 | 2.2
422 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 19.7 | 19.7
423 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) |  | DG_HYDRO_CAP_CONT |  |  |  |  | 19.7 | 16.399
424
425 | Operational Capacity Hydroelectric Unavailable due to Extended Outage or Derate |  | HYDRO_UNAVAIL |  |  |  |  | -6 | -4.9946
426 | Operational Capacity Hydroelectric Total |  | HYDRO_OPERATIONAL |  |  |  |  | 563.3 | 475.4044
427
428 | Operational Resources (Switchable)
429 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 54
430 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 54
431 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 54
432 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 190
433 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 190
434 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 160
435 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 160
436 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 160
437 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS-CC | NORTH | 2000 | 400 | 400
438 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 179 | 156
439 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179 | 135
440 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 179 | 153
441 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 400 | 402
442 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 151
443 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 148
444 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS-CC | NORTH | 2003 | 318 | 310
445 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 150
446 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 152
447 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 318 | 311
448 | Switchable Capacity Total | [6 empty] | 3840.12 | 3490
449
450 | Switchable Capacity Unavailable to ERCOT
451 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56.04 | -54
452 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56.04 | -54
453 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56.04 | -54
454 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -202 | -190
455 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -202 | -190
456 | Switchable Capacity Unavailable to ERCOT Total | [6 empty] | -572.12 | -542
457
458 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  |  |  |  | 470 | 365
459
460 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 11249 | 4407
461 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  |  | -145
462
463 | Operational Resources (Wind)
464 | WESTERN TRAIL WIND (AJAX WIND) |  | AJAXWIND_UNIT1 | WILBARGER | WIND-O | WEST | 2022 | 225.6 | 225.6
465 | WESTERN TRAIL WIND (AJAX WIND) U2 |  | AJAXWIND_UNIT2 | WILBARGER | WIND-O | WEST | 2022 | 141 | 141
466 | AMADEUS WIND 1 U1 |  | AMADEUS1_UNIT1 | FISHER | WIND-O | WEST | 2021 | 36.7 | 36.7
467 | AMADEUS WIND 1 U2 |  | AMADEUS1_UNIT2 | FISHER | WIND-O | WEST | 2021 | 35.8 | 35.8
468 | AMADEUS WIND 2 U1 |  | AMADEUS2_UNIT3 | FISHER | WIND-O | WEST | 2021 | 177.7 | 177.7
469 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.83 | 99.8
470 | AVIATOR WIND U1 |  | AVIATOR_UNIT1 | COKE | WIND-O | WEST | 2021 | 180.12 | 180.1
471 | AVIATOR WIND U2 |  | AVIATOR_UNIT2 | COKE | WIND-O | WEST | 2021 | 145.64 | 145.6
472 | AVIATOR WIND U3 |  | DEWOLF_UNIT1 | COKE | WIND-O | WEST | 2021 | 199.26 | 199.3
473 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100 | 100
474 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102 | 102
475 | BARROW RANCH (JUMBO HILL WIND) 1 |  | BARROW_UNIT1 | ANDREWS | WIND-O | WEST | 2021 | 90.2 | 90.2
476 | BARROW RANCH (JUMBO HILL WIND) 2 |  | BARROW_UNIT2 | ANDREWS | WIND-O | WEST | 2021 | 70.5 | 70.5
477 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120 | 120
478 | BLUE SUMMIT WIND 1 A | 22INR0550 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 9 | 8.8
479 | BLUE SUMMIT WIND 1 B | 22INR0550 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 126.4 | 124.3
480 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 92.5 | 89.7
481 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 6.86 | 6.7
482 | BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WILBARGER | WIND-O | WEST | 2020 | 13.7 | 13.4
483 | BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WILBARGER | WIND-O | WEST | 2020 | 186.5 | 182.4
484 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2020 | 162 | 162
485 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.85 | 149.8
486 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120 | 120
487 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108 | 108
488 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9 | 44.9
489 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7 | 55.7
490 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6 | 120.6
491 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5 | 115.5
492 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117 | 117
493 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2 | 170.2
494 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 89 | 88
495 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 91 | 90
496 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2 | 115.2
497 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4 | 122.4
498 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 123.1 | 123.1
499 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165 | 165
500 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 134.42 | 130.5
501 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 123.6 | 120
502 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1 | 210.1
503 | CAPRICORN RIDGE WIND 1 | 17INR0054 | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 231.7 | 231.7
504 | CAPRICORN RIDGE WIND 2 | 17INR0054 | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5 | 149.5
505 | CAPRICORN RIDGE WIND 3 | 17INR0054 | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 200.9 | 200.9
506 | CAPRICORN RIDGE WIND 4 | 17INR0061 | CAPRIDG4_CR4 | STERLING | WIND-O | WEST | 2008 | 121.5 | 121.5
507 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 75 | 75
508 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 75 | 75
509 | CHALUPA WIND |  | CHALUPA_UNIT1 | CAMERON | WIND-C | COASTAL | 2021 | 173.25 | 173.3
510 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5 | 126.5
511 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6 | 150.6
512 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4 | 98.4
513 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4 | 50.4
514 | CRANELL WIND |  | CRANELL_UNIT1 | REFUGIO | WIND-C | COASTAL | 2022 | 220 | 220
515 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5
516 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5
517 | DESERT SKY WIND 1 A |  | DSKYWND1_UNIT_1A | PECOS | WIND-O | WEST | 2022 | 65.79 | 64.5
518 | DESERT SKY WIND 2 A |  | DSKYWND1_UNIT_1B | PECOS | WIND-O | WEST | 2022 | 23.93 | 23.4
519 | DESERT SKY WIND 1 B |  | DSKYWND2_UNIT_2A | PECOS | WIND-O | WEST | 2022 | 65.79 | 64.5
520 | DESERT SKY WIND 2 B |  | DSKYWND2_UNIT_2B | PECOS | WIND-O | WEST | 2022 | 14.74 | 14.4
521 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2
522 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2
523 | EAST RAYMOND WIND (EL RAYO) U1 |  | EL_RAYO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 101.2 | 98
524 | EAST RAYMOND WIND (EL RAYO) U2 |  | EL_RAYO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 99 | 96
525 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 121.9 | 121.9
526 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2017 | 101.31 | 98.9
527 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2017 | 134.29 | 131.1
528 | ESPIRITU WIND |  | CHALUPA_UNIT2 | CAMERON | WIND-C | COASTAL | 2021 | 25.2 | 25.2
529 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200 | 200
530 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8 | 79.8
531 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6 | 75.6
532 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.48 | 186.5
533 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8 | 163.8
534 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2 | 124.2
535 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80 | 80
536 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6 | 69.6
537 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6 | 148.6
538 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82 | 82
539 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76 | 76
540 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4 | 107.4
541 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8 | 103.8
542 | GREEN MOUNTAIN WIND (BRAZOS) U1 | 21INR0532 | BRAZ_WND_WND1 | SCURRY | WIND-O | WEST | 2003 | 99 | 99
543 | GREEN MOUNTAIN WIND (BRAZOS) U2 | 21INR0532 | BRAZ_WND_WND2 | SCURRY | WIND-O | WEST | 2003 | 61 | 61
544 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150
545 | GRIFFIN TRAIL WIND U1 |  | GRIF_TRL_UNIT1 | KNOX | WIND-O | WEST | 2021 | 98.7 | 98.7
546 | GRIFFIN TRAIL WIND U2 |  | GRIF_TRL_UNIT2 | KNOX | WIND-O | WEST | 2021 | 126.9 | 126.9
547 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6
548 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6
549 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.93 | 119.9
550 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 165.6 | 163.5
551 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9 | 9
552 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 99.9 | 99.9
553 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 100 | 100
554 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REAGAN | WIND-O | WEST | 2018 | 152.5 | 152.5
555 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REAGAN | WIND-O | WEST | 2018 | 147.5 | 147.5
556 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52 | 52
557 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98 | 98
558 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100 | 100
559 | HIDALGO II WIND |  | MIRASOLE_MIR13 | HIDALGO | WIND-O | SOUTH | 2021 | 50.4 | 50.4
560 | HIGH LONESOME W 1A |  | HI_LONE_WGR1A | CROCKETT | WIND-O | WEST | 2021 | 46 | 46
561 | HIGH LONESOME W 1B |  | HI_LONE_WGR1B | CROCKETT | WIND-O | WEST | 2021 | 51.9 | 52
562 | HIGH LONESOME W 1C |  | HI_LONE_WGR1C | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3
563 | HIGH LONESOME W 2 |  | HI_LONE_WGR2 | CROCKETT | WIND-O | WEST | 2021 | 122.4 | 122.5
564 | HIGH LONESOME W 2A |  | HI_LONE_WGR2A | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3
565 | HIGH LONESOME W 3 |  | HI_LONE_WGR3 | CROCKETT | WIND-O | WEST | 2021 | 127.5 | 127.6
566 | HIGH LONESOME W 4 |  | HI_LONE_WGR4 | CROCKETT | WIND-O | WEST | 2021 | 101.5 | 101.6
567 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 134.81 | 131.1
568 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 101.69 | 98.9
569 | HORSE HOLLOW WIND 1 | 17INR0052 | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230 | 230
570 | HORSE HOLLOW WIND 2 | 17INR0053 | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184 | 184
571 | HORSE HOLLOW WIND 3 | 17INR0053 | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4 | 241.4
572 | HORSE HOLLOW WIND 4 | 17INR0053 | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115 | 115
573 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95 | 95
574 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102 | 102
575 | INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.8 | 91.8
576 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.69 | 19.7
577 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230 | 230
578 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96 | 96
579 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74 | 74
580 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30 | 30
581 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.15 | 146.2
582 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.55 | 153.6
583 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3
584 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3
585 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.42 | 100.4
586 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2015 | 110 | 110
587 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 159.96 | 160
588 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7 | 183.7
589 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.26 | 106.3
590 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.85 | 103.8
591 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194 | 194
592 | LONE STAR WIND 2 (POST OAK) U1 | 22INR0479 | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98 | 98
593 | LONE STAR WIND 2 (POST OAK) U2 | 22INR0479 | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100 | 100
594 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100
595 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100
596 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 48 | 48
597 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51 | 51
598 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5 | 25.5
599 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24 | 24
600 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200 | 200
601 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200 | 200
602 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110 | 110
603 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1 | 200.1
604 | LOS VIENTOS WIND II |  | LV2_LV2 | WILLACY | WIND-C | COASTAL | 2013 | 201.6 | 201.6
605 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.83 | 99.8
606 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.46 | 103.5
607 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2
608 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2
609 | MAVERICK CREEK WIND WEST U1 |  | MAVCRK_W_UNIT1 | CONCHO | WIND-O | WEST | 2022 | 201.6 | 201.6
610 | MAVERICK CREEK WIND WEST U2 |  | MAVCRK_W_UNIT2 | CONCHO | WIND-O | WEST | 2022 | 11.1 | 11.1
611 | MAVERICK CREEK WIND WEST U3 |  | MAVCRK_W_UNIT3 | CONCHO | WIND-O | WEST | 2022 | 33.6 | 33.6
612 | MAVERICK CREEK WIND WEST U4 |  | MAVCRK_W_UNIT4 | CONCHO | WIND-O | WEST | 2022 | 22.2 | 22.2
613 | MAVERICK CREEK WIND EAST U1 |  | MAVCRK_E_UNIT5 | CONCHO | WIND-O | WEST | 2022 | 71.4 | 71.4
614 | MAVERICK CREEK WIND EAST U2 |  | MAVCRK_E_UNIT6 | CONCHO | WIND-O | WEST | 2022 | 33.3 | 33.3
615 | MAVERICK CREEK WIND EAST U3 |  | MAVCRK_E_UNIT7 | CONCHO | WIND-O | WEST | 2022 | 22 | 22
616 | MAVERICK CREEK WIND EAST U4 |  | MAVCRK_E_UNIT8 | CONCHO | WIND-O | WEST | 2022 | 20 | 20
617 | MAVERICK CREEK WIND EAST U5 |  | MAVCRK_E_UNIT9 | CONCHO | WIND-O | WEST | 2022 | 76.8 | 76.8
618 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150 | 150
619 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6
620 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6
621 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3
622 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3
623 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8 | 162.8
624 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2018 | 196.6 | 196.6
625 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.61 | 92.6
626 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60 | 60
627 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 58.8 | 58.8
628 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2 | 151.2
629 | OVEJA WIND U1 |  | OVEJA_G1 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2
630 | OVEJA WIND U2 |  | OVEJA_G2 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2
631 | PALMAS ALTAS WIND |  | PALMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2020 | 144.9 | 144.9
632 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2
633 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2
634 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.19 | 94.2
635 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6 | 96.6
636 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5 | 142.5
637 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5 | 115.5
638 | PANTHER CREEK WIND 3 A |  | PC_SOUTH_PANTH31 | HOWARD | WIND-O | WEST | 2022 | 106.92 | 106.9
639 | PANTHER CREEK WIND 3 B |  | PC_SOUTH_PANTH32 | HOWARD | WIND-O | WEST | 2022 | 108.54 | 108.5
640 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.85 | 179.9
641 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.12 | 200.1
642 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 91.7 | 91.7
643 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86 | 85.8
644 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8 | 160.8
645 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6 | 141.6
646 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8 | 100.8
647 | PEYTON CREEK WIND |  | PEY_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2 | 151.2
648 | PYRON WIND 1 |  | PYR_PYRON1 | NOLAN | WIND-O | WEST | 2008 | 121.5 | 121.5
649 | PYRON WIND 2 |  | PYR_PYRON2 | NOLAN | WIND-O | WEST | 2008 | 127.5 | 127.5
650 | RANCHERO WIND |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150
651 | RANCHERO WIND |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150
652 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 104.26 | 104.3
653 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 102.99 | 103
654 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6 | 89.6
655 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9 | 121.9
656 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.44 | 27.4
657 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114 | 114
658 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95 | 95
659 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150 | 150
660 | RTS 2 WIND (HEART OF TEXAS WIND) U1 |  | RTS2_U1 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9
661 | RTS 2 WIND (HEART OF TEXAS WIND) U2 |  | RTS2_U2 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9
662 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160 | 160
663 | SAGE DRAW WIND U1 |  | SAGEDRAW_UNIT1 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2
664 | SAGE DRAW WIND U2 |  | SAGEDRAW_UNIT2 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2
665 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64 | 64
666 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110 | 110
667 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.25 | 95.2
668 | SAND BLUFF WIND | 20INR0296 | MCDLD_SBW1 | GLASSCOCK | WIND-O | WEST | 2008 | 90 | 90
669 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150 | 150
670 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 78 | 78
671 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.24 | 30.2
672 | SHAFFER (PATRIOT WIND/PETRONILLA) |  | SHAFFER_UNIT1 | NUECES | WIND-C | COASTAL | 2021 | 226.05 | 226.1
673 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1 | 204.1
674 | SHERBINO 2 WIND | 19INR0120 | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2011 | 132 | 132
675 | SILVER STAR WIND | 18INR0064 | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8 | 52.8
676 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102 | 102
677 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98 | 98
678 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5 | 148.5
679 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8 | 151.8
680 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 101.2 | 98.2
681 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 160.95 | 161
682 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98 | 98
683 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96 | 96
684 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 123.6 | 120
685 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201 | 201
686 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 213.82 | 211.2
687 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 166.52 | 164.7
688 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 37.5 | 42.5
689 | SWEETWATER WIND 2A | 17INR0068 | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16 | 16.8
690 | SWEETWATER WIND 2B | 17INR0068 | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 105.3 | 110.8
691 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 30.78 | 33.6
692 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 108.54 | 118.6
693 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 119 | 125
694 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 105.8 | 112
695 | SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | NOLAN | WIND-O | WEST | 2007 | 80.5 | 85
696 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150 | 150
697 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150 | 150
698 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.72 | 27.7
699 | TEXAS BIG SPRING WIND B |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6 | 6.6
700 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150 | 150
701 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23 | 23
702 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5 | 127.5
703 | TRENT WIND 1 A | 17INR0069 | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 38.25 | 38.3
704 | TRENT WIND 1 B |  | TRENT_UNIT_1B | NOLAN | WIND-O | WEST | 2018 | 15.59 | 15.6
705 | TRENT WIND 2 |  | TRENT_UNIT_2 | NOLAN | WIND-O | WEST | 2018 | 50.49 | 50.5
706 | TRENT WIND 3 A |  | TRENT_UNIT_3A | NOLAN | WIND-O | WEST | 2018 | 38.25 | 38.3
707 | TRENT WIND 3 B |  | TRENT_UNIT_3B | NOLAN | WIND-O | WEST | 2018 | 13.79 | 13.8
708 | TRINITY HILLS WIND 1 | 20INR0019 | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4 | 103.4
709 | TRINITY HILLS WIND 2 | 20INR0019 | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6 | 94.6
710 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2 | 2
711 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 174.6 | 169.5
712 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2017 | 125.6 | 125.6
713 | VENADO WIND U1 |  | VENADO_UNIT1 | ZAPATA | WIND-O | SOUTH | 2021 | 105 | 105
714 | VENADO WIND U2 |  | VENADO_UNIT2 | ZAPATA | WIND-O | SOUTH | 2021 | 96.6 | 96.6
715 | VERA WIND 1 |  | VERAWIND_UNIT1 | KNOX | WIND-O | WEST | 2021 | 12 | 12
716 | VERA WIND 2 |  | VERAWIND_UNIT2 | KNOX | WIND-O | WEST | 2021 | 7.2 | 7.2
717 | VERA WIND 3 |  | VERAWIND_UNIT3 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8
718 | VERA WIND 4 |  | VERAWIND_UNIT4 | KNOX | WIND-O | WEST | 2021 | 22 | 22
719 | VERA WIND 5 |  | VERAWIND_UNIT5 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8
720 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150
721 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.91 | 114.9
722 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.35 | 142.3
723 | WEST RAYMOND (EL TRUENO) WIND U1 |  | TRUENO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 116.6 | 116.6
724 | WEST RAYMOND (EL TRUENO) WIND U2 |  | TRUENO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 123.2 | 123.2
725 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 59.8 | 57
726 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.34 | 92.3
727 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125 | 125
728 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125 | 125
729 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5 | 199.5
730 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.62 | 67.6
731 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30 | 30
732 | WOLF RIDGE WIND | 21INR0511 | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 112.5 | 112.5
733 | Operational Capacity Total (Wind) | [6 empty] | 29418.88 | 29398
734
735 | Operational Wind Capacity Sub-total (Coastal Counties) |  | WIND_OPERATIONAL_C |  |  |  |  | 4664.9 | 4664.9
736 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 100 | 57
737
738 | Operational Wind Capacity Sub-total (Panhandle Counties) |  | WIND_OPERATIONAL_P |  |  |  |  | 4244.5 | 4244.5
739 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PEAK_PCT_P | % |  |  |  | 100 | 30
740
741 | Operational Wind Capacity Sub-total (Other Counties) |  | WIND_OPERATIONAL_O |  |  |  |  | 20488.6 | 20488.6
742 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PEAK_PCT_O | % |  |  |  | 100 | 20
743
744 | Operational Resources (Wind) - Synchronized but not Approved for Commercial Operations
745 | ANCHOR WIND I | 21INR0387 | ANCHOR_WIND2 | EASTLAND | WIND-O | WEST | 2022 | 98.9 | 98.9
746 | ANCHOR WIND II | 21INR0539 | ANCHOR_WIND3 | EASTLAND | WIND-O | WEST | 2022 | 90 | 90
747 | ANCHOR WIND II B | 21INR0539 | ANCHOR_WIND4 | EASTLAND | WIND-O | WEST | 2022 | 38.7 | 38.7
748 | ANCHOR WIND IV | 22INR0562 | ANCHOR_WIND5 | EASTLAND | WIND-O | NORTH | 2022 | 19.3 | 19.3
749 | APOGEE WIND U1 | 21INR0467 | APOGEE_UNIT1 | THROCKMORTON | WIND-O | WEST | 2022 | 25 | 25
750 | APOGEE WIND U2 | 21INR0467 | APOGEE_UNIT2 | THROCKMORTON | WIND-O | WEST | 2022 | 14 | 14
751 | APOGEE WIND U3 | 21INR0467 | APOGEE_UNIT3 | THROCKMORTON | WIND-O | WEST | 2022 | 30.2 | 30.2
752 | APOGEE WIND U4 | 21INR0467 | APOGEE_UNIT4 | THROCKMORTON | WIND-O | WEST | 2022 | 115 | 115
753 | APOGEE WIND U5 | 21INR0467 | APOGEE_UNIT5 | THROCKMORTON | WIND-O | WEST | 2022 | 110 | 110
754 | APOGEE WIND U6 | 21INR0467 | APOGEE_UNIT6 | THROCKMORTON | WIND-O | WEST | 2022 | 24 | 24
755 | APOGEE WIND U7 | 21INR0467 | APOGEE_UNIT7 | THROCKMORTON | WIND-O | WEST | 2022 | 75 | 75
756 | AQUILLA LAKE WIND U1 | 19INR0145 | AQUILLA_U1_23 | HILL | WIND-O | NORTH | 2022 | 13.9 | 13.9
757 | AQUILLA LAKE WIND U2 | 19INR0145 | AQUILLA_U1_28 | HILL | WIND-O | NORTH | 2022 | 135.4 | 135.4
758 | AQUILLA LAKE 2 WIND | 20INR0256 | AQUILLA_U2_23 | HILL | WIND-O | NORTH | 2022 | 7 | 7
759 | AQUILLA LAKE 2 WIND U2 | 20INR0256 | AQUILLA_U2_28 | HILL | WIND-O | NORTH | 2022 | 143.8 | 143.8
760 | BAIRD NORTH WIND U1 | 20INR0083 | BAIRDWND_UNIT1 | CALLAHAN | WIND-O | WEST | 2022 | 195 | 195
761 | BAIRD NORTH WIND U2 | 20INR0083 | BAIRDWND_UNIT2 | CALLAHAN | WIND-O | WEST | 2022 | 145 | 145
762 | BLACKJACK CREEK WIND U1 | 20INR0068 | BLACKJAK_UNIT1 | BEE | WIND-O | SOUTH | 2022 | 120 | 120
763 | BLACKJACK CREEK WIND U2 | 20INR0068 | BLACKJAK_UNIT2 | BEE | WIND-O | SOUTH | 2022 | 120 | 120
764 | CACTUS FLATS WIND U1 | 16INR0086 | CFLATS_U1 | CONCHO | WIND-O | WEST | 2022 | 148.4 | 148.4
765 | COYOTE WIND U1 | 17INR0027b | COYOTE_W_UNIT1 | SCURRY | WIND-O | WEST | 2022 | 90 | 90
766 | COYOTE WIND U2 | 17INR0027b | COYOTE_W_UNIT2 | SCURRY | WIND-O | WEST | 2022 | 26.6 | 26.6
767 | COYOTE WIND U3 | 17INR0027b | COYOTE_W_UNIT3 | SCURRY | WIND-O | WEST | 2022 | 126 | 126
768 | FOXTROT WIND U1 | 20INR0129 | FOXTROT_UNIT1 | BEE | WIND-O | SOUTH | 2022 | 130.2 | 130.2
769 | FOXTROT WIND U2 | 20INR0129 | FOXTROT_UNIT2 | BEE | WIND-O | SOUTH | 2022 | 84 | 84
770 | FOXTROT WIND U3 | 20INR0129 | FOXTROT_UNIT3 | BEE | WIND-O | SOUTH | 2022 | 54 | 54
771 | HARALD (BEARKAT WIND B) | 15INR0064b | HARALD_UNIT1 | GLASSCOCK | WIND-O | WEST | 2022 | 162.1 | 162.1
772 | LAS MAJADAS WIND U1 | 17INR0035 | LMAJADAS_UNIT1 | WILLACY | WIND-C | COASTAL | 2022 | 110 | 110
773 | LAS MAJADAS WIND U2 | 17INR0035 | LMAJADAS_UNIT2 | WILLACY | WIND-C | COASTAL | 2022 | 24 | 24
774 | LAS MAJADAS WIND U3 | 17INR0035 | LMAJADAS_UNIT3 | WILLACY | WIND-C | COASTAL | 2022 | 138.6 | 138.6
775 | EL ALGODON ALTO W U1 | 15INR0034 | ALGODON_UNIT1 | WILLACY | WIND-C | COASTAL | 2022 | 171.6 | 171.6
776 | EL ALGODON ALTO W U2 | 15INR0034 | ALGODON_UNIT2 | WILLACY | WIND-C | COASTAL | 2022 | 28.6 | 28.6
777 | MARYNEAL WINDPOWER | 18INR0031 | MARYNEAL_UNIT1 | NOLAN | WIND-O | WEST | 2022 | 182.4 | 182.4
778 | MESTENO WIND | 16INR0081 | MESTENO_UNIT_1 | STARR | WIND-O | SOUTH | 2022 | 201.6 | 201.6
779 | PRAIRIE HILL WIND U1 | 19INR0100 | PHILLWND_UNIT1 | LIMESTONE | WIND-O | NORTH | 2022 | 153 | 153
780 | PRAIRIE HILL WIND U2 | 19INR0100 | PHILLWND_UNIT2 | LIMESTONE | WIND-O | NORTH | 2022 | 147 | 147
781 | PRIDDY WIND U1 | 16INR0085 | PRIDDY_UNIT1 | MILLS | WIND-O | NORTH | 2022 | 187.2 | 187.2
782 | PRIDDY WIND U2 | 16INR0085 | PRIDDY_UNIT2 | MILLS | WIND-O | NORTH | 2022 | 115.2 | 115.2
783 | RELOJ DEL SOL WIND U1 | 17INR0025 | RELOJ_UNIT1 | ZAPATA | WIND-O | SOUTH | 2022 | 55.4 | 55.4
784 | RELOJ DEL SOL WIND U2 | 17INR0025 | RELOJ_UNIT2 | ZAPATA | WIND-O | SOUTH | 2022 | 48 | 48
785 | RELOJ DEL SOL WIND U3 | 17INR0025 | RELOJ_UNIT3 | ZAPATA | WIND-O | SOUTH | 2022 | 83.1 | 83.1
786 | RELOJ DEL SOL WIND U4 | 17INR0025 | RELOJ_UNIT4 | ZAPATA | WIND-O | SOUTH | 2022 | 22.8 | 22.8
787 | TG EAST WIND U1 | 19INR0052 | TRUSGILL_UNIT1 | KNOX | WIND-O | WEST | 2022 | 42 | 42
788 | TG EAST WIND U2 | 19INR0052 | TRUSGILL_UNIT2 | KNOX | WIND-O | WEST | 2022 | 44.8 | 44.8
789 | TG EAST WIND U3 | 19INR0052 | TRUSGILL_UNIT3 | KNOX | WIND-O | WEST | 2022 | 42 | 42
790 | TG EAST WIND U4 | 19INR0052 | TRUSGILL_UNIT4 | KNOX | WIND-O | WEST | 2022 | 207.2 | 207.2
791 | VORTEX WIND | 20INR0120 | VORTEX_WIND1 | THROCKMORTON | WIND-O | WEST | 2022 | 153.6 | 153.6
792 | VORTEX WIND U2 | 20INR0120 | VORTEX_WIND2 | THROCKMORTON | WIND-O | WEST | 2022 | 24.2 | 24.2
793 | VORTEX WIND U3 | 20INR0120 | VORTEX_WIND3 | THROCKMORTON | WIND-O | WEST | 2022 | 158.4 | 158.4
794 | VORTEX WIND U4 | 20INR0120 | VORTEX_WIND4 | THROCKMORTON | WIND-O | WEST | 2022 | 14 | 14
795 | WHITE MESA WIND U1 | 19INR0128 | WHMESA_UNIT1 | CROCKETT | WIND-O | WEST | 2022 | 152.3 | 152.3
796 | WHITE MESA 2 WIND | 21INR0521 | WHMESA_UNIT2_23 | CROCKETT | WIND-O | WEST | 2022 | 13.92 | 13.9
797 | WHITE MESA 2 WIND U2 | 21INR0521 | WHMESA_UNIT2_28 | CROCKETT | WIND-O | WEST | 2022 | 183.3 | 183.3
798 | WHITE MESA 2 WIND U3 | 21INR0521 | WHMESA_UNIT3_23 | CROCKETT | WIND-O | WEST | 2022 | 18.56 | 18.6
799 | WHITE MESA 2 WIND U4 | 21INR0521 | WHMESA_UNIT3_28 | CROCKETT | WIND-O | WEST | 2022 | 132.54 | 132.5
800 | WHITEHORSE WIND U1 | 19INR0080 | WH_WIND_UNIT1 | FISHER | WIND-O | WEST | 2020 | 209.4 | 209.4
801 | WHITEHORSE WIND U2 | 19INR0080 | WH_WIND_UNIT2 | FISHER | WIND-O | WEST | 2020 | 209.5 | 209.5
802 | WILDWIND | 20INR0033 | WILDWIND_UNIT1 | COOKE | WIND-O | NORTH | 2022 | 18.38 | 18.4
803 | WILDWIND U2 | 20INR0033 | WILDWIND_UNIT2 | COOKE | WIND-O | NORTH | 2022 | 48 | 48
804 | WILDWIND U3 | 20INR0033 | WILDWIND_UNIT3 | COOKE | WIND-O | NORTH | 2022 | 6.3 | 6.3
805 | WILDWIND U4 | 20INR0033 | WILDWIND_UNIT4 | COOKE | WIND-O | NORTH | 2022 | 54.6 | 54.6
806 | WILDWIND U5 | 20INR0033 | WILDWIND_UNIT5 | COOKE | WIND-O | NORTH | 2022 | 52.8 | 52.8
807 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Wind) | [6 empty] | 5795.8 | 5795.8
808
809 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Coastal Counties) |  | WIND_SYNCHRONIZED_C |  |  |  |  | 472.8 | 472.8
810 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_SYNC_PEAK_PCT_C | % |  |  |  | 100 | 57
811
812 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Panhandle Counties) |  | WIND_SYNCHRONIZED_P |  |  |  |  | 0 | 0
813 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_SYNC_PEAK_PCT_P | % |  |  |  | 100 | 30
814
815 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Other Counties) |  | WIND_SYNCHRONIZED_O |  |  |  |  | 5323 | 5323
816 | Wind Peak Average Capacity Percentage (Other) |  | WIND_SYNC_PEAK_PCT_O | % |  |  |  | 100 | 20
817
818 | Operational Resources (Solar)
819 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10 | 10
820 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10 | 10
821 | ANSON SOLAR U1 |  | ANSON1_UNIT1 | JONES | SOLAR | WEST | 2022 | 100.8 | 100
822 | ANSON SOLAR U2 |  | ANSON1_UNIT2 | JONES | SOLAR | WEST | 2022 | 100.8 | 100
823 | ARAGORN SOLAR |  | ARAGORN_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 188.2 | 185
824 | AZURE SKY SOLAR U1 |  | AZURE_SOLAR1 | HASKELL | SOLAR | WEST | 2021 | 74.9 | 74.9
825 | AZURE SKY SOLAR U2 |  | AZURE_SOLAR2 | HASKELL | SOLAR | WEST | 2021 | 153.5 | 153.5
826 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1 | 1
827 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 50 | 49.1
828 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6 | 7.6
829 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3
830 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30 | 30
831 | BLUEBELL SOLAR II 1 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV1 | STERLING | SOLAR | WEST | 2021 | 100 | 100
832 | BLUEBELL SOLAR II 2 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV2 | STERLING | SOLAR | WEST | 2021 | 15 | 15
833 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6 | 101.6
834 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50 | 50
835 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5
836 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5
837 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5
838 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5
839 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5
840 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5
841 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180 | 180
842 | CATAN SOLAR |  | DG_CS10_CATAN | KARNES | SOLAR | SOUTH | 2020 | 10 | 10
843 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10 | 10
844 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5 | 5
845 | CONIGLIO SOLAR |  | CONIGLIO_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 125.7 | 125.7
846 | CORAZON SOLAR PHASE I |  | CORAZON_UNIT1 | WEBB | SOLAR | SOUTH | 2021 | 202.6 | 202.6
847 | EAST BLACKLAND SOLAR (PFLUGERVILLE SOLAR) |  | E_BLACK_UNIT_1 | TRAVIS | SOLAR | SOUTH | 2021 | 144 | 144
848 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10 | 10
849 | ELARA SOLAR |  | ELARA_SL_UNIT1 | FRIO | SOLAR | SOUTH | 2022 | 132.4 | 132.4
850 | EUNICE SOLAR U1 |  | EUNICE_PV1 | ANDREWS | SOLAR | WEST | 2021 | 189.6 | 189.6
851 | EUNICE SOLAR U2 |  | EUNICE_PV2 | ANDREWS | SOLAR | WEST | 2021 | 237.1 | 237.1
852 | FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6 | 1.6
853 | FOWLER RANCH |  | FWLR_SLR_UNIT1 | CRANE | SOLAR | WEST | 2020 | 152.5 | 150
854 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22 | 22
855 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 126 | 121.1
856 | GALLOWAY 1 SOLAR |  | GALLOWAY_SOLAR1 | CONCHO | SOLAR | WEST | 2021 | 250 | 250
857 | GREASEWOOD SOLAR 1 |  | GREASWOD_UNIT1 | PECOS | SOLAR | WEST | 2021 | 126.3 | 124.6
858 | GREASEWOOD SOLAR 2 |  | GREASWOD_UNIT2 | PECOS | SOLAR | WEST | 2021 | 132.2 | 130.4
859 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLENNAN | SOLAR | NORTH | 2019 | 5 | 5
860 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3 | 5.3
861 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6 | 1.6
862 | HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | NOLAN | SOLAR | WEST | 2020 | 102.2 | 102.2
863 | HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | NOLAN | SOLAR | WEST | 2020 | 102.3 | 102.3
864 | IMPACT SOLAR |  | IMPACT_UNIT1 | LAMAR | SOLAR | NORTH | 2021 | 198.5 | 198.5
865 | JUNO SOLAR PHASE I |  | JUNO_UNIT1 | BORDEN | SOLAR | WEST | 2021 | 162.1 | 162.1
866 | JUNO SOLAR PHASE II |  | JUNO_UNIT2 | BORDEN | SOLAR | WEST | 2021 | 143.5 | 143.5
867 | KELLAM SOLAR |  | KELAM_SL_UNIT1 | VAN ZANDT | SOLAR | NORTH | 2020 | 59.8 | 59.8
868 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | WEST | 2019 | 7.5 | 7.5
869 | LAPETUS SOLAR |  | LAPETUS_UNIT_1 | ANDREWS | SOLAR | WEST | 2020 | 100.7 | 100.7
870 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10 | 10
871 | LILY SOLAR |  | LILY_SOLAR1 | KAUFMAN | SOLAR | NORTH | 2021 | 147.6 | 147.6
872 | LONG DRAW SOLAR U1 |  | LGDRAW_S_UNIT1_1 | BORDEN | SOLAR | WEST | 2021 | 98.5 | 98.5
873 | LONG DRAW SOLAR U2 |  | LGDRAW_S_UNIT1_2 | BORDEN | SOLAR | WEST | 2021 | 128.3 | 128.3
874 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3 | 5.3
875 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10 | 10
876 | MISAE SOLAR U1 |  | MISAE_UNIT1 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 121.4 | 121.4
877 | MISAE SOLAR U2 |  | MISAE_UNIT2 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 118.6 | 118.6
878 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2 | 5.2
879 | OBERON SOLAR |  | OBERON_UNIT_1 | ECTOR | SOLAR | WEST | 2020 | 180 | 180
880 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.18 | 39.2
881 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4 | 4.4
882 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5 | 5.5
883 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.62 | 37.6
884 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 100 | 100
885 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2 | 110.2
886 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112 | 112
887 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.04 | 125.1
888 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 127.95 | 128.1
889 | PHOENIX SOLAR |  | PHOENIX_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 83.9 | 83.9
890 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6 | 2.6
891 | PROSPERO SOLAR 1 U1 |  | PROSPERO_UNIT1 | ANDREWS | SOLAR | WEST | 2020 | 153.6 | 153.6
892 | PROSPERO SOLAR 1 U2 |  | PROSPERO_UNIT2 | ANDREWS | SOLAR | WEST | 2020 | 150 | 150
893 | PROSPERO SOLAR 2 U1 |  | PRSPERO2_UNIT1 | ANDREWS | SOLAR | WEST | 2021 | 126.5 | 126.5
894 | PROSPERO SOLAR 2 U2 |  | PRSPERO2_UNIT2 | ANDREWS | SOLAR | WEST | 2021 | 126.4 | 126.4
895 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5
896 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5
897 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR3 | UPTON | SOLAR | WEST | 2020 | 97.5 | 97.5
898 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR4 | UPTON | SOLAR | WEST | 2020 | 107.5 | 107.5
899 | RAMBLER SOLAR |  | RAMBLER_UNIT1 | TOM GREEN | SOLAR | WEST | 2020 | 211.19 | 200
900 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8
901 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8
902 | REDBARN SOLAR 1 (RE MAPLEWOOD 2A SOLAR) |  | REDBARN_UNIT_1 | PECOS | SOLAR | WEST | 2021 | 222 | 222
903 | REDBARN SOLAR 2 (RE MAPLEWOOD 2B SOLAR) |  | REDBARN_UNIT_2 | PECOS | SOLAR | WEST | 2021 | 28 | 28
904 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2 | 2
905 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 155.44 | 150
906 | RIPPEY SOLAR |  | RIPPEY_UNIT1 | COOKE | SOLAR | NORTH | 2020 | 59.8 | 59.8
907 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50 | 50
908 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5 | 157.5
909 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10 | 10
910 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9
911 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9
912 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6 | 5.6
913 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5
914 | TAYGETE SOLAR 1 U1 |  | TAYGETE_UNIT1 | PECOS | SOLAR | WEST | 2021 | 125.9 | 125.9
915 | TAYGETE SOLAR 1 U2 |  | TAYGETE_UNIT2 | PECOS | SOLAR | WEST | 2021 | 128.9 | 128.9
916 | TITAN SOLAR (IP TITAN) U1 |  | TI_SOLAR_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 136.8 | 136.8
917 | TITAN SOLAR (IP TITAN) U2 |  | TI_SOLAR_UNIT2 | CULBERSON | SOLAR | WEST | 2021 | 131.1 | 131.1
918 | TPE ERATH SOLAR |  | DG_ERATH_ERATH21 | ERATH | SOLAR | NORTH | 2021 | 10 | 10
919 | WAGYU SOLAR |  | WGU_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2021 | 120 | 120
920 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10 | 10
921 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182 | 182
922 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7 | 26.7
923 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5 | 5
924 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 100 | 100
925 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5
926 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5
927 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10 | 10
928 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10 | 10
929 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5 | 5
930 | Operational Capacity Total (Solar) | [6 empty] | 8611.22 | 8578.3
931 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 100 | 81
932
933 | Operational Resources (Solar) - Synchronized but not Approved for Commercial Operations
934 | BLUE JAY SOLAR I | 21INR0538 | BLUEJAY_UNIT1 | GRIMES | SOLAR | NORTH | 2022 | 69 | 69
935 | BRIGHTSIDE SOLAR | 18INR0060 | BRIGHTSD_UNIT1 | BEE | SOLAR | SOUTH | 2022 | 53.4 | 50
936 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U1 | 21INR0406 | BCK_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2022 | 217.5 | 217.5
937 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U2 | 21INR0406 | BCK_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2022 | 221.3 | 221.3
938 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 | EGROVESL_UNIT1 | CRANE | SOLAR | WEST | 2022 | 109.5 | 108
939 | FIGHTING JAYS SOLAR U1 | 21INR0278 | JAY_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2022 | 179.5 | 179.6
940 | FIGHTING JAYS SOLAR U2 | 21INR0278 | JAY_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2022 | 171.8 | 171.9
941 | NEBULA SOLAR (RAYOS DEL SOL) U1 | 19INR0045 | NEBULA_UNIT1 | CAMERON | SOLAR | COASTAL | 2022 | 137.5 | 137.5
942 | NOBLE SOLAR U1 | 20INR0214 | NOBLESLR_SOLAR1 | DENTON | SOLAR | NORTH | 2022 | 148.8 | 146.7
943 | NOBLE SOLAR U2 | 20INR0214 | NOBLESLR_SOLAR2 | DENTON | SOLAR | NORTH | 2022 | 130.2 | 128.3
944 | PLAINVIEW SOLAR (RAMSEY SOLAR) U1 | 20INR0130 | PLN_UNIT1 | WHARTON | SOLAR | SOUTH | 2022 | 257 | 257
945 | PLAINVIEW SOLAR (RAMSEY SOLAR) U2 | 20INR0130 | PLN_UNIT2 | WHARTON | SOLAR | SOUTH | 2022 | 257 | 257
946 | SAMSON SOLAR 1 U1 | 21INR0221 | SAMSON_1_G1 | LAMAR | SOLAR | NORTH | 2022 | 128.42 | 125
947 | SAMSON SOLAR 1 U2 | 21INR0221 | SAMSON_1_G2 | LAMAR | SOLAR | NORTH | 2022 | 128.42 | 125
948 | SAMSON SOLAR 3 U1 | 21INR0491 | SAMSON_3_G1 | LAMAR | SOLAR | NORTH | 2022 | 128.42 | 125
949 | SAMSON SOLAR 3 U2 | 21INR0491 | SAMSON_3_G2 | LAMAR | SOLAR | NORTH | 2022 | 128.42 | 125
950 | STRATEGIC SOLAR 1 | 20INR0081 | STRATEGC_UNIT1 | ELLIS | SOLAR | NORTH | 2022 | 135 | 135
951 | VISION SOLAR 1 | 20INR0082 | VISION_UNIT1 | NAVARRO | SOLAR | NORTH | 2022 | 129.2 | 127
952 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Solar) | [6 empty] | 2730.38 | 2705.8
953 | Solar Peak Average Capacity Percentage |  | SOLAR_SYNC_PEAK_PCT | % |  |  |  | 100 | 81
954
955 | Operational Resources (Storage)
956 | BAT CAVE |  | BATCAVE_BES1 | MASON | STORAGE | SOUTH | 2021 | 100.5 | 100.5
957 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30 | 30
958 | BRP ALVIN (DGR) |  | BRPALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.95 | 9.9
959 | BRP ANGELTON (DGR) |  | BRPANGLE_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.95 | 9.9
960 | BRP BRAZORIA (DGR) |  | BRP_BRAZ_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.95 | 9.9
961 | BRP DICKINSON (DGR) |  | BRP_DIKN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2021 | 9.95 | 9.9
962 | BRP HEIGHTS (DGR) |  | BRHEIGHT_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 9.95 | 9.9
963 | BRP LOOP 463 (DGR) |  | BRP_4631_UNIT1 | VICTORIA | STORAGE | SOUTH | 2021 | 9.95 | 9.9
964 | BRP LOPENO (DGR) |  | BRP_LOP1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.9
965 | BRP MAGNOLIA (DGR) |  | BRPMAGNO_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 9.95 | 9.9
966 | BRP ODESSA SW (DGR) |  | BRPODESA_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 9.95 | 9.9
967 | BRP PUEBLO I (DGR) |  | BRP_PBL1_UNIT1 | MAVERICK | STORAGE | SOUTH | 2022 | 9.95 | 9.9
968 | BRP PUEBLO II (DGR) |  | BRP_PBL2_UNIT1 | MAVERICK | STORAGE | SOUTH | 2022 | 9.95 | 9.9
969 | BRP RANCHTOWN (DGR) |  | BRP_RNC1_UNIT1 | BEXAR | STORAGE | SOUTH | 2021 | 9.95 | 9.9
970 | BRP SWEENY (DGR) |  | BRP_SWNY_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.95 | 10
971 | BRP ZAPATA I (DGR) |  | BRP_ZPT1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.9
972 | BRP ZAPATA II (DGR) |  | BRP_ZPT2_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.9
973 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2018 | 9.9 | 9.9
974 | CHISHOLM GRID |  | CHISMGRD_BES1 | TARRANT | STORAGE | NORTH | 2021 | 101.7 | 100
975 | COMMERCE ST ESS (DGR) |  | X443ESS1_SWRI | BEXAR | STORAGE | SOUTH | 2020 | 10 | 10
976 | EUNICE STORAGE |  | EUNICE_BES1 | ANDREWS | STORAGE | WEST | 2021 | 40.3 | 40.3
977 | FLAT TOP BATTERY (DGR) |  | FLTBES_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9 | 9.9
978 | FLOWER VALLEY BATTERY (DGR) |  | FLVABES1_FLATU1 | REEVES | STORAGE | WEST | 2021 | 9.9 | 9.9
979 | FLOWER VALLEY II BATT |  | FLOWERII_BESS1 | REEVES | STORAGE | WEST | 2022 | 101.5 | 100
980 | GAMBIT BATTERY |  | GAMBIT_BESS1 | BRAZORIA | STORAGE | COASTAL | 2021 | 102.4 | 100
981 | HOEFSROAD BESS (DGR) |  | HRBESS_BESS | REEVES | STORAGE | WEST | 2020 | 2 | 2
982 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9 | 9.9
983 | JOHNSON CITY BESS (DGR) |  | JC_BAT_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 2.25 | 2.3
984 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5 | 1.5
985 | LILY STORAGE |  | LILY_BESS1 | KAUFMAN | STORAGE | NORTH | 2021 | 51.7 | 51.7
986 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5 | 1.5
987 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 36 | 33.7
988 | NORTH FORK |  | NF_BRP_BES1 | WILLIAMSON | STORAGE | SOUTH | 2021 | 100.5 | 100.5
989 | OCI ALAMO 1 |  | OCI_ALM1_ASTRO1 | BEXAR | STORAGE | SOUTH | 2016 | 1 | 1
990 | PORT LAVACA BATTERY (DGR) |  | PTLBES_BESS1 | CALHOUN | STORAGE | COASTAL | 2020 | 9.9 | 9.9
991 | PROSPECT STORAGE (DGR) |  | WCOLLDG_BSS_U1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.9 | 9.9
992 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9 | 9.9
993 | RABBIT HILL ENERGY STORAGE PROJECT (DGR) |  | RHESS2_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2020 | 9.9 | 9.9
994 | SADDLEBACK BESS (DGR) |  | SADLBACK_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.95
995 | SNYDER (DGR) |  | SNY_BESS_UNIT1 | SCURRY | STORAGE | WEST | 2021 | 9.95 | 9.9
996 | SWEETWATER BESS (DGR) |  | SWT_BESS_UNIT1 | NOLAN | STORAGE | WEST | 2021 | 9.95 | 9.9
997 | SWOOSE BATTERY (DGR) |  | SWOOSE1_SWOOSEU1 | WARD | STORAGE | WEST | 2021 | 9.9 | 9.9
998 | TOS BATTERY STORAGE (DGR) |  | TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2 | 2
999 | TOYAH POWER STATION (DGR) |  | TOYAH_BESS | REEVES | STORAGE | WEST | 2021 | 9.95 | 9.9
1000 | TRIPLE BUTTE (DGR) |  | TRIPBUT1_BELU1 | PECOS | STORAGE | WEST | 2021 | 9.18 | 7.5
1001 | WESTOVER BESS (DGR) |  | WOV_BESS_UNIT1 | ECTOR | STORAGE | WEST | 2021 | 9.95 | 9.9
1002 | WORSHAM BATTERY (DGR) |  | WRSBES_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9 | 9.9
1003 | YOUNICOS FACILITY |  | DG_YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 2 | 2
1004 | Operational Capacity Total (Storage) | [6 empty] | 994.03 | 983.65
1005 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 100 | 0
1006
1007 | Operational Resources (Storage) - Synchronized but not Approved for Commercial Operations
1008 | AZURE SKY BESS | 21INR0476 | AZURE_BESS1 | HASKELL | STORAGE | WEST | 2022 | 77.6 | 77.6
1009 | CROSSETT POWER U1 | 21INR0510 | CROSSETT_BES1 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100
1010 | CROSSETT POWER U2 | 21INR0510 | CROSSETT_BES2 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100
1011 | DECORDOVA BESS U1 | 21INR0459 | DCSES_BES1 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5
1012 | DECORDOVA BESS U2 | 21INR0459 | DCSES_BES2 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5
1013 | DECORDOVA BESS U3 | 21INR0459 | DCSES_BES3 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5
1014 | DECORDOVA BESS U4 | 21INR0459 | DCSES_BES4 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5
1015 | FAULKNER BESS (DGR) | 22INR0571 | FAULKNER_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.95
1016 | QUEEN BESS | 20INR0281 | QUEEN_BA_BESS1 | UPTON | STORAGE | WEST | 2022 | 51.1 | 50
1017 | REPUBLIC ROAD STORAGE | 21INR0460 | RPUBRDS_ESS1 | ROBERTSON | STORAGE | NORTH | 2022 | 51.75 | 50
1018 | SWOOSE II | 21INR0497 | SWOOSEII_BESS1 | WARD | STORAGE | WEST | 2022 | 101.5 | 100
1019 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Storage) | [6 empty] | 757.9 | 747.55
1020 | Storage Peak Average Capacity Percentage |  | STORAGE_SYNC_PEAK_PCT | % |  |  |  | 100 | 0
1021
1022 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  |  |  |  | 0 | 0
1023
1024 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0 | 0
1025
1026 | Non-Synchronous Tie Resources
1027 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600 | 600
1028 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220 | 220
1029 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100 | 100
1030 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300 | 300
1031 | Non-Synchronous Ties Total | [6 empty] | 1220 | 1220
1032 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 100 | 69.67
1033
1034 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
1035 | AIR PRODUCTS GCA | 21INR0012 |  | GALVESTON | GAS-ST | HOUSTON | 2023 | 0 | 0
1036 | BEACHWOOD POWER STATION (MARK ONE) | 22INR0369 |  | BRAZORIA | GAS-GT | COASTAL | 2022 | 267.6 | 267.6
1037 | CHAMON 2 | 19INR0056 |  | HARRIS | GAS-GT | HOUSTON | 2022 | 88 | 88
1038 | COLORADO BEND I EXPANSION | 21INR0512 |  | WHARTON | GAS-GT | SOUTH | 2022 | 0 | 0
1039 | MIRAGE CTG 1 | 17INR0022 |  | HARRIS | GAS-GT | HOUSTON | 2023 | 0 | 0
1040 | RABBS POWER STATION (UNITS 1-2) | 23INR0482 |  | FORT BEND | GAS-GT | HOUSTON | 2022 | 0 | 0
1041 | Planned Thermal Resources Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 355.6 | 355.6
1042
1043 | Planned Wind Resources with Executed SGIA
1044 | AGUAYO WIND | 20INR0250 |  | MILLS | WIND-O | NORTH | 2022 | 0 | 0
1045 | ANCHOR WIND III | 21INR0546 |  | EASTLAND | WIND-O | NORTH | 2022 | 16 | 16
1046 | APPALOOSA RUN WIND_ | 20INR0249 |  | UPTON | WIND-O | WEST | 2023 | 0 | 0
1047 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2024 | 0 | 0
1048 | BOARD CREEK WP | 21INR0324 |  | NAVARRO | WIND-O | NORTH | 2022 | 0 | 0
1049 | CANYON WIND | 18INR0030 |  | SCURRY | WIND-O | WEST | 2023 | 0 | 0
1050 | CAROL WIND | 20INR0217 |  | POTTER | WIND-P | PANHANDLE | 2024 | 0 | 0
1051 | CRAWFISH | 19INR0177 |  | WHARTON | WIND-O | SOUTH | 2023 | 0 | 0
1052 | EL SUAZ RANCH | 20INR0097 |  | WILLACY | WIND-C | COASTAL | 2022 | 0 | 0
1053 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND-P | PANHANDLE | 2023 | 0 | 0
1054 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2023 | 0 | 0
1055 | INERTIA WIND | 22INR0326 |  | HASKELL | WIND-O | WEST | 2022 | 0 | 0
1056 | LACY CREEK WIND | 18INR0043 |  | GLASSCOCK | WIND-O | WEST | 2022 | 0 | 0
1057 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2023 | 0 | 0
1058 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND-O | WEST | 2024 | 0 | 0
1059 | MONARCH CREEK WIND | 21INR0263 |  | THROCKMORTON | WIND-O | WEST | 2023 | 0 | 0
1060 | MONTE ALTO 1 WIND | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2023 | 0 | 0
1061 | MONTE ALTO 2 WIND | 19INR0023 |  | WILLACY | WIND-C | COASTAL | 2023 | 0 | 0
1062 | MONTGOMERY RANCH WIND | 20INR0040 |  | FOARD | WIND-O | WEST | 2023 | 0 | 0
1063 | ROADRUNNER CROSSING WIND 1 | 19INR0117 |  | EASTLAND | WIND-O | NORTH | 2022 | 0 | 0
1064 | SHEEP CREEK WIND | 21INR0325 |  | CALLAHAN | WIND-O | WEST | 2023 | 0 | 0
1065 | YOUNG WIND | 21INR0401 |  | YOUNG | WIND-O | WEST | 2022 | 0 | 0
1066 | Planned Capacity Total (Wind) | [6 empty] | 16 | 16
1067
1068 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 0 | 0
1069 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 100 | 57
1070
1071 | Planned Wind Capacity Sub-total (Panhandle Counties) |  | WIND_PLANNED_P |  |  |  |  | 0 | 0
1072 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PL_PEAK_PCT_P | % |  |  |  | 100 | 30
1073
1074 | Planned Wind Capacity Sub-total (Other counties) |  | WIND_PLANNED_O |  |  |  |  | 16 | 16
1075 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PL_PEAK_PCT_O | % |  |  |  | 100 | 20
1076
1077 | Planned Solar Resources with Executed SGIA
1078 | 7V SOLAR | 21INR0351 |  | FAYETTE | SOLAR | SOUTH | 2023 | 0 | 0
1079 | AMSTERDAM SOLAR | 21INR0256 |  | BRAZORIA | SOLAR | COASTAL | 2023 | 0 | 0
1080 | ANDROMEDA SOLAR | 22INR0412 |  | SCURRY | SOLAR | WEST | 2023 | 0 | 0
1081 | ANGELO SOLAR | 19INR0203 |  | TOM GREEN | SOLAR | WEST | 2023 | 0 | 0
1082 | ANGUS SOLAR | 20INR0035 |  | BOSQUE | SOLAR | NORTH | 2023 | 0 | 0
1083 | ARMADILLO SOLAR | 21INR0421 |  | NAVARRO | SOLAR | NORTH | 2023 | 0 | 0
1084 | ARROYO SOLAR | 20INR0086 |  | CAMERON | SOLAR | COASTAL | 2024 | 0 | 0
1085 | BAKER BRANCH SOLAR | 23INR0026 |  | LAMAR | SOLAR | NORTH | 2023 | 0 | 0
1086 | BIG STAR SOLAR | 21INR0413 |  | BASTROP | SOLAR | SOUTH | 2022 | 0 | 0
1087 | BLUE JAY SOLAR II | 19INR0085 |  | GRIMES | SOLAR | NORTH | 2022 | 141.1 | 141.1
1088 | BLUE SKY SOL | 22INR0455 |  | CROCKETT | SOLAR | WEST | 2023 | 0 | 0
1089 | BPL FILES SOLAR | 20INR0164 |  | HILL | SOLAR | NORTH | 2023 | 0 | 0
1090 | BRASS FORK SOLAR | 22INR0270 |  | HASKELL | SOLAR | WEST | 2024 | 0 | 0
1091 | BRIGHT ARROW SOLAR | 22INR0242 |  | HOPKINS | SOLAR | NORTH | 2022 | 0 | 0
1092 | CACHENA SOLAR | 23INR0027 |  | WILSON | SOLAR | SOUTH | 2024 | 0 | 0
1093 | CAROL SOLAR | 21INR0274 |  | POTTER | SOLAR | PANHANDLE | 2024 | 0 | 0
1094 | CASTRO SOLAR | 20INR0050 |  | CASTRO | SOLAR | PANHANDLE | 2023 | 0 | 0
1095 | CHARGER SOLAR | 23INR0047 |  | REFUGIO | SOLAR | COASTAL | 2023 | 0 | 0
1096 | CHILLINGHAM SOLAR | 23INR0070 |  | BELL | SOLAR | NORTH | 2023 | 0 | 0
1097 | CONCHO VALLEY SOLAR | 21INR0384 |  | TOM GREEN | SOLAR | WEST | 2022 | 0 | 0
1098 | CORAL SOLAR | 22INR0295 |  | FALLS | SOLAR | NORTH | 2023 | 0 | 0
1099 | CORAZON SOLAR PHASE II | 22INR0257 |  | WEBB | SOLAR | SOUTH | 2025 | 0 | 0
1100 | COTTONWOOD BAYOU SOLAR I | 19INR0134 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 0 | 0
1101 | COTTONWOOD BAYOU SOLAR II | 21INR0228 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 0 | 0
1102 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2024 | 0 | 0
1103 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2025 | 0 | 0
1104 | DANCIGER SOLAR | 20INR0098 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0 | 0
1105 | DANISH FIELDS SOLAR I | 20INR0069 |  | WHARTON | SOLAR | SOUTH | 2023 | 0 | 0
1106 | DAWN SOLAR | 20INR0255 |  | DEAF SMITH | SOLAR | PANHANDLE | 2023 | 0 | 0
1107 | DELILAH SOLAR 1 | 22INR0202 |  | LAMAR | SOLAR | NORTH | 2022 | 0 | 0
1108 | DELILAH SOLAR 2 | 22INR0203 |  | LAMAR | SOLAR | NORTH | 2023 | 0 | 0
1109 | DELILAH SOLAR 3 | 23INR0042 |  | LAMAR | SOLAR | NORTH | 2023 | 0 | 0
1110 | DELILAH SOLAR 4 | 23INR0060 |  | LAMAR | SOLAR | NORTH | 2023 | 0 | 0
1111 | DILEO SOLAR | 22INR0359 |  | BOSQUE | SOLAR | NORTH | 2023 | 0 | 0
1112 | DR SOLAR | 22INR0454 |  | CULBERSON | SOLAR | WEST | 2023 | 0 | 0
1113 | EIFFEL SOLAR | 22INR0223 |  | LAMAR | SOLAR | NORTH | 2023 | 0 | 0
1114 | ELLIS SOLAR | 21INR0493 |  | ELLIS | SOLAR | NORTH | 2022 | 0 | 0
1115 | EQUINOX SOLAR 1 | 21INR0226 |  | STARR | SOLAR | SOUTH | 2025 | 0 | 0
1116 | ESTONIAN SOLAR FARM | 22INR0335 |  | DELTA | SOLAR | NORTH | 2023 | 0 | 0
1117 | FAGUS SOLAR PARK (MISAE SOLAR II) | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2023 | 0 | 0
1118 | FENCE POST SOLAR | 22INR0404 |  | NAVARRO | SOLAR | NORTH | 2022 | 0 | 0
1119 | TAVNER (FORT BEND SOLAR) | 18INR0053 |  | FORT BEND | SOLAR | HOUSTON | 2023 | 0 | 0
1120 | FRYE SOLAR | 20INR0080 |  | SWISHER | SOLAR | PANHANDLE | 2023 | 0 | 0
1121 | GALLOWAY 2 SOLAR | 21INR0431 |  | CONCHO | SOLAR | WEST | 2023 | 0 | 0
1122 | GOLINDA SOLAR | 21INR0434 |  | FALLS | SOLAR | NORTH | 2023 | 0 | 0
1123 | GP SOLAR | 23INR0045 |  | VAN ZANDT | SOLAR | NORTH | 2023 | 0 | 0
1124 | GRANDSLAM SOLAR | 21INR0391 |  | ATASCOSA | SOLAR | SOUTH | 2023 | 0 | 0
1125 | GREEN HOLLY SOLAR | 21INR0021 |  | DAWSON | SOLAR | WEST | 2024 | 0 | 0
1126 | GREYHOUND SOLAR | 21INR0268 |  | ECTOR | SOLAR | WEST | 2023 | 0 | 0
1127 | GRIZZLY RIDGE SOLAR | 21INR0375 |  | HAMILTON | SOLAR | NORTH | 2022 | 0 | 0
1128 | G-STAR SOLAR | 23INR0111 |  | WHARTON | SOLAR | SOUTH | 2023 | 0 | 0
1129 | HAYHURST TEXAS SOLAR | 22INR0363 |  | CULBERSON | SOLAR | WEST | 2023 | 0 | 0
1130 | HOPKINS SOLAR | 20INR0210 |  | HOPKINS | SOLAR | NORTH | 2023 | 0 | 0
1131 | HORIZON SOLAR | 21INR0261 |  | FRIO | SOLAR | SOUTH | 2023 | 0 | 0
1132 | HORNET SOLAR | 23INR0021 |  | SWISHER | SOLAR | PANHANDLE | 2023 | 0 | 0
1133 | INDIGO SOLAR | 21INR0031 |  | FISHER | SOLAR | WEST | 2023 | 0 | 0
1134 | INERTIA SOLAR | 22INR0374 |  | HASKELL | SOLAR | WEST | 2023 | 0 | 0
1135 | JACKALOPE SOLAR | 23INR0180 |  | SAN PATRICIO | SOLAR | COASTAL | 2023 | 0 | 0
1136 | JADE SOLAR | 22INR0360 |  | SCURRY | SOLAR | WEST | 2023 | 0 | 0
1137 | JUNGMANN SOLAR | 22INR0356 |  | MILAM | SOLAR | SOUTH | 2023 | 0 | 0
1138 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2023 | 0 | 0
1139 | LONGBOW SOLAR | 20INR0026 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0 | 0
1140 | LUNIS CREEK SOLAR 1 | 21INR0344 |  | JACKSON | SOLAR | SOUTH | 2024 | 0 | 0
1141 | MALEZA SOLAR | 21INR0220 |  | WHARTON | SOLAR | SOUTH | 2023 | 0 | 0
1142 | MARKUM SOLAR | 20INR0230 |  | MCLENNAN | SOLAR | NORTH | 2024 | 0 | 0
1143 | MCLEAN (SHAKES) SOLAR | 19INR0073 |  | ZAVALA | SOLAR | SOUTH | 2022 | 0 | 0
1144 | MERCURY I SOLAR | 21INR0257 |  | HILL | SOLAR | NORTH | 2022 | 0 | 0
1145 | MERCURY II SOLAR | 23INR0153 |  | HILL | SOLAR | NORTH | 2022 | 0 | 0
1146 | MORROW LAKE SOLAR | 19INR0155 |  | FRIO | SOLAR | SOUTH | 2023 | 0 | 0
1147 | MUSTANG CREEK SOLAR | 18INR0050 |  | JACKSON | SOLAR | SOUTH | 2023 | 0 | 0
1148 | MYRTLE SOLAR | 19INR0041 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0 | 0
1149 | NABATOTO SOLAR NORTH | 21INR0428 |  | LEON | SOLAR | NORTH | 2023 | 0 | 0
1150 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2023 | 0 | 0
1151 | NEPTUNE SOLAR | 21INR0499 |  | JACKSON | SOLAR | SOUTH | 2022 | 0 | 0
1152 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2023 | 0 | 0
1153 | OLD HICKORY SOLAR | 20INR0236 |  | JACKSON | SOLAR | SOUTH | 2023 | 0 | 0
1154 | OUTPOST SOLAR | 23INR0007 |  | WEBB | SOLAR | SOUTH | 2024 | 0 | 0
1155 | OYSTERCATCHER SOLAR | 21INR0362 |  | ELLIS | SOLAR | NORTH | 2024 | 0 | 0
1156 | PEREGRINE SOLAR | 22INR0283 |  | GOLIAD | SOLAR | SOUTH | 2024 | 0 | 0
1157 | PINE FOREST SOLAR | 20INR0203 |  | HOPKINS | SOLAR | NORTH | 2024 | 0 | 0
1158 | PISGAH RIDGE SOLAR | 22INR0254 |  | NAVARRO | SOLAR | NORTH | 2022 | 0 | 0
1159 | PITTS DUDIK SOLAR | 20INR0074 |  | HILL | SOLAR | NORTH | 2022 | 0 | 0
1160 | PORTER SOLAR | 21INR0458 |  | DENTON | SOLAR | NORTH | 2023 | 0 | 0
1161 | RADIAN SOLAR | 21INR0205 |  | BROWN | SOLAR | NORTH | 2022 | 0 | 0
1162 | RED HOLLY SOLAR | 21INR0022 |  | DAWSON | SOLAR | WEST | 2024 | 0 | 0
1163 | REDONDA SOLAR | 23INR0162 |  | ZAPATA | SOLAR | SOUTH | 2023 | 0 | 0
1164 | RED-TAILED HAWK SOLAR | 21INR0389 |  | WHARTON | SOLAR | SOUTH | 2024 | 0 | 0
1165 | ROCINANTE SOLAR | 23INR0231 |  | GONZALES | SOLAR | SOUTH | 2023 | 0 | 0
1166 | ROSELAND SOLAR | 20INR0205 |  | FALLS | SOLAR | NORTH | 2023 | 0 | 0
1167 | ROSELAND SOLAR II | 22INR0506 |  | FALLS | SOLAR | NORTH | 2023 | 0 | 0
1168 | ROWLAND SOLAR I | 19INR0131 |  | FORT BEND | SOLAR | HOUSTON | 2022 | 0 | 0
1169 | ROWLAND SOLAR II | 22INR0482 |  | FORT BEND | SOLAR | HOUSTON | 2023 | 0 | 0
1170 | RUETER SOLAR | 20INR0202 |  | BOSQUE | SOLAR | NORTH | 2022 | 0 | 0
1171 | SAMSON SOLAR 2 | 21INR0490 |  | LAMAR | SOLAR | NORTH | 2023 | 0 | 0
1172 | SBRANCH SOLAR PROJECT | 22INR0205 |  | WHARTON | SOLAR | SOUTH | 2023 | 0 | 0
1173 | SCHOOLHOUSE SOLAR | 22INR0211 |  | LEE | SOLAR | SOUTH | 2023 | 0 | 0
1174 | SECOND DIVISION SOLAR | 20INR0248 |  | BRAZORIA | SOLAR | COASTAL | 2023 | 0 | 0
1175 | SHAULA I SOLAR | 22INR0251 |  | DEWITT | SOLAR | SOUTH | 2024 | 0 | 0
1176 | SIGNAL SOLAR | 20INR0208 |  | HUNT | SOLAR | NORTH | 2023 | 0 | 0
1177 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2023 | 0 | 0
1178 | SPACE CITY SOLAR | 21INR0341 |  | WHARTON | SOLAR | SOUTH | 2022 | 0 | 0
1179 | SPANISH CROWN | 21INR0323 |  | FALLS | SOLAR | NORTH | 2023 | 0 | 0
1180 | SPARTA SOLAR | 22INR0352 |  | BEE | SOLAR | SOUTH | 2022 | 0 | 0
1181 | STAMPEDE SOLAR | 22INR0409 |  | HOPKINS | SOLAR | NORTH | 2022 | 0 | 0
1182 | STARLING SOLAR | 23INR0035 |  | GONZALES | SOLAR | SOUTH | 2023 | 0 | 0
1183 | STARR SOLAR RANCH | 20INR0216 |  | STARR | SOLAR | SOUTH | 2023 | 0 | 0
1184 | SUN VALLEY | 19INR0169 |  | HILL | SOLAR | NORTH | 2022 | 0 | 0
1185 | SUNRAY | 21INR0395 |  | UVALDE | SOLAR | SOUTH | 2023 | 0 | 0
1186 | TEXANA SOLAR | 18INR0058 |  | WHARTON | SOLAR | SOUTH | 2022 | 0 | 0
1187 | TEXAS SOLAR NOVA | 19INR0001 |  | KENT | SOLAR | WEST | 2023 | 0 | 0
1188 | TRES BAHIAS SOLAR | 20INR0266 |  | CALHOUN | SOLAR | COASTAL | 2023 | 0 | 0
1189 | TYSON NICK SOLAR | 20INR0222 |  | LAMAR | SOLAR | NORTH | 2023 | 0 | 0
1190 | VANCOURT SOLAR | 21INR0213 |  | CAMERON | SOLAR | COASTAL | 2022 | 0 | 0
1191 | WESTORIA SOLAR | 20INR0101 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0 | 0
1192 | ZIER SOLAR | 21INR0019 |  | KINNEY | SOLAR | SOUTH | 2023 | 0 | 0
1193 | Planned Capacity Total (Solar) | [6 empty] | 141.1 | 141.1
1194 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 100 | 81
1195
1196 | Planned Storage Resources with Executed SGIA
1197 | AMSTERDAM STORAGE | 22INR0417 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 0 | 0
1198 | ANCHOR BESS | 21INR0474 |  | EASTLAND | STORAGE | NORTH | 2022 | 0 | 0
1199 | ANEMOI ENERGY STORAGE | 23INR0369 |  | HIDALGO | STORAGE | SOUTH | 2023 | 0 | 0
1200 | BIG STAR STORAGE | 21INR0469 |  | BASTROP | STORAGE | SOUTH | 2022 | 0 | 0
1201 | BLUE JAY BESS | 23INR0019 |  | GRIMES | STORAGE | NORTH | 2022 | 0 | 0
1202 | BRIGHT ARROW STORAGE | 22INR0302 |  | HOPKINS | STORAGE | NORTH | 2023 | 0 | 0
1203 | BRP ANTLIA BESS | 22INR0349 |  | VAL VERDE | STORAGE | WEST | 2023 | 0 | 0
1204 | BRP CACHI BESS | 22INR0388 |  | GUADALUPE | STORAGE | SOUTH | 2023 | 0 | 0
1205 | BRP CARINA BESS | 22INR0353 |  | NUECES | STORAGE | COASTAL | 2023 | 0 | 0
1206 | BRP DICKENS BESS | 22INR0325 |  | DICKENS | STORAGE | PANHANDLE | 2023 | 0 | 0
1207 | BRP HYDRA BESS | 22INR0372 |  | PECOS | STORAGE | WEST | 2022 | 0 | 0
1208 | BRP LIBRA BESS | 22INR0366 |  | GUADALUPE | STORAGE | SOUTH | 2023 | 0 | 0
1209 | BRP PALEO BESS | 22INR0322 |  | HALE | STORAGE | PANHANDLE | 2022 | 0 | 0
1210 | BRP PAVO BESS | 22INR0384 |  | PECOS | STORAGE | WEST | 2022 | 0 | 0
1211 | BRP TORTOLAS BESS | 23INR0072 |  | BRAZORIA | STORAGE | COASTAL | 2022 | 0 | 0
1212 | BURRO BESS (DGR) | 22INR0573 |  | LA SALLE | STORAGE | SOUTH | 2022 | 0 | 0
1213 | BYRD RANCH STORAGE | 21INR0281 |  | BRAZORIA | STORAGE | COASTAL | 2022 | 0 | 0
1214 | CEDARVILLE BESS (DGR) | 22INR0577 |  | REEVES | STORAGE | WEST | 2022 | 0 | 0
1215 | CHILLINGHAM STORAGE | 23INR0079 |  | BELL | STORAGE | NORTH | 2023 | 0 | 0
1216 | COTTONWOOD BAYOU STORAGE | 21INR0443 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 0 | 0
1217 | COYOTE SPRINGS BESS (DGR) | 22INR0574 |  | REEVES | STORAGE | WEST | 2022 | 0 | 0
1218 | ENDURANCE PARK STORAGE | 21INR0479 |  | SCURRY | STORAGE | WEST | 2022 | 0 | 0
1219 | ESTONIAN ENERGY STORAGE | 22INR0336 |  | DELTA | STORAGE | NORTH | 2023 | 0 | 0
1220 | EVAL STORAGE | 22INR0401 |  | CAMERON | STORAGE | COASTAL | 2023 | 0 | 0
1221 | FENCE POST BESS | 22INR0405 |  | NAVARRO | STORAGE | NORTH | 2022 | 0 | 0
1222 | GIGA TEXAS ENERGY STORAGE | 23INR0239 |  | TRAVIS | STORAGE | SOUTH | 2023 | 0 | 0
1223 | GREEN HOLLY STORAGE | 21INR0029 |  | DAWSON | STORAGE | WEST | 2024 | 0 | 0
1224 | HIGH LONESOME BESS | 20INR0280 |  | CROCKETT | STORAGE | WEST | 2022 | 0 | 0
1225 | HOUSE MOUNTAIN 2 BATT | 22INR0485 |  | BREWSTER | STORAGE | WEST | 2023 | 0 | 0
1226 | HUMMINGBIRD STORAGE | 22INR0327 |  | DENTON | STORAGE | NORTH | 2023 | 0 | 0
1227 | INERTIA BESS | 22INR0328 |  | HASKELL | STORAGE | WEST | 2022 | 0 | 0
1228 | INERTIA BESS 2 | 22INR0375 |  | HASKELL | STORAGE | WEST | 2022 | 0 | 0
1229 | LA HUERTA BESS (DGR) | 22INR0572 |  | DIMMIT | STORAGE | SOUTH | 2022 | 0 | 0
1230 | LIMOUSIN OAK STORAGE | 22INR0338 |  | GRIMES | STORAGE | NORTH | 2023 | 0 | 0
1231 | MADERO GRID U1 | 21INR0244 |  | HIDALGO | STORAGE | SOUTH | 2022 | 100 | 100
1232 | MADERO GRID U2 (IGNACIO GRID) | 21INR0522 |  | HIDALGO | STORAGE | SOUTH | 2022 | 100 | 100
1233 | MATTA POWER STATION (DGR) | 22INR0565 |  | REEVES | STORAGE | WEST | 2022 | 9.9 | 9.9
1234 | MUSTANG CREEK STORAGE | 21INR0484 |  | JACKSON | STORAGE | SOUTH | 2023 | 0 | 0
1235 | NOBLE STORAGE | 22INR0436 |  | DENTON | STORAGE | NORTH | 2022 | 0 | 0
1236 | NOBLE STORAGE PHASE II | 22INR0598 |  | DENTON | STORAGE | NORTH | 2022 | 0 | 0
1237 | PYRON BESS II | 20INR0268 |  | NOLAN | STORAGE | WEST | 2022 | 0 | 0
1238 | RED HOLLY STORAGE | 21INR0033 |  | DAWSON | STORAGE | WEST | 2024 | 0 | 0
1239 | RIVER VALLEY STORAGE 1 | 20INR0290 |  | WILLIAMSON | STORAGE | SOUTH | 2022 | 0 | 0
1240 | RIVER VALLEY STORAGE 2 | 20INR0293 |  | WILLIAMSON | STORAGE | SOUTH | 2022 | 0 | 0
1241 | ROCINANTE BESS | 23INR0232 |  | GONZALES | STORAGE | SOUTH | 2023 | 0 | 0
1242 | ROSELAND STORAGE | 22INR0280 |  | FALLS | STORAGE | NORTH | 2022 | 0 | 0
1243 | ROUGHNECK STORAGE | 19INR0176 |  | BRAZORIA | STORAGE | COASTAL | 2022 | 50 | 50
1244 | RYAN ENERGY STORAGE | 20INR0246 |  | CORYELL | STORAGE | NORTH | 2023 | 0 | 0
1245 | SABAL STORAGE | 22INR0398 |  | CAMERON | STORAGE | COASTAL | 2023 | 0 | 0
1246 | SCREWBEAN BESS (DGR) | 22INR0587 |  | CULBERSON | STORAGE | WEST | 2022 | 0 | 0
1247 | SILICON HILL STORAGE | 20INR0291 |  | TRAVIS | STORAGE | SOUTH | 2022 | 0 | 0
1248 | SOWERS STORAGE | 22INR0552 |  | KAUFMAN | STORAGE | NORTH | 2023 | 0 | 0
1249 | SP TX-12B BESS | 21INR0357 |  | UPTON | STORAGE | WEST | 2022 | 22.7 | 22.7
1250 | STAMPEDE BESS | 22INR0410 |  | HOPKINS | STORAGE | NORTH | 2022 | 0 | 0
1251 | TIMBERWOLF BESS 2 | 22INR0495 |  | UPTON | STORAGE | WEST | 2023 | 0 | 0
1252 | TURQUOISE STORAGE | 22INR0509 |  | HUNT | STORAGE | NORTH | 2022 | 0 | 0
1253 | VORTEX BESS | 21INR0473 |  | THROCKMORTON | STORAGE | WEST | 2022 | 0 | 0
1254 | WOLF TANK STORAGE | 22INR0551 |  | WEBB | STORAGE | SOUTH | 2022 | 0 | 0
1255 | SMALL GENERATORS WITH SIGNED IAs AND 'MODEL READY DATES' PENDING * | [6 empty] | 0 | 0
1256 | Planned Capacity Total (Storage) | [6 empty] | 282.6 | 282.6
1257 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 100 | 0
1258
1259 | Inactive Planned Resources
1260 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 60 | 60
1261 | GUAJILLO ENERGY STORAGE | 23INR0343 |  | WEBB | STORAGE | SOUTH | 2023 | 0 | 0
1262 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2023 | 0 | 0
1263 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2023 | 0 | 0
1264 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 152.5 | 152.5
1265 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 150 | 150
1266 | PADUA GRID BESS | 22INR0368 |  | BEXAR | STORAGE | SOUTH | 2024 | 0 | 0
1267 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2022 | 0 | 0
1268 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2024 | 0 | 0
1269 | TAYGETE II SOLAR | 21INR0233 |  | PECOS | SOLAR | WEST | 2022 | 0 | 0
1270 | Inactive Planned Capacity Total | [6 empty] | 362.5 | 362.5
1271
1272 | Seasonal Mothballed Resources
1273 | GREGORY POWER PARTNERS GT1 (AS OF 1/1/2022, AVAILABLE 1/1 THROUGH 9/30) |  | LGE_LGE_GT1 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 145
1274 | GREGORY POWER PARTNERS GT2 (AS OF 1/1/2022, AVAILABLE 1/1 THROUGH 9/30) |  | LGE_LGE_GT2 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 145
1275 | GREGORY POWER PARTNERS STG (AS OF 1/1/2022, AVAILABLE 1/1 THROUGH 9/30) |  | LGE_LGE_STG | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 100 | 75
1276 | Total Seasonal Mothballed Capacity | [6 empty] | 470 | 365
1277
1278 | Mothballed Resources
1279 | RAY OLINGER STG 1 (AS OF 4/5/22) |  | OLINGR_OLING_1 | COLLIN | GAS-ST | NORTH | 1967 | 78 | 78
1280 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 420 | 420
1281 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420 | 420
1282 | Total Mothballed Capacity | [6 empty] | 918 | 918
1283
1284 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
1285 | Total Retiring Capacity | [6 empty] | 0 | 0
Notes:
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of updated resource registration system information. Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational/planned capacity formulae. These resources are assumed to provide Ancillary Services rather than sustained capacity available to meet system peak loads.
The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation are assumed to be available for the season regardless of their projected Commercial Operations Dates.
Planned projects for which maximum seasonal sustained capacity ratings have been provided are used in lieu of capacities entered into the online Resource Integration and Ongoing Operations - Interconnection Services (RIOO-IS) system.
Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer.
Note on J385: R W MILLER STG 1 (MIL_MILLERG1), -70 MW, on extended outage from 2/28/22 to 2/27/23
Note on J425: Extended outages: GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE (3.6 MW) and 2.4 MW of the 4.8 MW GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP Hydro unit.

## Planning Reserve Margin
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Summer 2022
Release Date: May 16, 2022
Planning Reserve Margin
Summer
| Peak Demand Forecast, MW | 77884
| Rooftop PV Forecast Reduction, MW | -567
| Adjusted Peak Load Forecast, MW | 77317
| Total Resources, MW | 91391.9494
| Emergency Resources Deployed by ERCOT, MW 1 | 2895
| Planning Reserve Margin 2 | 22.8%
Formula: PRM = (Total Resources / (Adjusted Peak Demand - Emergency Resources)) - 1
1 The derivation of the emergency resource amount is described in the Scenario Assumptions Details tab.
2 The Planning Reserve Margin (PRM) is the forecasted capacity reserve that can cover higher-than-expected peak demand and lower-than-expected resource availability when looking at months or longer in the future. This is in contrast to operating reserve measures that focus on actual available capacity during real-time and hour-ahead operating periods. Consequently, the PRM is not an appropriate measure of capacity reserves when operations timeframes are being considered.

## Scenario Assumption Details
| Base & Moderate Risk Scenarios | Extreme Risk Scenarios
Adjusted Peak Load Forecast | Based on average weather conditions from 2006 – 2020 at the time of the summer peak. These baseline forecasts are adjusted downwards to account for peak load reductions from rooftop solar installations that are not already accounted for in the baseline forecasts. The rooftop solar load reductions for the forecasted summer peak load hour (August 10, hour-ending 17 (5 pm) is 567 MW.
Load Adjustments | Based on the 90th percentile of forecasted summer peaks based on weather conditions from 2006 - 2020. These baseline forecasts are adjusted downwards to account for peak load reductions from rooftop solar installations that are not already accounted for in the baseline forecasts. The rooftop solar load reductions for the forecasted summer peak load hour (August 10, hour-ending 17 (5 pm) is 567 MW. | Based on the most extreme weather conditions from 2006 – 2020 at the time of the summer peak for each weather zone (2011). Each weather zone’s summer peak was assumed to occur at the same time. These baseline forecasts are adjusted downwards to account for peak load reductions from rooftop solar installations that are not already accounted for in the baseline forecasts. The rooftop solar load reductions for the forecasted summer peak load hour (August 10, hour-ending 17 (5 pm) is 567 MW.
Typical Planned Outages, Thermal | Based on the historical average of planned outages for July through August weekdays, hours ending 3 pm - 8 pm, for the last three summer seasons (2019 -2021). Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators.
Typical Unplanned Outages, Thermal | Based on historical average of forced outages for June through September weekdays, hours ending 3 pm - 8 pm, for the last three summer seasons (2019 - 2021). Outage history excludes units that are not expected to be in-service for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators.
Unplanned Outage Adjustments, Thermal | The High Unplanned Outage Adjustment is based on the 95th percentile of historical forced outages for June through September weekdays, hours ending 3 pm - 8 pm, for the last five summer seasons (2017 -2021); the adjustment is the 95th percentile value, 8,066 MW, less the typical forced outage amount of 4,081 MW. The outages for the High Unplanned Outage Adjustment include an incremental amount from Private Use Network (PUN) generators; specifically, the 95th percentile amount less the 50th percentile amount. See the Background tab for more information on the treatment of PUN capacity. Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators. | Based on the maximum historical forced outage level for June through September weekdays, hours ending 3 pm - 8 pm, for the last five summer seasons (2017 -2021); the adjustment is 13,676 MW, less the typical forced outage amount of 4,081 MW. The outages for the High Unplanned Outage Adjustment include an incremental amount from Private Use Network (PUN) generators; specifically, the 95th percentile amount less the 50th percentile amount. See the Background tab for more information on the treatment of PUN capacity. Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators.
Wind Output Adjustments | The adjustment is based on the 5th percentile of hourly wind capacity for the daily period hour-ending 15 - 19 (3 pm - 8 pm) for the months of June through September. The capacity values are derived from annual hourly simulated wind output profiles for the period 1980 - 2020. The profiles reflect hourly weather conditions for each of the 41 simulated weather years. A profile is developed for each current operational wind site as well as each planned wind site included in the 2022 Summer SARA. This low wind output level is 2,878 MW. The adjustment is the summer Peak Average Capacity Contribution, 9,367 MW, less 2,878 MW. The methodology report for profile development is available at: https://www.ercot.com/files/docs/2021/12/07/Report_ERCOT_1980-2020_WindSolarDGPVGenProfiles.pdf | The adjustments are based on the minimum hourly wind capacity value for the daily period hour-ending 15 - 19 (3 pm - 8 pm) for the months of June through September. The capacity values are derived from annual hourly simulated wind output profiles for the period 1980 - 2020. The profiles reflect hourly weather conditions for each of the 41 simulated weather years. A profile is developed for each current operational wind site as well as each planned wind site included in the 2022 Summer SARA. This extreme low wind output level is 263 MW. The adjustment is the summer Peak Average Capacity Contribution, 9,367 MW less 263 MW. Note that a scenario with a combined extreme peak load and extreme-low renewables output is not provided because an extreme peak load is associated with high solar output due to minimal cloud cover serving as a driver for both system conditions.
Solar Output Adjustments | The adjustment is based on the 5th percentile of hourly solar capacity for the daily period hour-ending 15 - 19 (3 pm - 8 pm) for the months of June through August. (Note that September is excluded due to very low output beginning in mid-month and the extremely low likelihood of a summer peak load occurring that late in September.) The capacity values are derived from annual hourly simulated wind output profiles for the period 1980 - 2020 inclusive. The profiles reflect hourly weather conditions for each of the 41 simulated weather years. A profile is developed for each current operational wind site as well as each planned wind site included in the 2022 Summer SARA. This low solar output level is 7,025 MW. The adjustment is the summer Peak Average Capacity Contribution, 9,367 MW, less 2,878 MW. The methodology report for profile development is available at: https://www.ercot.com/files/docs/2021/12/07/Report_ERCOT_1980-2020_WindSolarDGPVGenProfiles.pdf | The adjustment is based on the minimum solar capacity value for the daily period hour-ending 15 - 19 (3 pm - 8 pm) for the months of June through August. (Note that September is excluded due to very low output beginning in mid-month and the extremely low likelihood of a summer peak load occurring that late in September.) The capacity values are derived from annual hourly simulated wind output profiles for the period 1980 - 2020 inclusive. The profiles reflect hourly weather conditions for each of the 41 simulated weather years. A profile is developed for each current operational wind site as well as each planned wind site included in the 2022 Summer SARA. This low solar output level is 7,025 MW. The adjustment is the summer Peak Average Capacity Contribution, 9,367 MW, less 2,878 MW. Note that a scenario with a combined extreme peak load and extreme-low renewables output is not provided because an extreme peak load is associated with high solar output due to minimal cloud cover serving as a driver for both system conditions.
Emergency Resources Deployed by ERCOT | An amount is only shown if Capacity Available for Operating Reserves, line item [g], is at or below 2,300 MW. Consists of the sum of expected Load Resources Available for Responsive Reserves for the summer season (1,591 MW), Emergency Response Service (895 MW), Transmission and Distribution Service Provider (TDSP) load management programs (307 MW) and TDSP Voltage Reduction (102 MW). Each of these amounts reflect a 2% gross-up to account for avoided transmission losses. Other resources that may be available include voluntary customer Demand Response (including customer installation of backup generators), switchable generation resources currently serving the Eastern Interconnection, and additional DC tie imports subject to availability.

## Background
Release Date: May 16, 2022
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a probabilistic reliability standard.
For seasonal assessments that look ahead less than a year, specific information may be available (for example, an anticipated common-mode event such as a system-wide heat wave) which can be used to consider the range of resource adequacy outcomes in a more deterministic manner.
The SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. It uses operating reserve thresholds of 2,300 and 1,000 MW, respectively, to indicate the risk that an Energy Emergency Alert Level 1 (EEA1) and Level 3 (EEA3) may be triggered during the time of the forecasted seasonal peak load. These threshold levels are intended to be roughly analogous to the 2,300 and 1,000 MW Physical Responsive Capability (PRC) thresholds for EEA1 and EEA3 with controlled outages ordered by ERCOT, respectively. However, PRC is a real-time capability measure for Resources that can quickly respond to system disturbances. In contrast, the SARA operating reserve reflects additional capability assumed to be available before energy emergency procedures are initiated, such as from Resources qualified to provide non-spinning reserves. Additionally, the amount of operating reserves available may increase relative to what is included in the SARA report due to the market responding to wholesale market price increases and anticipated capacity scarcity conditions. Given these considerations, ERCOT believes that the 2,300 and 1,000 MW reserve capacity thresholds are reasonable indicators for the risk of Energy Emergency Alerts given the uncertainties in predicting system conditions months in advance.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. It serves as a situational awareness tool for ERCOT operational planning purposes, and helps fulfill the "extreme weather" resource adequacy assessment requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). In addition to a base scenario, several other scenarios are developed by varying the value of load forecast and resource availability parameters. The variations in these parameters are based on historic ranges of the parameter values, known changes expected in the near-term, or reasonable assumptions regarding potential future events.
Thermal Outage Accounting
Directly comparing SARA thermal unplanned (previously "forced") outage scenario capacity with outage amounts listed in ERCOT outage reports — such as the Unplanned Resource Outages Report — will yield misleading results. The reason is that the SARA report consists of multiple resource availability line items, and thermal outages for certain resource types are reflected elsewhere in the SARA reports rather than the thermal outage scenario line items. As a result, the SARA thermal outage scenario amounts will always be less than what is typically shown in other outage reports. The main differences include the following:
• Outages for Private Use Network (PUN) generators are incorporated in the line item called “Capacity from Private Use Networks.” This is an aggregate estimate of the amount of capacity available for the ERCOT grid during the highest 20 seasonal hourly demands for the last three years and incorporates average generator outage amounts over those hourly intervals. Additionally, the aggregate estimate reflects PUN owner decisions to supply power to their industrial loads versus export to the grid. PUN outages are thus already reflected in the SARA available resource capacity estimate.
• Extended outages are reported in the SARA Capacities tab in a line item called “Operational Capacity Unavailable due to Extended Outage or Derate.” Extended Outages are those forced outages that are expected to last a minimum of 180 days as reported by the resource owner via submission of a Notice of Suspension of Operations (NSO) form. These outages are thus already reflected in the SARA available resource capacity estimate.
• The capacity of Switchable Generation Resources (SWGRs) that are assumed to serve a neighboring grid for the season is deducted from available resource capacity, so outages associated with these SWGRs are not reflected anywhere in the SARA report.
To more closely align the SARA with other outage reports based on ERCOT Outage Scheduler data, a modification was made to the treatment of outages classified as Unavoidable Extensions, or UEs. UEs are defined as "a Planned or Maintenance Outage that is not completed within the ERCOT-approved timeframe and extended." For past SARA reports, if the original outage was classified as Planned in the Outage Scheduler, then the UE would continue to be classified as Planned. If the original outage was classified as Forced, then the UE would continue to be classified as Forced. In contrast, for other ERCOT outage reports, UE outages are all classified as Forced (Unplanned). SARA reports now treat all UEs as Unplanned. While this category change does not impact the total base outage amount, it does increase the high and extreme unplanned thermal adjustments used in several risk scenarios.