## Slide 1
ERCOT Frequency Control Report
April 2022
ERCOT
Operations Planning
PDCWG | May 18th, 2022

## Slide 2: Summary of April 2022
CPS1: 172.06%
Current CPS1 12-Month Rolling Average: 172.25%
0 BAAL Exceedance(s)
2 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2022 RMS1 Statistics
  Mean: 15.33 mHz
  Min: 12.43 mHz
  Max: 19.20 mHz
Energy Statistics
  Total Energy: 30,866,082 MWh
  Wind Energy: 11,743,813 MWh
  Percent Energy from Wind: 38.05 %
  Solar Energy: 1,820,140 MWh
  Percent Energy from Solar: 5.90%
Minimum System Inertia
  Mean: 148,287 MW*s
  Max: 193,300 MW*s on April 17th
  Min: 118,023 MW*s on April 9th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Apr-22 CPS1 (%): 172.06
Notes: 1. 81.1%@ 4/2/2022 HE 01:00
Expected Generation Deviation
Between 00:00-01:00am the Expected gen dev remained negative. The largest expected gen dev was -1701 MW @ 00:59am with signification contribution from wind generation.
IRR Ramps
Between 00:40-01:00am wind ramped down by ~1000MW
Regulation: Regulation up was exhausted during the last quarter of the hour.
2. 69.8% @ 4/8/2022 HE 20:00
Expected Generation Deviation
Expected gen dev remained negative for the hour. The largest expected gen dev was -2790 MW @ 7:30pm with signification contribution from thermal, solar, and wind resources.
IRR Ramps
Between 7:00pm to 8:00pm wind ramped down by ~2550 MW and solar ramped down by 4300 MW.
Regulation: Regulation up was exhausted during the first half of the hour. Multiple SCED offsets were applied, the largest being a 450 MW SCED manual offset.

## Slide 5: BAAL Exceedances & Violations
There are 0 BAAL exceedance(s) in April

## Slide 6: 15-Minute Average CPS1%
Apr-22 CPS1 (%): 172.06

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 172.25%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 15.33 mHz
  Min: 12.43 mHz
  Max: 19.20 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: 15.8mHz on avg

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 30,866,082 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 11,743,813 MWh

## Slide 23: % Energy from Wind Generation
Notes: 38.05%

## Slide 24: Total Energy From Solar Generation
Notes: 1,820,140 MWh

## Slide 25: % Energy from Solar Generation
Notes: 5.90%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia =118,023 MW*s on 04/09/2022
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 148,287 MW*s
Max: 193,300 MW*s on April 17th
Min: 118,023 MW*s on April 9th

## Slide 28: Questions?
Thank you!