## Slide 1
NPRR 1128 On FFR Procurement
PDCWG
May 18, 2022
Balancing Operations Planning

## Slide 2: Some points for consideration
NPRR 1128, proposes that Fast Frequency Response (FFR) Ancillary Service Offer price may not be less than -$0.01 per MW. This will allow FFR procurement up to the current FFR limit without proration.
When assessing this NPRR a few things that are worth noting are
  FFR triggers at 59.85 Hz, provides response within 15 cycles and for a single event, resource providing FFR must be capable of sustaining response for at least 15 minutes.
  During low inertia conditions, ERCOT’s Critical Inertia will reduce and the amount of RRS needed will also reduce in those hours. Under today’s setup, if 450 MW of FFR is available,
    Critical Inertia during hours with low inertia conditions will reduce by around 8-10 GW.s.
    Average RRS reduction for 2022 would be around 50 MW – 75 MW.
  During tight operating conditions and long drawn events like URI, due to its duration limited nature, FFR if deployed, may not be available after some time. During similar conditions, Load Resources providing RRS using under frequency relays (RRS-UFR) if deployed, are required to stay deployed till recalled.
  When FFR Advancement project is implemented (~early October 2022), several changes will be made to ERCOT systems to make offering and carrying FFR more efficient
    Resources will be able to offer FFR across their full range (charging + discharging);
    Resources will simultaneously be able provide FFR with other ancillary services

## Slide 3: Some points for consideration
From Ancillary Service (AS) qualification perspective to date approximately,
  83 MW of capacity from Energy Storage Resources (ESR) is qualified to provide Fast Responding Regulation Service Up (FRRS-Up) and 101 MW is qualified to provide FRRS-Down
  423 MW of capacity from ESRs is qualified to provide RRS-FFR.
  1,555 MW of capacity (815 MW on discharge and 740 MW on charge) from ESRs is qualified to provide RRS-PFR
From AS provision in Real Time perspective,
  Since implementation in Mar 2020, FFR has not been provided in Real Time
  In 2022, approximately 10% to 15% of RRS was provided by ESRs.

## Slide 4: References
Whitepaper, Inertia: Basic Concepts and Impacts on the ERCOT Grid
PDCWG | Aug 11, 2021 | Winter Event 2021 PDCWG 08112021 v2
FFR Advancement Workshop | Oct 27, 2021 | Link