## Slide 1
Status Update for Odessa Disturbance
IBRTF Meeting
May 23, 2022

## Slide 2: Overview of Recent Action Items
ERCOT recently had follow up conference calls with REs of 6 solar farms that tripped during Odessa Disturbance
  Inverter overvoltage (2)
  Inverter underfrequency (1)
  Momentary cessation and slow recovery (1)
  Feeder breaker overvoltage (1)
  Feeder breaker underfrequency (1)
Call with OEM rep for momentary cessation and delayed reactive injection
Sent out emails to all plants with TMEIC inverters to verify loss of synchronism protection disabled

## Slide 3: Inverter Overvoltage
Two plants reviewing possible k factor adjustments with TMEIC
  Plant 1 has provided update on 5/20 with plan (no timeline yet)
    Contracting with firm to provide PSCAD modeling to replicate event, tune model by adjusting k-factor, ensure tuning complies with PRC-024-2
    Will need to resubmit model to ERCOT
  Plant 2 responded 5/16 but has not provided plan/timeline for adjusting k-factor/tuning
    TMEIC has suggested increasing overvoltage trip to 1.4pu; momentary cessation above 1.25pu
    Will follow up this week for plan/timeline
Both plants still susceptible to trips for similar event

## Slide 4: Inverter Underfrequency
Single plant that had all inverters trip on underfrequency below 58.4 Hz
Plant has submitted a plan to begin work on 6/17/2022 to:
  Inquire with OEM on how to test and calibrate frequency sensing device within the inverters
  Assess inverter limits and propose new frequency no-trip zone to comply with ERCOT NOG
  Update models and submit
  Upon model approval, implement new inverter parameters
Timeline to submit models TBD

## Slide 5: Momentary Cessation/ Slow Recovery
Single plant with legacy inverters which cannot disable momentary cessation without risking equipment damage
  One possible upgrade but will not mitigate root cause seen in Odessa event (loss of synch invokes MC)
Plant has installed new plant level control system
Were not able to find cause of slow/variable response of the two units in old system
Expectation that recovery would be within one second for similar event, i.e, plant level control would not impede inverter ramp rate
RE to provide update to RFI and written verification of plant’s expected response
Will need to resubmit model

## Slide 6: Feeder Breaker Overvoltage
Single plant that had all feeder breakers trip on overvoltage above 1.25pu
Feeder breaker overvoltage protection disabled at site
Concern that inverter overvoltage protection may trip for similar event (1.25 pu at 0.2 seconds)
RE to perform studies to verify if overvoltage protection is sufficient to ride through or needs to be relaxed
Site increased reactive injection after POI voltage returned to nominal
Site also had active power go to zero immediately following fault
Plant personnel to work with OEM to study MW/MVAR response to disturbance

## Slide 7: Feeder Breaker Underfrequency
Single plant that had one feeder breaker trip on underfrequency < 57.5 Hz
Site has not yet addressed erroneous measurement but in progress
  Frequency should be measured with at least 3-5 delay, and filtered for spikes that may occur during fault conditions
Plant personnel working with OEM to set voltage and frequency ride through curves to equipment tolerances instead of directly on “No Trip Zones”
Timeline TBD; waiting for plan submittal
Will need to resubmit models (concern with OEM not providing up to date models that meet requirements)

## Slide 8: TMEIC PLL Loss of Synchronism
All 3 plants that tripped on loss of synch during Odessa Disturbance have disabled function
Emails sent to all remaining plants with TMEIC inverters to confirm function has been disabled
12 of 21 remaining plants have confirmed function disabled
1 to be disabled in June, 1 with date TBD
Will follow up with rest this week (due 5/20)

## Slide 9: Other Remaining Work
Two plants with KACO inverters that were not able to identify root cause of trips during Odessa Disturbance
ERCOT to meet with OEM that took over service of KACO inverters
Follow up with plants to make sure they are capable of capturing data/logs/fault records for future events

## Slide 10: General Comments
Only 4 of 10 plants in NERC report have implemented corrective actions at this time
Remaining 6 are still susceptible to trip/MW reduction on same root cause for similar event
Only 2 out of 10 require no additional follow up for performance requirements (Loss of synchronism)
Multiple plants have new personnel since Odessa Disturbance
Still receiving limited information from RFI responses; asking REs to provide more details in writing after calls
REs can expect continued communications from ERCOT (monthly) until issues resolved and models resubmitted

## Slide 11
Questions?